HUMBOLDT | UKIAH | POINT ARENA-1101 | 43381101 | FUSE | 6523 | 20241230 | 1538 | 20241230 | 1935 | 2672679 | 237 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 474 | 38.9471 | -123.6914 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0148229 | OH | Sus | 0 | NORTH COAST | DEC | Force Out | 0 | No | No | No | 2001477 | 0 | EPSS Ckt | N | 2024
HUMBOLDT | UKIAH | BIG RIVER-1101 | 43081101 | FUSE | 1579 | 20241230 | 2125 | 20241231 | 413 | 2672840 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 6936 | 39.3059 | -123.7923 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0148254 | OH | Sus | 31721307 | NORTH COAST | DEC | Line to Ground | 0 | No | No | No | 2001507 | 0 | EPSS Ckt | N | 2024
HUMBOLDT | UKIAH | HARTLEY-1102 | 43211102 | OCB | 1102/2 | 20241230 | 2345 | 20241231 | 1000 | 2672866 | 615 | Distribution Circuit | 3rd Party | Vehicle | 1754 | 164690 | 39.0767 | -122.9334 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0148259 | OH | Sus | 0 | NORTH COAST | DEC | Three Phase Fault | 0 | No | No | No | 2001513 | 0 | EPSS Ckt | N | 2024 | ABC
HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | FUSE | 695 | 20241231 | 708 | 20241231 | 857 | 2672950 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 5235 | 39.0409 | -122.9433 | No | Partly Cloudy;Below 32 F |  |  | 24-0148286 | OH | Sus | 0 | NORTH COAST | DEC | Line to Ground | 0 | No | No | No | 2001575 | 1 | EPSS Ckt | N | 2024
HUMBOLDT | UKIAH | ELK-1101 | 42981101 | TRANSFORMER | 215209949929 | 20241231 | 709 | 20241231 | 838 | 2672958 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 712 | 39.0256 | -123.6874 | No | Clear;32-90 F | Other | Malfunctioning | 24-0148279 | OH | Sus | 0 | NORTH COAST | DEC | Line to Ground | 0 | No | No | No | 2001546 | 0 | EPSS Ckt | N | 2024
HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | FUSE | 5407 | 20241231 | 812 | 20241231 | 955 | 2672993 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 309 | 39.0945 | -122.9631 | No | Partly Cloudy;32-90 F |  |  | 24-0148281 | OH | Sus | 0 | NORTH COAST | DEC | Line to Line | 0 | No | No | No | 2001548 | 0 | EPSS Ckt | N | 2024
HUMBOLDT | FORTUNA | EEL RIVER-1102 | 192381102 | TRANSFORMER | 113905045357 | 20241231 | 927 | 20250101 | 852 | 2673019 | 1405 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2810 | 40.5577 | -124.1951 | No | Partly Cloudy-Fog;32-90 F | Secondary | Broken | 24-0148288 | OH | Sus | 31721310 | NORTH COAST | DEC | Line to Ground | 0 | No | No | No | 2001579 | 0 | EPSS Ckt | N | 2024
HUMBOLDT | EUREKA | ARCATA-1105 | 192021105 | JUMPER | TSB 4 SS OF CGC 114112658698 | 20241231 | 1329 | 20241231 | 1455 | 2673268 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 774 | 40.9236 | -124.1288 | No | Overcast;32-90 F | Insulator | Broken | 24-0148304 | OH | Sus | 0 | NORTH COAST | DEC | Force Out | 0 | No | No | No | 2001597 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 883676 | 20230101 | 728 | 20230101 | 1544 | 1907906 | 496 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 4960 | 35.7753 | -119.5181 | No | Clear;32-90F |  |  | 23-0004501 | OH | Sus | 45614887 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1795101 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT 1102 | 253911102 | FUSE | 9780 | 20230102 | 323 | 20230102 | 1040 | 1909465 | 437 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 4807 | 35.3336 | -118.7585 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004644 | OH | Sus | 45614891 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1795262 | 1 | EPSS Ckt | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | OCB | 1102/2 | 20230102 | 352 | 20230102 | 1320 | 1909484 | 568 | Distribution Circuit | Animal | Bird found | 130 | 47600 | 35.6142 | -119.8539 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004643 | OH | Sus | 45613130 | CENTRAL VALLEY | JAN | Multi-Fault | 0 | No | Yes | No | 1795261 | 0 | Non-EPSS | N | 2023 | B- C- GRD- PH OC
KERN | KERN | MAGUNDEN-1101 | 252771101 | OCB | 1101/2 | 20230103 | 503 | 20230104 | 240 | 1910931 | 1282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1444 | 280473 | 35.3618 | -118.924 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004952 | OH | Sus | 35419773 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1795560 | 0 | Non-EPSS | N | 2023 | B- GRD- PH OC TIME
KERN | KERN | WESTPARK-1104 | 253701104 | TRANSFORMER | 516956868560 | 20230103 | 621 | 20230103 | 1449 | 1911022 | 508 | Transformer only | 3rd Party | Vehicle | 20 | 10160 | 35.3796 | -119.0218 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0004975 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1795570 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1103 | 254561103 | RECLOSER | 75380 | 20230103 | 1505 | 20230103 | 2125 | 1911756 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 12134 | 35.4027 | -119.2231 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0005233 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1795732 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | FAMOSO-1101 | 252461101 | FUSE | 7048 | 20230104 | 1054 | 20230104 | 1159 | 1913626 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 130 | 35.6281 | -119.1335 | Yes | Clear;32-90F | Fuse | Broken | 23-0005853 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1796239 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7457 | 20230104 | 1151 | 20230104 | 1600 | 1913612 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1494 | 35.4799 | -119.5648 | Yes | Rain-Strong Winds; |  |  | 23-0006145 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1796465 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1105 | 253951105 | TRIP-SAVER | 4059 | 20230104 | 1306 | 20230104 | 1427 | 1913945 | 81 | Distribution Circuit | Vegetation | Tree - branch fell on line | 140 | 11340 | 35.4359 | -118.9498 | Yes | Rain-Strong Winds; | Conductor- Overhead | Normal | 23-0006071 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1796400 | 0 | Non-EPSS | N | 2023 | AC
KERN | KERN | BAKERSFIELD-2109 | 253372109 | OCB | 2109/2 | 20230104 | 1342 | 20230104 | 1448 | 1914276 | 66 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 4049 | 253434 | 35.3885 | -119.0044 | Yes | Rain-Strong Winds; | Conductor- Overhead | Normal | 23-0006007 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | No | No | 1796358 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | BAKERSFIELD-1115 | 253371115 | TRANSFORMER | 516980268633 | 20230104 | 1347 | 20230104 | 2214 | 1914221 | 507 | Transformer only | Vegetation | Tree - fell into line | 9 | 4563 | 35.3818 | -119.0135 | Yes | Strong Winds-Rain;32-90 F | Transformer | Broken- wire on ground | 23-0006196 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1796509 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517174368277 | 20230104 | 1349 | 20230104 | 2140 | 1914250 | 471 | Transformer only | Vegetation | Tree - grew into line | 10 | 4710 | 35.3728 | -118.9482 | Yes | Rain-Strong Winds; | Conductor- Overhead | Broken | 23-0006417 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1796715 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | OTHER | LINE DOWN 11 SPANS S/OF 2001 | 20230104 | 1425 | 20230104 | 1816 | 1914463 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1617 | 35.2058 | -118.9944 | Yes | Rain-Strong Winds; | Conductor- Overhead | Broken- wire on ground | 23-0006124 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | Yes | No | 1796446 | 1 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 16363 | 20230104 | 1525 | 20230105 | 10 | 1914792 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1650 | 35.6452 | -119.2592 | Yes | Rain-Strong Winds; | Transformer (OH) | Leaking | 23-0006519 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1796816 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517499862218 | 20230104 | 1533 | 20230104 | 2118 | 1914632 | 345 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1725 | 35.2069 | -118.8376 | Yes | Rain-Strong Winds; | Cutout- fuse holder | Burned/flashed | 23-0006374 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1796672 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7119 | 20230104 | 1629 | 20230104 | 1825 | 1915253 | 116 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 464 | 35.5719 | -119.5985 | Yes | Rain-Strong Winds; | Conductor- Overhead | Normal | 23-0006316 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1796616 | 1 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL 1106 | 252721106 | FUSE | 172155 | 20230104 | 1759 | 20230104 | 2000 | 1917061 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 807 | 35.4378 | -118.8832 | Yes | Rain-Strong Winds; |  |  | 23-0006573 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1796870 | 1 | EPSS Ckt | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | RECLOSER | 4981 | 20230104 | 1842 | 20230105 | 1034 | 1917714 | 952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 13420 | 35.3535 | -119.2523 | Yes | Rain-Strong Winds; | Insulator | Broken- wire on ground | 23-0006489 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1796787 | 0 | Non-EPSS | N | 2023 | A B C
KERN | KERN | MAGUNDEN 1108 | 252771108 | FUSE | 15342 | 20230104 | 1928 | 20230104 | 2007 | 1917644 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 156 | 35.3691 | -118.8547 | Yes | Rain-Strong Winds; |  |  | 23-0006528 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1796826 | 1 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-1110 | 254071110 | TRANSFORMER | 516928066708 | 20230104 | 1949 | 20230105 | 934 | 1919809 | 825 | Distribution Circuit | Vegetation | Tree - grew into line | 13 | 10725 | 35.3285 | -119.0308 | Yes | Rain-Strong Winds; | Transformer (OH) | Failed/Faulted | 23-0006848 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1797152 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 17531 | 20230104 | 1951 | 20230105 | 156 | 1917858 | 365 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 16068 | 35.2307 | -119.0922 | Yes | Rain-Strong Winds; |  |  | 23-0006931 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797231 | 1 | Non-EPSS | N | 2023
KERN | KERN | TEJON 1102 | 252931102 | TRANSFORMER | 517387049075 | 20230104 | 1957 | 20230104 | 2228 | 1917904 | 151 | Transformer only | Vegetation | Tree - fell into line | 3 | 453 | 34.8453 | -118.8711 | Yes | Rain-Strong Winds; | Service conductor | Broken- wire on ground | 23-0006781 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797082 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-1106 | 254071106 | FUSE | 5977 | 20230104 | 2005 | 20230105 | 130 | 1919090 | 325 | Distribution Circuit | Vegetation | Tree - grew into line | 43 | 13975 | 35.3322 | -119.0484 | Yes | Rain-Strong Winds; | Conductor- Overhead | Arcing | 23-0006715 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797017 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | RECLOSER | 4151 | 20230104 | 2005 | 20230104 | 2056 | 1918049 | 51 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 697 | 35547 | 35.346 | -119.0737 | Yes | Rain-Strong Winds; | Conductor- Overhead | Normal | 23-0006568 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1796866 | 0 | Non-EPSS | N | 2023 | A B C
KERN | KERN | MAGUNDEN-2108 | 252772108 | RECLOSER | 92790 | 20230104 | 2038 | 20230105 | 134 | 1918414 | 296 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 711 | 210456 | 35.3531 | -118.9851 | Yes | Rain-Strong Winds; |  |  | 23-0006612 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1796913 | 0 | Non-EPSS | N | 2023 | AC
KERN | KERN | KERN OIL-1109 | 252721109 | TRANSFORMER | 516914770012 | 20230104 | 2042 | 20230105 | 958 | 1920524 | 796 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 11656 | 35.4193 | -119.0362 | Yes | Clear;32-90 F | Transformer | Broken | 23-0006970 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797273 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2108 | 253372108 | TRANSFORMER | 517062067754 | 20230104 | 2049 | 20230105 | 1517 | 1918480 | 1108 | Transformer only | Vegetation | Tree - fell into line | 12 | 13296 | 35.3582 | -118.9858 | Yes | Clear;32-90 F | Transformer | Broken | 23-0007270 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797536 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 16158 | 20230104 | 2051 | 20230105 | 358 | 1918528 | 424 | Distribution Circuit | Vegetation | Tree - branch fell on line | 91 | 38584 | 35.3439 | -119.0747 | Yes | Rain-Strong Winds; | Conductor- Overhead | Broken- wire on ground | 23-0006783 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1797084 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2108 | 253372108 | TRANSFORMER | T2385 | 20230104 | 2058 | 20230105 | 227 | 1918008 | 329 | Transformer only | Vegetation | Tree - grew into line | 1 | 329 | 35.3714 | -119.0018 | Yes | Rain-Strong Winds; | Secondary | Normal | 23-0006867 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797169 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2108 | 253372108 | TRANSFORMER | 517063067835 | 20230104 | 2106 | 20230105 | 1525 | 1918618 | 1099 | Transformer only | Vegetation | Tree - fell into line | 10 | 10990 | 35.3599 | -118.9858 | Yes | Strong Winds-Rain;32-90 F | Transformer | Broken | 23-0006792 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797093 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1108 | 252771108 | FUSE | 9900 | 20230104 | 2112 | 20230107 | 1945 | 1918695 | 4233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 39152 | 35.3619 | -118.8776 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007579 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1797790 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 9452 | 20230104 | 2132 | 20230105 | 15 | 1918893 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 870 | 34.9843 | -118.8731 | Yes | Rain-Strong Winds; |  |  | 23-0006878 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797178 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2110 | 254072110 | SWITCH | 86002 | 20230104 | 2134 | 20230105 | 2240 | 1918497 | 1471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5232 | 963466 | 35.3252 | -119.0569 | Yes | Rain-Strong Winds; | Pole-Wood | Broken | 23-0006687 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1796988 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | RECLOSER | 4151 | 20230104 | 2144 | 20230105 | 22 | 1919070 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 697 | 110126 | 35.346 | -119.0737 | Yes | Rain-Strong Winds; |  |  | 23-0006840 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797144 | 0 | Non-EPSS | N | 2023 | A B C
KERN | KERN | WESTPARK-1104 | 253701104 | FUSE | 2180 | 20230104 | 2227 | 20230105 | 1230 | 1919421 | 843 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 25290 | 35.3806 | -119.0294 | Yes | Clear;32-90 F |  |  | 23-0007418 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797661 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | RECLOSER | 1267 | 20230104 | 2228 | 20230107 | 1041 | s1797240 | 3613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 20143 | 35.3539 | -118.9586 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006939 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1797240 | 0 | Non-EPSS | N | 2023 | A GRD
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15062 | 20230104 | 2236 | 20230105 | 117 | 1919502 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 8698 | 35.3325 | -118.9142 | Yes | Rain-Strong Winds; |  |  | 23-0006906 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797206 | 1 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 517007064421 | 20230104 | 2307 | 20230105 | 1600 | 1919653 | 1013 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3039 | 35.2657 | -119.0025 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0006949 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797251 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 8396 | 20230104 | 2344 | 20230105 | 1325 | 1919835 | 821 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 59112 | 35.4119 | -119.07 | Yes | Rain-Strong Winds; | Pole-Wood | Broken | 23-0006855 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1797159 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA 1101 | 254211101 | TRANSFORMER | 515888059175 | 20230105 | 11 | 20230105 | 736 | 1920026 | 445 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 445 | 35.1181 | -119.376 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0007046 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1797344 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 14210 | 20230105 | 26 | 20230105 | 140 | 1920062 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 3108 | 35.1424 | -119.4656 | Yes | Rain-Strong Winds; |  |  | 23-0006909 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797209 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 15368 | 20230105 | 48 | 20230105 | 911 | 1920091 | 503 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 33198 | 35.3461 | -119.0345 | Yes | Clear;32-90 F |  |  | 23-0007097 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797390 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 16363 | 20230105 | 108 | 20230105 | 1801 | 1920146 | 1013 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 4052 | 35.6452 | -119.2592 | Yes | Clear;32-90 F |  |  | 23-0007808 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797970 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 9452 | 20230105 | 146 | 20230105 | 1300 | 1920288 | 674 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 3596 | 34.9843 | -118.8731 | Yes | Clear;32-90 F |  |  | 23-0007437 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797676 | 1 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | JUMPER | OJ @ L&B POLE | 20230105 | 324 | 20230105 | 1315 | 1920484 | 591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 9456 | 35.3643 | -118.9387 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0006993 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797295 | 1 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 13296 | 20230105 | 327 | 20230105 | 1412 | 1920501 | 645 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 13337 | 35.42 | -119.2516 | Yes | Clear;32-90 F |  |  | 23-0007537 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797752 | 1 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1101 | 252861101 | FUSE | 7572 | 20230105 | 426 | 20230105 | 1235 | 1920982 | 489 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 17115 | 35.4563 | -119.2622 | Yes | Clear;32-90 F |  |  | 23-0007429 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797670 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | OTHER | BROKEN OH CONDUCTOR 1 N/OF 14844 | 20230105 | 447 | 20230105 | 1104 | 1920682 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 890 | 220291 | 35.4073 | -118.9854 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007004 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1797307 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 8549 | 20230105 | 454 | 20230105 | 1035 | 1920609 | 341 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 3069 | 35.4119 | -119.0495 | Yes | Clear;32-90 F |  |  | 23-0007273 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797539 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1106 | 253701106 | TRANSFORMER | 516958268095 | 20230105 | 627 | 20230105 | 1708 | 1920723 | 641 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 7051 | 35.3668 | -119.0206 | Yes | Clear;32-90 F | Transformer | Burned/flashed | 23-0007096 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797389 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2105 | 255322105 | TRANSFORMER | T8952 | 20230105 | 716 | 20230105 | 2106 | 1920858 | 830 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 14161 | 35.3194 | -119.1123 | Yes | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0007846 | UG | Sus | 35149823 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1798008 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1102 | 252861102 | RECLOSER | 2676 | 20230105 | 806 | 20230105 | 1808 | 1921097 | 602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 39674 | 35.4854 | -119.2803 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007064 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1797361 | 0 | Non-EPSS | N | 2023 | C GRD
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13476 | 20230105 | 947 | 20230105 | 1138 | 1921517 | 111 | Distribution Circuit | Animal | Bird found | 95 | 10545 | 35.3649 | -118.9745 | Yes | Clear;32-90 F | Fuse | Burned Open | 23-0007347 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797607 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 7540 | 20230105 | 1231 | 20230105 | 1552 | 1922188 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2412 | 35.4637 | -119.3144 | Yes | Clear;32-90 F |  |  | 23-0007658 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797856 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | OCB | 2102/2 | 20230105 | 1320 | 20230105 | 1517 | 1922457 | 117 | Distribution Circuit | 3rd Party | Metallic Balloon | 6139 | 447173 | 35.2955 | -119.0219 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007488 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797710 | 0 | Non-EPSS | N | 2023 | AB
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 14676 | 20230105 | 1443 | 20230106 | 1133 | 1924344 | 1250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 10000 | 35.2696 | -119.1186 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0008127 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1798221 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | FUSE | 15689 | 20230105 | 1525 | 20230105 | 1623 | 1922949 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1333 | 35.2446 | -119.0833 | Yes | Clear;32-90 F |  |  | 23-0007709 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797892 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1105 | 253371105 | TRANSFORMER | 516944468724 | 20230105 | 1531 | 20230105 | 2152 | 1922963 | 381 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 7239 | 35.3837 | -119.0259 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0007749 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797924 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL 1104 | 252721104 | OCB | 1104/2 | 20230105 | 1531 | 20230105 | 1807 | 1922967 | 156 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 194 | 30264 | 35.4407 | -119.0204 | Yes | Clear;32-90 F |  |  | 23-0007818 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797982 | 0 | EPSS Ckt | N | 2023 | AC
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517057669236 | 20230105 | 1555 | 20230106 | 430 | 1923066 | 755 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 4530 | 35.3985 | -118.9877 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0008005 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1798137 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2103 | 255322103 | FUSE | 18232 | 20230105 | 1610 | 20230105 | 1925 | 1923142 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 390 | 35.355 | -119.1281 | Yes | Clear;32-90 F |  |  | 23-0007887 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1798048 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1105 | 253701105 | FUSE | 14915 | 20230105 | 1645 | 20230105 | 2244 | 1923208 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 11900 | 35.3492 | -119.0524 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0007720 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1797901 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516999366162 | 20230105 | 1822 | 20230106 | 1021 | 1922342 | 959 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 5754 | 35.3137 | -119.0062 | Yes | Clear;32-90 F | Secondary | Broken | 23-0007838 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1798002 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1104 | 254541104 | TRANSFORMER | 515849571927 | 20230106 | 1153 | 20230106 | 1400 | 1924526 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 127 | 35.4685 | -119.3947 | No | Clear;32-90F | Transformer (OH) | Burned/flashed | 23-0008278 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1798311 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | FUSE | 13514 | 20230106 | 1223 | 20230106 | 1703 | 1925057 | 280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 746 | 35.3137 | -119.0745 | No | Clear;32-90F |  |  | 23-0008388 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1798369 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20230106 | 1406 | 20230106 | 2142 | 1925021 | 456 | Distribution Circuit | 3rd Party | Metallic Balloon | 4557 | 377968 | 35.3885 | -119.0046 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0008391 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1798370 | 0 | Non-EPSS | N | 2023 | ABC TIME OC
KERN | KERN | LAMONT-1107 | 253911107 | RECLOSER | 1988 | 20230106 | 1500 | 20230107 | 934 | 1925280 | 1114 | Distribution Circuit | 3rd Party | Vehicle | 43 | 47902 | 35.3097 | -118.9144 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0008480 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1798415 | 0 | Non-EPSS | N | 2023 | BC
KERN | KERN | GOOSE LAKE-2104 | 254202104 | TRANSFORMER | 515002576771 | 20230106 | 1530 | 20230106 | 1630 | 1925008 | 60 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 120 | 35.5982 | -119.6816 | No | Clear;32-90 F |  |  | 23-0008474 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1798408 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | JUMPER | BURNED OJ | 20230106 | 2157 | 20230106 | 2357 | 1925779 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2877 | 345240 | 35.3673 | -118.9514 | No | Clear;32-90F | Jumper | Burned Open | 23-0008391 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1798528 | 1 | Non-EPSS | N | 2023
KERN | KERN | COPUS-1102 | 253871102 | RECLOSER | 2399 | 20230107 | 1111 | 20230107 | 1345 | 1926460 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 4774 | 35.094 | -119.3131 | Yes | Clear;32-90F |  |  | 23-0008743 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Multi-Fault | 0 | No | No | No | 1798624 | 0 | Non-EPSS | N | 2023 | A B C
KERN | KERN | FELLOWS 2104 | 254242104 | RECLOSER | 42100 | 20230108 | 513 | 20230109 | 933 | 1933384 | 1700 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 18754 | 35.138 | -119.4832 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010089 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1799935 | 0 | EPSS Ckt | N | 2023 | UNK
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 15443 | 20230108 | 513 | 20230109 | 505 | s1823120 | 1432 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2431 | 86554 | 35.1338 | -119.4656 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009822 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1823120 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1108 | 252081108 | OCB | 1108/2 | 20230108 | 513 | 20230109 | 1120 | 1932221 | 1807 | Distribution Circuit | Equipment Failure/Involved | Overhead | 476 | 177210 | 35.1362 | -119.4822 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009822 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1799662 | 0 | Non-EPSS | N | 2023 | PH OC- A B- C
KERN | KERN | TAFT-1104 | 252081104 | TRANSFORMER | 515613459788 | 20230108 | 738 | 20230108 | 2250 | 1932548 | 912 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 20064 | 35.1338 | -119.4682 | Yes | Clear;32-90F | Transformer (OH) | Leaking | 23-0010251 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1800100 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 14210 | 20230108 | 758 | 20230108 | 1205 | 1933253 | 247 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 10374 | 35.1424 | -119.4656 | Yes | Clear;32-90F |  |  | 23-0010112 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1799960 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1101 | 253371101 | TRANSFORMER | 517014268998 | 20230108 | 928 | 20230108 | 1026 | 1932912 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 580 | 35.3916 | -119.002 | Yes | Clear;32-90F | Secondary | Broken | 23-0009949 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1799799 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | RECLOSER | 4222 | 20230108 | 1745 | 20230109 | 1231 | 1934290 | 1126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 2819 | 35.3258 | -118.804 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0010394 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1800241 | 0 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 11993 | 20230108 | 2330 | 20230109 | 105 | 1935019 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 190 | 35.3178 | -119.0491 | Yes | Clear;32-90F |  |  | 23-0010679 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1800536 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1105 | 253551105 | TRANSFORMER | 515742081542 | 20230109 | 1144 | 20230109 | 1200 | 1937088 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 16 | 35.732 | -119.4368 | Yes | Clear;32-90F | Jumper | Broken | 23-0011150 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1800955 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516960969639 | 20230109 | 1242 | 20230109 | 1317 | 1937749 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 560 | 35.4091 | -119.0203 | Yes | Clear;32-90F | Connector or Splice (OH) | Deteriorated | 23-0011234 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1801025 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 9681 | 20230109 | 1721 | 20230109 | 1814 | 1939035 | 53 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 18 | 954 | 35.2378 | -118.9626 | Yes | Strong Winds | Conductor- Overhead | Normal | 23-0011520 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1801278 | 1 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1110 | 253951110 | FUSE | 14181 | 20230109 | 1824 | 20230109 | 1915 | 1939286 | 51 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 2550 | 35.387 | -118.9495 | Yes | Strong Winds | Conductor- Overhead | Normal | 23-0011564 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1801326 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | RECLOSER | 4088 | 20230109 | 1837 | 20230109 | 2028 | 1939133 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1220 | 67423 | 35.256 | -118.9136 | Yes | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0011536 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1801295 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | CUYAMA 1103 | 253141103 | RECLOSER | 282557 | 20230109 | 1851 | 20230110 | 315 | 1939099 | 504 | Distribution Circuit | Vegetation | Tree - branch fell on line | 231 | 15566 | 34.9474 | -119.6881 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0011545 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1801306 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | OLD RIVER-1101 | 252821101 | FUSE | 15706 | 20230109 | 1916 | 20230112 | 1234 | 1939658 | 3918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 7836 | 35.1801 | -119.1727 | Yes | Strong Winds; | Pole-Wood | Burned/flashed | 23-0011576 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1801391 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | JUMPER | OJ MILLUX RD 1P E/ OF I5 | 20230109 | 1918 | 20230109 | 2325 | 1939513 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 16692 | 35.1801 | -119.1604 | Yes | Strong Winds; | Jumper | Burned Open | 23-0011576 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1801339 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1103 | 252861103 | FUSE | 14012 | 20230109 | 2120 | 20230110 | 306 | 1939715 | 105 | Distribution Circuit | 3rd Party | Vehicle | 7 | 1295 | 35.4198 | -119.1988 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011675 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1801439 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | TRIP-SAVER | 2455 | 20230110 | 251 | 20230110 | 530 | 1941060 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 270 | 42930 | 34.8582 | -118.8838 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0011912 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1801683 | 0 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | CARRIZO PLAINS 1101 | 253461101 | FUSE | 16488 | 20230110 | 417 | 20230110 | 734 | 1941696 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 11300 | 35.3663 | -120.0409 | Yes | Clear;32-90F |  |  | 23-0011931 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1801704 | 1 | EPSS Ckt | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | OCB | 2103/2 | 20230110 | 432 | 20230111 | 211 | 1942241 | 1299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 16755 | 35.3831 | -119.6964 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011882 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1801649 | 0 | Non-EPSS | N | 2023 | A- B- C- 50RLY
KERN | KERN | LERDO-1113 | 253491113 | FUSE | 15148 | 20230110 | 501 | 20230110 | 722 | 1942570 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1269 | 35.5514 | -119.1691 | Yes | Clear;32-90F |  |  | 23-0011948 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1801726 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1107 | 253371107 | OCB | 1107/2 | 20230110 | 730 | 20230110 | 1207 | 1943329 | 277 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 649 | 33311 | 35.3886 | -119.0044 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011998 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1801774 | 0 | Non-EPSS | N | 2023 | A- GRD
KERN | KERN | TEJON 1103 | 252931103 | FUSE | 8097 | 20230110 | 818 | 20230111 | 1100 | 1943843 | 1602 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3204 | 35.0437 | -118.7745 | Yes | Clear;32-90F |  |  | 23-0012169 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1801936 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13898 | 20230110 | 843 | 20230110 | 1725 | 1943878 | 522 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1566 | 35.6882 | -119.7631 | Yes | Strong Winds-Rain-Overcast;32-90 F |  |  | 23-0012876 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1802450 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1103 | 254561103 | TRANSFORMER | 516298269079 | 20230110 | 919 | 20230110 | 1142 | 1944118 | 143 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 143 | 35.3918 | -119.2429 | Yes | Clear;32-90F |  |  | 23-0012317 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1802064 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | FUSE | 7333 | 20230110 | 1043 | 20230110 | 1929 | 1944580 | 526 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 1052 | 35.6313 | -119.0988 | Yes | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0012546 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1802235 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | JUMPER | OPEN JUMPER CENTER PHASE | 20230110 | 1112 | 20230110 | 1506 | 1945158 | 234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 232 | 54288 | 35.3214 | -118.9856 | Yes | Overcast;32-90 F | Jumper | Broken | 23-0012432 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1802150 | 1 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 16363 | 20230110 | 1246 | 20230110 | 1445 | 1945105 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 476 | 35.6452 | -119.2592 | Yes | Strong Winds-Rain-Overcast;32-90 F |  |  | 23-0012649 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1802308 | 0 | Non-EPSS | N | 2023
KERN | KERN | NORCO-1102 | 254691102 | FUSE | 49723 | 20230110 | 1313 | 20230111 | 450 | 1945191 | 937 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1065 | 35.3105 | -119.3178 | Yes | Clear;32-90 F | Secondary | Broken | 23-0012646 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802306 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 9791 | 20230110 | 1330 | 20230110 | 1722 | 1945273 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1392 | 35.3257 | -118.7986 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0012500 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1802199 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEMBLOR 1104 | 252551104 | OCB | 1104/2 | 20230110 | 1340 | 20230110 | 1354 | 1945274 | 14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 1498 | 35.3831 | -119.6964 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0012499 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1802198 | 0 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | BAKERSFIELD-1105 | 253371105 | FUSE | 528495 | 20230110 | 1405 | 20230111 | 338 | 1945441 | 813 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 29 | 23577 | 35.3845 | -119.0242 | Yes | Overcast;32-90 F | Pole-Wood | Burned/flashed | 23-0012566 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1802247 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517293764213 | 20230110 | 1505 | 20230110 | 1905 | 1945697 | 240 | Transformer only | Vegetation | Tree - grew into line | 13 | 3120 | 35.2611 | -118.9075 | Yes | Strong Winds-Rain-Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012694 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1802333 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516353161886 | 20230110 | 1554 | 20230110 | 1611 | 1945376 | 17 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 17 | 35.1944 | -119.2215 | Yes | Strong Winds-Rain-Overcast;32-90 F |  |  | 23-0012772 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1802373 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1105 | 252771105 | FUSE | 15258 | 20230110 | 2159 | 20230111 | 5 | 1946683 | 126 | Distribution Circuit | 3rd Party | Vehicle | 64 | 8064 | 35.3687 | -118.9296 | Yes | Strong Winds-Rain-Overcast;32-90 F | Conductor- Overhead | Normal | 23-0013232 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1802786 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1105 | 252771105 | FUSE | 53885 | 20230111 | 853 | 20230111 | 1148 | 1947190 | 175 | Distribution Circuit | 3rd Party | Vehicle | 29 | 5075 | 35.3678 | -118.9297 | No | Strong Winds-Rain-Overcast;32-90 F | Pole-Wood | Broken | 23-0013398 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1802933 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | RECLOSER | 2686 | 20230111 | 1340 | 20230111 | 1559 | 1948152 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 1398 | 35.6313 | -119.1355 | No | Strong Winds-Rain-Overcast;32-90 F | Pole-Wood | Deteriorated | 23-0013651 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1803135 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7119 | 20230111 | 1555 | 20230111 | 2106 | 1948555 | 311 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1245 | 35.5719 | -119.5985 | No | Strong Winds-Rain-Overcast;32-90 F |  |  | 23-0014048 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1803397 | 1 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1110 | 252901110 | FUSE | 7517 | 20230111 | 1835 | 20230111 | 2217 | 1948900 | 222 | Distribution Circuit | 3rd Party | Other | 6 | 1332 | 35.6562 | -119.4025 | No | Strong Winds-Rain-Overcast;32-90 F | Conductor- Overhead | Normal | 23-0013933 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1803288 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | INTERRUPTER | 12002 | 20230112 | 217 | 20230112 | 1704 | 1949244 | 887 | Distribution Circuit | Equipment Failure/Involved | Underground | 472 | 97589 | 35.3396 | -119.096 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0014231 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1803582 | 1 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 15211 | 20230112 | 803 | 20230112 | 1024 | 1949532 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1693 | 34.9859 | -118.9087 | No | Clear;32-90F |  |  | 23-0014361 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1803673 | 1 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | SWITCH | 1041 | 20230112 | 1656 | 20230112 | 2109 | 1950679 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1771 | 35.4417 | -119.6399 | No | Clear;32-90F | Pole-Wood | Broken | 23-0014719 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1803866 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515582271141 | 20230112 | 1759 | 20230112 | 2101 | 1950788 | 182 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 182 | 35.4458 | -119.4842 | No | Clear;32-90F |  |  | 23-0014813 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1803928 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 13502 | 20230112 | 1904 | 20230112 | 2005 | 1950869 | 61 | Distribution Circuit | 3rd Party | Other | 45 | 2745 | 35.3544 | -118.9586 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0014809 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1803924 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2103 | 254582103 | OCB | 2103/2/NORM | 20230112 | 2311 | 20230113 | 51 | 1951145 | 100 | Distribution Circuit | 3rd Party | Vehicle | 1041 | 97725 | 35.4397 | -119.1312 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0014954 | OH | Sus | 35421343 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1804064 | 0 | Non-EPSS | N | 2023 | A- B- 51RLY
KERN | KERN | WHEELER RIDGE 1101 | 253481101 | TRANSFORMER | 517025355681 | 20230113 | 709 | 20230113 | 1133 | 1951320 | 264 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 264 | 35.0262 | -118.9945 | No | Clear;32-90F | Jumper | Broken | 23-0015265 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1804246 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 13502 | 20230113 | 711 | 20230113 | 835 | 1951321 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 3780 | 35.3544 | -118.9586 | No | Clear;32-90F |  |  | 23-0015096 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1804175 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1103 | 252081103 | TRANSFORMER | 515644260540 | 20230113 | 1154 | 20230113 | 1718 | 1952189 | 324 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 1296 | 35.1547 | -119.4582 | No | Clear;32-90 F |  |  | 23-0015457 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1804331 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1103 | 252081103 | TRANSFORMER | 515644260554 | 20230113 | 1154 | 20230113 | 1717 | 1952188 | 323 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 1292 | 35.155 | -119.4582 | No | Clear;32-90 F |  |  | 23-0015466 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1804337 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 15351 | 20230113 | 1603 | 20230113 | 1639 | 1952226 | 36 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 864 | 35.4193 | -119.0496 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0015459 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1804332 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1103 | 252081103 | FUSE | 96379 | 20230114 | 706 | 20230114 | 850 | 1952903 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 784 | 35.1547 | -119.4582 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0015856 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1804697 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1103 | 252721103 | FUSE | 8068 | 20230114 | 1307 | 20230114 | 1713 | 1954381 | 246 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 7380 | 35.4141 | -119.0507 | Yes | Clear;32-90F | Conductor- Underground | Deteriorated | 23-0016256 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1805017 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 4525 | 20230115 | 727 | 20230115 | 941 | 1955553 | 134 | Distribution Circuit | Animal | Bird found | 22 | 2948 | 34.9716 | -118.9397 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016544 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1805296 | 0 | EPSS Ckt | N | 2023 | BC
KERN | KERN | CHARCA-1102 | 254501102 | OCB | 1102/2 | 20230115 | 1156 | 20230115 | 1626 | 1955891 | 270 | Distribution Circuit | 3rd Party | Vehicle | 286 | 29920 | 35.6081 | -119.3255 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016656 | OH | Sus | 45642526 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1805393 | 0 | Non-EPSS | N | 2023 | AC G
KERN | KERN | TAFT-1104 | 252081104 | TRANSFORMER | 515607759905 | 20230115 | 1221 | 20230115 | 1343 | 1955925 | 82 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 738 | 35.1372 | -119.4702 | No | Clear;32-90F |  |  | 23-0016692 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1805417 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 16488 | 20230116 | 117 | 20230116 | 427 | 1956501 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 10899 | 35.3663 | -120.0409 | Yes | Clear;32-90F |  |  | 23-0016882 | OH | Sus | 45642596 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1805583 | 1 | EPSS Ckt | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 9452 | 20230116 | 153 | 20230116 | 835 | 1956531 | 402 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3216 | 34.9843 | -118.8731 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0016908 | OH | Sus | 45642277 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1805612 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-1104 | 252551104 | FUSE | 17872 | 20230116 | 521 | 20230116 | 939 | 1956863 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1806 | 35.3975 | -119.7532 | Yes | Strong Winds; |  |  | 23-0017090 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1805783 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MCKITTRICK 1101 | 252781101 | RECLOSER | 1639 | 20230116 | 704 | 20230116 | 1550 | 1957140 | 526 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 20032 | 35.3213 | -119.6741 | Yes | Strong Winds | Pole-Wood | Broken | 23-0016979 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1805684 | 0 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | TEMBLOR-1104 | 252551104 | FUSE | 18215 | 20230116 | 1328 | 20230116 | 1748 | 1958176 | 260 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 260 | 35.3506 | -119.6542 | Yes | Strong Winds | Pole-Wood | Normal | 23-0017221 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1805897 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | RECLOSER | 1913 | 20230116 | 1402 | 20230117 | 228 | 1958142 | 746 | Distribution Circuit | 3rd Party | Vehicle | 628 | 215412 | 35.3126 | -118.9145 | Yes | Strong Winds; | Pole-Wood | Broken | 23-0017236 | OH | Sus | 35421464 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1805911 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRANSFORMER | 513759569282 | 20230116 | 1403 | 20230116 | 1855 | 1958242 | 292 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 292 | 35.3857 | -120.0945 | Yes | Strong Winds; | Pole-Wood | Broken | 23-0017235 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1805910 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | RECLOSER | 2862 | 20230116 | 2007 | 20230117 | 257 | 1958818 | 410 | Distribution Circuit | 3rd Party | Vehicle | 227 | 19542 | 35.2817 | -118.8798 | Yes | Strong Winds; | Pole-Wood | Broken- wire on ground | 23-0017388 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1806059 | 0 | EPSS Ckt | N | 2023 | C PHASE & GRD
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 99477 | 20230116 | 2145 | 20230116 | 2305 | 1958935 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 320 | 35.4623 | -119.2786 | Yes | Clear;32-90F |  |  | 23-0017438 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1806108 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2103 | 254582103 | FUSE | 461433 | 20230117 | 853 | 20230117 | 1455 | 1959264 | 362 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 362 | 35.4633 | -119.1449 | No | Clear;32-90F | Crossarm- Wood | Burned/flashed | 23-0017585 | OH | Sus | 31634688 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1806186 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | SWITCH | 10176 | 20230117 | 1110 | 20230117 | 1118 | 1959524 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 25 | 200 | 35.3359 | -118.9091 | No | Clear;32-90F | Other | Normal | 23-0017236 | OH | Sus | 35421464 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1806195 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1103 | 252461103 | JUMPER | 52637 | 20230117 | 1402 | 20230117 | 2123 | 1959773 | 441 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 441 | 35.5915 | -119.1158 | No | Clear;32-90F | Jumper | Burned Open | 23-0017853 | OH | Sus | 45643786 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1806275 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7509 | 20230117 | 1825 | 20230119 | 1726 | 1960257 | 2821 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 21726 | 35.7175 | -119.4906 | No | Clear;32-90 F |  |  | 23-0017898 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1806308 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1109 | 254071109 | TRANSFORMER | T2445 | 20230118 | 1613 | 20230119 | 1230 | 1961230 | 1217 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 18255 | 35.3054 | -119.0583 | No | Clear;32-90F | Transformer (UG) | Broken | 23-0018561 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1806637 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1109 | 254071109 | FUSE | 8699 | 20230119 | 727 | 20230119 | 759 | 1961834 | 32 | Distribution Circuit | Equipment Failure/Involved | Underground | 178 | 2713 | 35.3067 | -119.0566 | No | Clear;32-90F | Transformer (UG) | Broken | 23-0018565 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1806728 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 436323 | 20230119 | 840 | 20230119 | 1255 | 1961884 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 510 | 35.3466 | -118.9364 | No | Clear;32-90F | Pole-Wood | Broken | 23-0018713 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1806742 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517230266019 | 20230119 | 1118 | 20230119 | 1226 | 1962066 | 68 | Transformer only | Environmental/External | Flood/Erosion | 3 | 204 | 35.3106 | -118.9294 | No | Clear;32-90 F | Transformer | Normal | 23-0018872 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1806791 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1109 | 254071109 | SWITCH | 6618 | 20230119 | 1208 | 20230119 | 1233 | 1962124 | 25 | Distribution Circuit | Company Initiated | Return Circuit Normal | 178 | 1938 | 35.3041 | -119.058 | No | Clear;32-90F | Transformer (UG) | Normal | 23-0018565 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1806792 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | RECLOSER | 2469 | 20230119 | 1415 | 20230119 | 1636 | 1962253 | 141 | Distribution Circuit | 3rd Party | Vehicle | 109 | 15369 | 35.3122 | -118.8965 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0018958 | OH | Sus | 31634860 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1806810 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | T7004 | 20230120 | 1058 | 20230120 | 1724 | 1963196 | 386 | Transformer only | Equipment Failure/Involved | Underground | 13 | 5018 | 35.3579 | -118.9488 | No | Clear;32-90F | Secondary | Broken | 23-0019448 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807057 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 16247 | 20230120 | 1454 | 20230120 | 1917 | 1963439 | 263 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 5260 | 35.3986 | -119.4831 | No | Clear;32-90F |  |  | 23-0019622 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1807096 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA 2101 | 253142101 | FUSE | 17608 | 20230121 | 712 | 20230121 | 954 | 1963778 | 162 | Distribution Circuit | Animal | Bird found | 10 | 1620 | 34.9053 | -119.5547 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019706 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1807185 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16169 | 20230121 | 844 | 20230121 | 1143 | 1963856 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 537 | 35.0946 | -119.1072 | No | Clear;32-90F |  |  | 23-0019717 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1807194 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | OCB | 2103/2 | 20230121 | 1925 | 20230122 | 1434 | 1964333 | 1149 | Distribution Circuit | 3rd Party | Vehicle | 1608 | 197400 | 35.3871 | -119.1643 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0019783 | OH | Sus | 35422600 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1807242 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 9868 | 20230122 | 31 | 20230122 | 2145 | 1964412 | 1274 | Distribution Circuit | 3rd Party | Vehicle | 7 | 3203 | 35.2377 | -118.995 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0019813 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1807273 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | RECLOSER | 4409 | 20230122 | 2257 | 20230122 | 2329 | 1965133 | 32 | Distribution Circuit | 3rd Party | Vehicle | 115 | 3680 | 35.2807 | -118.8786 | No | Clear;32-90F | Pole-Wood | Broken | 23-0019971 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1807404 | 0 | EPSS Ckt | N | 2023 | 99
KERN | KERN | FAMOSO-1102 | 252461102 | TRANSFORMER | 516527677440 | 20230123 | 840 | 20230123 | 1000 | 1965474 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 80 | 35.6217 | -119.1689 | No | Clear;32-90F | Fuse | Normal | 23-0020115 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807550 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517117267714 | 20230123 | 900 | 20230123 | 1407 | 1965518 | 307 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 307 | 35.3568 | -118.9677 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0020190 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807577 | 0 | Non-EPSS | N | 2023
KERN | KERN | MCKITTRICK-1101 | 252781101 | FUSE | 3005 | 20230123 | 1252 | 20230123 | 1609 | 1966200 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 591 | 35.2836 | -119.7227 | No | Clear;32-90 F | Insulator | Normal | 23-0020437 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1807642 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WESTPARK-1103 | 253701103 | OCB | 1103/2 | 20230123 | 1817 | 20230124 | 24 | s1807651 | 367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1385 | 163566 | 35.374 | -119.0404 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0020453 | OH | Sus | 31635055 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1807651 | 0 | Non-EPSS | N | 2023 | BC T
KERN | KERN | RENFRO-2105 | 254572105 | FUSE | 16756 | 20230124 | 231 | 20230124 | 342 | 1966405 | 71 | Distribution Circuit | Equipment Failure/Involved | Underground | 116 | 2428 | 35.398 | -119.1326 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0020248 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1807699 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1108 | 253391108 | TRANSFORMER | T248027 | 20230124 | 745 | 20230124 | 850 | 1966490 | 65 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 130 | 35.3805 | -119.0624 | No | Clear;32-90F |  |  | 23-0020593 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1807773 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | FUSE | 18477 | 20230124 | 852 | 20230124 | 1136 | 1966652 | 164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1640 | 35.0616 | -119.3491 | No | Clear;32-90F | Service conductor | Broken- wire on ground | 23-0020710 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807853 | 1 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 17742 | 20230124 | 1053 | 20230124 | 1204 | 1966912 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 4260 | 35.3323 | -118.9899 | No | Clear;32-90F |  |  | 23-0020735 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1807867 | 0 | Non-EPSS | N | 2023
KERN | KERN | FELLOWS-2104 | 254242104 | FUSE | 372119 | 20230124 | 1222 | 20230125 | 137 | 1967139 | 795 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1590 | 35.2282 | -119.6721 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0020865 | OH | Sus | 45649002 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1807906 | 1 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517044066817 | 20230124 | 1322 | 20230124 | 1510 | 1967070 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 432 | 35.3322 | -118.9914 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0020900 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807920 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1112 | 252901112 | TRANSFORMER | 515650778635 | 20230124 | 1407 | 20230124 | 2205 | 1967122 | 478 | Transformer only | Animal | Other | 1 | 478 | 35.6521 | -119.4641 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0020910 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807921 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARNERAS 1103 | 252321103 | TRANSFORMER | 514474574101 | 20230124 | 1445 | 20230125 | 440 | 1967172 | 835 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 835 | 35.5222 | -119.8576 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0020956 | OH | Sus | 35423063 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807940 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MCKITTRICK-1101 | 252781101 | OCB | 1101/2 | 20230124 | 1445 | 20230124 | 1615 | 1967186 | 90 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 248 | 21366 | 35.297 | -119.6266 | No | Clear;32-90 F |  |  | 23-0020912 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807923 | 0 | EPSS Ckt | N | 2023 | A GRD INST
KERN | KERN | ARVIN 1101 | 253801101 | FUSE | 15908 | 20230124 | 1516 | 20230124 | 2325 | 1967291 | 489 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 978 | 35.1584 | -118.8247 | No | Clear;32-90F | Pole-Wood | Broken | 23-0020927 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1807928 | 0 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | RECLOSER | 3290 | 20230125 | 531 | 20230125 | 1022 | 1967527 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 9312 | 35.5999 | -119.545 | No | Clear;32-90F | Booster | Failed/Faulted | 23-0021008 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1807983 | 0 | Non-EPSS | N | 2023 | BC
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 8925 | 20230125 | 646 | 20230125 | 829 | 1967535 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1957 | 35.3448 | -119.0484 | No | Clear;32-90F |  |  | 23-0021074 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1808021 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1110 | 253951110 | RECLOSER | 77274 | 20230125 | 1307 | 20230125 | 1609 | 1968051 | 182 | Distribution Circuit | 3rd Party | Vandalism | 57 | 8257 | 35.3937 | -118.9497 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0021298 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1808157 | 0 | Non-EPSS | N | 2023 | AG
KERN | KERN | SEMITROPIC-1112 | 252901112 | TRANSFORMER | 515650778635 | 20230125 | 1324 | 20230125 | 1642 | 1968068 | 198 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 198 | 35.6521 | -119.4641 | No | Clear;32-90F |  |  | 23-0021413 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1808181 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 16471 | 20230125 | 1350 | 20230126 | 210 | 1968103 | 740 | Distribution Circuit | 3rd Party | Vehicle | 259 | 35570 | 35.3179 | -119.1402 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0021387 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | No | No | 1808173 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2112 | 254072112 | TRANSFORMER | T9427 | 20230125 | 1500 | 20230125 | 2115 | 1967959 | 374 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 9056 | 35.2976 | -119.0645 | No | Clear;32-90F | Bus | Arcing | 23-0021397 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1808176 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 14971 | 20230125 | 1553 | 20230125 | 1915 | 1968215 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 808 | 35.2235 | -118.8831 | No | Clear;32-90F |  |  | 23-0021447 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1808195 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515721271795 | 20230126 | 804 | 20230126 | 934 | 1968542 | 90 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 270 | 35.4646 | -119.4381 | No | Clear;32-90F | Fuse | Broken | 23-0021641 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1808363 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 710019 | 20230126 | 1010 | 20230126 | 1523 | 1968804 | 313 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1252 | 35.6956 | -119.4907 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0021771 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1808421 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | TRANSFORMER | 515625879437 | 20230126 | 1237 | 20230126 | 1319 | 1968927 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 42 | 35.674 | -119.4734 | No | Clear;32-90 F | Fuse | Broken | 23-0021849 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1808450 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | 516982059055 | 20230127 | 1437 | 20230127 | 1452 | 1969966 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 15 | 35.1191 | -119.01 | No | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0022470 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1808707 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516865062058 | 20230127 | 1532 | 20230127 | 1632 | 1970061 | 60 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 60 | 35.2007 | -119.0499 | No | Clear;32-90 F |  |  | 23-0022535 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1808719 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1105 | 253701105 | SWITCH | 6091 | 20230127 | 1809 | 20230127 | 1818 | 1970167 | 9 | Distribution Circuit | Company Initiated | Improper Construction | 76 | 684 | 35.347 | -119.0586 | No | Clear;32-90F | Conductor- Underground | Normal | 23-0011210 | UG | Sus | 35382737 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1808729 | 0 | Non-EPSS | N | 2023
KERN | KERN | SISQUOC-1102 | 182811102 | FUSE | 15497 | 20230128 | 1022 | 20230128 | 1620 | 1970383 | 358 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1074 | 35.1908 | -119.9528 | No | Clear;32-90F |  |  | 23-0022659 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1808848 | 0 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7343 | 20230128 | 1053 | 20230128 | 1311 | 1970413 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 690 | 35.5865 | -119.5086 | No | Clear;32-90F |  |  | 23-0022637 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1808830 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | SWITCH | 2548 | 20230128 | 1213 | 20230128 | 1249 | 1970494 | 36 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2714 | 97704 | 35.3561 | -119.0028 | No | Clear;32-90 F |  |  | 23-0022632 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1808824 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2103 | 254582103 | OCB | 2103/2/NORM | 20230128 | 1618 | 20230129 | 22 | 1970629 | 484 | Distribution Circuit | 3rd Party | Vehicle | 1041 | 44210 | 35.4397 | -119.1312 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0022655 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1808845 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516865062058 | 20230128 | 1647 | 20230128 | 2202 | 1970640 | 315 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 315 | 35.2007 | -119.0499 | No | Clear;32-90 F |  |  | 23-0022693 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1808887 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | JUMPER | OJ 1 POLE N/OF 43369 TWD THE WEST | 20230129 | 2328 | 20230130 | 1150 | 1971288 | 742 | Distribution Circuit | 3rd Party | Vehicle | 1 | 742 | 35.2979 | -118.9144 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0022789 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1808995 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | JUMPER | OJ 4 POLE S/E OF CGC #516852569901 | 20230130 | 1920 | 20230131 | 121 | 1972265 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 12996 | 35.4149 | -119.056 | No | Clear;32-90F | Pole-Wood | Broken | 23-0023188 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1809264 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13447 | 20230131 | 1125 | 20230131 | 1215 | 1972822 | 50 | Distribution Circuit | Animal | Bird found | 131 | 6550 | 35.365 | -118.9703 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0023448 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1809479 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-2102 | 254762102 | FUSE | 11450 | 20230131 | 1249 | 20230131 | 1534 | 1972923 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 5671 | 35.3589 | -119.0613 | No | Clear;32-90F |  |  | 23-0023503 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1809498 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7257 | 20230131 | 1631 | 20230131 | 1920 | 1973146 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2535 | 35.5998 | -119.5268 | No | Clear;32-90F |  |  | 23-0023676 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1809537 | 0 | Non-EPSS | N | 2023
KERN | KERN | ELK HILLS-1104 | 252441104 | RECLOSER | 3522 | 20230131 | 1715 | 20230131 | 2145 | 1973170 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 798 | 35.2297 | -119.3762 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0023644 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1809527 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | STOCKDALE-2109 | 254072109 | TRANSFORMER | T641470 | 20230201 | 1052 | 20230201 | 2025 | 1973556 | 573 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1146 | 35.2945 | -119.0387 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0023962 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1809786 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1105 | 252771105 | TRANSFORMER | 517189968451 | 20230201 | 1311 | 20230201 | 1507 | 1974185 | 116 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 464 | 35.3777 | -118.943 | No | Clear;32-90 F |  |  | 23-0024066 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1809809 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1109 | 253951109 | TRANSFORMER | 517208868874 | 20230201 | 1447 | 20230202 | 537 | 1974159 | 890 | Transformer only | Vegetation | Tree - grew into line | 2 | 1780 | 35.389 | -118.937 | No | Clear;32-90 F | Transformer | Normal | 23-0024040 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1809803 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | TRANSFORMER | 516380775057 | 20230201 | 1631 | 20230201 | 1648 | 1974191 | 17 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 34 | 35.5563 | -119.2172 | No | Clear;32-90F |  |  | 23-0024110 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1809816 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1111 | 254071111 | TRANSFORMER | 516919666797 | 20230201 | 1857 | 20230202 | 133 | 1974415 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2368 | 35.331 | -119.0336 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0024198 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1809861 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | OCB | 1101/2 | 20230201 | 1909 | 20230201 | 2056 | 1974343 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2005 | 135286 | 35.3618 | -118.924 | No | Clear;32-90 F |  |  | 23-0024146 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1809836 | 0 | Non-EPSS | N | 2023 | BC PH TIME OC
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | 515426071015 | 20230202 | 1556 | 20230202 | 1840 | 1975211 | 164 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 164 | 35.4418 | -119.5359 | No | Overcast;32-90 F |  |  | 23-0024650 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1810124 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 15923 | 20230203 | 100 | 20230203 | 213 | 1975468 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 438 | 35.3653 | -118.943 | No | Clear;32-90 F |  |  | 23-0024708 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1810178 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1104 | 254541104 | FUSE | 74013 | 20230203 | 951 | 20230203 | 1218 | 1975838 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 441 | 35.4848 | -119.4035 | No | Clear;32-90F |  |  | 23-0024947 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1810337 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARNERAS-1102 | 252321102 | TRANSFORMER | 514975874528 | 20230203 | 1003 | 20230203 | 1305 | 1975849 | 182 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 182 | 35.5363 | -119.6893 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0024884 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1810322 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1104 | 254541104 | FUSE | 17080 | 20230203 | 1054 | 20230203 | 1251 | 1976039 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 936 | 35.5007 | -119.4392 | No | Partly Cloudy;32-90 F |  |  | 23-0024981 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1810349 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517282967453 | 20230203 | 1624 | 20230203 | 1908 | 1976242 | 164 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 164 | 35.3507 | -118.9121 | No | Clear;32-90F | Fuse | Broken | 23-0025119 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1810394 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 7498 | 20230203 | 1629 | 20230203 | 1723 | 1976212 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 890 | 18420 | 35.5069 | -119.2632 | No | Clear;32-90F | Lightning Arrestor | Burned/flashed | 23-0025107 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1810386 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRIP-SAVER | 13017 | 20230204 | 1422 | 20230204 | 2250 | 1976694 | 508 | Distribution Circuit | 3rd Party | Vehicle | 128 | 65024 | 35.335 | -119.0029 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0025224 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1810535 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | MC FARLAND-1101 | 253181101 | FUSE | 16610 | 20230204 | 1750 | 20230204 | 2145 | 1976800 | 235 | Distribution Circuit | 3rd Party | Metallic Balloon | 279 | 47273 | 35.6819 | -119.2319 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0025254 | OH | Sus | 45658833 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1810555 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | RECLOSER | 4227 | 20230205 | 112 | 20230205 | 1426 | 1977161 | 794 | Distribution Circuit | 3rd Party | Vehicle | 1142 | 106780 | 35.353 | -118.9304 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0025317 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1810621 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13447 | 20230205 | 154 | 20230205 | 813 | 1977170 | 379 | Distribution Circuit | Animal | Bird found | 131 | 49649 | 35.365 | -118.9703 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 23-0025352 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1810652 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 9686 | 20230205 | 956 | 20230205 | 2136 | 1977331 | 700 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 110 | 77000 | 35.3648 | -118.9407 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0025374 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1810669 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | SWITCH | 4911 | 20230205 | 1117 | 20230205 | 1206 | 1977409 | 49 | Distribution Circuit | 3rd Party | Vehicle | 363 | 17787 | 35.2948 | -119.0029 | No | Clear;32-90F | Crossarm- Steel | Broken | 23-0025390 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1810684 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515936856309 | 20230205 | 1315 | 20230205 | 1513 | 1977480 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 354 | 35.0398 | -119.3586 | No | Clear;32-90F | Fuse | Broken | 23-0025419 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1810708 | 0 | EPSS Ckt | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | RECLOSER | 3310 | 20230205 | 1615 | 20230206 | 318 | 1977571 | 663 | Distribution Circuit | 3rd Party | Vehicle | 348 | 31864 | 35.2085 | -119.0417 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0025429 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1810716 | 0 | Non-EPSS | N | 2023 | B C
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17784 | 20230205 | 1741 | 20230205 | 2014 | 1977640 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 10750 | 35.3447 | -119.0708 | No | Partly Cloudy;32-90 F |  |  | 23-0025472 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1810756 | 1 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 7199 | 20230205 | 1817 | 20230205 | 2300 | 1977662 | 283 | Distribution Circuit | Animal | Bird found | 9 | 2547 | 35.7313 | -119.8141 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0025511 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1810793 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1104 | 254541104 | TRANSFORMER | 515660572470 | 20230205 | 1905 | 20230205 | 2217 | 1977691 | 192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 192 | 35.4817 | -119.459 | No | Clear;32-90F | Fuse | Broken | 23-0025505 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1810790 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1105 | 252931105 | OCB | 1105/2 | 20230205 | 2040 | 20230206 | 12 | 1977715 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 18588 | 35.0198 | -118.9547 | No | Clear;32-90 F |  |  | 23-0025473 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | No | No | 1810757 | 0 | Non-EPSS | N | 2023 | B PH- GROUND- INST PH OC
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 13151 | 20230206 | 553 | 20230206 | 1542 | 1977828 | 589 | Distribution Circuit | 3rd Party | Vehicle | 40 | 10162 | 35.3466 | -119 | No | Partly Cloudy-Rain;32-90 F | Pole-Wood | Broken | 23-0025551 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1810821 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 14833 | 20230206 | 1000 | 20230206 | 1023 | 1978127 | 23 | Distribution Circuit | 3rd Party | Metallic Balloon | 94 | 2162 | 35.3971 | -118.9907 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0025685 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1810983 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | TRANSFORMER | 516380775057 | 20230206 | 1054 | 20230206 | 1206 | 1978238 | 72 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 144 | 35.5563 | -119.2172 | No | Clear;32-90F |  |  | 23-0025711 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1810993 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2101 | 255322101 | RECLOSER | 1007 | 20230207 | 649 | 20230207 | 1154 | 1978819 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2440 | 35.2962 | -119.1703 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0026023 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1811125 | 0 | Non-EPSS | N | 2023 | A & GRD
KERN | KERN | WELLFIELD 1102 | 254291102 | FUSE | 18843 | 20230207 | 1013 | 20230207 | 1412 | 1979323 | 239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1754 | 35.2092 | -118.8064 | No | Clear;32-90F | Lightning Arrestor | Burned/flashed | 23-0026310 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1811336 | 1 | EPSS Ckt | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | 100000018653 | 20230207 | 1039 | 20230207 | 2220 | 1979143 | 701 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 701 | 35.4052 | -119.5104 | No | Clear;32-90F | Transformer (OH) | Burned/flashed | 23-0026398 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1811363 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | FUSE | 77937 | 20230207 | 1045 | 20230207 | 1210 | 1979131 | 85 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 1785 | 35.2241 | -118.8423 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0026152 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1811284 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | 515575469681 | 20230207 | 2207 | 20230208 | 440 | 1979606 | 393 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 786 | 35.4057 | -119.486 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0026489 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1811416 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 100000091946 | 20230208 | 1146 | 20230208 | 1614 | 1980045 | 268 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 268 | 35.4777 | -119.5728 | No | Clear;32-90F |  |  | 23-0026808 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1811657 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 15365 | 20230209 | 626 | 20230209 | 734 | 1980460 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 4080 | 35.354 | -119.0344 | No | Clear;32-90F |  |  | 23-0026937 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1811730 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 14493 | 20230209 | 900 | 20230209 | 1136 | 1980742 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 779 | 35.3327 | -118.9323 | No | Clear;32-90F |  |  | 23-0027063 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1811919 | 1 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN 2103 | 253642103 | TRANSFORMER | 517224074840 | 20230209 | 924 | 20230209 | 1713 | 1980803 | 469 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 469 | 35.5533 | -118.9337 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0027110 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1811934 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CARNERAS-1102 | 252321102 | TRANSFORMER | 514974474258 | 20230209 | 1418 | 20230209 | 1810 | 1981112 | 232 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 232 | 35.5287 | -119.6898 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0027202 | OH | Sus | 45662386 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1811961 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA 2102 | 253142102 | TRANSFORMER | 515558652574 | 20230210 | 934 | 20230210 | 1822 | 1981682 | 528 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 528 | 34.9378 | -119.48 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0027591 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812235 | 0 | EPSS Ckt | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516511662245 | 20230210 | 1102 | 20230210 | 1130 | 1981685 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 35.2054 | -119.1682 | No | Clear;32-90F | Jumper |  | 23-0027561 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812220 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1105 | 253911105 | FUSE | 13382 | 20230210 | 1241 | 20230210 | 2005 | 1981871 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 444 | 35.2675 | -118.8338 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0027602 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | Yes | 1812242 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1110 | 252721110 | OTHER | COIS @ T8766 TWD T8767 | 20230210 | 1356 | 20230210 | 1512 | s1812265 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 3040 | 35.4279 | -119.0338 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0027619 | UG | Sus | 35425935 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1812265 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | T7989 | 20230210 | 1430 | 20230210 | 1456 | 1981956 | 20 | Transformer only | Equipment Failure/Involved | Underground | 14 | 280 | 35.3859 | -119.1645 | No | Clear;32-90 F | Bus | Deteriorated | 23-0027674 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1812271 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517216666800 | 20230210 | 1550 | 20230210 | 1740 | 1982004 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 220 | 35.3322 | -118.9359 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0027726 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812297 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1103 | 253391103 | FUSE | 13203 | 20230210 | 1633 | 20230210 | 2153 | 1982032 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 19840 | 35.3786 | -119.1127 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0027704 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1812284 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | T10200 | 20230210 | 2131 | 20230210 | 2141 | 1981484 | 10 | Transformer only | Equipment Failure/Involved | Underground | 10 | 100 | 35.4046 | -119.1153 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 23-0027523 | UG | Sus | 35425899 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812210 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1108 | 252771108 | RECLOSER | 250674 | 20230211 | 628 | 20230211 | 725 | 1982209 | 57 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 102 | 5814 | 35.3618 | -118.8954 | No | Clear;32-90 F |  |  | 23-0027784 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812340 | 0 | EPSS Ckt | Y | 2023 | BG
KERN | KERN | WEEDPATCH-1101 | 252971101 | TRANSFORMER | 517431362805 | 20230211 | 1014 | 20230211 | 1451 | 1982358 | 277 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 277 | 35.2227 | -118.8603 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0027824 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812412 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1102 | 252971102 | TRANSFORMER | 517379262173 | 20230211 | 1042 | 20230211 | 1210 | 1982390 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 88 | 35.2052 | -118.8782 | No | Clear;32-90 F | Service conductor | On Ground | 23-0027833 | OH | Sus | 31636585 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812419 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2101 | 255322101 | FUSE | 917795 | 20230211 | 1125 | 20230211 | 1235 | 1982398 | 70 | Distribution Circuit | Animal | Bird found | 33 | 2310 | 35.289 | -119.1155 | No | Clear;32-90 F | Fuse | Normal | 23-0027835 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812422 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 14376 | 20230211 | 1301 | 20230211 | 1404 | 1982462 | 63 | Distribution Circuit | 3rd Party | Metallic Balloon | 9 | 566 | 35.2668 | -119.0302 | No | Clear;32-90 F | Fuse | Normal | 23-0027846 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812434 | 1 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN 2101 | 253642101 | FUSE | 8534 | 20230212 | 500 | 20230212 | 1242 | 1982763 | 462 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 21252 | 35.6212 | -118.8485 | No | Partly Cloudy;32-90 F |  |  | 23-0027907 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812498 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 883676 | 20230212 | 643 | 20230212 | 1028 | 1982820 | 225 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2250 | 35.7753 | -119.5181 | No | Clear;32-90 F |  |  | 23-0027917 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1812507 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | OCB | 2102/2 | 20230212 | 1511 | 20230212 | 1550 | 1983009 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3928 | 66308 | 35.2955 | -119.0219 | No | Clear;32-90 F |  |  | 23-0027940 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1812537 | 0 | Non-EPSS | N | 2023 | AB
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | 516982059055 | 20230213 | 753 | 20230213 | 1006 | 1983269 | 133 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 133 | 35.1191 | -119.01 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0028091 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812746 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1105 | 253371105 | FUSE | 9581 | 20230213 | 847 | 20230213 | 957 | 1983309 | 70 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 70 | 35.387 | -119.0153 | No | Clear;32-90 F | Metering Equipment | Broken | 23-0028063 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1812683 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516893063934 | 20230213 | 907 | 20230213 | 1242 | 1983400 | 215 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 215 | 35.2525 | -119.0414 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0028179 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812807 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1101 | 252081101 | TRANSFORMER | 515647559966 | 20230213 | 942 | 20230213 | 1439 | 1983464 | 297 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1188 | 35.1389 | -119.457 | No | Clear;32-90 F | Fuse | Broken | 23-0028257 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812835 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | 515614270758 | 20230213 | 1001 | 20230213 | 1110 | 1983490 | 69 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 69 | 35.435 | -119.4732 | No | Clear;32-90 F | Fuse | Broken | 23-0028119 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812770 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1104 | 254541104 | TRANSFORMER | 515954770955 | 20230213 | 1031 | 20230213 | 1039 | 1983440 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 8 | 35.4421 | -119.3587 | No | Clear;32-90 F | Fuse | Broken | 23-0028105 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812761 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | RECLOSER | 894740 | 20230213 | 1301 | 20230213 | 1308 | 1983570 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 536 | 3752 | 35.4442 | -119.5178 | No | Clear;32-90 F | Capacitor | Burned/flashed | 23-0028173 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1812803 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | MIDWAY-1101 | 252611101 | RECLOSER | 389356 | 20230213 | 1852 | 20230213 | 1904 | 1984273 | 12 | Distribution Circuit | Company Initiated | Operating error | 44 | 528 | 35.4427 | -119.4394 | No | Clear;32-90 F | Recloser | Normal | 23-0000009 | OH | Sus | 74029661 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812952 | 0 | Non-EPSS | N | 2023 | SGF
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515522780376 | 20230213 | 2218 | 20230214 | 903 | 1983918 | 645 | Transformer only | Animal | Bird found | 1 | 645 | 35.6992 | -119.5085 | No | Clear;32-90F | Cutout- fuse holder | Burned/flashed | 23-0028390 | OH | Sus | 31636820 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812943 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 16235 | 20230214 | 640 | 20230214 | 801 | 1984333 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 243 | 35.3734 | -119.1631 | No | Clear;32-90 F |  |  | 23-0028466 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1812995 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 13269 | 20230214 | 751 | 20230214 | 1626 | 1984373 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 515 | 35.1007 | -118.9675 | No | Clear;32-90 F | Fuse | Broken | 23-0028537 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1813102 | 1 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | FUSE | 9816 | 20230214 | 809 | 20230214 | 1203 | 1984405 | 234 | Distribution Circuit | 3rd Party | Vehicle | 4 | 936 | 35.0955 | -119.0212 | No | Overcast-Snow;Below 32 F | Pole-Wood | Broken | 23-0028467 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1812996 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | 516982059055 | 20230214 | 928 | 20230214 | 1303 | 1984589 | 215 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 215 | 35.1191 | -119.01 | No | Clear;32-90 F | Fuse | Broken | 23-0028731 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1813194 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1103 | 252611103 | FUSE | 67253 | 20230214 | 1143 | 20230214 | 1842 | 1984796 | 419 | Distribution Circuit | 3rd Party | Vehicle | 7 | 2933 | 35.4274 | -119.4112 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0028738 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1813197 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | RECLOSER | 708132 | 20230214 | 1324 | 20230215 | 301 | 1984989 | 817 | Distribution Circuit | Equipment Failure/Involved | Overhead | 113 | 26630 | 35.6735 | -119.2588 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0028752 | OH | Sus | 45671983 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1813204 | 0 | Non-EPSS | N | 2023 | B- GRD
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 13289 | 20230214 | 1456 | 20230214 | 1617 | 1985167 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 5346 | 35.3833 | -119.2166 | No | Clear;32-90 F |  |  | 23-0028892 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1813252 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | 515997773057 | 20230214 | 1524 | 20230214 | 1733 | 1985224 | 129 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 129 | 35.5 | -119.3459 | No | Clear;32-90 F |  |  | 23-0028912 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1813266 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2103 | 255262103 | OTHER | T10242 TWD T10243 | 20230214 | 2116 | 20230215 | 49 | s1813308 | 213 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 2769 | 35.4003 | -119.1132 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0028853 | UG | Sus | 35426521 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1813308 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T8908 TWD T8909 | 20230215 | 156 | 20230215 | 237 | 1985644 | 41 | Distribution Circuit | Equipment Failure/Involved | Underground | 71 | 2911 | 35.4094 | -119.1222 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0028824 | UG | Sus | 35426540 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1813317 | 0 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1103 | 253801103 | FUSE | 13215 | 20230215 | 625 | 20230215 | 1225 | 1985679 | 360 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1800 | 35.1438 | -118.9169 | No | Clear;32-90 F | Insulator | Broken | 23-0029087 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1813451 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OCB | 2104/2 | 20230215 | 900 | 20230215 | 1333 | 1985995 | 212 | Distribution Circuit | Animal | Bird found | 753 | 203434 | 35.6018 | -119.5799 | No | Clear;32-90 F | Recloser | Burned/flashed | 23-0029143 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1813493 | 0 | Non-EPSS | N | 2023 | C PHASE INST
KERN | KERN | MAGUNDEN-1101 | 252771101 | OCB | 1101/2 | 20230215 | 1018 | 20230215 | 1440 | 1986038 | 262 | Distribution Circuit | 3rd Party | Metallic Balloon | 1583 | 127788 | 35.3618 | -118.924 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0029141 | OH | Sus | 45672447 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1813491 | 0 | Non-EPSS | N | 2023 | A- C- PHASE OC INST
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 18856 | 20230215 | 1346 | 20230215 | 1859 | 1986368 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1670 | 35.1086 | -119.1641 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0029422 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1813566 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 516003082162 | 20230215 | 1739 | 20230215 | 1916 | 1986401 | 97 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 97 | 35.7502 | -119.3478 | No | Clear;32-90 F |  |  | 23-0029451 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1813582 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2109 | 254072109 | FUSE | 9332 | 20230216 | 928 | 20230216 | 1020 | 1986770 | 52 | Distribution Circuit | Animal | Bird found | 53 | 2756 | 35.3032 | -119.0246 | No | Clear;32-90F | Fuse | Burned Open | 23-0029645 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1813739 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 166285 | 20230217 | 1412 | 20230217 | 1754 | 1987929 | 222 | Distribution Circuit | 3rd Party | Metallic Balloon | 1 | 296 | 35.3694 | -119.3756 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0030326 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1814056 | 1 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD 1101 | 253191101 | RECLOSER | 641042 | 20230217 | 1618 | 20230217 | 1743 | 1987891 | 85 | Distribution Circuit | Equipment Failure/Involved | Substation | 17 | 1445 | 35.0927 | -118.8388 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0030310 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1814054 | 0 | EPSS Ckt | Y | 2023 | A- B
KERN | KERN | RENFRO-2102 | 254572102 | TRANSFORMER | T135037 | 20230218 | 546 | 20230218 | 1105 | 1988046 | 319 | Transformer only | Equipment Failure/Involved | Underground | 3 | 957 | 35.3695 | -119.1473 | No | Clear;32-90F | Fuse | Broken | 23-0030461 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1814195 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | OCB | 1102/2 | 20230219 | 523 | 20230219 | 715 | 1988498 | 112 | Distribution Circuit | 3rd Party | Vehicle | 148 | 16576 | 35.0936 | -119.1012 | Yes | Clear;32-90 F | Anchor or Guy | Broken | 23-0030521 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1814259 | 0 | Non-EPSS | N | 2023 | C GRD PH OC INST
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | 517009059050 | 20230220 | 955 | 20230220 | 1121 | 1989341 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 86 | 35.1185 | -119.001 | No | Clear;32-90F | Fuse | Broken | 23-0030665 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1814461 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516952762208 | 20230220 | 1334 | 20230220 | 1603 | 1989464 | 149 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 149 | 35.205 | -119.0204 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0030708 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1814489 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517074268479 | 20230220 | 1451 | 20230220 | 1758 | 1989527 | 187 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1122 | 35.3781 | -118.9819 | No | Clear;32-90 F | Fuse | Broken | 23-0030720 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1814496 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 13891 | 20230221 | 213 | 20230221 | 531 | 1989704 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1386 | 35.2823 | -118.8873 | Yes | Clear;32-90F |  |  | 23-0030760 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1814530 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CHARCA-1102 | 254501102 | TRANSFORMER | 515737676551 | 20230221 | 1407 | 20230221 | 1730 | 1990256 | 203 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 203 | 35.5952 | -119.4346 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0031238 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1814909 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1101 | 253191101 | FUSE | 9920 | 20230221 | 1600 | 20230222 | 500 | 1995686 | 780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 3900 | 35.0817 | -118.8643 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0032040 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815643 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 14809 | 20230221 | 1707 | 20230221 | 2034 | 1994893 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 110 | 22770 | 35.3325 | -119.0561 | Yes | Clear;32-90 F |  |  | 23-0031861 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815459 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | INTERRUPTER | 586112 | 20230221 | 1757 | 20230221 | 2320 | 1994498 | 323 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 5181 | 35.2961 | -118.9786 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0031716 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1815323 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | OCB | 1101/2 | 20230221 | 1823 | 20230222 | 930 | 1996261 | 907 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3588 | 1245596 | 35.3618 | -118.924 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0031989 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1815586 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 16363 | 20230221 | 1828 | 20230222 | 555 | 1994934 | 687 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2748 | 35.6452 | -119.2592 | Yes | Clear;32-90F |  |  | 23-0032047 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815648 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1106 | 253371106 | FUSE | 15937 | 20230221 | 1833 | 20230222 | 345 | 1994964 | 552 | Distribution Circuit | 3rd Party | Metallic Balloon | 30 | 16560 | 35.3893 | -118.9786 | Yes | Clear;32-90F | Conductor- Overhead | Burned/flashed | 23-0032009 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815608 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 14419 | 20230221 | 1841 | 20230221 | 1951 | 1995055 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 7752 | 35.3269 | -119.0219 | Yes | Strong Winds-Strong Winds; |  |  | 23-0031799 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1815398 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 9681 | 20230221 | 1844 | 20230222 | 1252 | 1995093 | 1088 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 11666 | 35.2378 | -118.9626 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031979 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1815576 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 18173 | 20230221 | 1849 | 20230221 | 2335 | 1995162 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 11154 | 35.4091 | -119.0193 | Yes | Clear;32-90F | Fuse | Burned Open | 23-0031970 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815567 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 16241 | 20230221 | 1902 | 20230222 | 555 | 1995346 | 653 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2613 | 35.4269 | -119.5169 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0032044 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1815646 | 1 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | FUSE | 75817 | 20230221 | 1909 | 20230222 | 247 | 1995397 | 458 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2748 | 35.0954 | -119.0127 | Yes | Clear;32-90F |  |  | 23-0032023 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815622 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | RECLOSER | 993374 | 20230221 | 1914 | 20230222 | 6 | 1995441 | 292 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 687 | 200604 | 35.6016 | -119.6899 | Yes | Partly Cloudy-Fog-Strong Winds;32-90 F |  |  | 23-0031784 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815383 | 0 | Non-EPSS | N | 2023 | BC
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20230221 | 1915 | 20230222 | 1418 | 1995415 | 1143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 35433 | 35.3618 | -119.1627 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0031996 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1815593 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1102 | 253191102 | OCB | 1102/2 | 20230221 | 1923 | 20230222 | 241 | 1995494 | 438 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 18834 | 35.0921 | -118.8779 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0031782 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815381 | 0 | Non-EPSS | N | 2023 | AC PH TIME OC- SET A RLY TRIP
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20230221 | 1929 | 20230221 | 2253 | 1995529 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4555 | 823950 | 35.3885 | -119.0046 | Yes | Partly Cloudy;32-90 F |  |  | 23-0031787 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1815386 | 0 | Non-EPSS | N | 2023 | A- B- C
KERN | KERN | WESTPARK-1109 | 253701109 | FUSE | 15251 | 20230221 | 1929 | 20230222 | 921 | 1995511 | 832 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 6656 | 35.4009 | -119.0434 | Yes | Clear;32-90F |  |  | 23-0031994 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815591 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | OCB | 1102/2 | 20230221 | 1930 | 20230222 | 1154 | 1995573 | 984 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 74151 | 35.0891 | -118.9767 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0031798 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1815397 | 0 | Non-EPSS | N | 2023 | A- C
KERN | KERN | SAN BERNARD-1101 | 253191101 | FUSE | 15966 | 20230221 | 1931 | 20230222 | 345 | 1996372 | 494 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1482 | 35.1072 | -118.8492 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0032032 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815632 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 52116 | 20230221 | 1935 | 20230222 | 154 | 1995557 | 379 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 758 | 35.0759 | -118.9846 | Yes | Clear;32-90F |  |  | 23-0032013 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815612 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2107 | 254072107 | SWITCH | 4192 | 20230221 | 1936 | 20230222 | 1437 | 1995586 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3952 | 865607 | 35.318 | -119.0681 | Yes | Partly Cloudy;32-90 F | Switch (OH) | Burned/flashed | 23-0031942 | OH | Sus | 35427506 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1815560 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 9841 | 20230221 | 1936 | 20230222 | 640 | 1995567 | 664 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 5312 | 35.0308 | -118.8435 | Yes | Clear;32-90F |  |  | 23-0032062 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815656 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | OCB | 1107/2 | 20230221 | 1938 | 20230222 | 1706 | 1995608 | 1288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1139 | 189044 | 35.2971 | -118.8618 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031811 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1815409 | 0 | Non-EPSS | N | 2023 | C- GRD
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 9868 | 20230221 | 1953 | 20230222 | 553 | 1995695 | 600 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2801 | 35.2377 | -118.995 | Yes | Clear;32-90F |  |  | 23-0032049 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1815650 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT 1104 | 253911104 | FUSE | 14789 | 20230221 | 1955 | 20230222 | 754 | 1995702 | 719 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1438 | 35.2666 | -118.7528 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0032105 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815686 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WEEDPATCH-1101 | 252971101 | FUSE | 12183 | 20230221 | 1956 | 20230221 | 2202 | 1995715 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 378 | 35.2111 | -118.8337 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0031913 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815511 | 0 | Non-EPSS | N | 2023
KERN | KERN | ELK HILLS-1104 | 252441104 | RECLOSER | 3522 | 20230221 | 2015 | 20230222 | 1207 | 1995838 | 952 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 141848 | 35.2297 | -119.3762 | Yes | Clear;32-90 F |  |  | 23-0031846 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815443 | 0 | Non-EPSS | N | 2023 | BC
KERN | KERN | MCKITTRICK-1101 | 252781101 | OCB | 1101/2 | 20230221 | 2020 | 20230223 | 1630 | 1995866 | 2650 | Distribution Circuit | Equipment Failure/Involved | Overhead | 153 | 128978 | 35.297 | -119.6266 | Yes | Clear-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0031858 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1815456 | 0 | EPSS Ckt | N | 2023 | BC-GRD TIME OC
KERN | KERN | MCKITTRICK-1101 | 252781101 | SWITCH | 155664 | 20230221 | 2020 | 20230222 | 1252 | 1996398 | 992 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 992 | 35.3132 | -119.6468 | Yes | Clear-Strong Winds;32-90 F | Customer Equipment | Burned Open | 23-0031858 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1815637 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WASCO-1102 | 252961102 | JUMPER | OJ @ SW 14686 | 20230221 | 2027 | 20230222 | 501 | 1995878 | 514 | Distribution Circuit | Equipment Failure/Involved | Overhead | 389 | 194421 | 35.6012 | -119.3329 | Yes | Clear-Strong Winds;32-90 F | Jumper | Broken | 23-0032028 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1815628 | 1 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | SWITCH | 2349 | 20230221 | 2038 | 20230221 | 2215 | 1995874 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 97 | 35.3878 | -119.549 | Yes | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0031850 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1815448 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1106 | 254071106 | FUSE | 8333 | 20230221 | 2110 | 20230222 | 841 | 1996413 | 691 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 17275 | 35.3311 | -119.0456 | Yes | Overcast-Strong Winds;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0032041 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1815644 | 1 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1108 | 252081108 | FUSE | 58885 | 20230221 | 2153 | 20230221 | 2244 | 1996122 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 153 | 35.1376 | -119.4597 | Yes | Clear;32-90F | Connector or Splice (OH) | Arcing | 23-0031926 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1815524 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 9865 | 20230221 | 2157 | 20230222 | 503 | 1996123 | 426 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 852 | 35.2086 | -119.0515 | Yes | Clear;32-90F |  |  | 23-0032039 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815642 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 17107 | 20230222 | 641 | 20230222 | 1152 | 1996481 | 311 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 19904 | 35.3339 | -119.0566 | No | Overcast;32-90 F |  |  | 23-0032229 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815787 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1106 | 252901106 | FUSE | 15178 | 20230222 | 714 | 20230222 | 1150 | 1996680 | 276 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3036 | 35.5288 | -119.4471 | No | Partly Cloudy;32-90 F |  |  | 23-0032285 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815819 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7447 | 20230222 | 810 | 20230222 | 1440 | 1996760 | 390 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1561 | 35.6301 | -119.5817 | No | Clear;32-90 F |  |  | 23-0032485 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1815928 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 53339 | 20230222 | 833 | 20230222 | 1255 | 1996836 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1310 | 35.6597 | -119.5177 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0032115 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1815701 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW 1103 | 253411103 | FUSE | 4488 | 20230222 | 839 | 20230222 | 1515 | 1996815 | 396 | Distribution Circuit | 3rd Party | Vehicle | 57 | 6834 | 35.0647 | -119.1346 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0032111 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815697 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | OCB | 1103/2 | 20230222 | 858 | 20230222 | 908 | 1996631 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 570 | 5700 | 35.0891 | -118.9767 | No | Overcast-Strong Winds;Below 32 F | Woodpin | Broken | 23-0032135 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1815725 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | WEEDPATCH-1101 | 252971101 | FUSE | 15713 | 20230222 | 904 | 20230222 | 2315 | 1996907 | 851 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2553 | 35.2088 | -118.8691 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0032136 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1815726 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 14809 | 20230222 | 1050 | 20230222 | 1125 | 1997254 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 1610 | 35.3325 | -119.0561 | No | Overcast;32-90 F |  |  | 23-0032233 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1815790 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515344472612 | 20230222 | 1104 | 20230222 | 1420 | 1997314 | 196 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 196 | 35.4853 | -119.5646 | No | Clear;32-90 F |  |  | 23-0032467 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1815916 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | T8105 | 20230222 | 1300 | 20230222 | 1451 | 1997651 | 111 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 111 | 35.3578 | -119.3209 | No | Clear;32-90 F |  |  | 23-0032575 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1815996 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 514600 | 20230222 | 1410 | 20230222 | 1818 | 1997920 | 248 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 3720 | 35.2613 | -119.1283 | No | Clear;32-90 F |  |  | 23-0032483 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1815926 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 81603 | 20230222 | 1446 | 20230222 | 1651 | 1997957 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 666 | 35.2473 | -119.0029 | No | Clear;32-90 F |  |  | 23-0032614 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816023 | 1 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1107 | 253701107 | FUSE | 9521 | 20230222 | 1511 | 20230222 | 2114 | 1998036 | 363 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 7200 | 35.4025 | -119.0478 | No | Partly Cloudy;32-90 F | Switch (UG) | Failed/Faulted | 23-0032565 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1815983 | 1 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 7563 | 20230222 | 1738 | 20230222 | 2008 | 1998382 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 300 | 35.3617 | -119.4744 | No | Clear;32-90 F |  |  | 23-0032733 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816111 | 1 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | FUSE | 16521 | 20230222 | 1812 | 20230223 | 43 | 1998436 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 5083 | 35.1091 | -119.3765 | No | Clear;32-90F | Pole-Wood | Broken | 23-0032789 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1816150 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-1108 | 252771108 | FUSE | 15342 | 20230222 | 1933 | 20230222 | 2155 | 1998539 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 474 | 35.3691 | -118.8547 | No | Clear;32-90F |  |  | 23-0032780 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816148 | 1 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-1106 | 252771106 | FUSE | 14782 | 20230223 | 800 | 20230223 | 1330 | 1998888 | 330 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 6270 | 35.3833 | -118.9413 | Yes | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0032853 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1816186 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517085268688 | 20230223 | 830 | 20230223 | 1245 | 1998990 | 255 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 255 | 35.3835 | -118.9787 | Yes | Clear;32-90F | Conductor- Overhead | Arcing | 23-0033053 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816267 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | OCB | 1102/2 | 20230223 | 916 | 20230223 | 1123 | 1999107 | 127 | Distribution Circuit | Vegetation | Tree - branch fell on line | 130 | 16510 | 35.6142 | -119.8539 | Yes | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0032962 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | No | No | 1816220 | 0 | Non-EPSS | N | 2023 | B- C- PH OC TIME
KERN | KERN | ANTELOPE 1102 | 252021102 | TRANSFORMER | 514137579641 | 20230223 | 1004 | 20230223 | 1329 | 1999179 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 205 | 35.6723 | -119.9746 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0033188 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816320 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ANTELOPE 1101 | 252021101 | FUSE | 7078 | 20230223 | 1610 | 20230224 | 730 | 2000163 | 920 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2760 | 35.6586 | -120.0555 | Yes | Clear;32-90F | Pole-Wood | Burned/flashed | 23-0033364 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1816417 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13389 | 20230224 | 434 | 20230224 | 604 | 2002538 | 90 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 630 | 35.1793 | -118.9679 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0033641 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1816679 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 514600 | 20230224 | 451 | 20230224 | 723 | 2002691 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2280 | 35.2613 | -119.1283 | Yes | Clear;32-90 F |  |  | 23-0033658 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1816696 | 0 | Non-EPSS | N | 2023 | 3EO
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 2771 | 20230224 | 452 | 20230224 | 1545 | 2002679 | 653 | Distribution Circuit | Equipment Failure/Involved | Overhead | 460 | 22832 | 35.2234 | -119.1004 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033656 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1816694 | 0 | Non-EPSS | N | 2023 | ABC-GRD
KERN | KERN | WEEDPATCH-1106 | 252971106 | JUMPER | BURNED OJ 2 W/OF L1260 | 20230224 | 505 | 20230224 | 634 | 2003046 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 14755 | 35.2379 | -118.9526 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0033686 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816723 | 1 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1106 | 252081106 | TRANSFORMER | 515661960383 | 20230224 | 508 | 20230224 | 1040 | 2002708 | 332 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3984 | 35.1505 | -119.452 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0033718 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816753 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 16363 | 20230224 | 548 | 20230224 | 1110 | 2003045 | 322 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1288 | 35.6452 | -119.2592 | Yes | Clear;32-90F |  |  | 23-0033896 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1816892 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | OCB | 1103/2 | 20230224 | 639 | 20230227 | 1022 | 2003524 | 4543 | Distribution Circuit | Animal | Other | 146 | 70211 | 35.6018 | -119.58 | Yes | Clear;32-90F | Pole-Wood | Normal | 23-0033729 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816760 | 0 | Non-EPSS | N | 2023 | B GRD
KERN | KERN | TEJON-1102 | 252931102 | FUSE | 14923 | 20230224 | 713 | 20230226 | 1940 | 2003695 | 3627 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 21762 | 34.8339 | -118.861 | Yes | Overcast-Fog-Snow-Strong Winds;32-90 F |  |  | 23-0035862 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1818684 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15062 | 20230224 | 939 | 20230224 | 1444 | 2004802 | 305 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 16478 | 35.3325 | -118.9142 | Yes | Clear;32-90 F |  |  | 23-0034297 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817182 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 14843 | 20230224 | 958 | 20230224 | 1534 | 2004878 | 336 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 41 | 13776 | 35.4044 | -118.9855 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0033998 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1816970 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1108 | 254071108 | OCB | 8133 | 20230224 | 1039 | 20230225 | 336 | 2005035 | 1017 | Distribution Circuit | 3rd Party | Vehicle | 1317 | 277711 | 35.3368 | -119.0528 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033991 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1816963 | 0 | Non-EPSS | N | 2023 | ABC-GRD
KERN | KERN | TEJON-1103 | 252931103 | TRANSFORMER | 517752855528 | 20230224 | 1130 | 20230224 | 1205 | 2004430 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 35 | 35.0232 | -118.7505 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0034088 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817034 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 16363 | 20230224 | 1158 | 20230224 | 1703 | 2005266 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1220 | 35.6452 | -119.2592 | Yes | Overcast;32-90 F | Conductor- Overhead | Together | 23-0034079 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1817026 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | RECLOSER | 3310 | 20230224 | 1200 | 20230225 | 542 | 2005281 | 896 | Distribution Circuit | Equipment Failure/Involved | Overhead | 350 | 85913 | 35.2085 | -119.0417 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034083 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817031 | 0 | Non-EPSS | N | 2023 | BG
KERN | KERN | TUPMAN-1106 | 254561106 | RECLOSER | 4981 | 20230224 | 1339 | 20230224 | 1906 | 2005687 | 327 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 47 | 8786 | 35.3535 | -119.2523 | Yes | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0034206 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1817109 | 0 | Non-EPSS | N | 2023 | 99
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 514600 | 20230224 | 1356 | 20230224 | 1426 | 2005743 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 450 | 35.2613 | -119.1283 | Yes | Clear;32-90 F | Recloser | Malfunctioning | 23-0034220 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817118 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 514600 | 20230224 | 1356 | 20230224 | 1547 | 2005839 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1665 | 35.2613 | -119.1283 | Yes | Clear;32-90 F | Recloser | Malfunctioning | 23-0034220 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1817139 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | STOCKDALE-2114 | 254072114 | SWITCH | 4149 | 20230224 | 1417 | 20230224 | 1634 | 2005813 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 697 | 95489 | 35.3546 | -119.0744 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0034241 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1817135 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1108 | 252771108 | TRANSFORMER | 517452067967 | 20230224 | 1419 | 20230224 | 2100 | 2005796 | 401 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 401 | 35.3644 | -118.856 | Yes | Clear;32-90 F | Fuse | Broken | 23-0034588 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817444 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | FUSE | 9035 | 20230224 | 1505 | 20230225 | 1110 | 2005934 | 1205 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 3615 | 35.4428 | -119.6531 | Yes | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0034453 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1817307 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 13844 | 20230224 | 1517 | 20230225 | 756 | 2005977 | 966 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 32898 | 35.2704 | -119.0027 | Yes | Clear;32-90 F | Pole-Wood | Normal | 23-0034310 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1817191 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1104 | 253701104 | TRANSFORMER | 516926068529 | 20230224 | 1526 | 20230224 | 2023 | 2006014 | 297 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1188 | 35.3787 | -119.0321 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0034571 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817426 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | JUMPER | CENTER PHASE OPEN JUMPER | 20230224 | 1532 | 20230224 | 2042 | 2006251 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 627 | 134190 | 35.3615 | -118.9677 | Yes | Partly Cloudy-Strong Winds;32-90 F | Jumper | Broken | 23-0034423 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1817276 | 1 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13338 | 20230224 | 1551 | 20230224 | 1856 | 2006217 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1665 | 35.0765 | -119.0204 | Yes | Clear;32-90 F |  |  | 23-0034530 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1817380 | 0 | EPSS Ckt | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | T8282 | 20230224 | 1936 | 20230225 | 1255 | 2006878 | 1039 | Transformer only | Equipment Failure/Involved | Underground | 9 | 9351 | 35.3789 | -119.1775 | Yes | Clear;32-90F | Conductor- Underground | Burned/flashed | 23-0034772 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817632 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 17107 | 20230224 | 1937 | 20230225 | 231 | 2006501 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 113 | 29485 | 35.3339 | -119.0566 | Yes | Overcast-Rain;32-90 F | Jumper | Arcing | 23-0034540 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1817393 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | RECLOSER | 711854 | 20230224 | 2001 | 20230227 | 1757 | 2006994 | 4196 | Distribution Circuit | 3rd Party | Customer Equipment | 6 | 25176 | 35.319 | -120.0073 | Yes | Overcast-Fog-Rain;32-90 F | Customer Equipment | Malfunctioning | 23-0034553 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817408 | 0 | EPSS Ckt | N | 2023 | B G TIME
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13989 | 20230224 | 2017 | 20230224 | 2200 | 2007040 | 103 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 122 | 12566 | 35.365 | -118.959 | Yes | Overcast-Rain;32-90 F | Fuse | Failed/Faulted | 23-0034838 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817698 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 9163 | 20230224 | 2112 | 20230302 | 2039 | 2010116 | 8607 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 51642 | 35.353 | -119.9873 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0035016 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818570 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 1635 | 20230224 | 2113 | 20230307 | 1543 | 2007212 | 15510 | Distribution Circuit | Environmental/External | Ice or snow | 90 | 525904 | 34.9498 | -119.6935 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034638 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817494 | 0 | EPSS Ckt | N | 2023 | A B C
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 934590 | 20230224 | 2113 | 20230226 | 1744 | 2009384 | 2671 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 80130 | 34.9828 | -119.7854 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035495 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1818343 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 16488 | 20230224 | 2126 | 20230228 | 1830 | 2009668 | 5584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 240978 | 35.3663 | -120.0409 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035016 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1818447 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | FUSE | 2321 | 20230224 | 2207 | 20230225 | 2100 | 2008768 | 1373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2746 | 34.9395 | -119.6393 | Yes | Clear;32-90F | Crossarm- Wood |  | 23-0034638 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1818163 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 10718 | 20230225 | 19 | 20230225 | 312 | 2007428 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 5882 | 35.326 | -119.0813 | Yes | Clear;32-90F |  |  | 23-0035021 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817888 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1109 | 253951109 | RECLOSER | 4443 | 20230225 | 130 | 20230225 | 1523 | 2007469 | 833 | Distribution Circuit | Equipment Failure/Involved | Underground | 759 | 367130 | 35.397 | -118.9321 | Yes | Overcast-Heavy Rain;32-90 F | Elbow | Broken | 23-0035013 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817880 | 0 | Non-EPSS | N | 2023 | B & GRD
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 13508 | 20230225 | 133 | 20230225 | 458 | 2007470 | 205 | Distribution Circuit | Equipment Failure/Involved | Underground | 55 | 11275 | 35.3192 | -119.0514 | Yes | Overcast-Heavy Rain;32-90 F | Elbow | Deteriorated | 23-0035022 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817889 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | RECLOSER | 384116 | 20230225 | 201 | 20230301 | 825 | 2007218 | 6144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 109950 | 35.3799 | -120.0401 | Yes | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0035016 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817883 | 0 | EPSS Ckt | N | 2023 | A GRD
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 303287 | 20230225 | 229 | 20230225 | 811 | 2007514 | 342 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 68 | 23256 | 35.4112 | -119.3119 | Yes | Clear;32-90F |  |  | 23-0035058 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1817921 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2103 | 255262103 | FUSE | 84578 | 20230225 | 252 | 20230225 | 1953 | -2007547 | 1021 | Distribution Circuit | Equipment Failure/Involved | Underground | 262 | 219450 | 35.3954 | -119.1101 | Yes | Clear;32-90F | Elbow | Burned/flashed | 23-0035264 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818159 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 10718 | 20230225 | 404 | 20230225 | 718 | 2007618 | 194 | Distribution Circuit | Equipment Failure/Involved | Underground | 34 | 6596 | 35.326 | -119.0813 | Yes | Clear;32-90F | Elbow | Normal | 23-0035043 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817913 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14955 | 20230225 | 616 | 20230225 | 1207 | 2007733 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 146 | 28770 | 35.4036 | -118.9766 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0035074 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817937 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 883676 | 20230225 | 642 | 20230227 | 1834 | 2007742 | 3592 | Distribution Circuit | Environmental/External | Flood/Erosion | 10 | 35920 | 35.7753 | -119.5181 | Yes | Overcast-Fog-Drizzle;32-90 F | Insulator | Failed/Faulted | 23-0035184 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1818033 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517134367997 | 20230225 | 1213 | 20230225 | 2008 | 2008411 | 475 | Transformer only | Environmental/External | Water | 1 | 475 | 35.365 | -118.9615 | Yes | Clear;32-90 F | Transformer | Burned/flashed | 23-0035363 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818200 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1109 | 253951109 | SWITCH | 10450 | 20230225 | 1556 | 20230225 | 1605 | 2008870 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 143 | 1287 | 35.3949 | -118.9272 | Yes | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0035013 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1818205 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1107 | 253701107 | SWITCH | 12221 | 20230225 | 1641 | 20230225 | 1708 | 2008965 | 27 | Distribution Circuit | Company Initiated | Return Circuit Normal | 10 | 216 | 35.4003 | -119.0526 | Yes | Clear;32-90F | Conductor- Underground | Normal | 23-0032565 | UG | Sus | 35427507 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1818222 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | RECLOSER | 1689 | 20230225 | 2228 | 20230226 | 537 | 2009464 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1727 | 183958 | 35.3028 | -119.0029 | Yes | Clear;32-90F | Conductor- Overhead | Arcing | 23-0035570 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1818421 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | RENFRO-2102 | 254572102 | FUSE | 18345 | 20230225 | 2329 | 20230226 | 212 | 2009500 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 6520 | 35.3687 | -119.1441 | Yes | Overcast;32-90 F |  |  | 23-0035580 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818432 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1106 | 253371106 | FUSE | 8113 | 20230226 | 734 | 20230227 | 103 | 2009678 | 1049 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1049 | 35.3849 | -118.9697 | Yes | Clear;32-90F | Elbow | Failed/Faulted | 23-0035628 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818474 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2102 | 253142102 | FUSE | 9030 | 20230226 | 900 | 20230302 | 2054 | 2009801 | 6474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 140114 | 34.9366 | -119.5065 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0035663 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818506 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 18663 | 20230226 | 920 | 20230227 | 1058 | 2009780 | 1538 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 50754 | 34.9114 | -119.5953 | Yes | Clear;32-90 F | Anchor or Guy | Broken | 23-0035790 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1818614 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CUYAMA 1104 | 253141104 | FUSE | 9212 | 20230226 | 1037 | 20230302 | 1206 | 2009628 | 5849 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 45237 | 34.9275 | -119.6963 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035661 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818503 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 10718 | 20230226 | 1254 | 20230226 | 2036 | 2010091 | 462 | Distribution Circuit | Equipment Failure/Involved | Underground | 34 | 7338 | 35.326 | -119.0813 | Yes | Clear;32-90 F | Elbow | Contaminated | 23-0035761 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818596 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 516988864616 | 20230226 | 1700 | 20230227 | 1315 | 2010394 | 1215 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 13988 | 35.2715 | -119.0095 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0035933 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818746 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2102 | 254572102 | FUSE | 18345 | 20230227 | 454 | 20230227 | 1027 | 2011150 | 333 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 13320 | 35.3687 | -119.1441 | Yes | Clear;32-90F | Elbow | Contaminated | 23-0036060 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818869 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1101 | 253181101 | FUSE | 16837 | 20230227 | 706 | 20230227 | 848 | 2011217 | 102 | Distribution Circuit | 3rd Party | Vehicle | 13 | 1326 | 35.6891 | -119.2587 | Yes | Clear;32-90F | Other | Broken | 23-0036142 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1818900 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516965169990 | 20230227 | 741 | 20230227 | 1009 | 2011278 | 148 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 148 | 35.4189 | -119.0189 | Yes | Clear;32-90F | Fuse | Broken | 23-0036230 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818951 | 0 | Non-EPSS | N | 2023
KERN | KERN | SISQUOC-1102 | 182811102 | TRIP-SAVER | 45261 | 20230227 | 1000 | 20230412 | 1252 | 2011718 | 63532 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 193577 | 35.1099 | -120.09 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | On Ground | 23-0036225 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818948 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | CARNERAS-1102 | 252321102 | FUSE | 17120 | 20230227 | 1200 | 20230227 | 1230 | 2012151 | 30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 90 | 35.543 | -119.7342 | Yes | Clear;32-90F |  |  | 23-0036347 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819020 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1104 | 253191104 | OCB | 1104/2 | 20230227 | 1256 | 20230228 | 39 | 2012291 | 703 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 7977 | 35.0921 | -118.8779 | Yes | Partly Cloudy-Fog;32-90 F | Pole-Wood | Deteriorated | 23-0036419 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1819062 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | TEMBLOR-1104 | 252551104 | TRIP-SAVER | 14233 | 20230227 | 1556 | 20230227 | 2215 | 2012738 | 379 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2275 | 35.3678 | -119.7357 | Yes | Clear;32-90F |  |  | 23-0037027 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1819566 | 1 | EPSS Ckt | N | 2023 | 3
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | T4453 | 20230227 | 1628 | 20230227 | 1751 | 2013110 | 83 | Transformer only | Equipment Failure/Involved | Underground | 4 | 332 | 35.337 | -118.9117 | Yes | Clear;32-90F | Secondary | Broken | 23-0036637 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1819210 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516770863324 | 20230227 | 1743 | 20230227 | 2006 | 2013344 | 143 | Transformer only | Equipment Failure/Involved | Underground | 4 | 572 | 35.2355 | -119.0824 | Yes | Clear;32-90F | Customer Equipment | Burned/flashed | 23-0036765 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1819314 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | FUSE | 7066 | 20230227 | 1820 | 20230228 | 345 | 2013508 | 565 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 565 | 35.5782 | -119.7075 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Burned/flashed | 23-0036707 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | Yes | 1819268 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | FUSE | 14746 | 20230227 | 1829 | 20230228 | 127 | 2013540 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 569 | 131435 | 34.8751 | -118.8937 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0036718 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819278 | 0 | EPSS Ckt | N | 2023
KERN | KERN | RIO BRAVO-1103 | 252861103 | FUSE | 14008 | 20230228 | 925 | 20230228 | 2016 | 2014645 | 651 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3255 | 35.4404 | -119.2164 | Yes | Clear;32-90F | Woodpin | Burned/flashed | 23-0037199 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819660 | 0 | Non-EPSS | N | 2023
KERN | KERN | DEVILS DEN 1102 | 253451102 | TRANSFORMER | 514087581622 | 20230228 | 948 | 20230228 | 1745 | 2014712 | 477 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 477 | 35.7271 | -119.9923 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0037399 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1819807 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13338 | 20230228 | 1018 | 20230228 | 1522 | 2014826 | 302 | Distribution Circuit | Animal | Bird found | 9 | 2718 | 35.0765 | -119.0204 | Yes | Clear;32-90F | Transformer (OH) | Normal | 23-0037541 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819897 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-1106 | 252771106 | RECLOSER | 4176 | 20230228 | 1340 | 20230228 | 1355 | 2015590 | 15 | Distribution Circuit | 3rd Party | Vehicle | 743 | 11145 | 35.3833 | -118.9438 | Yes | Clear;32-90F | Anchor or Guy | Broken- wire on ground | 23-0037334 | OH | Sus | 34529228 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1819794 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 7477 | 20230228 | 1600 | 20230228 | 1623 | 2016158 | 23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 46 | 35.631 | -119.2234 | Yes | Clear;32-90F |  |  | 23-0037592 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1819930 | 1 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7256 | 20230228 | 1836 | 20230228 | 2243 | 2016471 | 247 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2306 | 35.6023 | -119.5268 | Yes | Clear;32-90F |  |  | 23-0037840 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1820169 | 1 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516958062789 | 20230301 | 920 | 20230301 | 1130 | 2017912 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 260 | 35.221 | -119.0192 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0038069 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820335 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 9841 | 20230301 | 1057 | 20230301 | 1353 | 2018109 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1320 | 35.0308 | -118.8435 | No | Overcast-Snow-Strong Winds;Below 32 F |  |  | 23-0038219 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1820444 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 15542 | 20230301 | 1146 | 20230302 | 131 | 2018198 | 825 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 33000 | 35.3787 | -118.994 | No | Clear;32-90F | Pole-Wood | Broken | 23-0038440 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1820634 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 14547 | 20230301 | 1438 | 20230301 | 2150 | 2018476 | 432 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 864 | 35.2014 | -119.0746 | No | Clear;32-90F | Cutout- fuse holder | Broken | 23-0038349 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820543 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 883676 | 20230302 | 615 | 20230302 | 1459 | 2019362 | 524 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 5240 | 35.7753 | -119.5181 | No | Clear;32-90F |  |  | 23-0038862 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1820900 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516860764050 | 20230302 | 901 | 20230302 | 1139 | 2019515 | 158 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 158 | 35.2554 | -119.0522 | No | Clear;32-90 F | Fuse | Broken | 23-0038736 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820823 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1106 | 254501106 | FUSE | 18052 | 20230302 | 1033 | 20230302 | 1205 | 2019627 | 92 | Distribution Circuit | 3rd Party | Metallic Balloon | 45 | 4140 | 35.5798 | -119.3436 | No | Clear;32-90F | Fuse | Burned Open | 23-0038747 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820833 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 7549 | 20230302 | 1237 | 20230302 | 1604 | 2019828 | 207 | Distribution Circuit | Vegetation | Other ground vegetation | 12 | 2484 | 35.6018 | -119.2414 | No | Clear;32-90F | Fuse | Burned Open | 23-0038950 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820958 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 100000046124 | 20230302 | 1255 | 20230302 | 1505 | 2019860 | 130 | Transformer only | Environmental/External | Ice or snow | 1 | 130 | 35.2722 | -118.8964 | No | Clear;32-90 F | Transformer | Broken | 23-0038795 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820861 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1104 | 252721104 | SWITCH | 77965 | 20230302 | 1312 | 20230302 | 1702 | 2019878 | 230 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 230 | 35.5183 | -119.0376 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0038896 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1820923 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ARVIN-1103 | 253801103 | TRANSFORMER | 517269059565 | 20230302 | 2047 | 20230302 | 2133 | 2020227 | 46 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 46 | 35.133 | -118.9147 | No | Clear;32-90 F |  |  | 23-0039113 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1821102 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514795471178 | 20230303 | 810 | 20230303 | 1245 | 2020853 | 275 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 550 | 35.4439 | -119.748 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0039451 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1821298 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FRUITVALE-1104 | 253391104 | FUSE | 17270 | 20230303 | 1101 | 20230303 | 1158 | 2021154 | 57 | Distribution Circuit | Animal | Bird found | 38 | 1990 | 35.4195 | -119.092 | No | Clear;32-90 F | Fuse | Burned Open | 23-0039428 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1821283 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 8888 | 20230304 | 638 | 20230304 | 830 | 2022083 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1232 | 35.3655 | -118.9626 | No | Clear;32-90 F |  |  | 23-0039882 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1821646 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 14833 | 20230305 | 1208 | 20230305 | 1320 | 2023699 | 72 | Distribution Circuit | 3rd Party | Metallic Balloon | 94 | 6768 | 35.3971 | -118.9907 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0040366 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822090 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1116 | 253491116 | FUSE | 49515 | 20230305 | 1252 | 20230305 | 1411 | 2023740 | 79 | Distribution Circuit | Animal | Bird found | 2 | 158 | 35.571 | -119.1156 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0040382 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822108 | 1 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | OCB | 1104/2 | 20230305 | 1519 | 20230306 | 221 | 2023903 | 662 | Distribution Circuit | 3rd Party | Vehicle | 1373 | 146088 | 35.6882 | -119.2769 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0040404 | OH | Sus | 35429278 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1822138 | 0 | Non-EPSS | N | 2023 | A- GRD- PH OC TIME
KERN | KERN | MC FARLAND-1104 | 253181104 | SWITCH | 1237 | 20230306 | 305 | 20230306 | 313 | 2024209 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 26 | 208 | 35.647 | -119.241 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0040404 | OH | Sus | 35429278 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822274 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2108 | 254072108 | TRANSFORMER | T5230 | 20230306 | 341 | 20230306 | 514 | 2024214 | 93 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 1023 | 35.3174 | -119.1054 | No | Clear;32-90F |  |  | 23-0040546 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1822281 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1116 | 253491116 | FUSE | 49515 | 20230306 | 835 | 20230306 | 953 | 2024359 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 156 | 35.571 | -119.1156 | No | Clear;32-90F |  |  | 23-0040608 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822317 | 1 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 16664 | 20230306 | 845 | 20230306 | 1339 | 2024376 | 294 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 21168 | 35.4018 | -119.1279 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0040589 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822297 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1110 | 253951110 | TRANSFORMER | T15015 | 20230306 | 946 | 20230306 | 1233 | 2024468 | 167 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 167 | 35.3902 | -118.9595 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0040698 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822357 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1110 | 253951110 | JUMPER | 17286 HI SIDE CTR PH JMPR | 20230306 | 946 | 20230306 | 1245 | 2024694 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 179 | 35.3904 | -118.9582 | No | Clear;32-90F | Jumper | Broken | 23-0040722 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1822368 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 58355 | 20230306 | 1344 | 20230306 | 1457 | 2024768 | 73 | Distribution Circuit | Animal | Other | 1 | 73 | 35.0749 | -118.9218 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0040842 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822417 | 1 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13401 | 20230306 | 1436 | 20230307 | 221 | 2024907 | 705 | Distribution Circuit | 3rd Party | Vehicle | 5 | 3525 | 35.2379 | -118.8954 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0040865 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1822428 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | SWITCH | 1567 | 20230306 | 1823 | 20230306 | 1913 | 2025051 | 50 | Distribution Circuit | Animal | Bird found | 1123 | 56150 | 35.405 | -119.0256 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0040902 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1822454 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | FUSE | 441807 | 20230307 | 908 | 20230307 | 1836 | 2025362 | 568 | Distribution Circuit | Animal | Other | 2 | 1137 | 35.0167 | -119.853 | No | Clear;32-90F | Cutout- fuse holder | Burned/flashed | 23-0041371 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822698 | 1 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517109867856 | 20230307 | 1219 | 20230307 | 1225 | 2025584 | 6 | Transformer only | 3rd Party | Customer Equipment | 1 | 6 | 35.3615 | -118.9697 | No | Partly Cloudy;32-90 F | Customer Equipment | Broken | 23-0041179 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822622 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW 1106 | 253411106 | TRANSFORMER | 516735056557 | 20230307 | 1336 | 20230307 | 1840 | 2025670 | 304 | Transformer only | 3rd Party | Vandalism | 1 | 304 | 35.0488 | -119.0914 | No | Clear;32-90 F | Transformer | Broken | 23-0041356 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822686 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LERDO-1114 | 253491114 | TRANSFORMER | 516620772558 | 20230307 | 2130 | 20230308 | 927 | 2025775 | 717 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 717 | 35.4884 | -119.1365 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0041434 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822764 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517521962278 | 20230308 | 744 | 20230308 | 1119 | 2026301 | 215 | Transformer only | Animal | Bird found | 7 | 1505 | 35.2086 | -118.8302 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0041650 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822904 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | SWITCH | 96457 | 20230308 | 856 | 20230309 | 921 | 2026395 | 799 | Distribution Circuit | 3rd Party | Vehicle | 35 | 21305 | 35.3536 | -118.9673 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0041449 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822848 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | FUSE | 17759 | 20230308 | 1252 | 20230308 | 1515 | 2026694 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 143 | 35.2669 | -119.0963 | No | Clear;32-90F |  |  | 23-0041786 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822956 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1106 | 253391106 | JUMPER | COIS @T9296 TWDS T9297 | 20230308 | 1327 | 20230308 | 1621 | 2026716 | 174 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 9048 | 35.4144 | -119.0614 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0041691 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822925 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1104 | 252721104 | FUSE | 13348 | 20230308 | 1654 | 20230308 | 2130 | 2026928 | 276 | Distribution Circuit | Animal | Other | 24 | 6627 | 35.4993 | -119.0111 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0041846 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822986 | 1 | EPSS Ckt | N | 2023
KERN | KERN | COLUMBUS-1105 | 253951105 | OTHER | J9 TWD T0076 | 20230308 | 2047 | 20230309 | 229 | 2027076 | 342 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 3420 | 35.4109 | -118.9586 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0041793 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822994 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1104 | 252721104 | FUSE | 13348 | 20230308 | 2336 | 20230309 | 155 | 2027128 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 3338 | 35.4993 | -119.0111 | No | Clear;32-90 F |  |  | 23-0041908 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823046 | 1 | EPSS Ckt | N | 2023
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 16420 | 20230309 | 22 | 20230309 | 229 | 2027138 | 127 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 127 | 35.4129 | -119.0588 | Yes | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0041903 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823043 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 20244 | 20230309 | 959 | 20230310 | 230 | 2027425 | 991 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1 | 991 | 34.9273 | -119.5955 | Yes | Clear;32-90F | Secondary | Burned/flashed | 23-0042087 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823101 | 1 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517382066103 | 20230309 | 1049 | 20230309 | 1431 | 2027403 | 222 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 222 | 35.3132 | -118.8786 | Yes | Clear;32-90F | Fuse | Broken | 23-0042212 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823147 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 7549 | 20230309 | 1213 | 20230309 | 1452 | 2027490 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1273 | 35.6018 | -119.2414 | Yes | Partly Cloudy;32-90 F | Fuse | Broken | 23-0042289 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823166 | 1 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 622728 | 20230309 | 1448 | 20230309 | 2226 | 2027526 | 458 | Distribution Circuit | Environmental/External | Flood/Erosion | 55 | 25190 | 35.0056 | -119.808 | Yes | Clear;32-90 F | Pole-Wood | On Ground | 23-0042176 | OH | Sus | 35431353 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823134 | 0 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | SEMITROPIC-1106 | 252901106 | FUSE | 16104 | 20230309 | 1717 | 20230309 | 1914 | 2028227 | 117 | Distribution Circuit | Animal | Bird found | 4 | 468 | 35.6026 | -119.4203 | Yes | Clear;32-90F | Bushing | Normal | 23-0042477 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823301 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1106 | 253951106 | FUSE | 14505 | 20230309 | 2008 | 20230310 | 334 | 2029188 | 446 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 3761 | 35.3975 | -118.9567 | Yes | Overcast-Drizzle;32-90 F | Transformer (UG) | Leaking | 23-0042061 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823324 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | TRANSFORMER | 515434476769 | 20230309 | 2041 | 20230310 | 28 | 2027947 | 227 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 227 | 35.6002 | -119.5358 | Yes | Clear;32-90 F | Transformer | Burned Open | 23-0042530 | OH | Sus | 31639769 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823350 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-1104 | 252551104 | TRIP-SAVER | 14233 | 20230309 | 2128 | 20230316 | 1313 | 2029889 | 9585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 25239 | 35.3678 | -119.7357 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Woodpin | Broken | 23-0042755 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823569 | 0 | EPSS Ckt | N | 2023 | #1 & #3
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 684566 | 20230310 | 352 | 20230323 | 1449 | 2030031 | 19377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 116262 | 35.0707 | -119.9955 | No | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042719 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1823530 | 0 | EPSS Ckt | N | 2023 | B C
KERN | KERN | FRUITVALE-1104 | 253391104 | RECLOSER | 2464 | 20230310 | 726 | 20230310 | 745 | 2030209 | 19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1689 | 32091 | 35.3991 | -119.1101 | No | Overcast-Drizzle;32-90 F | Cutout- fuse holder | Arcing | 23-0042776 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823578 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 303287 | 20230310 | 855 | 20230310 | 1037 | 2030495 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 4626 | 35.4112 | -119.3119 | No | Overcast-Fog;32-90 F |  |  | 23-0042893 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823646 | 1 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1112 | 252901112 | FUSE | 87100 | 20230310 | 1101 | 20230310 | 1511 | 2030757 | 250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1750 | 35.6304 | -119.4561 | No | Clear;32-90 F |  |  | 23-0043175 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823775 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | OCB | 1101/2 | 20230310 | 1105 | 20230310 | 1300 | 2030775 | 115 | Distribution Circuit | Animal | Bird found | 136 | 15568 | 35.6055 | -119.2033 | No | Overcast;32-90 F | Lightning Arrestor | Burned/flashed | 23-0042984 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823686 | 0 | Non-EPSS | N | 2023 | B-GRD TIME OC
KERN | KERN | KERN OIL-1108 | 252721108 | SWITCH | 547820 | 20230310 | 1127 | 20230311 | 506 | 2031623 | 1059 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 3177 | 35.4483 | -119.0512 | No | Clear;32-90 F | Switch (UG) | Normal | 23-0013382 | UG | Sus | 47022648 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1823848 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16181 | 20230310 | 1219 | 20230310 | 1426 | 2030936 | 127 | Distribution Circuit | Animal | Bird found | 6 | 762 | 35.0943 | -119.1542 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0043142 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823756 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1103 | 253391103 | FUSE | 15309 | 20230310 | 1559 | 20230310 | 2144 | 2031350 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 8625 | 35.383 | -119.1191 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0043208 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823801 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | T2197 | 20230310 | 1856 | 20230310 | 2015 | 2031583 | 79 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 79 | 35.3626 | -118.9665 | No | Overcast;32-90 F |  |  | 23-0043267 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823852 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | OCB | 1103/2 | 20230310 | 2030 | 20230311 | 1019 | 2031667 | 829 | Distribution Circuit | Animal | Other | 146 | 33926 | 35.6018 | -119.58 | No | Overcast-Fog;32-90 F | Recloser | Normal | 23-0043273 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1823858 | 0 | Non-EPSS | N | 2023 | ABC TIME OC
KERN | KERN | CHARCA-1102 | 254501102 | RECLOSER | 826046 | 20230311 | 601 | 20230311 | 1420 | 2031902 | 499 | Distribution Circuit | 3rd Party | Vehicle | 48 | 7152 | 35.6161 | -119.333 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043337 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1823921 | 0 | Non-EPSS | N | 2023 | A- B- C- G- SGF- 51RLY
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | SWITCH | 18049 | 20230311 | 1200 | 20230312 | 441 | 2032333 | 1001 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1001 | 35.3182 | -120.0001 | No | Clear;32-90F | Anchor or Guy | Deteriorated | 23-0043436 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823997 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515899457293 | 20230311 | 1434 | 20230311 | 1530 | 2032509 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 56 | 35.0665 | -119.3708 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0043505 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824051 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WASCO-1102 | 252961102 | OCB | 1102/2 | 20230312 | 24 | 20230312 | 302 | 2032976 | 158 | Distribution Circuit | 3rd Party | Vehicle | 1637 | 258646 | 35.6018 | -119.326 | No | Fog;32-90 F | Conductor- Overhead | Normal | 23-0043612 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | No | No | 1824153 | 0 | Non-EPSS | N | 2023 | B- C- PH OC TIME
KERN | KERN | STOCKDALE-2108 | 254072108 | FUSE | 10946 | 20230312 | 1422 | 20230313 | 1141 | 2033375 | 1279 | Distribution Circuit | Equipment Failure/Involved | Underground | 37 | 13856 | 35.3113 | -119.1042 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0043747 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824264 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | OCB | 1102/2 | 20230313 | 639 | 20230314 | 1258 | 2033968 | 1819 | Distribution Circuit | Equipment Failure/Involved | Overhead | 449 | 54351 | 35.2083 | -119.101 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043945 | OH | Sus | 45698282 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1824455 | 0 | Non-EPSS | N | 2023 | A & C & INST
KERN | KERN | RIO BRAVO-1102 | 252861102 | TRANSFORMER | 100000088295 | 20230313 | 746 | 20230315 | 1610 | 2034055 | 3384 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 10152 | 35.4244 | -119.2426 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0044058 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824508 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1109 | 254071109 | OCB | 1109/2 | 20230313 | 1427 | 20230313 | 1650 | 2034694 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 916 | 130988 | 35.3164 | -119.0682 | No | Clear;32-90 F |  |  | 23-0044251 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | No | No | 1824572 | 0 | Non-EPSS | N | 2023 | A- B- 50RLY
KERN | KERN | STOCKDALE-2106 | 254072106 | OCB | 2106/2 | 20230313 | 1427 | 20230313 | 1611 | 2034697 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1630 | 151712 | 35.3165 | -119.068 | No | Clear;32-90 F |  |  | 23-0044238 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824569 | 0 | Non-EPSS | N | 2023 | PH OC TIME
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | 100000012788 | 20230313 | 1515 | 20230313 | 1526 | 2034755 | 11 | Transformer only | 3rd Party | Customer Equipment | 1 | 11 | 35.4932 | -119.4797 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 23-0044252 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1824573 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1102 | 253701102 | SWITCH | 5693 | 20230313 | 2345 | 20230314 | 18 | 2035111 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 99 | 35.3725 | -119.0254 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0044370 | OH | Sus | 31639865 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1824718 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | OCB | 1101/2 | 20230314 | 524 | 20230324 | 1032 | 2035177 | 13240 | Distribution Circuit | 3rd Party | Vehicle | 217 | 273106 | 35.7178 | -119.4554 | Yes | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0044471 | OH | Sus | 31639871 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1824737 | 0 | Non-EPSS | N | 2023 | A- B- C- 51 TIME
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 516069668360 | 20230314 | 805 | 20230314 | 1702 | 2035287 | 537 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 537 | 35.371 | -119.3191 | Yes | Clear;32-90 F | Fuse | Broken | 23-0045621 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825568 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | 515958873589 | 20230314 | 914 | 20230314 | 1414 | 2035425 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 300 | 35.5146 | -119.3591 | Yes | Overcast-Rain;32-90 F | Connector or Splice (OH) | Arcing | 23-0045295 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825305 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | TRANSFORMER | 517406871465 | 20230314 | 920 | 20230314 | 1106 | 2035443 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 106 | 35.4595 | -118.8716 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0044769 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824897 | 0 | EPSS Ckt | N | 2023
KERN | KERN | 7TH STANDARD-2101 | 254582101 | OTHER | T8625 TWD T9722 | 20230314 | 929 | 20230314 | 1049 | 2035497 | 80 | Distribution Circuit | Equipment Failure/Involved | Underground | 25 | 2000 | 35.4084 | -119.1149 | Yes | Clear;32-90 F | Transformer (UG) | Leaking | 23-0044048 | UG | Sus | 35431606 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1824791 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1103 | 252461103 | OCB | 1103/2 | 20230314 | 1100 | 20230314 | 1253 | s1825138 | 113 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 158 | 17854 | 35.6055 | -119.2033 | Yes | Clear;32-90 F |  |  | 23-0045074 |  | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825138 | 0 | Non-EPSS | N | 2023 | CG
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 16158 | 20230314 | 1323 | 20230314 | 1630 | 2040470 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 17017 | 35.3439 | -119.0747 | Yes | Clear;32-90 F |  |  | 23-0045356 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825345 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | OTHER | J2390 TWD 18049 | 20230314 | 1815 | 20230314 | 2304 | 2044841 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 354 | 35.321 | -120.0039 | Yes | Overcast-Fog-Strong Winds;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0045677 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1825825 | 0 | EPSS Ckt | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | TRANSFORMER | 517094873650 | 20230315 | 218 | 20230315 | 1838 | 2045106 | 980 | Transformer only | Animal | Other | 2 | 1960 | 35.52 | -118.9786 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0046374 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826182 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16172 | 20230315 | 259 | 20230315 | 1449 | 2045139 | 710 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 4468 | 35.1513 | -119.071 | No | Clear;32-90 F |  |  | 23-0046061 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825982 | 1 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | RECLOSER | 4745 | 20230315 | 330 | 20230315 | 754 | 2045165 | 264 | Distribution Circuit | Animal | Other | 11 | 2904 | 35.6222 | -119.8552 | No | Overcast-Fog-Drizzle;32-90 F | Regulator | Burned/flashed | 23-0046056 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825975 | 0 | Non-EPSS | N | 2023 | C- GRD
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 516926463811 | 20230315 | 756 | 20230315 | 840 | 2045471 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 44 | 35.2492 | -119.03 | No | Clear;32-90F | Fuse | Broken | 23-0046138 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826033 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515887259556 | 20230315 | 858 | 20230315 | 925 | 2045292 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 27 | 35.1287 | -119.3766 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0046162 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826049 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | TRANSFORMER | 516263479112 | 20230315 | 1311 | 20230315 | 1510 | 2046214 | 119 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 119 | 35.6676 | -119.2588 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0046386 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826192 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517404663097 | 20230315 | 1545 | 20230315 | 1618 | 2046607 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 33 | 35.2305 | -118.8693 | No | Clear;32-90 F | Fuse | Broken | 23-0046521 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826265 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | 516944469438 | 20230315 | 2343 | 20230316 | 343 | 2047481 | 240 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2400 | 35.4034 | -119.0261 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0046833 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826460 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1102 | 254501102 | FUSE | 252293 | 20230316 | 451 | 20230316 | 830 | 2047631 | 219 | Distribution Circuit | Environmental/External | Flood/Erosion | 3 | 657 | 35.6669 | -119.3662 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0046868 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1826475 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 9611 | 20230316 | 802 | 20230316 | 855 | 2047778 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 53 | 35.2962 | -118.9677 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0046908 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826497 | 1 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2102 | 253142102 | TRANSFORMER | 515257552995 | 20230316 | 1012 | 20230316 | 1356 | 2047757 | 224 | Transformer only | Animal | Other | 1 | 224 | 34.9449 | -119.5823 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0046957 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826527 | 0 | EPSS Ckt | N | 2023
KERN | KERN | RENFRO-2102 | 254572102 | FUSE | 11571 | 20230316 | 1518 | 20230317 | 1026 | 2048794 | 1148 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 21216 | 35.3707 | -119.1553 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0047176 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826652 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRIP-SAVER | 3527 | 20230317 | 347 | 20230317 | 1212 | 2049433 | 505 | Distribution Circuit | Equipment Failure/Involved | Overhead | 212 | 53363 | 35.3482 | -120.0054 | No | Partly Cloudy-Fog;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0047371 | OH | Sus | 31639905 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826795 | 1 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516370863475 | 20230317 | 733 | 20230317 | 1546 | 2049518 | 493 | Transformer only | Animal | Bird found | 1 | 493 | 35.2381 | -119.2165 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0047687 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826941 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 9689 | 20230317 | 844 | 20230317 | 1018 | 2049632 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 188 | 35.4099 | -119.0622 | No | Clear;32-90 F |  |  | 23-0047483 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826847 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | SWITCH | 108849 | 20230317 | 1107 | 20230317 | 1640 | 2050514 | 333 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2664 | 35.6878 | -119.4908 | No | Clear;32-90 F |  |  | 23-0047709 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826956 | 1 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | TRANSFORMER | 517090974382 | 20230317 | 1214 | 20230320 | 2205 | 2050025 | 4911 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 9822 | 35.5407 | -118.9793 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0047658 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826928 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | 517000262017 | 20230317 | 1244 | 20230317 | 1352 | 2050080 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 136 | 35.1996 | -119.0049 | No | Clear;32-90 F | Transformer | Broken | 23-0047628 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826920 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRIP-SAVER | 13390 | 20230317 | 1659 | 20230317 | 2206 | 2050479 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 10745 | 35.1795 | -118.9669 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0047703 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1826951 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | FRUITVALE-1106 | 253391106 | TRANSFORMER | T1271 | 20230318 | 803 | 20230318 | 1352 | 2050922 | 349 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 698 | 35.421 | -119.0645 | No | Clear;32-90 F |  |  | 23-0043161 | OH | Sus | 45104492 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1827475 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | OCB | 1101/2 | 20230318 | 2058 | 20230324 | 2027 | 2051561 | 8609 | Distribution Circuit | Equipment Failure/Involved | Overhead | 95 | 344319 | 35.7178 | -119.4554 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048362 | OH | Sus | 31640083 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1827566 | 0 | Non-EPSS | N | 2023 | B G TIME
KERN | KERN | STOCKDALE-2112 | 254072112 | RECLOSER | 2858 | 20230319 | 202 | 20230319 | 1514 | 2051623 | 773 | Distribution Circuit | Equipment Failure/Involved | Overhead | 546 | 142654 | 35.2981 | -119.0919 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0048420 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827626 | 0 | Non-EPSS | N | 2023 | B&C
KERN | KERN | BAKERSFIELD-2104 | 253372104 | OCB | 2104/2 | 20230319 | 312 | 20230319 | 920 | 2051643 | 368 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4192 | 387659 | 35.3885 | -119.0046 | No | Overcast;32-90 F | Jumper | Broken- wire on ground | 23-0048422 | OH | Sus | 45702820 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1827629 | 0 | Non-EPSS | N | 2023 | B&c
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 18300 | 20230319 | 458 | 20230320 | 1100 | 2051674 | 1802 | Distribution Circuit | 3rd Party | Other | 10 | 4884 | 35.076 | -118.9578 | No | Overcast-Strong Winds;32-90 F | Pole-Wood | On Ground | 23-0048437 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | No | No | 1827645 | 0 | EPSS Ckt | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRANSFORMER | 516065269650 | 20230319 | 633 | 20230319 | 841 | 2051717 | 128 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 384 | 35.4068 | -119.3212 | No | Overcast;32-90 F | Fuse | Broken | 23-0048453 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827663 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2102 | 253142102 | SWITCH | 195688 | 20230319 | 828 | 20230320 | 241 | 2051804 | 1093 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 44964 | 34.9379 | -119.4727 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0048450 | OH | Sus | 31640141 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1827660 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 4113 | 20230319 | 846 | 20230319 | 1154 | 2051820 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 6204 | 35.312 | -118.843 | No | Overcast-Drizzle;32-90 F |  |  | 23-0048455 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827665 | 0 | EPSS Ckt | Y | 2023 | C G
KERN | KERN | CUYAMA-2101 | 253142101 | OCB | 2101/2 | 20230319 | 916 | 20230319 | 1244 | 2051899 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 295 | 61360 | 34.9276 | -119.6203 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0048470 | OH | Sus | 45702786 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827681 | 0 | EPSS Ckt | N | 2023 | BC TIME
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 14210 | 20230319 | 957 | 20230319 | 1549 | 2051906 | 352 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 14784 | 35.1424 | -119.4656 | No | Overcast;32-90 F |  |  | 23-0048511 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827718 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1101 | 252971101 | JUMPER | SOUTH PHASE JUMPER BROKEN | 20230319 | 1051 | 20230319 | 1315 | 2052015 | 144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 4590 | 35.2088 | -118.8979 | No | Overcast-Strong Winds;32-90 F | Jumper | Broken | 23-0048483 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1827693 | 1 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 15479 | 20230319 | 1128 | 20230319 | 1631 | 2051975 | 303 | Distribution Circuit | 3rd Party | Metallic Balloon | 52 | 15756 | 35.1455 | -119.4617 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0048530 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827738 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | FUSE | 18650 | 20230319 | 1151 | 20230320 | 1057 | 2051993 | 1386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1386 | 34.9438 | -118.8351 | No | Partly Cloudy-Strong Winds;32-90 F | Connector or Splice (OH) | Broken | 23-0048515 | OH | Sus | 45702765 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827722 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SAN BERNARD-1104 | 253191104 | OCB | 1104/2 | 20230319 | 1257 | 20230319 | 1355 | 2052044 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 4756 | 35.0921 | -118.8779 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0048492 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827701 | 0 | Non-EPSS | N | 2023 | BC INST
KERN | KERN | CUYAMA-2101 | 253142101 | OCB | 2101/2 | 20230319 | 1332 | 20230319 | 2013 | 2052074 | 401 | Distribution Circuit | Equipment Failure/Involved | Overhead | 295 | 118295 | 34.9276 | -119.6203 | No | Overcast;32-90 F | Conductor- Overhead | Together | 23-0048502 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827709 | 0 | EPSS Ckt | N | 2023 | BC
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 517019864446 | 20230319 | 1341 | 20230319 | 1601 | 2052093 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 560 | 35.2668 | -118.9986 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0048519 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827726 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 57521 | 20230319 | 1543 | 20230319 | 1745 | 2052191 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 244 | 35.4424 | -119.4839 | No | Partly Cloudy;32-90 F |  |  | 23-0048544 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827753 | 1 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1106 | 252771106 | FUSE | 14028 | 20230319 | 1609 | 20230319 | 1800 | 2052210 | 111 | Distribution Circuit | 3rd Party | Metallic Balloon | 111 | 12321 | 35.383 | -118.9287 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0048547 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827756 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1103 | 252721103 | RECLOSER | 5247 | 20230319 | 1644 | 20230319 | 1815 | 2052247 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 608 | 54212 | 35.4262 | -119.0257 | No | Overcast-Rain;32-90 F |  |  | 23-0048536 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | No | No | 1827744 | 0 | Non-EPSS | N | 2023 | B/C GRD
KERN | KERN | CHARCA-1102 | 254501102 | FUSE | 7521 | 20230320 | 1157 | 20230320 | 1410 | 2052986 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1508 | 35.6524 | -119.3338 | No | Partly Cloudy;32-90 F |  |  | 23-0048930 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827934 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | FUSE | 15933 | 20230320 | 1213 | 20230321 | 2118 | 2053005 | 1985 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 3970 | 35.362 | -118.8234 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0048877 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1827922 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13405 | 20230320 | 1316 | 20230320 | 1539 | 2053081 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 191 | 35.2452 | -118.9321 | No | Clear;32-90 F |  |  | 23-0048972 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827951 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 11993 | 20230320 | 1720 | 20230321 | 901 | 2053354 | 941 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1882 | 35.3178 | -119.0491 | No | Partly Cloudy;32-90 F | Bus | Failed/Faulted | 23-0049051 | UG | Sus | 45704246 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828009 | 1 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1103 | 252461103 | FUSE | 7302 | 20230320 | 1812 | 20230320 | 2157 | 2053395 | 225 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 4725 | 35.6015 | -119.088 | No | Overcast;32-90 F |  |  | 23-0049052 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828008 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | JUMPER | OJ 4 P W/OF CGC 517128468113 | 20230320 | 2017 | 20230321 | 15 | 2053477 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2142 | 35.3682 | -118.9649 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0049023 | OH | Sus | 45704241 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1827980 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | T5086 | 20230320 | 2115 | 20230321 | 1043 | 2053475 | 808 | Distribution Circuit | Equipment Failure/Involved | Underground | 58 | 13561 | 35.3628 | -119.1772 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0049070 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828028 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2108 | 254072108 | TRANSFORMER | T5306 | 20230320 | 2312 | 20230321 | 1123 | 2053496 | 731 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 9040 | 35.3172 | -119.1036 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0049056 | UG | Sus | 35433040 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828013 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 46985 | 20230321 | 656 | 20230321 | 1029 | 2053581 | 213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 3195 | 35.2595 | -119.0066 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0049126 | OH | Sus | 31640098 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1828048 | 1 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | TRIP-SAVER | 2455 | 20230321 | 656 | 20230321 | 923 | 2053584 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 270 | 39690 | 34.8582 | -118.8838 | Yes | Clear;32-90 F |  |  | 23-0049152 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828062 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | OLD RIVER-1101 | 252821101 | FUSE | 8869 | 20230321 | 830 | 20230321 | 1441 | 2053672 | 371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2227 | 35.1804 | -119.1816 | Yes | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0049216 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828090 | 1 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | SWITCH | 1330 | 20230321 | 912 | 20230321 | 933 | 2053785 | 21 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 693 | 35.4421 | -119.3691 | Yes | Partly Cloudy;32-90 F | Regulator | Failed/Faulted | 23-0000064 | OH | Sus | 74029661 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828076 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1106 | 254501106 | TRANSFORMER | 516049576805 | 20230321 | 930 | 20230322 | 841 | 2053836 | 1391 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2782 | 35.603 | -119.3302 | Yes | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049525 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828284 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | JUMPER | OJ 2 N/ OF CGC 514086566087 | 20230321 | 1033 | 20230322 | 1400 | 2055690 | 1647 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1647 | 35.2931 | -119.976 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Anchor or Guy | Normal | 23-0049558 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828313 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | RECLOSER | 1200 | 20230321 | 1035 | 20230321 | 1235 | 2053990 | 120 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 166 | 11392 | 35.7176 | -119.4204 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049261 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1828106 | 0 | Non-EPSS | N | 2023 | B & C
KERN | KERN | TEMBLOR-1104 | 252551104 | JUMPER | WIRE DOWN | 20230321 | 1134 | 20230321 | 2318 | 2056390 | 704 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 12672 | 35.4395 | -119.7377 | Yes | Partly Cloudy-Rain;32-90 F | Crossarm- Wood | Broken | 23-0049628 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828366 | 0 | EPSS Ckt | N | 2023
KERN | KERN | KERN POWER-2104 | 255262104 | INTERRUPTER | 12589 | 20230321 | 1153 | 20230321 | 1822 | 2054192 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 353 | 105943 | 35.3545 | -119.0844 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049421 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1828195 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1106 | 254071106 | FUSE | 14064 | 20230321 | 1157 | 20230321 | 1632 | 2054237 | 275 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 9900 | 35.3364 | -119.0434 | Yes | Partly Cloudy-Rain;32-90 F |  |  | 23-0049870 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828567 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517011166035 | 20230321 | 1200 | 20230321 | 1654 | 2054268 | 294 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 2352 | 35.3104 | -119.0021 | Yes | Partly Cloudy-Rain;32-90 F |  |  | 23-0049892 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1828585 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | RECLOSER | 3851 | 20230321 | 1201 | 20230321 | 1510 | 2054233 | 189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 2847 | 35.209 | -119.1478 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0049371 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828157 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 37032 | 20230321 | 1209 | 20230321 | 1738 | 2054250 | 329 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 11515 | 35.2524 | -118.9664 | Yes | Clear;32-90 F |  |  | 23-0049947 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828635 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 878715 | 20230321 | 1211 | 20230321 | 1400 | 2054265 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 6867 | 35.3972 | -118.9853 | Yes | Partly Cloudy-Rain;32-90 F |  |  | 23-0049598 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828342 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 18448 | 20230321 | 1213 | 20230321 | 1548 | 2054276 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 717 | 35.6232 | -119.5092 | Yes | Partly Cloudy;32-90 F |  |  | 23-0049755 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828467 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15062 | 20230321 | 1213 | 20230321 | 1503 | 2054279 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 9185 | 35.3325 | -118.9142 | Yes | Partly Cloudy;32-90 F |  |  | 23-0049698 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828422 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 13177 | 20230321 | 1219 | 20230321 | 2145 | 2054316 | 566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 6226 | 35.3573 | -119.0085 | Yes | Partly Cloudy-Rain;32-90 F | Pole-Wood | Deteriorated | 23-0049437 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828207 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1103 | 253651103 | FUSE | 79677 | 20230321 | 1220 | 20230321 | 1413 | 2054321 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 3051 | 35.5216 | -119.3137 | Yes | Partly Cloudy;32-90 F |  |  | 23-0049666 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828396 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1112 | 253701112 | TRANSFORMER | 516871567492 | 20230321 | 1256 | 20230321 | 1540 | 2054910 | 164 | Transformer only | Vegetation | Tree - grew into line | 9 | 1476 | 35.35 | -119.05 | Yes | Partly Cloudy-Rain;32-90 F | Fuse | Failed/Faulted | 23-0049773 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828482 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516971166716 | 20230321 | 1348 | 20230321 | 1801 | 2056031 | 253 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 2530 | 35.329 | -119.0157 | Yes | Clear;32-90 F |  |  | 23-0049988 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1828676 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN 1102 | 254401102 | TRANSFORMER | 514413083555 | 20230321 | 1640 | 20230321 | 1705 | 2056042 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 50 | 35.7809 | -119.8843 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Burned Open | 23-0049913 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828602 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517213266680 | 20230321 | 1923 | 20230321 | 2209 | 2060321 | 166 | Transformer only | Vegetation | Tree - bark fell into line | 3 | 498 | 35.3285 | -118.9354 | Yes | Clear;32-90F | Jumper | Contaminated | 23-0050257 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828916 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517202965810 | 20230321 | 2007 | 20230322 | 144 | 2060564 | 337 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 674 | 35.3046 | -118.9384 | Yes | Overcast-Drizzle;32-90 F | Fuse | Broken | 23-0050287 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828949 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1105 | 253371105 | TRANSFORMER | 516969868822 | 20230321 | 2339 | 20230322 | 215 | 2061364 | 156 | Transformer only | 3rd Party | Vandalism | 10 | 1560 | 35.3865 | -119.0169 | Yes | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0050268 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1828929 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | T10272 | 20230322 | 705 | 20230322 | 1025 | 2061735 | 200 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 200 | 35.39 | -119.5456 | No | Clear;32-90 F |  |  | 23-0050494 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829080 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1108 | 252721108 | FUSE | 15240 | 20230322 | 809 | 20230322 | 1704 | 2061862 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 23622 | 35.4484 | -119.0264 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0050473 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829069 | 1 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | 515001553430 | 20230322 | 859 | 20230322 | 1333 | 2062032 | 274 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 274 | 34.9566 | -119.6674 | No | Overcast;32-90 F | Fuse | Broken | 23-0050719 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829195 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 9770 | 20230322 | 1005 | 20230322 | 1155 | 2062217 | 110 | Distribution Circuit | Animal | Bird found | 4 | 440 | 35.2313 | -118.751 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0050642 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1829149 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FELLOWS-2104 | 254242104 | FUSE | 372119 | 20230322 | 1126 | 20230323 | 1600 | 2062437 | 1714 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3428 | 35.2287 | -119.6729 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050705 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1829185 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | TRANSFORMER | 515899081521 | 20230322 | 1203 | 20230322 | 1647 | 2054239 | 284 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 284 | 35.7323 | -119.3817 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 23-0050903 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829311 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | TRANSFORMER | 517406871465 | 20230322 | 1227 | 20230322 | 1640 | 2062664 | 253 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 253 | 35.4595 | -118.8716 | No | Overcast-Drizzle;32-90 F |  |  | 23-0050938 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1829338 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 13787 | 20230322 | 1404 | 20230322 | 1909 | 2062917 | 305 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 610 | 35.0926 | -118.9439 | No | Overcast-Rain;32-90 F |  |  | 23-0050994 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1829381 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1109 | 253701109 | JUMPER | OPEN JUMPER @ CGC 516905869696 | 20230322 | 1544 | 20230322 | 1926 | 2063285 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2886 | 35.4107 | -119.0393 | No | Overcast-Rain;32-90 F | Jumper | Burned Open | 23-0050940 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1829339 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 14086 | 20230322 | 1614 | 20230322 | 1635 | 2063284 | 21 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 1176 | 35.3595 | -118.95 | No | Overcast-Drizzle;32-90 F |  |  | 23-0050881 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829296 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 15446 | 20230323 | 158 | 20230323 | 356 | 2063997 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 5074 | 35.1338 | -119.4754 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0051134 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829511 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514296580008 | 20230323 | 1214 | 20230323 | 1501 | 2064650 | 167 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 167 | 35.6829 | -119.9211 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0051429 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829667 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13898 | 20230323 | 1233 | 20230323 | 1533 | 2064741 | 180 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 180 | 35.6882 | -119.7631 | No | Partly Cloudy;32-90 F |  |  | 23-0051523 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829716 | 1 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OCB | 2104/2 | 20230324 | 706 | 20230324 | 1240 | 2065644 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 752 | 97964 | 35.6018 | -119.5799 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051723 | OH | Sus | 31640440 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1829844 | 0 | Non-EPSS | N | 2023 | B
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516710361425 | 20230324 | 1238 | 20230324 | 1418 | 2066063 | 100 | Transformer only | Environmental/External | Water | 1 | 100 | 35.1833 | -119.1008 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0051930 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829935 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T63213 TWD T54658 | 20230324 | 1759 | 20230324 | 2206 | 2066525 | 247 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 3705 | 35.4029 | -119.1682 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0052023 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1829990 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1106 | 254501106 | TRANSFORMER | 516049576805 | 20230324 | 1945 | 20230324 | 2208 | 2066446 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 286 | 35.603 | -119.3302 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052049 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830011 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517222166602 | 20230325 | 553 | 20230325 | 748 | 2066739 | 115 | Transformer only | 3rd Party | Vehicle | 2 | 230 | 35.3265 | -118.9321 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0052427 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830392 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517222166602 | 20230325 | 855 | 20230325 | 1220 | 2066835 | 205 | Transformer only | 3rd Party | Vehicle | 2 | 410 | 35.3265 | -118.9321 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0052424 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1830414 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1105 | 252461105 | FUSE | 27263 | 20230325 | 1620 | 20230325 | 1829 | 2067302 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 258 | 35.5803 | -119.2045 | No | Clear;32-90 F |  |  | 23-0052545 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830494 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2109 | 254072109 | TRANSFORMER | T7971 | 20230325 | 2257 | 20230326 | 1746 | 2067800 | 1129 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 15806 | 35.2792 | -119.0422 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0052656 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830626 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 20151 | 20230326 | 855 | 20230326 | 1010 | 2067542 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 900 | 35.4475 | -118.9044 | No | Clear;32-90 F |  |  | 23-0052641 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830584 | 0 | EPSS Ckt | N | 2023
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8657 | 20230326 | 1727 | 20230326 | 1838 | 2067892 | 71 | Distribution Circuit | 3rd Party | Metallic Balloon | 122 | 8662 | 35.3531 | -119.0839 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0052713 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1830647 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | 517325550185 | 20230326 | 2006 | 20230326 | 2221 | 2067969 | 135 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 135 | 34.876 | -118.8932 | No | Partly Cloudy;32-90 F |  |  | 23-0052756 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1830690 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1105 | 253911105 | TRANSFORMER | T7577 | 20230326 | 2325 | 20230327 | 1332 | 2068337 | 847 | Transformer only | Company Initiated | Construction Activity/equip- company | 17 | 14399 | 35.2507 | -118.8436 | No | Clear;32-90 F | Transformer | Normal | 23-0052826 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1830735 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | RECLOSER | 931236 | 20230327 | 950 | 20230327 | 1950 | 2068478 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 11942 | 35.1084 | -119.3727 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0052861 | OH | Sus | 31640502 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1830772 | 0 | EPSS Ckt | N | 2023 | SGF
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | 516938769528 | 20230327 | 1039 | 20230327 | 1149 | 2068559 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 560 | 35.4059 | -119.0281 | No | Clear;32-90 F | Fuse | Normal | 23-0052938 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830809 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1103 | 252461103 | TRANSFORMER | 516499876538 | 20230327 | 1340 | 20230327 | 1359 | 2068794 | 19 | Transformer only | Animal | Bird found | 2 | 38 | 35.5972 | -119.1779 | No | Clear;32-90 F | Bushing | Normal | 23-0053024 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830841 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | 515962074515 | 20230327 | 1544 | 20230327 | 1711 | 2069035 | 87 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 87 | 35.54 | -119.3586 | No | Clear;32-90 F | Fuse | Broken | 23-0053126 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830886 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 9681 | 20230327 | 2326 | 20230328 | 1058 | 2069445 | 692 | Distribution Circuit | 3rd Party | Vehicle | 27 | 18684 | 35.2378 | -118.9626 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0053214 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1830967 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1112 | 253491112 | FUSE | 7557 | 20230328 | 231 | 20230328 | 717 | 2069483 | 286 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2002 | 35.5139 | -119.0819 | No | Clear;32-90 F |  |  | 23-0053218 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1830972 | 0 | Non-EPSS | N | 2023
KERN | KERN | DEVILS DEN-1102 | 253451102 | TRANSFORMER | 514194581520 | 20230328 | 802 | 20230328 | 1222 | 2069616 | 260 | Transformer only | Animal | Other | 1 | 260 | 35.7243 | -119.9566 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0053552 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831180 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | RECLOSER | 931236 | 20230328 | 956 | 20230328 | 1324 | 2070067 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 12849 | 35.1084 | -119.3727 | No | Clear;32-90 F |  |  | 23-0053378 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831078 | 0 | EPSS Ckt | N | 2023 | GRD SGF
KERN | KERN | WEEDPATCH-1101 | 252971101 | TRANSFORMER | 517218861783 | 20230328 | 1102 | 20230328 | 1635 | 2070271 | 333 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 333 | 35.1941 | -118.9318 | No | Clear;32-90 F |  |  | 23-0053799 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831311 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OCB | 2104/2 | 20230328 | 1306 | 20230328 | 1548 | 2070620 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 753 | 106430 | 35.6018 | -119.5799 | No | Partly Cloudy;32-90 F |  |  | 23-0053600 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831206 | 0 | Non-EPSS | N | 2023 | AB INST OC
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13389 | 20230328 | 1451 | 20230328 | 1755 | 2070866 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1288 | 35.1793 | -118.9679 | No | Clear;32-90 F |  |  | 23-0053857 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831352 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1101 | 253371101 | TRANSFORMER | 517022569514 | 20230328 | 1840 | 20230329 | 534 | 2071298 | 654 | Transformer only | Vegetation | Tree - grew into line | 1 | 654 | 35.4058 | -118.9998 | No | Clear;32-90 F | Transformer | Broken | 23-0053897 | OH | Sus | 31640690 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831381 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 9973 | 20230328 | 2224 | 20230328 | 2320 | 2072159 | 56 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 99 | 5544 | 35.4048 | -118.9927 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0053975 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831453 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | TRANSFORMER | 517094873650 | 20230329 | 240 | 20230329 | 435 | 2072235 | 115 | Transformer only | Animal | Other | 2 | 230 | 35.52 | -118.9786 | No | Overcast-Rain;32-90 F | Fuse | Failed/Faulted | 23-0053988 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831470 | 0 | EPSS Ckt | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517035065856 | 20230329 | 642 | 20230329 | 1728 | 2072331 | 646 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 6460 | 35.3055 | -118.994 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 23-0054060 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831497 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | RECLOSER | 3776 | 20230329 | 711 | 20230329 | 1933 | 2072369 | 742 | Distribution Circuit | 3rd Party | Vehicle | 47 | 16922 | 35.1108 | -119.1095 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0054025 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1831478 | 0 | Non-EPSS | N | 2023 | AC-GRD
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515943056635 | 20230329 | 850 | 20230329 | 2130 | 2072541 | 760 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 760 | 35.0485 | -119.3558 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0054513 | OH | Sus | 31640709 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831679 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-1106 | 254071106 | FUSE | 14067 | 20230329 | 1038 | 20230329 | 1205 | 2072777 | 87 | Distribution Circuit | 3rd Party | Metallic Balloon | 30 | 2610 | 35.3282 | -119.0457 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0054326 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831615 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2103 | 255262103 | TRANSFORMER | T0944 | 20230329 | 1249 | 20230329 | 1942 | 2073072 | 413 | Distribution Circuit | Equipment Failure/Involved | Underground | 101 | 14740 | 35.3927 | -119.1204 | No | Partly Cloudy;32-90 F | Secondary | Arcing | 23-0054410 | UG | Sus | 45711404 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831649 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 15691 | 20230329 | 1839 | 20230329 | 2015 | 2073600 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1793 | 35.2075 | -119.0391 | No | Clear;32-90 F |  |  | 23-0054656 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831753 | 1 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 15691 | 20230329 | 2029 | 20230329 | 2046 | 2073712 | 17 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 317 | 35.2075 | -119.0391 | No | Clear;32-90 F |  |  | 23-0054732 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831820 | 1 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2101 | 254572101 | OTHER | T11999 TWD T12000 | 20230329 | 2043 | 20230329 | 2129 | 2073721 | 46 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 598 | 35.3749 | -119.1735 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Leaking | 23-0054654 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1831760 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 17506 | 20230329 | 2333 | 20230330 | 205 | 2073794 | 152 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 304 | 35.4122 | -119.0583 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Leaking | 23-0054708 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1831797 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 7100 | 20230330 | 634 | 20230330 | 826 | 2073868 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1456 | 35.4915 | -119.206 | No | Overcast-Fog;32-90 F |  |  | 23-0054791 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831846 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | 517379064137 | 20230330 | 714 | 20230330 | 922 | 2073886 | 128 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 128 | 35.2591 | -118.8785 | No | Clear;32-90 F |  |  | 23-0054850 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1831887 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516877467188 | 20230330 | 1105 | 20230330 | 1645 | 2074319 | 340 | Distribution Circuit | 3rd Party | Customer Equipment | 8 | 1844 | 35.3417 | -119.0477 | No | Overcast;32-90 F | Secondary | Broken- wire on ground | 23-0055018 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | Yes | 1831970 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1114 | 253491114 | OCB | 1114/2 | 20230330 | 1108 | 20230330 | 1335 | 2074323 | 147 | Distribution Circuit | Animal | Bird found | 37 | 4339 | 35.5004 | -119.1519 | No | Clear;32-90 F | Regulator | Burned/flashed | 23-0054944 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831943 | 0 | Non-EPSS | N | 2023 | A- B & PH OC TIME
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516844560730 | 20230330 | 1406 | 20230330 | 1643 | 2074543 | 157 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 157 | 35.1612 | -119.0567 | No | Overcast;32-90 F |  |  | 23-0055188 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1832009 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-2102 | 254762102 | SWITCH | 11442 | 20230330 | 2211 | 20230331 | 146 | 2074920 | 215 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 1666 | 35.3626 | -119.0722 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0055076 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1832077 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | T68386 | 20230331 | 1052 | 20230331 | 1440 | 2075370 | 228 | Transformer only | Equipment Failure/Involved | Underground | 1 | 228 | 35.0153 | -119.8567 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0055629 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1832246 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CUYAMA-2102 | 253142102 | FUSE | 18660 | 20230331 | 1831 | 20230401 | 946 | 2075772 | 915 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 11895 | 34.9398 | -119.5933 | No | Partly Cloudy;32-90 F | Anchor or Guy | Deteriorated | 23-0055680 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1832277 | 0 | EPSS Ckt | N | 2023
KERN | KERN | RIO BRAVO-1103 | 252861103 | TRANSFORMER | 516382171377 | 20230401 | 11 | 20230401 | 1330 | 2076398 | 799 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 799 | 35.4552 | -119.216 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055831 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832428 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1106 | 253951106 | FUSE | 8156 | 20230401 | 44 | 20230401 | 853 | 2076475 | 489 | Distribution Circuit | 3rd Party | Thrown Object | 4 | 1957 | 35.3975 | -118.9511 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0055817 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832407 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 14978 | 20230401 | 625 | 20230401 | 757 | 2076459 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 208 | 19136 | 35.3213 | -119.0211 | No | Clear;32-90 F |  |  | 23-0055808 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832401 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 9868 | 20230401 | 633 | 20230401 | 951 | 2076464 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 924 | 35.2377 | -118.995 | No | Clear;32-90 F |  |  | 23-0055837 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832448 | 1 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | RECLOSER | 56686 | 20230401 | 1334 | 20230402 | 719 | 2076758 | 1065 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 10577 | 35.5424 | -119.6191 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0055868 | OH | Sus | 45713900 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1832471 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | RIO BRAVO-1102 | 252861102 | RECLOSER | 1578 | 20230401 | 1549 | 20230401 | 1700 | 2076834 | 71 | Distribution Circuit | Equipment Failure/Involved | Overhead | 134 | 2902 | 35.4417 | -119.2592 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0055878 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1832474 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | STOCKDALE-2112 | 254072112 | FUSE | 86685 | 20230401 | 2135 | 20230402 | 1525 | 2077073 | 1070 | Distribution Circuit | 3rd Party | Vehicle | 10 | 10700 | 35.2958 | -119.0749 | No | Clear;32-90 F | Switch (UG) | Broken | 23-0055977 | UG | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1832572 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1116 | 253491116 | FUSE | 17117 | 20230401 | 2223 | 20230402 | 1415 | 2077070 | 952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3808 | 35.5299 | -119.1238 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0055978 | OH | Sus | 35435960 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832573 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | SWITCH | 169345 | 20230402 | 740 | 20230402 | 747 | 2077286 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 50 | 350 | 35.4995 | -119.6208 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0055868 | OH | Sus | 45713900 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1832594 | 0 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 513957380245 | 20230402 | 1028 | 20230402 | 1158 | 2077159 | 90 | Transformer only | Animal | Other | 2 | 180 | 35.6874 | -120.0368 | No | Clear;32-90 F | Transformer | Normal | 23-0056021 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832616 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | FUSE | 14923 | 20230403 | 648 | 20230403 | 1025 | 2077851 | 217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1302 | 34.8339 | -118.861 | No | Overcast;Below 32 F |  |  | 23-0056274 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832835 | 0 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 18448 | 20230403 | 1433 | 20230404 | 1215 | 2078524 | 1302 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 4482 | 35.6232 | -119.5092 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0056604 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1832993 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20230403 | 1522 | 20230403 | 2128 | 2078665 | 366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4555 | 442302 | 35.3885 | -119.0046 | No | Partly Cloudy-Strong Winds;32-90 F | Jumper | Burned Open | 23-0056469 | OH | Sus | 45714859 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832913 | 0 | Non-EPSS | N | 2023 | A B 50
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 4525 | 20230403 | 1548 | 20230404 | 451 | 2078747 | 783 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 12806 | 34.9716 | -118.9397 | No | Partly Cloudy-Strong Winds;32-90 F | Insulator | Broken | 23-0056487 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832921 | 0 | EPSS Ckt | N | 2023 | APH & G
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516240662409 | 20230403 | 1743 | 20230404 | 945 | 2079092 | 962 | Transformer only | Animal | Other | 1 | 962 | 35.2087 | -119.2597 | No | Partly Cloudy-Strong Winds;32-90 F | Transformer (OH) | Arcing | 23-0056595 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832989 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | RECLOSER | 3727 | 20230403 | 1758 | 20230404 | 100 | 2079156 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1897 | 148951 | 35.3673 | -118.9514 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0056572 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1832972 | 0 | Non-EPSS | N | 2023 | A PH
KERN | KERN | MAGUNDEN-1108 | 252771108 | TRANSFORMER | 517297967978 | 20230403 | 1823 | 20230403 | 1942 | 2079233 | 79 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 553 | 35.365 | -118.907 | No | Clear-Strong Winds;32-90 F |  |  | 23-0056628 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1833011 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516926367628 | 20230403 | 1849 | 20230403 | 2244 | 2078961 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 235 | 35.354 | -119.0317 | No | Strong Winds-Clear;32-90 F | Transformer | Arcing | 23-0056606 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832994 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 516975056500 | 20230404 | 720 | 20230405 | 230 | 2079561 | 1150 | Transformer only | Animal | Other | 1 | 1150 | 35.0507 | -119.0115 | No | Partly Cloudy-Strong Winds;Below 32 F | Transformer (OH) | Burned/flashed | 23-0057206 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833293 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2110 | 254072110 | SWITCH | 834283 | 20230404 | 846 | 20230404 | 937 | 2079670 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 1632 | 35.3553 | -119.0485 | No | Clear-Strong Winds;32-90 F | Secondary | Broken | 23-0056800 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1833141 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 14559 | 20230404 | 849 | 20230404 | 1017 | 2079686 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 704 | 35.5093 | -119.2692 | No | Clear;32-90 F |  |  | 23-0056862 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833209 | 1 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517227263639 | 20230404 | 1248 | 20230404 | 1838 | 2079989 | 350 | Transformer only | Animal | Other | 1 | 350 | 35.2452 | -118.9296 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0057204 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833291 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1102 | 253181102 | FUSE | 15989 | 20230404 | 1306 | 20230404 | 1410 | 2080004 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 64 | 35.6886 | -119.3572 | No | Clear;32-90 F |  |  | 23-0057100 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833260 | 1 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1104 | 254541104 | JUMPER | 7285 | 20230404 | 1408 | 20230404 | 1913 | 2080073 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3280 | 35.4569 | -119.4382 | No | Clear;32-90 F | Jumper | Burned Open | 23-0057159 | OH | Sus | 45715565 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833273 | 1 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1103 | 253801103 | OTHER | 18537 | 20230404 | 2111 | 20230405 | 100 | 2080318 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 88 | 35.1498 | -118.8961 | No | Clear;32-90 F |  |  | 23-0057220 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833305 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1103 | 253951103 | FUSE | 9456 | 20230405 | 145 | 20230406 | 18 | 2080353 | 1353 | Distribution Circuit | Equipment Failure/Involved | Underground | 216 | 81305 | 35.4054 | -118.9436 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0057245 | UG | Sus | 45715576 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833330 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | 517242264432 | 20230405 | 725 | 20230405 | 1058 | 2080443 | 213 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 852 | 35.2664 | -118.9244 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0057451 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833489 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | SWITCH | 6548 | 20230405 | 740 | 20230405 | 909 | 2080460 | 31 | Distribution Circuit | Company Initiated | Return Circuit Normal | 43 | 1068 | 35.3133 | -119.0092 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0032590 | UG | Sus | 35411296 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1833358 | 0 | Non-EPSS | N | 2023
KERN | KERN | DEVILS DEN-1102 | 253451102 | TRANSFORMER | 514357881721 | 20230405 | 836 | 20230405 | 1017 | 2080526 | 101 | Transformer only | Vegetation | Other ground vegetation | 1 | 101 | 35.7308 | -119.9015 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 23-0057412 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833476 | 0 | EPSS Ckt | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | RECLOSER | 38252 | 20230405 | 1047 | 20230405 | 1935 | 2080722 | 528 | Distribution Circuit | 3rd Party | Vehicle | 460 | 33926 | 35.2737 | -119.0029 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0057443 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1833486 | 0 | Non-EPSS | N | 2023 | ACG INST
KERN | KERN | GOOSE LAKE-1103 | 254201103 | JUMPER | BLOWN JUMPERS 7 E/OF L123 | 20230405 | 1109 | 20230405 | 1407 | 2080744 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 146 | 1338 | 35.5573 | -119.6026 | No | Clear;32-90 F | Jumper | Burned Open | 23-0057562 | OH | Sus | 45716351 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1833524 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1104 | 253951104 | FUSE | 17623 | 20230405 | 1330 | 20230405 | 1530 | 2080894 | 120 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 120 | 35.3867 | -118.9661 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0057569 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1833526 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 100000004212 | 20230405 | 1724 | 20230405 | 1745 | 2080985 | 21 | Transformer only | Animal | Bird found | 1 | 21 | 35.1229 | -119.1634 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0057693 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833560 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 13021 | 20230405 | 1949 | 20230405 | 2140 | 2081154 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 777 | 35.3541 | -119.1898 | No | Clear;32-90 F |  |  | 23-0057712 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1833574 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 8693 | 20230406 | 402 | 20230406 | 951 | s1833775 | 349 | Distribution Circuit | Animal | Other | 10 | 3490 | 35.2253 | -119.2078 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0057870 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1833775 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516652063727 | 20230406 | 1406 | 20230406 | 1448 | 2081907 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 42 | 35.2458 | -119.1213 | No | Clear;32-90 F | Fuse | Broken | 23-0058114 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833846 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | TRANSFORMER | 515625879437 | 20230406 | 1649 | 20230406 | 1929 | 2082055 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 160 | 35.674 | -119.4734 | No | Clear;32-90 F | Fuse | Broken | 23-0058184 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833870 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1112 | 253651112 | FUSE | 7358 | 20230406 | 1840 | 20230406 | 2136 | 2082112 | 176 | Distribution Circuit | 3rd Party | Vehicle | 13 | 2288 | 35.5286 | -119.4032 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0058176 | OH | Sus | 31641512 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1833864 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 15209 | 20230406 | 2150 | 20230407 | 111 | 2082178 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 402 | 34.9849 | -118.9307 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0058201 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1833888 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 16960 | 20230407 | 1301 | 20230407 | 1425 | 2082696 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 168 | 35.2962 | -118.9098 | No | Clear;32-90 F |  |  | 23-0058616 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834099 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1104 | 253191104 | JUMPER | OJ 1 E/OF CGC#517321558360 | 20230407 | 1721 | 20230408 | 850 | 2082966 | 929 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2787 | 35.1005 | -118.896 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0058721 | OH | Sus | 45719313 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1834159 | 1 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516605362170 | 20230408 | 1004 | 20230408 | 1127 | 2083162 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 83 | 35.2032 | -119.1373 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0058753 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834214 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 517252665492 | 20230408 | 2021 | 20230408 | 2202 | 2083445 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 404 | 35.2961 | -118.9217 | No | Clear;32-90 F |  |  | 23-0058823 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834272 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 7469 | 20230409 | 707 | 20230409 | 835 | 2083553 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2054 | 35.7188 | -119.3302 | No | Clear;32-90 F |  |  | 23-0058853 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834302 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2108 | 254072108 | RECLOSER | 4267 | 20230409 | 920 | 20230409 | 1815 | 2083602 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 810 | 128004 | 35.3182 | -119.0974 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0058856 | OH | Sus | 45719861 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834305 | 0 | Non-EPSS | N | 2023 | B-GRD
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OCB | 2104/2 | 20230409 | 1649 | 20230409 | 1838 | 2083790 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 751 | 81859 | 35.6018 | -119.5799 | No | Clear;32-90 F |  |  | 23-0058897 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834347 | 0 | Non-EPSS | N | 2023 | A
KERN | KERN | TEVIS-2105 | 255322105 | RECLOSER | 4116 | 20230409 | 1928 | 20230410 | 1346 | 2083889 | 1098 | Distribution Circuit | Equipment Failure/Involved | Underground | 1633 | 55729 | 35.3254 | -119.1083 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0058900 | UG | Sus | 45719818 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834349 | 0 | Non-EPSS | N | 2023 | A-GRD
KERN | KERN | TUPMAN-1106 | 254561106 | OCB | 1106/2 | 20230410 | 224 | 20230410 | 357 | 2083995 | 93 | Distribution Circuit | 3rd Party | Vehicle | 150 | 13950 | 35.3531 | -119.2709 | No | Clear;32-90 F | Jumper | Broken | 23-0058928 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834381 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 17089 | 20230410 | 1249 | 20230411 | 1320 | 2084535 | 96 | Distribution Circuit | Animal | Other | 2 | 192 | 35.4422 | -119.4381 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0059206 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834598 | 1 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1110 | 252901110 | RECLOSER | 37810 | 20230410 | 1852 | 20230411 | 1208 | 2084851 | 1036 | Distribution Circuit | 3rd Party | Vehicle | 7 | 7252 | 35.604 | -119.4025 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0059273 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1834633 | 0 | Non-EPSS | N | 2023 | C- GRD
KERN | KERN | COLUMBUS-1109 | 253951109 | TRANSFORMER | 517209768920 | 20230410 | 2003 | 20230411 | 1234 | 2084856 | 991 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1982 | 35.3903 | -118.9368 | No | Clear;32-90 F | Secondary | Burned/flashed | 23-0059316 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834651 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1101 | 253371101 | TRANSFORMER | 517011469209 | 20230410 | 2019 | 20230411 | 353 | 2084904 | 454 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 454 | 35.3974 | -119.0032 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0059340 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834665 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T13414 TWD T13415 | 20230410 | 2202 | 20230410 | 2346 | 2084937 | 104 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 1872 | 35.3973 | -119.177 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0059202 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834676 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | JUMPER | WIRE DOWN EAST PHASE | 20230411 | 10 | 20230411 | 1145 | 2084976 | 695 | Distribution Circuit | 3rd Party | Vehicle | 13 | 8978 | 35.4861 | -119.2062 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0059381 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | Yes | No | 1834689 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | FUSE | 7331 | 20230411 | 1752 | 20230412 | 956 | 2085941 | 205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 776 | 35.6311 | -119.2052 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0059803 | OH | Sus | 45726919 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1834966 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | 516931369560 | 20230411 | 2205 | 20230411 | 2216 | 2086058 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 22 | 35.4069 | -119.0305 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0059837 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834999 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1102 | 254501102 | TRANSFORMER | 516103778324 | 20230412 | 825 | 20230412 | 1548 | 2086288 | 443 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 443 | 35.6452 | -119.3126 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0060279 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835266 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 517163059962 | 20230412 | 901 | 20230412 | 1035 | 2086366 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 94 | 35.1438 | -118.9501 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0060061 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835202 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1104 | 253551104 | TRANSFORMER | 515709783178 | 20230412 | 949 | 20230412 | 1542 | 2086493 | 353 | Transformer only | Animal | Other | 1 | 353 | 35.7769 | -119.4464 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0060310 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835277 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1105 | 252461105 | FUSE | 7209 | 20230412 | 1002 | 20230413 | 1215 | 2086514 | 1573 | Distribution Circuit | 3rd Party | Vehicle | 3 | 4719 | 35.5876 | -119.2035 | No | Partly Cloudy;32-90 F | Crossarm- Steel | Broken | 23-0060346 | OH | Sus | 31641995 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835283 | 0 | Non-EPSS | N | 2023
KERN | KERN | DEVILS DEN-1102 | 253451102 | TRANSFORMER | 100000031960 | 20230412 | 1224 | 20230412 | 1729 | 2086684 | 305 | Transformer only | Animal | Other | 1 | 305 | 35.7139 | -119.9567 | No | Partly Cloudy;32-90 F | Transformer (OH) |  | 23-0060362 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835286 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SAN BERNARD-1101 | 253191101 | OCB | 1101/2 | 20230413 | 715 | 20230413 | 805 | 2087270 | 50 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 85 | 4250 | 35.0921 | -118.878 | No | Partly Cloudy;32-90 F |  |  | 23-0060488 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1835378 | 0 | EPSS Ckt | N | 2023 | A- B- C- 51RLY
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 516069668360 | 20230413 | 805 | 20230413 | 1229 | 2087319 | 264 | Transformer only | Animal | Other | 1 | 264 | 35.371 | -119.3191 | No | Clear;32-90 F | Other | Contaminated | 23-0060667 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835563 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | T7459 | 20230413 | 851 | 20230413 | 1236 | 2087416 | 225 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 3250 | 35.3961 | -119.1508 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0060565 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835511 | 0 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1102 | 253801102 | TRANSFORMER | 517291060720 | 20230413 | 1556 | 20230413 | 1913 | 2087884 | 197 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 197 | 35.1656 | -118.9053 | No | Clear;32-90 F |  |  | 23-0060888 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1835629 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 16247 | 20230413 | 1755 | 20230413 | 1848 | 2087971 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1060 | 35.3986 | -119.4831 | No | Clear;32-90 F |  |  | 23-0060867 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835617 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1101 | 252971101 | RECLOSER | 4574 | 20230413 | 2138 | 20230414 | 1018 | 2088112 | 760 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 15337 | 35.2087 | -118.8811 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0060908 | OH | Sus | 45729924 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1835649 | 0 | Non-EPSS | N | 2023 | A GRD
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 516069668360 | 20230414 | 657 | 20230414 | 933 | 2088257 | 156 | Transformer only | Animal | Other | 1 | 156 | 35.371 | -119.3191 | No | Clear;32-90 F | Jumper | Contaminated | 23-0061067 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835845 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | JUMPER | WIRE DOWN 1 SP S/OF CGC #516832962883 | 20230414 | 950 | 20230414 | 1545 | 2088510 | 355 | Distribution Circuit | Animal | Bird found | 459 | 3345 | 35.2234 | -119.0607 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0061096 | OH | Sus | 31642367 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | Yes | No | 1835864 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515975358552 | 20230414 | 1236 | 20230414 | 1414 | 2088693 | 98 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 98 | 35.1012 | -119.3467 | No | Clear;32-90 F |  |  | 23-0061205 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1835904 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRANSFORMER | 513858172670 | 20230414 | 1303 | 20230414 | 1818 | 2088711 | 315 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 315 | 35.4793 | -120.0635 | No | Clear;32-90 F | Fuse | Burned Open | 23-0061270 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835926 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WEEDPATCH-1101 | 252971101 | RECLOSER | 4574 | 20230414 | 1602 | 20230414 | 1740 | 2088862 | 98 | Distribution Circuit | 3rd Party | Vehicle | 55 | 5390 | 35.2087 | -118.8811 | No | Clear;32-90 F | Anchor or Guy | Bent or Twisted | 23-0061241 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835915 | 0 | Non-EPSS | N | 2023 | B C
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 15560 | 20230415 | 218 | 20230415 | 1200 | 2089016 | 582 | Distribution Circuit | 3rd Party | Vehicle | 193 | 34116 | 35.3699 | -118.9854 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0061300 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835955 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | RECLOSER | 4550 | 20230415 | 246 | 20230415 | 2004 | 2089035 | 1038 | Distribution Circuit | 3rd Party | Vehicle | 1 | 1038 | 35.7078 | -119.4371 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0061301 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1835957 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | 7TH STANDARD-2103 | 254582103 | FUSE | 18866 | 20230415 | 1526 | 20230415 | 1728 | 2089327 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2196 | 35.4415 | -119.0916 | No | Clear;32-90 F |  |  | 23-0061387 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836070 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | FUSE | 39130 | 20230416 | 957 | 20230416 | 1425 | 2089714 | 268 | Distribution Circuit | Animal | Other | 2 | 536 | 35.5022 | -119.5439 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Burned/flashed | 23-0061470 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836171 | 1 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1103 | 253651103 | FUSE | 14588 | 20230416 | 1752 | 20230416 | 1928 | 2089773 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 384 | 35.5726 | -119.2938 | No | Clear;32-90 F |  |  | 23-0061499 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836187 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | RECLOSER | 47676 | 20230417 | 701 | 20230417 | 843 | 2089971 | 102 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 102 | 35.3174 | -118.9897 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0061540 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1836235 | 0 | Non-EPSS | N | 2023 | b- c & grd
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 15855 | 20230417 | 1143 | 20230417 | 1230 | 2090441 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 137 | 6439 | 35.3727 | -118.9585 | No | Clear;32-90 F |  |  | 23-0061685 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836424 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 53612 | 20230417 | 1501 | 20230417 | 1558 | 2090681 | 57 | Distribution Circuit | Animal | Bird found | 1 | 57 | 35.3404 | -119.3679 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0061771 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836474 | 0 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1103 | 253801103 | FUSE | 13096 | 20230418 | 1040 | 20230419 | 230 | 2091448 | 950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3800 | 35.1371 | -118.9324 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0062045 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836733 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 14334 | 20230418 | 1210 | 20230418 | 1320 | 2091523 | 70 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 140 | 35.4924 | -119.179 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 23-0062059 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836741 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13341 | 20230418 | 1226 | 20230418 | 1410 | 2091536 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 312 | 35.0473 | -119.0115 | No | Partly Cloudy;32-90 F |  |  | 23-0062166 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836773 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | OTHER | J4415 TWD T24521 | 20230418 | 1506 | 20230418 | 1535 | 2091605 | 29 | Distribution Circuit | 3rd Party | Vandalism | 1 | 29 | 35.3786 | -119.0109 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0062192 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836777 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1104 | 253551104 | TRANSFORMER | 515233383719 | 20230418 | 1508 | 20230419 | 1534 | 2091691 | 1466 | Transformer only | Animal | Other | 1 | 1466 | 35.7896 | -119.6077 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0062205 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836782 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1106 | 252771106 | RECLOSER | 199938 | 20230418 | 1722 | 20230418 | 1835 | 2091783 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1262 | 88340 | 35.3834 | -118.9363 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 23-0062239 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1836796 | 1 | Non-EPSS | N | 2023 | N/A
KERN | KERN | GOOSE LAKE-1103 | 254201103 | SWITCH | 343947 | 20230418 | 2123 | 20230418 | 2229 | 2091905 | 66 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 5 | 330 | 35.5291 | -119.621 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 23-0062255 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836810 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | TRANSFORMER | 516357979248 | 20230419 | 1921 | 20230420 | 335 | 2092804 | 494 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4446 | 35.6712 | -119.2272 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0062715 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837100 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515711368123 | 20230420 | 754 | 20230420 | 1446 | 2092910 | 412 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 412 | 35.3633 | -119.439 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0063109 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837282 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 100000017937 | 20230420 | 1047 | 20230420 | 1412 | 2093100 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 205 | 35.5778 | -119.6133 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0062918 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837236 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1103 | 252461103 | FUSE | 128957 | 20230420 | 1624 | 20230421 | 833 | 2093327 | 969 | Distribution Circuit | 3rd Party | Other | 2 | 1938 | 35.595 | -119.115 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0063203 | OH | Sus | 45737389 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837300 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | T7008 | 20230421 | 732 | 20230421 | 1750 | 2093505 | 618 | Transformer only | Equipment Failure/Involved | Underground | 8 | 4944 | 35.2586 | -118.9189 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0063445 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837537 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARNERAS-1103 | 252321103 | TRANSFORMER | 514510472632 | 20230421 | 1318 | 20230421 | 2118 | 2093979 | 480 | Transformer only | Animal | Bird found | 1 | 480 | 35.4822 | -119.8455 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0063658 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837628 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MIDWAY-1103 | 252611103 | TRANSFORMER | 515768369920 | 20230421 | 1334 | 20230422 | 1410 | 2093995 | 1476 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1476 | 35.4128 | -119.421 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0063693 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837662 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1103 | 253651103 | RECLOSER | 1195 | 20230422 | 238 | 20230422 | 1156 | 2094393 | 558 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2790 | 35.529 | -119.3313 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0063701 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1837671 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | STOCKDALE-1110 | 254071110 | FUSE | 99370 | 20230423 | 521 | 20230424 | 449 | 2094908 | 1408 | Distribution Circuit | Equipment Failure/Involved | Underground | 284 | 291041 | 35.3218 | -119.0391 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0063811 | UG | Sus | 35439343 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837839 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1101 | 253191101 | OCB | 1101/2 | 20230423 | 839 | 20230423 | 1455 | 2094969 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 9736 | 35.0921 | -118.878 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0063824 | OH | Sus | 45739101 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1837854 | 0 | EPSS Ckt | N | 2023 | A- B- C- 51RLY
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 16471 | 20230423 | 1048 | 20230423 | 1244 | 2095009 | 116 | Distribution Circuit | Animal | Bird found | 259 | 30044 | 35.3179 | -119.1402 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0063851 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837878 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | RECLOSER | 4401 | 20230423 | 1949 | 20230423 | 2030 | 2095167 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2686 | 110126 | 35.3395 | -119.1281 | No | Clear;32-90 F |  |  | 23-0063880 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837902 | 0 | Non-EPSS | N | 2023 | BC
KERN | KERN | RIO BRAVO-1103 | 252861103 | TRANSFORMER | 516407771087 | 20230423 | 2050 | 20230424 | 905 | 2095201 | 735 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 735 | 35.4476 | -119.2071 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0063886 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837909 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | OTHER | 122865 | 20230424 | 1046 | 20230424 | 1450 | 2095608 | 244 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1464 | 35.34 | -119.1496 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0064040 | OH | Sus | 31643064 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | Yes | Yes | 1838104 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 16027 | 20230424 | 1136 | 20230424 | 1437 | 2095673 | 181 | Distribution Circuit | 3rd Party | Vehicle | 5 | 905 | 35.5794 | -119.4742 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 23-0064110 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1838146 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARNERAS-1102 | 252321102 | RECLOSER | 573054 | 20230424 | 1401 | 20230425 | 717 | 2095838 | 1036 | Distribution Circuit | 3rd Party | Vehicle | 9 | 5837 | 35.5736 | -119.6899 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0064160 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1838162 | 0 | Non-EPSS | N | 2023 | A & C
KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | 517342849954 | 20230425 | 625 | 20230425 | 1244 | 2096211 | 379 | Transformer only | 3rd Party | Vehicle | 1 | 379 | 34.869 | -118.8858 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 23-0064311 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1838244 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | T468900 | 20230425 | 1023 | 20230425 | 1222 | 2096534 | 119 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 119 | 35.6221 | -119.0785 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0064510 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838432 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1103 | 252611103 | TRANSFORMER | 515821771074 | 20230425 | 1114 | 20230425 | 1816 | 2096594 | 422 | Transformer only | Animal | Other | 1 | 422 | 35.4448 | -119.4036 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 23-0064701 | OH | Sus | 31642995 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838503 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1102 | 252861102 | TRANSFORMER | 516301870672 | 20230425 | 1210 | 20230425 | 1218 | 2096668 | 8 | Transformer only | Animal | Other | 1 | 8 | 35.4355 | -119.2422 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0064501 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1838428 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 14184 | 20230425 | 1319 | 20230425 | 1417 | 2096760 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 290 | 35.3561 | -118.9408 | No | Clear;32-90 F |  |  | 23-0064600 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838472 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1103 | 252461103 | RECLOSER | 3652 | 20230425 | 1405 | 20230426 | 1023 | 2096820 | 1218 | Distribution Circuit | 3rd Party | Vehicle | 158 | 45491 | 35.6023 | -119.1425 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0064586 | OH | Sus | 35439739 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1838466 | 0 | Non-EPSS | N | 2023 | A B & C
KERN | KERN | WASCO-1104 | 252961104 | FUSE | 16002 | 20230425 | 2010 | 20230425 | 2116 | 2097078 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 133 | 8778 | 35.5907 | -119.3448 | No | Clear;32-90 F |  |  | 23-0064724 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838522 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1101 | 253371101 | TRANSFORMER | 517031969266 | 20230425 | 2012 | 20230425 | 2217 | 2097076 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1625 | 35.3991 | -118.9964 | No | Clear;32-90 F | Secondary | Together | 23-0064713 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838514 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1102 | 252861102 | TRANSFORMER | 516194872918 | 20230426 | 1010 | 20230426 | 1136 | 2097444 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 1548 | 35.4967 | -119.2789 | No | Clear;32-90 F | Fuse | Broken | 23-0064957 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838738 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1112 | 252901112 | TRANSFORMER | 100000038763 | 20230426 | 1102 | 20230427 | 1300 | 2097503 | 1558 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1558 | 35.6342 | -119.4733 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0064969 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838743 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | 515456773225 | 20230426 | 1416 | 20230426 | 1520 | 2097666 | 64 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 64 | 35.5012 | -119.5428 | No | Clear;32-90 F |  |  | 23-0065128 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1838785 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1114 | 253491114 | OCB | 1114/2 | 20230426 | 1629 | 20230427 | 816 | 2097771 | 947 | Distribution Circuit | 3rd Party | Vehicle | 37 | 8282 | 35.5004 | -119.1519 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0065180 | OH | Sus | 35440042 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1838797 | 0 | Non-EPSS | N | 2023 | A- B- PH OC INST
KERN | KERN | LERDO-1116 | 253491116 | TRANSFORMER | 516672676295 | 20230426 | 1946 | 20230427 | 1058 | 2097728 | 912 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 912 | 35.5913 | -119.1202 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0065204 | OH | Sus | 45742146 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838810 | 0 | Non-EPSS | N | 2023
KERN | KERN | FELLOWS-2104 | 254242104 | FUSE | 9132 | 20230427 | 725 | 20230427 | 1012 | 2098073 | 167 | Distribution Circuit | Animal | Other | 113 | 503 | 35.1946 | -119.5422 | No | Clear;32-90 F | Fuse | Burned Open | 23-0065424 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838995 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1105 | 253911105 | TRANSFORMER | 517489563855 | 20230427 | 1146 | 20230428 | 1300 | 2098418 | 1514 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4542 | 35.2515 | -118.8451 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0065632 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839057 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2101 | 254572101 | OCB | 2101/2 | 20230427 | 1349 | 20230428 | 523 | 2098538 | 934 | Distribution Circuit | 3rd Party | Vehicle | 1674 | 270344 | 35.3871 | -119.1644 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0065621 | OH | Sus | 35440360 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1839054 | 0 | Non-EPSS | N | 2023 | A-B- C- PH OC TIME
KERN | KERN | 7TH STANDARD-2101 | 254582101 | TRANSFORMER | T661776 | 20230427 | 1553 | 20230428 | 925 | 2098657 | 1052 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 26618 | 35.4507 | -119.107 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0065765 | UG | Sus | 35440119 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839123 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1105 | 253181105 | OCB | 1105/2 | 20230427 | 1715 | 20230428 | 633 | 2098744 | 798 | Distribution Circuit | 3rd Party | Vehicle | 116 | 63728 | 35.6882 | -119.2768 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 23-0065720 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1839082 | 0 | Non-EPSS | N | 2023 | A- B- G- PH OC TIME
KERN | KERN | SAN BERNARD-1101 | 253191101 | OCB | 1101/2 | 20230428 | 855 | 20230428 | 2103 | 2099159 | 728 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 34178 | 35.0921 | -118.878 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0065919 | OH | Sus | 31643529 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1839250 | 0 | EPSS Ckt | N | 2023 | ABC PH OC TIME
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 16924 | 20230428 | 1216 | 20230428 | 2019 | 2099376 | 483 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 966 | 35.4237 | -119.2876 | No | Clear;32-90 F |  |  | 23-0066178 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839385 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-2102 | 254762102 | TRANSFORMER | T4638 | 20230428 | 1405 | 20230429 | 1220 | 2099480 | 1335 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1335 | 35.3623 | -119.0623 | No | Clear;Above 90 |  |  | 23-0066139 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1839356 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517085268688 | 20230428 | 1628 | 20230428 | 1809 | 2099619 | 101 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 101 | 35.3835 | -118.9787 | No | Clear;Above 90 | Fuse | Broken | 23-0066161 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839371 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1103 | 252081103 | TRANSFORMER | 515666960565 | 20230429 | 1331 | 20230429 | 1529 | 2100111 | 118 | Transformer only | Unknown Cause | Patrol - found nothing | 22 | 2596 | 35.1554 | -119.4506 | No | Clear;Above 90 |  |  | 23-0066313 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1839538 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2101 | 255322101 | RECLOSER | 4690 | 20230429 | 2140 | 20230430 | 210 | 2100298 | 204 | Distribution Circuit | 3rd Party | Vehicle | 2168 | 426314 | 35.2974 | -119.1283 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0066348 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1839565 | 0 | Non-EPSS | N | 2023 | A GRD
KERN | KERN | PANAMA-2102 | 253422102 | RECLOSER | 1689 | 20230430 | 239 | 20230430 | 246 | 2100314 | 7 | Distribution Circuit | 3rd Party | Metallic Balloon | 1727 | 12089 | 35.3028 | -119.0029 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0066371 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839590 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | BAKERSFIELD-2109 | 253372109 | RECLOSER | 4129 | 20230430 | 1310 | 20230501 | 47 | 2100574 | 697 | Distribution Circuit | 3rd Party | Vehicle | 3370 | 226822 | 35.351 | -119.0084 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0066435 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1839656 | 0 | Non-EPSS | N | 2023 | B & GRD
KERN | KERN | STOCKDALE-2113 | 254072113 | TRIP-SAVER | 17747 | 20230430 | 1809 | 20230430 | 2104 | 2100905 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 199 | 34825 | 35.3321 | -119.0133 | No | Clear;32-90 F |  |  | 23-0066475 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839692 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 20151 | 20230501 | 142 | 20230501 | 426 | 2101071 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1313 | 35.4475 | -118.9044 | No | Clear;32-90 F |  |  | 23-0066517 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1839727 | 1 | EPSS Ckt | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516870661817 | 20230501 | 1024 | 20230501 | 1200 | 2101437 | 96 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 192 | 35.1941 | -119.048 | No | Clear;32-90 F |  |  | 23-0066661 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1839900 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1112 | 253491112 | TRANSFORMER | 516580272958 | 20230501 | 1057 | 20230501 | 1530 | 2101471 | 273 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 546 | 35.4992 | -119.1506 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0066639 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1839880 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARNERAS-1102 | 252321102 | OCB | 1102/2 | 20230501 | 1109 | 20230501 | 1115 | 2101487 | 6 | Distribution Circuit | Animal | Bird found | 14 | 84 | 35.5409 | -119.8047 | No | Partly Cloudy;32-90 F | Insulator | Burned/flashed | 23-0066640 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1839882 | 0 | Non-EPSS | N | 2023 | B C
KERN | KERN | ARVIN-1103 | 253801103 | TRANSFORMER | 517202559948 | 20230501 | 1120 | 20230501 | 1509 | 2101508 | 229 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 229 | 35.1437 | -118.9371 | No | Clear;32-90 F |  |  | 23-0066728 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1839925 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516923761005 | 20230501 | 1520 | 20230501 | 2257 | 2101793 | 457 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 457 | 35.1718 | -119.0305 | No | Clear;32-90 F |  |  | 23-0066868 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1839998 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7346 | 20230501 | 1541 | 20230501 | 2348 | 2101840 | 487 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1948 | 35.5721 | -119.5114 | No | Clear;32-90 F |  |  | 23-0066875 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840005 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARNERAS-1102 | 252321102 | RECLOSER | 3266 | 20230501 | 1650 | 20230501 | 2225 | 2101891 | 335 | Distribution Circuit | Animal | Bird found | 1 | 335 | 35.5372 | -119.803 | No | Clear-Strong Winds;32-90 F | Insulator | Burned/flashed | 23-0066823 | OH | Sus | 31643732 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1839957 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | ARVIN-1101 | 253801101 | RECLOSER | 53388 | 20230501 | 2327 | 20230502 | 1201 | 2102045 | 754 | Distribution Circuit | 3rd Party | Vehicle | 23 | 2822 | 35.1497 | -118.8507 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0066873 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840003 | 0 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | PANAMA-2102 | 253422102 | OTHER | J2209 TWD T13465 | 20230502 | 45 | 20230502 | 149 | 2102064 | 64 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 2240 | 35.2941 | -118.9979 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0066829 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840010 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | FUSE | 9138 | 20230502 | 1340 | 20230503 | 441 | 2102938 | 901 | Distribution Circuit | 3rd Party | Vehicle | 12 | 10812 | 35.18 | -119.1992 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0067279 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1840246 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1103 | 254561103 | SWITCH | 689329 | 20230502 | 1750 | 20230502 | 1831 | 2103192 | 41 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1 | 41 | 35.3783 | -119.2255 | No | Clear;32-90 F | Secondary | Broken | 23-0067366 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840276 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1101 | 253191101 | TRANSFORMER | 517549757271 | 20230503 | 910 | 20230504 | 840 | 2103527 | 1410 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1410 | 35.071 | -118.8201 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067629 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840500 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ARVIN-1101 | 253801101 | TRANSFORMER | 517539961501 | 20230503 | 1142 | 20230504 | 2015 | 2103801 | 1953 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1953 | 35.1872 | -118.824 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0067736 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840547 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | RECLOSER | 286542 | 20230503 | 1412 | 20230504 | 1200 | 2103925 | 1308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4542 | 35.0224 | -118.7703 | No | Partly Cloudy;32-90 F | Jumper | Broken | 23-0067751 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840551 | 0 | EPSS Ckt | N | 2023 | B C
KERN | KERN | TEVIS-2102 | 255322102 | TRANSFORMER | T7529 | 20230503 | 1455 | 20230504 | 1624 | 2103872 | 1529 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 13267 | 35.3353 | -119.1222 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0067782 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840557 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516870661817 | 20230503 | 1531 | 20230503 | 1851 | 2103992 | 200 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 400 | 35.1941 | -119.048 | No | Clear;32-90 F |  |  | 23-0067830 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1840577 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | JUMPER | 77437 | 20230503 | 1631 | 20230503 | 1927 | 2104033 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 5456 | 35.2379 | -119.0833 | No | Clear;32-90 F | Jumper | Broken | 23-0067835 | OH | Sus | 45748278 | CENTRAL VALLEY | MAY | Open Circuit | 0 | No | No | No | 1840579 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRIP-SAVER | 13071 | 20230503 | 1853 | 20230504 | 40 | 2104120 | 347 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 168 | 58296 | 35.3024 | -119.0028 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 23-0067853 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840586 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | BAKERSFIELD-1118 | 253371118 | RECLOSER | 3338 | 20230503 | 1954 | 20230504 | 251 | 2104149 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1124 | 102512 | 35.405 | -119.0199 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0067857 | OH | Sus | 45748441 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1840589 | 0 | Non-EPSS | N | 2023 | A/B/C
KERN | KERN | GOOSE LAKE-1106 | 254201106 | TRANSFORMER | 515570778391 | 20230503 | 2335 | 20230505 | 1119 | 2104219 | 2144 | Transformer only | Animal | Other | 1 | 2144 | 35.6449 | -119.4917 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 23-0067920 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840631 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | OCB | 2105/2 | 20230504 | 2 | 20230504 | 353 | 2104253 | 231 | Distribution Circuit | Animal | Other | 159 | 29737 | 35.7305 | -119.8581 | No | Overcast-Drizzle;32-90 F | Recloser | Burned/flashed | 23-0067923 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | No | No | 1840634 | 0 | Non-EPSS | N | 2023 | BCG TIME
KERN | KERN | GOOSE LAKE-1106 | 254201106 | TRANSFORMER | 515596078393 | 20230504 | 4 | 20230505 | 1345 | 2104220 | 2261 | Transformer only | Animal | Other | 1 | 2261 | 35.6449 | -119.4825 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 23-0067928 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840638 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | RECLOSER | 122328 | 20230504 | 7 | 20230504 | 248 | 2104255 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 18354 | 35.7029 | -119.4911 | No | Overcast;32-90 F |  |  | 23-0067925 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | No | No | 1840636 | 0 | Non-EPSS | N | 2023 | BCG
KERN | KERN | MIDWAY-1101 | 252611101 | RECLOSER | 1470 | 20230504 | 102 | 20230504 | 1554 | 2104272 | 892 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 43 | 22519 | 35.4417 | -119.5463 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0067937 | OH | Sus | 35441510 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1840645 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 108849 | 20230504 | 118 | 20230505 | 12 | 2104397 | 1374 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 8 | 10992 | 35.6878 | -119.4908 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0068045 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1840774 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | FUSE | 18477 | 20230504 | 218 | 20230504 | 755 | 2104282 | 337 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2248 | 35.0616 | -119.3491 | No | Overcast;32-90 F |  |  | 23-0068008 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840696 | 1 | EPSS Ckt | N | 2023
KERN | KERN | TEVIS-2101 | 255322101 | RECLOSER | 1515 | 20230504 | 236 | 20230504 | 1041 | 2104284 | 485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 15520 | 35.2955 | -119.1636 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0067944 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840652 | 0 | Non-EPSS | N | 2023 | BC
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 166285 | 20230504 | 300 | 20230504 | 1020 | 2104292 | 440 | Distribution Circuit | Animal | Other | 2 | 880 | 35.3694 | -119.3756 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0068085 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840816 | 0 | Non-EPSS | N | 2023
KERN | KERN | ELK HILLS-1106 | 252441106 | TRANSFORMER | 516314164023 | 20230504 | 301 | 20230504 | 1540 | 2104932 | 759 | Transformer only | Animal | Other | 1 | 759 | 35.2528 | -119.2355 | No | Clear;32-90 F | Fuse | Burned Open | 23-0068407 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840909 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514829280625 | 20230504 | 307 | 20230504 | 1446 | 2104533 | 699 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 699 | 35.703 | -119.7432 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0068347 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840891 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16181 | 20230504 | 309 | 20230504 | 1008 | 2104294 | 419 | Distribution Circuit | Animal | Other | 6 | 2514 | 35.0943 | -119.1542 | No | Clear;32-90 F | Fuse | Burned Open | 23-0068029 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840745 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | FUSE | 8705 | 20230504 | 318 | 20230504 | 1037 | 2104310 | 439 | Distribution Circuit | Animal | Other | 8 | 3512 | 35.361 | -119.3057 | No | Clear;32-90 F | Fuse | Burned Open | 23-0068116 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840829 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 135401 | 20230504 | 325 | 20230504 | 2127 | 2104301 | 1082 | Distribution Circuit | Animal | Other | 11 | 5822 | 35.3179 | -119.1725 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0068160 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840837 | 1 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | FUSE | 7368 | 20230504 | 330 | 20230505 | 1359 | 2104347 | 2069 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4426 | 35.6684 | -119.9032 | No | Overcast-Fog;32-90 F | Transformer (OH) | Burned/flashed | 23-0068349 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840892 | 1 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 514084178605 | 20230504 | 341 | 20230504 | 1159 | 2104309 | 498 | Transformer only | Animal | Other | 2 | 996 | 35.6434 | -119.9925 | No | Overcast-Fog-Drizzle;32-90 F | Transformer | Normal | 23-0068176 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840845 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LERDO-1116 | 253491116 | FUSE | 18386 | 20230504 | 401 | 20230505 | 830 | 2104322 | 1709 | Distribution Circuit | Animal | Other | 6 | 4204 | 35.5442 | -119.1541 | No | Overcast-Fog-Rain;32-90 F | Fuse | Burned Open | 23-0068192 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840851 | 1 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | JUMPER | JUMPERS 2 P S/OF CGC# 515519971050 | 20230504 | 404 | 20230504 | 1451 | 2104326 | 647 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 1294 | 35.4425 | -119.5036 | No | Overcast-Fog;32-90 F | Pole-Wood | Burned/flashed | 23-0067950 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840657 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | TRANSFORMER | 517094873650 | 20230504 | 405 | 20230504 | 827 | 2104325 | 262 | Transformer only | Animal | Bird found | 2 | 524 | 35.52 | -118.9786 | No | Partly Cloudy-Rain;32-90 F | Fuse | Failed/Faulted | 23-0068016 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840731 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ANTELOPE-1102 | 252021102 | FUSE | 7059 | 20230504 | 412 | 20230504 | 1300 | 2104330 | 528 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2113 | 35.6609 | -119.9389 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0068238 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840864 | 1 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OCB | 2104/2 | 20230504 | 414 | 20230504 | 637 | 2104327 | 143 | Distribution Circuit | Animal | Bird found | 751 | 107393 | 35.6018 | -119.5799 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0067953 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840660 | 0 | Non-EPSS | N | 2023 | AB INST PH OC
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 513931079735 | 20230504 | 422 | 20230504 | 1351 | 2104338 | 569 | Transformer only | Animal | Other | 1 | 569 | 35.673 | -120.0455 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 23-0068128 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840833 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | RECLOSER | 1200 | 20230504 | 433 | 20230504 | 741 | 2104334 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 31396 | 35.7176 | -119.4204 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0067955 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1840662 | 0 | Non-EPSS | N | 2023 | CG
KERN | KERN | LERDO-1116 | 253491116 | TRANSFORMER | 516708276175 | 20230504 | 506 | 20230504 | 1439 | 2104371 | 573 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 573 | 35.5881 | -119.1072 | No | Overcast-Fog;32-90 F | Fuse | Failed/Faulted | 23-0068333 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840886 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 14625 | 20230504 | 511 | 20230504 | 703 | 2104351 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 672 | 35.378 | -119.0095 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0067982 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840683 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514618781601 | 20230504 | 628 | 20230504 | 1311 | 2104540 | 403 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 403 | 35.7283 | -119.8141 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0068247 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840867 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OCB | 2104/2 | 20230504 | 642 | 20230504 | 702 | 2104373 | 20 | Distribution Circuit | Animal | Other | 751 | 15020 | 35.6018 | -119.5799 | No | Overcast-Fog;32-90 F | Capacitor | Burned/flashed | 23-0067953 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840680 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | TEMBLOR-2103 | 252552103 | OCB | 2103/2 | 20230504 | 723 | 20230504 | 1622 | 2104409 | 539 | Distribution Circuit | 3rd Party | Customer Equipment | 41 | 7470 | 35.3831 | -119.6964 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0067991 | OH | Sus | 40226977 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840685 | 0 | Non-EPSS | N | 2023 | AB TIME OC
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 14030 | 20230504 | 731 | 20230504 | 1051 | 2104413 | 200 | Distribution Circuit | Animal | Other | 16 | 3200 | 35.4921 | -119.1881 | No | Overcast-Fog;32-90 F | Fuse | Failed/Faulted | 23-0068118 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840830 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | 515339973162 | 20230504 | 732 | 20230504 | 1539 | 2104414 | 487 | Transformer only | Animal | Other | 1 | 487 | 35.5003 | -119.5673 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0068402 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840905 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1107 | 252461107 | FUSE | 7551 | 20230504 | 750 | 20230504 | 1534 | 2104431 | 464 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 5568 | 35.6036 | -119.2132 | No | Overcast-Fog;32-90 F |  |  | 23-0068375 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840900 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | TRANSFORMER | 516548875118 | 20230504 | 807 | 20230505 | 1255 | 2104455 | 1728 | Transformer only | Vegetation | Other ground vegetation | 1 | 1728 | 35.5587 | -119.1603 | No | Partly Cloudy;32-90 F | Transformer (OH) | Contaminated | 23-0068422 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840913 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515494379136 | 20230504 | 819 | 20230504 | 1132 | 2104475 | 193 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 193 | 35.6644 | -119.5174 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0068163 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840839 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-2101 | 254682101 | TRANSFORMER | 514796876646 | 20230504 | 837 | 20230513 | 305 | 2104501 | 12628 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 12628 | 35.5939 | -119.7511 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0068177 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840846 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 135401 | 20230504 | 941 | 20230504 | 1349 | 2104717 | 248 | Distribution Circuit | 3rd Party | Other | 3 | 826 | 35.3179 | -119.1725 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0068226 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840861 | 1 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1105 | 253181105 | TRANSFORMER | 516186380960 | 20230504 | 1009 | 20230504 | 1544 | 2104645 | 335 | Transformer only | Company Initiated | Operating error | 1 | 335 | 35.7178 | -119.2858 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0068405 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840907 | 0 | Non-EPSS | N | 2023
KERN | KERN | COPUS-1104 | 253871104 | TRANSFORMER | 516070856569 | 20230504 | 1038 | 20230504 | 1142 | 2104650 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 64 | 35.0474 | -119.3135 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0068170 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840841 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1104 | 253551104 | FUSE | 7293 | 20230504 | 1054 | 20230504 | 1350 | 2104686 | 176 | Distribution Circuit | Animal | Other | 9 | 1643 | 35.79 | -119.4629 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0068307 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840879 | 1 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1105 | 254561105 | FUSE | 8695 | 20230504 | 1119 | 20230504 | 1720 | 2104707 | 361 | Distribution Circuit | Animal | Other | 2 | 722 | 35.327 | -119.3323 | No | Clear;32-90 F | Fuse | Burned Open | 23-0068447 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840926 | 1 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | RECLOSER | 894740 | 20230504 | 1149 | 20230505 | 1322 | 2104740 | 1533 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 27 | 5589 | 35.4442 | -119.5178 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0068178 | OH | Sus | 35441510 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1840847 | 0 | Non-EPSS | N | 2023 | A- B- C- 51RLY
KERN | KERN | OLD RIVER-1101 | 252821101 | FUSE | 77165 | 20230504 | 1357 | 20230504 | 1620 | 2104844 | 143 | Distribution Circuit | Animal | Other | 1 | 143 | 35.18 | -119.1416 | No | Clear;32-90 F | Fuse | Burned Open | 23-0068423 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1840914 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516370863475 | 20230504 | 1359 | 20230504 | 1606 | 2104847 | 127 | Transformer only | Animal | Other | 1 | 127 | 35.2381 | -119.2165 | No | Clear;32-90 F | Jumper | Contaminated | 23-0068416 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840911 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516685560638 | 20230504 | 1401 | 20230504 | 1656 | 2104851 | 175 | Transformer only | Animal | Other | 1 | 175 | 35.1575 | -119.1096 | No | Clear;32-90 F | Fuse | Burned Open | 23-0068435 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840922 | 0 | Non-EPSS | N | 2023
KERN | KERN | COPUS-1104 | 253871104 | TRANSFORMER | 516313557055 | 20230504 | 1451 | 20230505 | 1415 | 2104825 | 1404 | Transformer only | Animal | Other | 2 | 2808 | 35.062 | -119.2338 | No | Partly Cloudy;32-90 F | Bushing | Burned/flashed | 23-0068359 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840895 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514425277752 | 20230504 | 1532 | 20230505 | 430 | 2104919 | 778 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3112 | 35.6221 | -119.8771 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0068430 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840917 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | TRANSFORMER | 516227566135 | 20230504 | 1627 | 20230504 | 1747 | 2104963 | 80 | Transformer only | Animal | Other | 1 | 80 | 35.3108 | -119.2652 | No | Clear;32-90 F | Jumper | Contaminated | 23-0068475 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840938 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 1635 | 20230504 | 1801 | 20230504 | 2144 | 2105043 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 119 | 26537 | 34.9498 | -119.6935 | No | Partly Cloudy;32-90 F |  |  | 23-0068453 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840928 | 0 | EPSS Ckt | N | 2023 | BC
KERN | KERN | TUPMAN-1106 | 254561106 | TRANSFORMER | 516270366120 | 20230504 | 1813 | 20230504 | 1836 | 2105020 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 23 | 35.3106 | -119.251 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0068471 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840936 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517235765945 | 20230505 | 12 | 20230509 | 1015 | 2105221 | 6363 | Transformer only | Animal | Other | 1 | 6363 | 35.3086 | -118.9274 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0068868 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841188 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1104 | 253191104 | FUSE | 2207 | 20230505 | 31 | 20230509 | 2145 | 2105166 | 7034 | Distribution Circuit | Animal | Other | 7 | 14913 | 35.0818 | -118.9001 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0068539 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840996 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1107 | 252461107 | TRANSFORMER | 516365277254 | 20230505 | 1057 | 20230507 | 1538 | 2105474 | 3161 | Transformer only | Animal | Bird found | 1 | 3161 | 35.616 | -119.2234 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0069058 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841236 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 515419882903 | 20230505 | 1100 | 20230509 | 928 | 2105478 | 5668 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 5668 | 35.7682 | -119.5436 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069895 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841973 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | RECLOSER | 4765 | 20230505 | 1127 | 20230505 | 1215 | 2105528 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3673 | 176304 | 35.3175 | -119.034 | No | Overcast;32-90 F | Recloser | Burned/flashed | 23-0068739 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | No | No | 1841160 | 0 | Non-EPSS | N | 2023 | ABC GRD
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516867778200 | 20230505 | 1508 | 20230505 | 1522 | 2105661 | 14 | Transformer only | Animal | Other | 1 | 14 | 35.644 | -119.0553 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0068954 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841202 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | TRANSFORMER | 515167976895 | 20230506 | 557 | 20230509 | 1044 | 2105962 | 4607 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 4607 | 35.6024 | -119.6269 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069121 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841312 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | 100000024400 | 20230506 | 738 | 20230506 | 847 | 2105992 | 69 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 69 | 35.1515 | -119.0216 | No | Clear;32-90 F | Fuse | Broken | 23-0069124 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841317 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515553870469 | 20230506 | 914 | 20230506 | 927 | 2105988 | 13 | Transformer only | Animal | Other | 1 | 13 | 35.4274 | -119.4934 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0069135 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841334 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516589561282 | 20230506 | 919 | 20230506 | 1231 | 2106099 | 192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 192 | 35.1792 | -119.1416 | No | Clear;32-90 F | Fuse | Broken | 23-0069163 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841363 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517318165993 | 20230506 | 1112 | 20230506 | 1255 | 2106149 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 103 | 35.3099 | -118.9 | No | Clear;32-90 F | Fuse | Broken | 23-0069168 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841367 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 517107057875 | 20230506 | 1421 | 20230507 | 1030 | 2106309 | 1209 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1209 | 35.0863 | -118.9681 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069189 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841386 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TAFT-1106 | 252081106 | TRANSFORMER | T869765 | 20230506 | 1434 | 20230506 | 1529 | 2106290 | 55 | Transformer only | Equipment Failure/Involved | Underground | 1 | 55 | 35.1464 | -119.4702 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0069199 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841393 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1104 | 253551104 | FUSE | 540701 | 20230506 | 1709 | 20230515 | 1255 | 2106376 | 12706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 12706 | 35.7898 | -119.491 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0069220 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1841409 | 1 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRANSFORMER | 515979769625 | 20230507 | 1146 | 20230507 | 1429 | 2106775 | 163 | Transformer only | Animal | Other | 1 | 163 | 35.4057 | -119.3498 | No | Clear;32-90 F | Jumper | Contaminated | 23-0069296 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841493 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1106 | 253391106 | INTERRUPTER | 19029 | 20230507 | 2018 | 20230509 | 259 | 2106966 | 1841 | Distribution Circuit | Equipment Failure/Involved | Underground | 1215 | 415193 | 35.4125 | -119.0773 | No | Clear;32-90 F | Interrupter | Broken | 23-0069330 | UG | Sus | 35442105 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1841523 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1101 | 252971101 | TRANSFORMER | 517432662862 | 20230508 | 814 | 20230508 | 2042 | 2107144 | 748 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 748 | 35.2239 | -118.8602 | No | Clear;32-90 F | Transformer | Broken | 23-0069485 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841697 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515560679967 | 20230508 | 1047 | 20230508 | 1248 | 2107343 | 121 | Transformer only | Animal | Other | 1 | 121 | 35.6885 | -119.4952 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 23-0069565 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841734 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515926268174 | 20230508 | 1159 | 20230508 | 1832 | 2107275 | 393 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 393 | 35.3657 | -119.3679 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0069534 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841722 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | T974753 | 20230508 | 1235 | 20230508 | 1347 | 2107541 | 72 | Transformer only | Animal | Other | 1 | 72 | 35.7357 | -119.507 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 23-0069608 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841746 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515500171504 | 20230508 | 1337 | 20230508 | 1630 | 2107398 | 173 | Transformer only | Animal | Bird found | 1 | 173 | 35.4552 | -119.512 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0069627 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841760 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 15543 | 20230508 | 1657 | 20230508 | 1829 | 2108023 | 92 | Distribution Circuit | 3rd Party | Vehicle | 82 | 7544 | 35.3769 | -118.9954 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0069716 | OH | Sus | 31644586 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1841787 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516589561282 | 20230508 | 1704 | 20230509 | 1415 | 2108029 | 1271 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1271 | 35.1792 | -119.1416 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069754 | OH | Sus | 35442410 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841820 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 516464372206 | 20230508 | 2154 | 20230509 | 1356 | 2108198 | 962 | Distribution Circuit | 3rd Party | Vehicle | 16 | 7969 | 35.4782 | -119.1886 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0069762 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1841826 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 9991 | 20230508 | 2216 | 20230509 | 232 | 2108196 | 256 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 9216 | 35.3234 | -119.0247 | No | Clear;32-90 F |  |  | 23-0069764 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841830 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 7469 | 20230508 | 2253 | 20230509 | 149 | 2108205 | 176 | Distribution Circuit | 3rd Party | Vehicle | 35 | 6160 | 35.7188 | -119.3302 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0069761 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1841824 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 7075 | 20230509 | 619 | 20230509 | 1444 | 2108695 | 505 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3535 | 35.702 | -119.4194 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Annealed | 23-0070026 | OH | Sus | 45753484 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842032 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2101 | 255322101 | TRANSFORMER | 516501264773 | 20230509 | 814 | 20230509 | 1547 | 2108331 | 453 | Transformer only | Animal | Bird found | 1 | 453 | 35.2741 | -119.1732 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0069946 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842002 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARNERAS-1103 | 252321103 | TRANSFORMER | 514821775595 | 20230509 | 837 | 20230509 | 1411 | 2108378 | 334 | Transformer only | Vegetation | Other ground vegetation | 1 | 334 | 35.5649 | -119.7417 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 23-0069924 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841992 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15061 | 20230509 | 1022 | 20230509 | 1125 | 2108550 | 63 | Distribution Circuit | Animal | Other | 20 | 1260 | 35.3107 | -118.9167 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0069966 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842010 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516971063405 | 20230509 | 1109 | 20230509 | 1116 | 2108598 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 7 | 35.2379 | -119.015 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0069982 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842019 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516867778200 | 20230509 | 1202 | 20230510 | 1435 | 2108658 | 1593 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1593 | 35.644 | -119.0553 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070100 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842051 | 1 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516575659596 | 20230509 | 1210 | 20230518 | 711 | 2108556 | 12661 | Transformer only | Animal | Bird found | 1 | 12661 | 35.1323 | -119.1458 | No | Clear;32-90 F | Transformer | Arcing | 23-0070011 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842028 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-2101 | 254682101 | TRANSFORMER | 514613277484 | 20230509 | 1417 | 20230509 | 1505 | 2108760 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 48 | 35.6159 | -119.8107 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0070125 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842057 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2108 | 254072108 | SWITCH | 10936SW | 20230509 | 2128 | 20230510 | 531 | 2109033 | 483 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 5086 | 35.3183 | -119.105 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Deteriorated | 23-0069990 | UG | Sus | 35442219 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842088 | 0 | Non-EPSS | N | 2023
KERN | KERN | WELLFIELD-1102 | 254291102 | TRANSFORMER | 517729862701 | 20230510 | 905 | 20230510 | 1057 | 2109284 | 112 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 112 | 35.2206 | -118.7616 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0070405 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842310 | 0 | EPSS Ckt | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516390460330 | 20230510 | 1331 | 20230519 | 851 | 2109612 | 12680 | Transformer only | Animal | Other | 1 | 12680 | 35.1519 | -119.2064 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0070642 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842365 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1103 | 253411103 | TRANSFORMER | 516602156293 | 20230510 | 1503 | 20230510 | 1517 | 2109642 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 14 | 35.0416 | -119.1358 | No | Clear;32-90 F | Fuse | Burned Open | 23-0070585 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842351 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517191766320 | 20230510 | 2120 | 20230510 | 2214 | 2109816 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 162 | 35.3187 | -118.9425 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0070666 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842375 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1110 | 252901110 | TRANSFORMER | 15121 | 20230511 | 729 | 20230516 | 823 | 2110041 | 57 | Transformer only | 3rd Party | Customer Equipment | 1 | 57 | 35.6236 | -119.3682 | No | Clear;32-90 F |  |  | 23-0070757 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842448 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 340104 | 20230511 | 1329 | 20230511 | 1456 | 2110437 | 87 | Distribution Circuit | Animal | Bird found | 3 | 261 | 34.9136 | -119.5866 | No | Clear;32-90 F | Fuse | Burned Open | 23-0071032 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842621 | 1 | EPSS Ckt | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516353161886 | 20230511 | 1525 | 20230511 | 1828 | 2110538 | 183 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 183 | 35.1944 | -119.2215 | No | Clear;32-90 F |  |  | 23-0071117 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1842651 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 8188 | 20230511 | 1605 | 20230511 | 1639 | 2110583 | 34 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 34 | 35.3961 | -118.9818 | No | Clear;32-90 F | Fuse | Burned Open | 23-0071091 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842634 | 1 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | JUMPER | OJ 1 S/ OF CGC 515520876817 | 20230511 | 1835 | 20230511 | 2201 | 2110630 | 206 | Distribution Circuit | 3rd Party | Vehicle | 4 | 824 | 35.6011 | -119.5075 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0071112 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842647 | 0 | Non-EPSS | N | 2023
KERN | KERN | COPUS-1103 | 253871103 | FUSE | 9490 | 20230511 | 2030 | 20230511 | 2157 | 2110689 | 87 | Distribution Circuit | 3rd Party | Vehicle | 1 | 87 | 35.1517 | -119.2335 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0071135 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842666 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13392 | 20230512 | 604 | 20230512 | 1303 | 2110850 | 419 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3352 | 35.1869 | -118.9673 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0071226 | OH | Sus | 31645051 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | Yes | 1842743 | 1 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 737153 | 20230512 | 924 | 20230512 | 1137 | 2111121 | 133 | Distribution Circuit | Animal | Squirrel | 2 | 266 | 35.3703 | -119.3768 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0071356 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842882 | 1 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517206165375 | 20230512 | 1254 | 20230513 | 750 | 2111211 | 1136 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1136 | 35.2927 | -118.9373 | No | Clear;32-90 F | Transformer | Burned Open | 23-0071408 | OH | Sus | 31645158 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842902 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516816861818 | 20230512 | 1357 | 20230512 | 1422 | 2111274 | 25 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 25 | 35.1942 | -119.0662 | No | Clear;32-90 F |  |  | 23-0071442 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1842912 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | INTERRUPTER | 588246 | 20230512 | 1421 | 20230512 | 1544 | 2111350 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 3569 | 35.3384 | -119.163 | No | Clear;32-90 F |  |  | 23-0071460 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1842921 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 9681 | 20230512 | 1748 | 20230512 | 2001 | 2111468 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2484 | 35.2378 | -118.9626 | No | Clear;32-90 F |  |  | 23-0071508 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842944 | 1 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516502677855 | 20230513 | 736 | 20230513 | 842 | 2111623 | 66 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 66 | 35.6334 | -119.1777 | No | Clear;32-90 F |  |  | 23-0071541 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1842996 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2107 | 254072107 | RECLOSER | 4712 | 20230513 | 1518 | 20230514 | 1317 | 2111846 | 1319 | Distribution Circuit | Equipment Failure/Involved | Underground | 644 | 112294 | 35.333 | -119.0745 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0071571 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843034 | 0 | Non-EPSS | N | 2023 | A GRD
KERN | KERN | FELLOWS 2103 | 254242103 | FUSE | 16517 | 20230513 | 2055 | 20230513 | 2245 | 2111977 | 110 | Distribution Circuit | Animal | Bird found | 10 | 1100 | 35.2471 | -119.5931 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0071613 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843065 | 0 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OCB | 2104/2 | 20230513 | 2307 | 20230514 | 517 | 2112003 | 370 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 751 | 274655 | 35.6018 | -119.5799 | No | Clear;32-90 F |  |  | 23-0071614 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843066 | 0 | Non-EPSS | N | 2023 | B PH TIME OC
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | T0174 | 20230514 | 705 | 20230515 | 542 | 2112065 | 1357 | Transformer only | Equipment Failure/Involved | Underground | 1 | 1357 | 35.3934 | -118.9742 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0071636 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843092 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OCB | 2104/2 | 20230514 | 851 | 20230514 | 1056 | 2112102 | 125 | Distribution Circuit | Animal | Other | 751 | 92040 | 35.6018 | -119.5799 | No | Clear;32-90 F | Jumper | Burned/flashed | 23-0071639 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1843095 | 0 | Non-EPSS | N | 2023 | TIME OC A B C
KERN | KERN | FELLOWS-2103 | 254242103 | FUSE | 15503 | 20230514 | 1126 | 20230515 | 30 | 2112143 | 784 | Distribution Circuit | Animal | Bird found | 2 | 1305 | 35.2312 | -119.5773 | No | Clear;Above 90 | Lightning Arrestor | Failed/Faulted | 23-0071674 | OH | Sus | 31645440 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843117 | 1 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14955 | 20230514 | 1527 | 20230514 | 1611 | 2112219 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 146 | 6424 | 35.4036 | -118.9766 | No | Clear;Above 90 |  |  | 23-0071681 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843126 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 3131 | 20230514 | 2100 | 20230515 | 713 | 2112376 | 613 | Distribution Circuit | Animal | Bird found | 4 | 2452 | 35.3105 | -119.0152 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0071701 | UG | Sus | 45762031 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843151 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 7575 | 20230515 | 748 | 20230515 | 940 | 2112473 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 523 | 35.4999 | -119.2191 | No | Clear;32-90 F |  |  | 23-0071799 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843263 | 1 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | TRANSFORMER | 515043575440 | 20230515 | 830 | 20230515 | 1337 | 2112533 | 307 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 614 | 35.5615 | -119.6673 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0071871 | OH | Sus | 31645485 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843309 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2109 | 254072109 | FUSE | 16216 | 20230515 | 854 | 20230515 | 1135 | 2112560 | 161 | Distribution Circuit | Animal | Other | 1 | 161 | 35.2961 | -119.0338 | No | Clear;32-90 F | Fuse | Normal | 23-0071876 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843313 | 1 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | 516335280445 | 20230515 | 1054 | 20230515 | 1315 | 2113034 | 141 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 282 | 35.7043 | -119.2349 | No | Clear;Above 90 |  |  | 23-0071955 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843347 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517277564098 | 20230515 | 1408 | 20230516 | 258 | 2113277 | 770 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1540 | 35.2578 | -118.9128 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0072126 | OH | Sus | 31645406 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843449 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | FUSE | 7267 | 20230515 | 1443 | 20230515 | 1706 | 2113310 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 286 | 35.6446 | -119.7142 | No | Partly Cloudy;Above 90 |  |  | 23-0072072 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843406 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | T1744 | 20230515 | 1809 | 20230516 | 1227 | 2113555 | 1098 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 13812 | 35.32 | -119.0091 | No | Clear;Above 90 | Transformer (UG) | Deteriorated | 23-0072095 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843419 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1102 | 252971102 | FUSE | 44421 | 20230515 | 2353 | 20230516 | 59 | 2113622 | 66 | Distribution Circuit | 3rd Party | Metallic Balloon | 7 | 484 | 35.1999 | -118.8421 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0072124 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843447 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 9330 | 20230516 | 538 | 20230517 | 1242 | 2113722 | 253 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 15204 | 35.304 | -119.0301 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0072193 | UG | Sus | 31645675 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843522 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | JUMPER | FB E/OF CGC# 514955477497 | 20230516 | 835 | 20230516 | 1250 | 2113838 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 510 | 35.6176 | -119.6972 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0072181 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843511 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | 514419558517 | 20230516 | 1418 | 20230516 | 1953 | 2114268 | 335 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 670 | 35.0915 | -119.8656 | No | Partly Cloudy;32-90 F |  |  | 23-0072388 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1843657 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | OCB | 1106/2 | 20230516 | 2209 | 20230516 | 2330 | 2114526 | 81 | Distribution Circuit | Equipment Failure/Involved | Overhead | 150 | 11156 | 35.3531 | -119.2709 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0072505 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1843730 | 0 | Non-EPSS | N | 2023 | A- B- C
KERN | KERN | TEJON-1105 | 252931105 | OCB | 1105/2 | 20230517 | 742 | 20230518 | 154 | 2114647 | 1092 | Distribution Circuit | 3rd Party | Vehicle | 98 | 19086 | 35.0198 | -118.9547 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0072613 | OH | Sus | 31645850 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1843851 | 0 | Non-EPSS | N | 2023 | B & GRD TIME
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 517137559700 | 20230517 | 833 | 20230517 | 1206 | 2114730 | 213 | Transformer only | Animal | Other | 3 | 639 | 35.1366 | -118.9588 | No | Clear;32-90 F | Transformer | Normal | 23-0072682 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843945 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | SWITCH | 1748 | 20230517 | 954 | 20230517 | 1039 | 2114894 | 45 | Distribution Circuit | Company Initiated | Return Circuit Normal | 8 | 360 | 35.3607 | -119.2868 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0072505 | OH | Sus | 31645747 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843920 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 9163 | 20230517 | 1041 | 20230517 | 1235 | 2114948 | 114 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 684 | 35.353 | -119.9873 | No | Clear;32-90 F |  |  | 23-0072698 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843957 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517124168248 | 20230517 | 1838 | 20230517 | 1956 | 2115442 | 78 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 390 | 35.3717 | -118.9651 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0072894 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844028 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1106 | 254501106 | TRANSFORMER | 516015375808 | 20230517 | 1911 | 20230518 | 25 | 2115414 | 314 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 314 | 35.5757 | -119.3413 | No | Clear;32-90 F | Jumper | Burned Open | 23-0072888 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844022 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516311361631 | 20230518 | 918 | 20230518 | 1307 | 2115685 | 229 | Transformer only | Vegetation | Other ground vegetation | 1 | 229 | 35.1873 | -119.2359 | No | Clear;32-90 F | Other | Normal | 23-0073142 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844224 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7256 | 20230518 | 1111 | 20230518 | 1535 | 2116029 | 264 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2465 | 35.6023 | -119.5268 | No | Clear;32-90 F | Woodpin | Broken | 23-0073138 | OH | Sus | 31645790 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844220 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517284264129 | 20230518 | 1627 | 20230519 | 103 | 2116344 | 516 | Transformer only | 3rd Party | Fire- house or bldg. | 14 | 7224 | 35.2584 | -118.9106 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0073246 | OH | Sus | 45768304 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844266 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1112 | 253701112 | FUSE | 8064 | 20230519 | 48 | 20230519 | 1231 | 2116570 | 477 | Distribution Circuit | Equipment Failure/Involved | Underground | 150 | 58907 | 35.3473 | -119.0567 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0073323 | UG | Sus | 45768251 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844326 | 1 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1103 | 252861103 | TRANSFORMER | 516319870835 | 20230519 | 1022 | 20230519 | 1600 | 2116930 | 338 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 338 | 35.4401 | -119.2362 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073567 | OH | Sus | 45769627 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844505 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | 517166264980 | 20230519 | 1143 | 20230519 | 1204 | 2116936 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 21 | 35.2816 | -118.9499 | No | Clear;32-90 F | Fuse | Burned Open | 23-0073566 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844504 | 0 | EPSS Ckt | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 2181 | 20230519 | 1231 | 20230519 | 1805 | 2117041 | 334 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 17034 | 35.5944 | -118.9585 | No | Clear;32-90 F |  |  | 23-0073584 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844511 | 0 | EPSS Ckt | Y | 2023 | C-GRD
KERN | KERN | STOCKDALE-1111 | 254071111 | TRANSFORMER | 516883866365 | 20230519 | 1427 | 20230519 | 1533 | 2117167 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 264 | 35.3198 | -119.045 | No | Clear;Above 90 | Fuse | Failed/Faulted | 23-0073694 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844537 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517041268681 | 20230519 | 2112 | 20230520 | 1250 | 2117351 | 938 | Transformer only | 3rd Party | Fire- house or bldg. | 13 | 12194 | 35.383 | -118.9927 | No | Clear;32-90 F | Service conductor | Burned/flashed | 23-0073763 | OH | Sus | 45769709 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844590 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 16153 | 20230520 | 953 | 20230520 | 1249 | 2117637 | 176 | Distribution Circuit | Animal | Bird found | 3 | 528 | 35.2085 | -119.0788 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0073842 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844690 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1108 | 254071108 | FUSE | 15079 | 20230520 | 1101 | 20230520 | 1152 | 2117591 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 380 | 35.333 | -119.055 | No | Clear;32-90 F |  |  | 23-0073835 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844686 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | T1054 | 20230521 | 608 | 20230521 | 630 | 2117878 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 22 | 35.3114 | -118.844 | No | Clear;32-90 F | Fuse | Burned Open | 23-0073942 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844767 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 16341 | 20230521 | 810 | 20230522 | 1549 | 2117926 | 1899 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 21087 | 35.3837 | -119.0563 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073980 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844799 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1112 | 253701112 | FUSE | 8066 | 20230521 | 830 | 20230521 | 1106 | 2117925 | 156 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 312 | 35.3536 | -119.0535 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0073951 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844775 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 17854 | 20230521 | 839 | 20230521 | 1027 | 2117943 | 108 | Distribution Circuit | Animal | Other | 9 | 972 | 35.4423 | -119.3327 | No | Clear;32-90 F | Insulator | Normal | 23-0073965 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844793 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14836 | 20230521 | 1323 | 20230521 | 1435 | 2118013 | 72 | Distribution Circuit | 3rd Party | Metallic Balloon | 169 | 12168 | 35.3918 | -118.9892 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0073991 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844805 | 0 | Non-EPSS | N | 2023
KERN | KERN | ELK HILLS-1106 | 252441106 | FUSE | 14931 | 20230521 | 1453 | 20230521 | 1741 | 2118043 | 152 | Distribution Circuit | Animal | Bird found | 8 | 1216 | 35.253 | -119.2513 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073999 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844831 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 17943 | 20230521 | 2106 | 20230522 | 520 | 2118200 | 494 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1482 | 35.3252 | -118.9667 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0074025 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1844846 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2103 | 254582103 | TRANSFORMER | T73563 | 20230522 | 1008 | 20230522 | 1022 | 2118640 | 14 | Transformer only | Company Initiated | Improper Construction | 22 | 308 | 35.4292 | -119.098 | No | Clear;32-90 F | Connector or Splice (UG) | Normal | 23-0074162 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845040 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 883676 | 20230522 | 1022 | 20230522 | 2123 | 2118661 | 661 | Distribution Circuit | 3rd Party | Vehicle | 39 | 7190 | 35.7753 | -119.5181 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0074226 | OH | Sus | 35448512 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1845073 | 0 | Non-EPSS | N | 2023
KERN | KERN | ELK HILLS-1104 | 252441104 | TRANSFORMER | 515680562528 | 20230522 | 1104 | 20230522 | 1400 | 2118696 | 176 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 176 | 35.2096 | -119.446 | No | Clear;32-90 F |  |  | 23-0074297 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1845091 | 0 | Non-EPSS | N | 2023
KERN | KERN | COPUS-1104 | 253871104 | FUSE | 15437 | 20230522 | 1422 | 20230522 | 2040 | 2118873 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2773 | 35.0581 | -119.2689 | No | Clear;Above 90 | Jumper | Burned Open | 23-0074373 | OH | Sus | 31646209 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845108 | 1 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516896864066 | 20230522 | 1453 | 20230523 | 59 | 2118871 | 606 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 606 | 35.256 | -119.0402 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0074331 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845100 | 0 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1103 | 253801103 | OCB | 1103/2 | 20230522 | 1723 | 20230523 | 254 | 2119031 | 571 | Distribution Circuit | Animal | Bird found | 105 | 24535 | 35.1499 | -118.8788 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0074386 | OH | Sus | 35448527 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1845113 | 0 | Non-EPSS | N | 2023 | PH OC- TIME
KERN | KERN | RENFRO-2102 | 254572102 | RECLOSER | 4923 | 20230522 | 1917 | 20230522 | 2009 | 2119103 | 52 | Distribution Circuit | Animal | Other | 902 | 46904 | 35.3686 | -119.1453 | No | Partly Cloudy;32-90 F | Recloser | Burned/flashed | 23-0074408 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | No | No | 1845130 | 0 | Non-EPSS | N | 2023 | B- C- GRD
KERN | KERN | WESTPARK SUB | 25370 | OCB | 1200/2 | 20230522 | 2113 | 20230523 | 100 | 2119154 | 227 | Distribution Circuit | Equipment Failure/Involved | Underground | 831 | 51878 | 35.374 | -119.0404 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0074418 | UG | Sus | 31646410 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845142 | 0 | Non-EPSS | N | 2023 | B C & GRD PHASE OC
KERN | KERN | STOCKDALE-1110 | 254071110 | FUSE | 128191 | 20230522 | 2133 | 20230523 | 500 | 2119122 | 447 | Distribution Circuit | 3rd Party | Vehicle | 40 | 8741 | 35.3231 | -119.0341 | No | Clear;32-90 F | Secondary | Broken | 23-0074422 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845145 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | RECLOSER | 317866 | 20230522 | 2155 | 20230523 | 435 | 2119179 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 10815 | 35.761 | -119.4796 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0074427 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845149 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | KERN OIL-1106 | 252721106 | JUMPER | FB 2/E/OF CGC# 517271371072 | 20230523 | 945 | 20230523 | 1435 | 2119448 | 290 | Distribution Circuit | Environmental/External | Water | 2 | 580 | 35.4499 | -118.9132 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0074520 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845245 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 517109156845 | 20230523 | 1101 | 20230523 | 1204 | 2119672 | 63 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 126 | 35.0588 | -118.9673 | No | Clear;32-90 F |  |  | 23-0074680 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1845368 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SEMITROPIC-1110 | 252901110 | TRANSFORMER | 515977077176 | 20230523 | 1353 | 20230523 | 2032 | 2119871 | 399 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 399 | 35.6124 | -119.3543 | No | Clear;32-90 F |  |  | 23-0074877 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1845437 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | FUSE | 9035 | 20230523 | 1423 | 20230523 | 2240 | 2119896 | 497 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 497 | 35.4428 | -119.6531 | No | Clear-Strong Winds;32-90 F |  |  | 23-0074904 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845460 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 13891 | 20230523 | 1455 | 20230524 | 121 | 2119918 | 626 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2923 | 35.2828 | -118.8873 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0074854 | OH | Sus | 31646566 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845418 | 1 | EPSS Ckt | N | 2023
KERN | KERN | SEMITROPIC-1110 | 252901110 | FUSE | 16077 | 20230523 | 1919 | 20230524 | 558 | 2120060 | 639 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 1278 | 35.6039 | -119.3849 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0074867 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845427 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 7469 | 20230524 | 535 | 20230524 | 1438 | 2120202 | 543 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 12676 | 35.7188 | -119.3302 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0074968 | OH | Sus | 31646587 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845481 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2106 | 254072106 | TRANSFORMER | T3509 | 20230524 | 714 | 20230524 | 915 | 2120233 | 121 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 1573 | 35.3096 | -119.0293 | No | Clear;32-90 F |  |  | 23-0075011 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1845596 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 8547 | 20230524 | 812 | 20230524 | 909 | 2120294 | 57 | Distribution Circuit | 3rd Party | Metallic Balloon | 166 | 9462 | 35.412 | -119.0433 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0075003 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1845570 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516687477758 | 20230524 | 1008 | 20230525 | 1358 | 2120499 | 1670 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1670 | 35.6313 | -119.1153 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0075068 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845627 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 517109156845 | 20230524 | 1018 | 20230524 | 1458 | 2120478 | 280 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 560 | 35.0588 | -118.9673 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0075079 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845632 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 14637 | 20230524 | 1207 | 20230524 | 1458 | 2120589 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2107 | 35.336 | -119.0151 | No | Clear;32-90 F |  |  | 23-0075225 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845685 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517379966017 | 20230524 | 1630 | 20230524 | 1704 | 2120752 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 34 | 35.3108 | -118.8792 | No | Clear;32-90 F | Fuse | Broken | 23-0075280 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845702 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1101 | 252861101 | FUSE | 2638 | 20230524 | 2030 | 20230525 | 258 | 2120854 | 388 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 32204 | 35.4642 | -119.2611 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0075311 | OH | Sus | 45773948 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1845716 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 515529783425 | 20230525 | 821 | 20230526 | 1012 | 2121041 | 1551 | Transformer only | Vegetation | Other ground vegetation | 1 | 1551 | 35.7827 | -119.5077 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0075648 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845937 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1101 | 252861101 | TRANSFORMER | 516226773050 | 20230525 | 909 | 20230525 | 1501 | 2121131 | 352 | Transformer only | Company Initiated | Personnel- company | 8 | 2816 | 35.5004 | -119.2687 | No | Clear;32-90 F | Other | Together | 23-0075449 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845869 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1105 | 252771105 | TRANSFORMER | 517191768389 | 20230525 | 1317 | 20230525 | 2056 | 2121337 | 459 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 6885 | 35.3754 | -118.943 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0075628 | OH | Sus | 31649069 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1845935 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRANSFORMER | 516141371530 | 20230525 | 1552 | 20230525 | 1859 | 2121443 | 187 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 187 | 35.4584 | -119.2969 | No | Clear;32-90 F |  |  | 23-0075740 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845970 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | JUMPER | FLYERS 1 N/OF CGC 517388270622 | 20230525 | 2155 | 20230525 | 2201 | 2121762 | 6 | Distribution Circuit | Environmental/External | Flood/Erosion | 2 | 12 | 35.4379 | -118.8777 | No | Clear;32-90 F | Pole-Wood | Contaminated | 23-0075787 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846016 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-1105 | 254071105 | RECLOSER | 1109/2 | 20230526 | 216 | 20230526 | 1744 | 2121814 | 830 | Distribution Circuit | 3rd Party | Vehicle | 3870 | 121628 | 35.3164 | -119.0682 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0075806 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846037 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7119 | 20230526 | 504 | 20230526 | 1015 | 2121833 | 311 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 1866 | 35.5719 | -119.5985 | No | Clear;32-90 F |  |  | 23-0075948 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846149 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 515493583022 | 20230526 | 1115 | 20230602 | 950 | 2122147 | 9995 | Transformer only | Animal | Bird found | 1 | 9995 | 35.7715 | -119.5195 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0076035 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846182 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 17498 | 20230526 | 1819 | 20230526 | 1943 | 2122382 | 84 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 1177 | 35.4558 | -118.9063 | No | Clear;32-90 F |  |  | 23-0076228 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846243 | 1 | EPSS Ckt | N | 2023
KERN | KERN | SEMITROPIC-1110 | 252901110 | RECLOSER | 4552 | 20230526 | 1926 | 20230527 | 115 | 2122400 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 9301 | 35.6023 | -119.3848 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0076229 | OH | Sus | 45779597 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1846244 | 0 | Non-EPSS | N | 2023 | C PHASE & GRD
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 44405 | 20230527 | 9 | 20230527 | 147 | 2122444 | 98 | Distribution Circuit | Animal | Other | 3 | 294 | 35.4926 | -119.2939 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0076255 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846274 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 17087 | 20230527 | 1421 | 20230528 | 1302 | 2122728 | 1360 | Distribution Circuit | 3rd Party | Vehicle | 12 | 7239 | 35.4569 | -119.4395 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0076337 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1846348 | 0 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1101 | 253801101 | RECLOSER | 69618 | 20230527 | 2348 | 20230528 | 1530 | 2122875 | 942 | Distribution Circuit | 3rd Party | Vehicle | 325 | 259347 | 35.178 | -118.824 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0076388 | OH | Sus | 35449780 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | Yes | No | 1846386 | 0 | EPSS Ckt | N | 2023 | B C & GRD
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17646 | 20230528 | 604 | 20230528 | 826 | 2122908 | 142 | Distribution Circuit | Animal | Bird found | 6 | 851 | 35.356 | -119.0644 | No | Clear;32-90 F | Insulator | Normal | 23-0076418 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846405 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | RECLOSER | 82037 | 20230528 | 856 | 20230528 | 1843 | 2122966 | 574 | Distribution Circuit | Company Initiated | Other Circuits | 48 | 17485 | 35.1659 | -119.107 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0076423 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846410 | 0 | Non-EPSS | N | 2023 | A B GRD
KERN | KERN | KERN OIL-1104 | 252721104 | OCB | 1703 | 20230528 | 1249 | 20230528 | 1923 | 2123035 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 194 | 57309 | 35.559 | -118.9797 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0076446 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846427 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13387 | 20230529 | 1051 | 20230530 | 243 | 2123444 | 949 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 30 | 28470 | 35.3703 | -118.9762 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0076560 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846522 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 16248 | 20230529 | 2337 | 20230530 | 44 | 2123626 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 6566 | 35.4018 | -119.4721 | No | Clear;32-90 F |  |  | 23-0076629 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846575 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1109 | 254071109 | INTERRUPTER | 595010 | 20230530 | 912 | 20230530 | 1432 | 2123862 | 320 | Distribution Circuit | 3rd Party | Vehicle | 43 | 13760 | 35.2905 | -119.0747 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0076734 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Open Circuit | 0 | No | No | No | 1846727 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514296079525 | 20230530 | 1247 | 20230530 | 2202 | 2123607 | 555 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1110 | 35.6692 | -119.921 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0076837 | OH | Sus | 45804989 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846771 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1104 | 252901104 | TRANSFORMER | 515701777055 | 20230530 | 1433 | 20230530 | 1934 | 2124167 | 301 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 301 | 35.6088 | -119.4471 | No | Partly Cloudy;32-90 F |  |  | 23-0077005 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1846826 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1101 | 252861101 | JUMPER | DDE JMPRS 1 W/OF CGC# 516196371981 | 20230530 | 1645 | 20230530 | 1835 | 2124237 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 330 | 35.4709 | -119.2787 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Annealed | 23-0076944 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846804 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-1102 | 254401102 | FUSE | 15111 | 20230531 | 600 | 20230601 | 1025 | 2124424 | 1705 | Distribution Circuit | Animal | Other | 24 | 5808 | 35.7746 | -119.8423 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0077062 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846865 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAKEVIEW-1106 | 253411106 | FUSE | 9183 | 20230531 | 702 | 20230531 | 1132 | 2124478 | 270 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 1350 | 35.0189 | -119.065 | No | Partly Cloudy;32-90 F |  |  | 23-0077227 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1847024 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517002268339 | 20230531 | 1000 | 20230531 | 1300 | 2124723 | 180 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1260 | 35.3738 | -119.006 | No | Clear;32-90 F | Transformer | Normal | 23-0077253 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1847036 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517004268301 | 20230531 | 1001 | 20230531 | 1302 | 2124724 | 181 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2172 | 35.3728 | -119.0049 | No | Clear;32-90 F | Transformer | Normal | 23-0077257 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1847038 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1105 | 252931105 | FUSE | 9964 | 20230531 | 1644 | 20230531 | 1925 | s1847097 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 322 | 35.0454 | -118.9356 | No | Clear;32-90 F |  |  | 23-0077484 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1847097 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1111 | 254071111 | TRANSFORMER | 516928566791 | 20230531 | 2023 | 20230531 | 2159 | 2125111 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1056 | 35.3308 | -119.0307 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0077506 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1847109 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1104 | 253191104 | TRANSFORMER | 517305957560 | 20230601 | 1237 | 20230601 | 2315 | 2126733 | 638 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1276 | 35.0783 | -118.9013 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0077892 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847335 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 9885 | 20230601 | 1644 | 20230601 | 1756 | 2126884 | 72 | Distribution Circuit | 3rd Party | Metallic Balloon | 119 | 8568 | 35.3503 | -119.0298 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0078003 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1847363 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | OTHER | T10280 TWD T10411 | 20230602 | 107 | 20230602 | 220 | 2127009 | 73 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 1752 | 35.2897 | -119.0109 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0077906 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1847407 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1106 | 253951106 | FUSE | 8164 | 20230602 | 501 | 20230602 | 2331 | 2127040 | 1110 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 12540 | 35.3982 | -118.9672 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0078067 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1847418 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517151161256 | 20230602 | 924 | 20230602 | 1704 | 2127236 | 460 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 460 | 35.1795 | -118.9543 | No | Clear;32-90 F |  |  | 23-0078178 | OH | Sus | 45811683 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1847547 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | OTHER | T8790 TWD T8791 | 20230602 | 1421 | 20230602 | 1539 | 2127486 | 78 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 1092 | 35.3782 | -119.1756 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 23-0078320 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1847596 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14955 | 20230602 | 1741 | 20230602 | 1857 | 2127584 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 146 | 11096 | 35.4036 | -118.9766 | No | Clear;32-90 F |  |  | 23-0078460 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1847612 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2103 | 254582103 | TRANSFORMER | T10704 | 20230602 | 2021 | 20230603 | 338 | 2127634 | 437 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 3428 | 35.429 | -119.1019 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0078482 | UG | Sus | 35452027 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847624 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 8914 | 20230602 | 2225 | 20230603 | 20 | 2127693 | 115 | Distribution Circuit | Animal | Other | 9 | 997 | 35.0216 | -118.7743 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0078509 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847644 | 1 | EPSS Ckt | N | 2023
KERN | KERN | SAN BERNARD-1102 | 253191102 | OCB | 1102/2 | 20230603 | 721 | 20230603 | 1020 | 2127777 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 7697 | 35.0921 | -118.8779 | No | Clear;32-90 F | Insulator | Broken | 23-0078532 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1847659 | 0 | Non-EPSS | N | 2023 | A B C PH OC TIME
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 9217 | 20230603 | 1132 | 20230603 | 1325 | 2127910 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1206 | 35.0415 | -118.9624 | No | Clear;32-90 F |  |  | 23-0078589 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847715 | 1 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517018667208 | 20230603 | 1137 | 20230603 | 1219 | 2127911 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 294 | 35.3428 | -119.0001 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0078593 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847716 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517222266477 | 20230604 | 1606 | 20230605 | 1613 | 2128490 | 1447 | Transformer only | Environmental/External | Fire- Forest/Grass | 2 | 2894 | 35.3231 | -118.9321 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0078735 | OH | Sus | 31651145 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847833 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1108 | 252081108 | TRANSFORMER | 515637059789 | 20230604 | 1622 | 20230605 | 158 | 2128638 | 576 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 6336 | 35.1341 | -119.4604 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0078745 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847847 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 17854 | 20230604 | 1628 | 20230605 | 955 | 2128502 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1188 | 35.4423 | -119.3327 | No | Clear;Above 90 | Jumper | Burned Open | 23-0078744 | OH | Sus | 31651200 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847844 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 18112 | 20230604 | 1732 | 20230605 | 300 | 2128613 | 568 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1136 | 35.2581 | -118.8786 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0078749 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847852 | 1 | EPSS Ckt | N | 2023
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 16026 | 20230604 | 2038 | 20230604 | 2306 | 2128703 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 987 | 35.5866 | -119.4739 | No | Clear;32-90 F |  |  | 23-0078761 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847862 | 1 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | OCB | 1104/2 | 20230605 | 1326 | 20230606 | 26 | 2129295 | 660 | Distribution Circuit | 3rd Party | Vehicle | 761 | 100949 | 35.4006 | -119.449 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0078969 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | Yes | No | 1848068 | 0 | Non-EPSS | N | 2023 | AC TIME OC
KERN | KERN | ARVIN-1102 | 253801102 | TRANSFORMER | 517327560405 | 20230605 | 1425 | 20230605 | 1734 | 2129360 | 189 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 189 | 35.1572 | -118.8951 | No | Clear;32-90 F |  |  | 23-0079090 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1848109 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | RECLOSER | 931236 | 20230605 | 1737 | 20230605 | 1922 | 2129547 | 105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 8715 | 35.1084 | -119.3727 | No | Partly Cloudy;32-90 F | Insulator | Broken- wire on ground | 23-0079087 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1848107 | 0 | EPSS Ckt | N | 2023 | SGF
KERN | KERN | FELLOWS-2103 | 254242103 | TRANSFORMER | 515231664144 | 20230605 | 2054 | 20230606 | 1255 | 2130119 | 961 | Transformer only | Environmental/External | Lightning | 1 | 961 | 35.2517 | -119.5981 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0079261 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848277 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FELLOWS-2103 | 254242103 | TRANSFORMER | 515239764198 | 20230605 | 2126 | 20230606 | 848 | 2130035 | 682 | Transformer only | Environmental/External | Lightning | 2 | 1364 | 35.253 | -119.5954 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0079151 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848160 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | OCB | 1101/2 | 20230605 | 2138 | 20230606 | 53 | 2130041 | 195 | Distribution Circuit | Animal | Other | 108 | 21060 | 35.1077 | -119.3972 | No | Partly Cloudy;32-90 F | Insulator | Broken- wire on ground | 23-0079137 | OH | Sus | 31651330 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1848147 | 0 | EPSS Ckt | N | 2023 | A- GRD & TIME
KERN | KERN | COPUS-1103 | 253871103 | FUSE | 8524 | 20230605 | 2140 | 20230606 | 2015 | 2130043 | 1355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 12195 | 35.1228 | -119.2343 | No | Lightning-Heavy Rain | Insulator | Burned/flashed | 23-0079162 | OH | Sus | 31651237 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848167 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 2181 | 20230605 | 2207 | 20230606 | 1134 | 2130053 | 807 | Distribution Circuit | 3rd Party | Customer Equipment | 51 | 41157 | 35.5944 | -118.9585 | No | Rain-Lightning-Partly Cloudy;32-90 F | Customer Equipment | Failed/Faulted | 23-0079149 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848157 | 0 | EPSS Ckt | Y | 2023 | B & GRD
KERN | KERN | RIO BRAVO-1106 | 252861106 | RECLOSER | 2635 | 20230605 | 2252 | 20230606 | 336 | 2130069 | 284 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 568 | 123208 | 35.4418 | -119.2902 | No | Partly Cloudy;32-90 F |  |  | 23-0079154 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1848161 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | LAKEVIEW-1102 | 253411102 | RECLOSER | 3776 | 20230606 | 140 | 20230606 | 146 | 2130077 | 6 | Distribution Circuit | Animal | Other | 47 | 282 | 35.1108 | -119.1095 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0079170 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848177 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516685059155 | 20230606 | 214 | 20230606 | 951 | 2130118 | 457 | Transformer only | Animal | Bird found | 2 | 914 | 35.1193 | -119.1096 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079172 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848178 | 0 | Non-EPSS | N | 2023
KERN | KERN | FELLOWS-2103 | 254242103 | TRANSFORMER | 515259664204 | 20230606 | 705 | 20230606 | 1258 | 2130199 | 353 | Transformer only | Environmental/External | Lightning | 1 | 353 | 35.2529 | -119.5891 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 23-0079283 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848325 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FELLOWS-2103 | 254242103 | TRANSFORMER | 515235564194 | 20230606 | 722 | 20230606 | 1048 | 2130214 | 206 | Transformer only | Environmental/External | Lightning | 2 | 412 | 35.253 | -119.5969 | No | Overcast;32-90 F | Transformer | Burned/flashed | 23-0079265 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848279 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAKEVIEW-1107 | 253411107 | TRANSFORMER | 516483057085 | 20230606 | 745 | 20230607 | 1056 | 2130233 | 1631 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1631 | 35.0625 | -119.1761 | No | Overcast-Partly Cloudy-Lightning-Rain | Transformer (OH) | Failed/Faulted | 23-0079564 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848482 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | RECLOSER | 2635 | 20230606 | 906 | 20230606 | 1358 | 2130433 | 292 | Distribution Circuit | Animal | Bird found | 567 | 99893 | 35.4418 | -119.2902 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0079284 | OH | Sus | 31651444 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848326 | 0 | Non-EPSS | N | 2023 | AB
KERN | KERN | STOCKDALE-2110 | 254072110 | OTHER | J79299 TWD T0094 | 20230606 | 921 | 20230606 | 2315 | 2130443 | 829 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 4974 | 35.3588 | -119.0532 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0079177 | UG | Sus | 35452917 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848351 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1110 | 253951110 | JUMPER | OJ S/OF CGC 517178468533 | 20230606 | 927 | 20230606 | 1539 | 2130343 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 27156 | 35.3794 | -118.9475 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 23-0079267 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848284 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516728878021 | 20230606 | 956 | 20230606 | 1745 | 2130483 | 469 | Transformer only | Animal | Other | 1 | 469 | 35.6386 | -119.1016 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079405 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848414 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1107 | 253411107 | TRANSFORMER | 516492156981 | 20230606 | 1017 | 20230606 | 1842 | 2130235 | 505 | Transformer only | Environmental/External | Lightning | 1 | 505 | 35.0598 | -119.173 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079327 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848375 | 0 | Non-EPSS | N | 2023
KERN | KERN | MCKITTRICK-1101 | 252781101 | TRANSFORMER | 515200264499 | 20230606 | 1032 | 20230606 | 1634 | 2130530 | 362 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 362 | 35.2623 | -119.6089 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0079331 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848379 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FELLOWS-2104 | 254242104 | FUSE | 372119 | 20230606 | 1229 | 20230615 | 800 | 2130624 | 12691 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 25382 | 35.2282 | -119.6721 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0079434 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848422 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515951156398 | 20230606 | 1358 | 20230607 | 2345 | 2130729 | 2027 | Transformer only | Animal | Other | 1 | 2027 | 35.0422 | -119.3538 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079620 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848532 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516788059815 | 20230606 | 1632 | 20230606 | 2329 | 2131139 | 417 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1251 | 35.1389 | -119.0752 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0079551 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848469 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 18665 | 20230606 | 1753 | 20230607 | 300 | 2131220 | 547 | Distribution Circuit | Animal | Other | 6 | 2078 | 34.9198 | -119.5431 | No | Overcast;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0079583 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848496 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | OCB | 2101/2 | 20230606 | 1805 | 20230606 | 2116 | 2131216 | 191 | Distribution Circuit | Animal | Other | 289 | 55199 | 34.9276 | -119.6203 | No | Lightning-Rain-Overcast;32-90 F | Fuse | Failed/Faulted | 23-0079553 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848471 | 0 | EPSS Ckt | N | 2023 | B- GRD- 51RLY- SET A
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515887259556 | 20230606 | 1950 | 20230607 | 730 | 2131274 | 700 | Transformer only | Environmental/External | Lightning | 1 | 700 | 35.1287 | -119.3766 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079624 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848537 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-1106 | 253371106 | FUSE | 14440 | 20230606 | 2011 | 20230607 | 53 | 2131280 | 282 | Distribution Circuit | Animal | Bird found | 193 | 54426 | 35.3835 | -118.99 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0079579 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848493 | 0 | Non-EPSS | N | 2023
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 9772 | 20230606 | 2032 | 20230607 | 2029 | 2131328 | 1437 | Distribution Circuit | Animal | Other | 7 | 4341 | 35.2236 | -118.7616 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 23-0079645 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848559 | 1 | EPSS Ckt | N | 2023
KERN | KERN | ARVIN-1103 | 253801103 | FUSE | 747533 | 20230606 | 2043 | 20230607 | 1513 | 2131331 | 1110 | Distribution Circuit | Animal | Other | 10 | 2901 | 35.1292 | -118.9323 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0079617 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848529 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | T8120 | 20230606 | 2105 | 20230607 | 1120 | 2131307 | 855 | Distribution Circuit | Equipment Failure/Involved | Underground | 136 | 15068 | 35.2842 | -119.0202 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0079626 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848539 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 14395 | 20230606 | 2117 | 20230607 | 730 | 2131312 | 613 | Distribution Circuit | Environmental/External | Lightning | 47 | 15434 | 35.4053 | -118.9768 | No | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079660 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848569 | 0 | Non-EPSS | N | 2023
KERN | KERN | CAL WATER 1102 | 255451102 | OCB | 1102/2/NORM | 20230606 | 2120 | 20230606 | 2340 | 2131317 | 140 | Distribution Circuit | Animal | Other | 2535 | 354900 | 35.4222 | -118.9007 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 23-0079589 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848501 | 0 | EPSS Ckt | N | 2023 | PH/GRD OC INST- BU PH/GRD TIME
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 3990 | 20230606 | 2122 | 20230608 | 808 | 2131325 | 2086 | Distribution Circuit | Animal | Other | 15 | 31290 | 35.5585 | -118.9767 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0079588 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848500 | 0 | EPSS Ckt | Y | 2023 | A- C
KERN | KERN | WELLFIELD-1102 | 254291102 | TRANSFORMER | 517687762811 | 20230606 | 2124 | 20230607 | 333 | 2131327 | 369 | Transformer only | Animal | Other | 1 | 369 | 35.2238 | -118.7746 | No | Overcast;32-90 F | Transformer (OH) | Contaminated | 23-0079640 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848553 | 0 | EPSS Ckt | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 2181 | 20230606 | 2210 | 20230608 | 148 | 2131343 | 1658 | Distribution Circuit | Animal | Other | 50 | 82900 | 35.5944 | -118.9585 | No | Partly Cloudy;32-90 F | Switch (OH) | Burned/flashed | 23-0079609 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848524 | 0 | EPSS Ckt | Y | 2023 | B- C
KERN | KERN | KERN OIL-1104 | 252721104 | TRANSFORMER | 516898074420 | 20230606 | 2217 | 20230607 | 1707 | 2131456 | 1130 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2260 | 35.5408 | -119.0431 | No | Partly Cloudy;32-90 F |  |  | 23-0080010 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1848813 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LERDO-1112 | 253491112 | RECLOSER | 4323 | 20230606 | 2225 | 20230607 | 110 | 2131347 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 123 | 20295 | 35.5151 | -119.0819 | No | Overcast-Heavy Rain;32-90 F |  |  | 23-0079619 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848531 | 0 | Non-EPSS | N | 2023 | A- B
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 8693 | 20230606 | 2236 | 20230607 | 1535 | 2131348 | 1019 | Distribution Circuit | Environmental/External | Lightning | 10 | 5663 | 35.2253 | -119.2078 | No | Clear-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079694 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848593 | 0 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1103 | 253801103 | TRANSFORMER | 517266559495 | 20230606 | 2249 | 20230606 | 2259 | 2131291 | 10 | Transformer only | Animal | Other | 1 | 10 | 35.1311 | -118.9155 | No | Clear;32-90 F | Jumper | Contaminated | 23-0079611 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848526 | 0 | Non-EPSS | N | 2023
KERN | KERN | ELK HILLS-1104 | 252441104 | FUSE | 7339 | 20230606 | 2304 | 20230607 | 238 | 2131351 | 214 | Distribution Circuit | Animal | Other | 3 | 642 | 35.2096 | -119.4337 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0079634 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848547 | 0 | Non-EPSS | N | 2023
KERN | KERN | COPUS-1103 | 253871103 | FUSE | 15522 | 20230606 | 2352 | 20230607 | 1100 | 2131361 | 668 | Distribution Circuit | Environmental/External | Lightning | 2 | 891 | 35.1081 | -119.2391 | No | Clear;32-90 F | Insulator | Failed/Faulted | 23-0079635 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848548 | 1 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | OTHER | WIRE DOWN 2P N/ OF 1436 | 20230607 | 23 | 20230607 | 1350 | 2131396 | 807 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1373 | 199618 | 35.6454 | -119.2766 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0079625 | OH | Sus | 45823906 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848538 | 1 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1116 | 253491116 | TRANSFORMER | 516688375115 | 20230607 | 38 | 20230607 | 2028 | 2131575 | 1190 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1190 | 35.5589 | -119.1139 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0080048 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848827 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7346 | 20230607 | 125 | 20230607 | 740 | 2131397 | 375 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1500 | 35.5721 | -119.5114 | No | Overcast;32-90 F |  |  | 23-0079661 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848570 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1102 | 252861102 | OCB | 1102/2 | 20230607 | 138 | 20230607 | 417 | s1848546 | 159 | Distribution Circuit | Environmental/External | Lightning | 2167 | 344553 | 35.442 | -119.2607 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0079633 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | Yes | No | 1848546 | 0 | Non-EPSS | N | 2023 | A- C- GRD- 51RLY
KERN | KERN | SAN BERNARD-1101 | 253191101 | TRANSFORMER | 517418558475 | 20230607 | 213 | 20230607 | 1816 | 2131398 | 963 | Transformer only | Animal | Bird found | 2 | 1926 | 35.1037 | -118.8641 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 23-0080067 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848833 | 0 | EPSS Ckt | N | 2023
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | RECLOSER | 388671 | 20230607 | 250 | 20230607 | 1112 | 2131438 | 502 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 502 | 35.5133 | -118.9036 | No | Clear;32-90 F |  |  | 23-0079644 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848558 | 0 | EPSS Ckt | Y | 2023 | A- C- 50RLY
KERN | KERN | TEMBLOR-2103 | 252552103 | RECLOSER | 768638 | 20230607 | 317 | 20230607 | 612 | 2131435 | 175 | Distribution Circuit | Environmental/External | Lightning | 34 | 5950 | 35.4378 | -119.6873 | No | Partly Cloudy;32-90 F | Recloser | Burned/flashed | 23-0079638 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848551 | 0 | Non-EPSS | N | 2023 | B C
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7291 | 20230607 | 351 | 20230608 | 1120 | 2131440 | 1889 | Distribution Circuit | Animal | Bird found | 6 | 6444 | 35.7173 | -119.5798 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0079932 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848798 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | OCB | 1103/2 | 20230607 | 400 | 20230607 | 934 | 2131425 | 334 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 145 | 48430 | 35.6018 | -119.58 | No | Overcast;32-90 F |  |  | 23-0079659 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848568 | 0 | Non-EPSS | N | 2023 | B- GRD- 50RLY
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517342966283 | 20230607 | 417 | 20230607 | 841 | 2131461 | 264 | Transformer only | Animal | Other | 1 | 264 | 35.318 | -118.8916 | No | Clear;32-90 F | Jumper | Contaminated | 23-0079729 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848661 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-1104 | 252551104 | OCB | 1104/2 | 20230607 | 443 | 20230607 | 1811 | 2131443 | 808 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 71 | 35501 | 35.3831 | -119.6964 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0079643 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848557 | 0 | EPSS Ckt | N | 2023 | A C RD
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 515471081044 | 20230607 | 448 | 20230607 | 958 | 2131439 | 310 | Transformer only | Animal | Bird found | 1 | 310 | 35.7173 | -119.5265 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0079786 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848724 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2102 | 254582102 | RECLOSER | 1499 | 20230607 | 510 | 20230607 | 1719 | 2131447 | 729 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 11209 | 35.4418 | -119.1812 | No | Overcast-Rain;32-90 F | Bushing | Burned/flashed | 23-0079821 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848744 | 0 | Non-EPSS | N | 2023 | A- GRD
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 15157 | 20230607 | 538 | 20230607 | 1350 | 2131453 | 492 | Distribution Circuit | Environmental/External | Lightning | 5 | 2460 | 35.3997 | -119.529 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 23-0079655 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848565 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 16245 | 20230607 | 538 | 20230607 | 2050 | 2131452 | 912 | Distribution Circuit | Animal | Other | 6 | 5472 | 35.3995 | -119.5095 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0080088 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1848846 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 93339 | 20230607 | 547 | 20230607 | 1717 | 2131478 | 690 | Distribution Circuit | Environmental/External | Lightning | 3 | 2070 | 35.3105 | -118.8877 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0079663 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1848571 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 59019 | 20230607 | 554 | 20230607 | 1410 | 2131468 | 496 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 33295 | 35.2671 | -118.9167 | No | Clear;32-90 F |  |  | 23-0079870 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848779 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2112 | 254072112 | JUMPER | 19394 | 20230607 | 618 | 20230607 | 1729 | 2131475 | 671 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 13373 | 35.2961 | -119.0717 | No | Partly Cloudy-Drizzle;32-90 F | Jumper | Burned Open | 23-0079963 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1848805 | 1 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | RECLOSER | 623146 | 20230607 | 623 | 20230607 | 1813 | 2131479 | 710 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 12780 | 35.7337 | -119.6897 | No | Overcast;32-90 F | Regulator | Burned/flashed | 23-0079664 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848572 | 0 | Non-EPSS | N | 2023 | GRD/SGF
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13476 | 20230607 | 649 | 20230607 | 924 | 2131486 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 14725 | 35.3649 | -118.9745 | No | Overcast-Drizzle;32-90 F |  |  | 23-0079760 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848703 | 0 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 514072578537 | 20230607 | 719 | 20230607 | 2011 | 2131565 | 772 | Transformer only | Environmental/External | Lightning | 1 | 772 | 35.6415 | -119.9962 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0079832 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848754 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CHARCA-1103 | 254501103 | TRANSFORMER | 516295075671 | 20230607 | 732 | 20230607 | 1801 | 2131573 | 629 | Transformer only | Environmental/External | Lightning | 1 | 629 | 35.5729 | -119.2465 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079823 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848747 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517110762039 | 20230607 | 742 | 20230607 | 1945 | 2131579 | 723 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 723 | 35.2014 | -118.9682 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0080042 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848824 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 100000091737 | 20230607 | 749 | 20230607 | 1338 | 2131588 | 349 | Transformer only | Animal | Bird found | 1 | 349 | 35.1737 | -119.0216 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0079921 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848795 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517061265734 | 20230607 | 851 | 20230607 | 1153 | 2131699 | 182 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 546 | 35.3021 | -118.9853 | No | Overcast-Rain;32-90 F |  |  | 23-0079855 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1848768 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | TRANSFORMER | 515392252156 | 20230607 | 856 | 20230607 | 1930 | 2131706 | 634 | Transformer only | Environmental/External | Lightning | 1 | 634 | 34.9233 | -119.5388 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079826 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848750 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FELLOWS-2104 | 254242104 | TRANSFORMER | 515032963470 | 20230607 | 859 | 20230609 | 931 | 2131711 | 2912 | Transformer only | Animal | Bird found | 1 | 2912 | 35.2324 | -119.6637 | No | Clear;32-90 F | Transformer | Normal | 23-0080479 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849112 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MC FARLAND-1105 | 253181105 | FUSE | 7464 | 20230607 | 955 | 20230608 | 1028 | 2131832 | 1473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1986 | 35.696 | -119.2755 | No | Overcast;32-90 F | Bushing | Burned/flashed | 23-0079856 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848769 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517275566804 | 20230607 | 1110 | 20230607 | 1117 | 2131713 | 7 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 7 | 35.3325 | -118.9143 | No | Clear;32-90 F |  |  | 23-0079837 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1848759 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 516017769348 | 20230607 | 1120 | 20230607 | 1502 | 2131910 | 222 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 222 | 35.3986 | -119.337 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0079976 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848807 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1105 | 253911105 | TRANSFORMER | 517522063365 | 20230607 | 1130 | 20230607 | 1557 | 2131919 | 267 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 267 | 35.2382 | -118.8304 | No | Partly Cloudy;32-90 F |  |  | 23-0080018 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1848816 | 0 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 514031578510 | 20230607 | 1208 | 20230607 | 1925 | 2131566 | 437 | Transformer only | Environmental/External | Lightning | 2 | 874 | 35.6408 | -120.0096 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0079859 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848774 | 0 | EPSS Ckt | N | 2023
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | RECLOSER | 388671 | 20230607 | 1328 | 20230607 | 1634 | 2132013 | 186 | Distribution Circuit | 3rd Party | Other | 1 | 186 | 35.5133 | -118.9036 | No | Overcast;32-90 F | Recloser | Normal | 23-0079939 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848800 | 0 | EPSS Ckt | Y | 2023 | C INST
KERN | KERN | COPUS-1103 | 253871103 | TRANSFORMER | 516364560077 | 20230607 | 1502 | 20230608 | 125 | 2131881 | 623 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 623 | 35.1446 | -119.2164 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0080023 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848817 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | FUSE | 7367 | 20230607 | 1606 | 20230607 | 2245 | 2132081 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1995 | 35.6705 | -119.9052 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0080071 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848836 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1116 | 253491116 | FUSE | 128957 | 20230607 | 1734 | 20230607 | 1758 | 2132128 | 24 | Distribution Circuit | 3rd Party | Other | 2 | 48 | 35.595 | -119.115 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0080057 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848829 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | FUSE | 7175 | 20230607 | 1800 | 20230607 | 1825 | 2131374 | 25 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 117 | 35.5386 | -119.1933 | No | Clear;32-90 F |  |  | 23-0080073 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848837 | 1 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRANSFORMER | 514104166094 | 20230608 | 628 | 20230608 | 1025 | 2132316 | 237 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 237 | 35.2996 | -119.9771 | No | Clear;32-90 F | Fuse | Broken | 23-0080285 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849052 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FELLOWS-2103 | 254242103 | TRANSFORMER | 515390462705 | 20230608 | 636 | 20230608 | 1225 | 2132320 | 349 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 349 | 35.2122 | -119.5461 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0080344 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849077 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515699067245 | 20230608 | 712 | 20230608 | 1044 | 2132338 | 212 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 212 | 35.3392 | -119.4429 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0080280 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849050 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 16968 | 20230608 | 825 | 20230608 | 1028 | 2132431 | 123 | Distribution Circuit | Animal | Other | 1 | 123 | 35.2597 | -118.9499 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0080283 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1849051 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | TRANSFORMER | 516421178302 | 20230608 | 843 | 20230609 | 1628 | 2132467 | 1905 | Transformer only | Environmental/External | Lightning | 2 | 3810 | 35.6455 | -119.2051 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0080936 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849425 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1105 | 252461105 | FUSE | 27263 | 20230608 | 900 | 20230608 | 1318 | 2132493 | 258 | Distribution Circuit | Animal | Bird found | 3 | 774 | 35.5803 | -119.2045 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0080380 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1849090 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1114 | 253491114 | TRANSFORMER | 516728272397 | 20230608 | 935 | 20230608 | 1201 | 2132556 | 146 | Transformer only | Animal | Other | 1 | 146 | 35.4845 | -119.1001 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0080332 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849072 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515608068133 | 20230608 | 1102 | 20230608 | 1116 | 2132538 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 14 | 35.3633 | -119.4743 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0080303 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849060 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515872857327 | 20230608 | 1228 | 20230608 | 2228 | 2132744 | 600 | Transformer only | Animal | Bird found | 1 | 600 | 35.0674 | -119.3795 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 23-0080582 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849191 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ELK HILLS-1104 | 252441104 | TRANSFORMER | 515855866713 | 20230608 | 1239 | 20230608 | 2121 | 2132755 | 522 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 522 | 35.3248 | -119.3904 | No | Clear;32-90 F |  |  | 23-0080554 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1849159 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1107 | 253411107 | TRANSFORMER | 516507457213 | 20230608 | 1358 | 20230608 | 2245 | 2132815 | 527 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 527 | 35.0662 | -119.1665 | No | Clear;32-90 F |  |  | 23-0080596 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1849206 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 100000047989 | 20230608 | 1415 | 20230608 | 2027 | 2132833 | 372 | Transformer only | Vegetation | Other ground vegetation | 2 | 744 | 35.4336 | -119.5597 | No | Clear;32-90 F | Transformer | Malfunctioning | 23-0080540 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849141 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | 515903572812 | 20230608 | 1500 | 20230608 | 2015 | 2132891 | 315 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 315 | 35.493 | -119.3767 | No | Partly Cloudy;32-90 F |  |  | 23-0080545 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1849149 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1116 | 252721116 | FUSE | 8947 | 20230608 | 1513 | 20230608 | 1721 | 2132901 | 128 | Distribution Circuit | Animal | Squirrel | 1 | 128 | 35.4413 | -119.06 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0080524 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849125 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516956766814 | 20230608 | 1544 | 20230608 | 1852 | 2132930 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2438 | 35.3317 | -119.0205 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0080486 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849113 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517000368340 | 20230608 | 2302 | 20230609 | 215 | 2133173 | 193 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2123 | 35.3738 | -119.0066 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0080589 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849198 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 8306 | 20230609 | 741 | 20230609 | 1053 | 2133282 | 192 | Distribution Circuit | Animal | Bird found | 65 | 12480 | 35.3151 | -119.017 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0080777 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849377 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517251263991 | 20230609 | 943 | 20230609 | 2020 | 2133487 | 637 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 10192 | 35.2544 | -118.9215 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0080926 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849422 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516418060706 | 20230609 | 1100 | 20230609 | 1114 | 2133486 | 14 | Transformer only | Animal | Other | 1 | 14 | 35.1625 | -119.1991 | No | Clear;32-90 F | Transformer (OH) |  | 23-0080803 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849385 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | 517500867354 | 20230609 | 1232 | 20230609 | 2309 | 2133467 | 637 | Transformer only | Animal | Bird found | 1 | 637 | 35.3475 | -118.8389 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0080879 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849414 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 7405 | 20230610 | 622 | 20230610 | 1234 | 2134058 | 372 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1860 | 35.7029 | -119.5825 | No | Overcast;32-90 F |  |  | 23-0081125 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1849589 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1101 | 253191101 | OCB | 1101/2 | 20230610 | 1558 | 20230611 | 2056 | 2134327 | 1738 | Distribution Circuit | 3rd Party | Vehicle | 86 | 12109 | 35.0921 | -118.878 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0081159 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | Yes | No | 1849608 | 0 | EPSS Ckt | N | 2023 | AB GRD PH TIME OC
KERN | KERN | TEMBLOR-1104 | 252551104 | OCB | 1104/2 | 20230611 | 221 | 20230611 | 1333 | 2134524 | 672 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 5206 | 35.3831 | -119.6964 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0081238 | OH | Sus | 45843401 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | Yes | No | 1849683 | 0 | EPSS Ckt | N | 2023 | BC&GRD
KERN | KERN | TEMBLOR-1104 | 252551104 | TRIP-SAVER | 9126 | 20230611 | 654 | 20230611 | 836 | 2134547 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2245 | 35.3913 | -119.703 | No | Partly Cloudy;32-90 F |  |  | 23-0081246 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849694 | 1 | EPSS Ckt | N | 2023 | 45660
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20230611 | 1801 | 20230611 | 1941 | 2134728 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 130 | 12947 | 35.5605 | -118.9587 | No | Partly Cloudy;32-90 F |  |  | 23-0081325 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849742 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
KERN | KERN | BAKERSFIELD-1105 | 253371105 | FUSE | 15611 | 20230612 | 53 | 20230612 | 235 | 2134897 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 6426 | 35.382 | -119.0269 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0081379 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849796 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 9681 | 20230612 | 814 | 20230612 | 1321 | 2135029 | 307 | Distribution Circuit | 3rd Party | Vehicle | 28 | 8596 | 35.2378 | -118.9626 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0081438 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1849903 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-1101 | 254401101 | OCB | 1101/2 | 20230612 | 934 | 20230612 | 1138 | 2135181 | 124 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 124 | 35.7305 | -119.8581 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0081459 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1849952 | 0 | Non-EPSS | N | 2023 | BC GRD PH OC INST
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 517012369583 | 20230612 | 955 | 20230612 | 1205 | 2135196 | 130 | Transformer only | Equipment Failure/Involved | Underground | 2 | 260 | 35.4077 | -119.0031 | No | Clear;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0081539 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850009 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1102 | 254501102 | FUSE | 492429 | 20230612 | 1021 | 20230612 | 1417 | 2135228 | 236 | Distribution Circuit | Animal | Other | 6 | 1416 | 35.6659 | -119.3752 | No | Clear;32-90 F | Fuse | Burned Open | 23-0081615 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1850045 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515345770095 | 20230612 | 1021 | 20230612 | 1321 | 2134967 | 180 | Transformer only | Animal | Other | 1 | 180 | 35.416 | -119.5628 | No | Clear;32-90 F | Jumper | Contaminated | 23-0081484 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849967 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | 100000002296 | 20230612 | 1031 | 20230612 | 1915 | 2135239 | 524 | Transformer only | Animal | Other | 1 | 524 | 34.9675 | -119.7055 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0081560 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850017 | 0 | EPSS Ckt | N | 2023
KERN | KERN | DEVILS DEN-1102 | 253451102 | TRANSFORMER | 514357881721 | 20230612 | 1052 | 20230612 | 1248 | 2135270 | 116 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 116 | 35.7308 | -119.9015 | No | Clear;32-90 F |  |  | 23-0081576 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1850024 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | TRANSFORMER | T77098 | 20230613 | 1104 | 20230613 | 1602 | 2136031 | 298 | Transformer only | Animal | Bird found | 1 | 298 | 34.9049 | -119.5644 | No | Partly Cloudy;32-90 F | Pothead/Riser Termination | Burned/flashed | 23-0081923 | OH | Sus | 31652260 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850336 | 0 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | TRANSFORMER | 515573078527 | 20230613 | 1109 | 20230614 | 424 | 2136093 | 1035 | Transformer only | Animal | Bird found | 1 | 1035 | 35.6484 | -119.491 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0082063 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850377 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1104 | 253391104 | TRANSFORMER | T8070 | 20230613 | 1129 | 20230614 | 51 | 2136467 | 802 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 12002 | 35.4235 | -119.1021 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0082013 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850408 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1107 | 252931107 | INTERRUPTER | 216260 | 20230613 | 1232 | 20230613 | 1553 | 2136167 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 201 | 34.9863 | -118.944 | No | Clear;32-90 F |  |  | 23-0081973 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1850351 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 100000008575 | 20230613 | 1329 | 20230614 | 135 | 2136203 | 726 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 726 | 35.6805 | -119.8677 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0082024 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850360 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1102 | 252961102 | FUSE | 14597 | 20230613 | 1803 | 20230613 | 2027 | 2136335 | 144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 8064 | 35.602 | -119.3403 | No | Clear;32-90 F | Jumper | Broken | 23-0082055 | OH | Sus | 45846548 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1850374 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2101 | 254582101 | FUSE | 16794 | 20230614 | 141 | 20230614 | 251 | 2136513 | 70 | Distribution Circuit | Animal | Bird found | 4490 | 25999 | 35.4075 | -119.1102 | No | Clear;32-90 F | Crossarm- Steel | Normal | 23-0082118 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850428 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 9686 | 20230614 | 817 | 20230614 | 937 | 2136639 | 80 | Distribution Circuit | 3rd Party | Metallic Balloon | 110 | 8800 | 35.3648 | -118.9407 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082215 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1850573 | 0 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 514086078492 | 20230614 | 830 | 20230621 | 1219 | 2136669 | 10309 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 10309 | 35.6405 | -119.9924 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0082340 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850629 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SHAFTER-1104 | 253651104 | OTHER | J898 TWD T9741 | 20230614 | 1247 | 20230614 | 1505 | 2136962 | 138 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 3588 | 35.5018 | -119.2879 | No | Partly Cloudy;32-90 F | Transformer (UG) | Deteriorated | 23-0077124 | UG | Sus | 31643785 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850626 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1102 | 252961102 | FUSE | 7262 | 20230614 | 1420 | 20230614 | 1553 | 2137045 | 93 | Distribution Circuit | Animal | Bird found | 106 | 9858 | 35.5865 | -119.3538 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0082438 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1850664 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 7119 | 20230614 | 1439 | 20230614 | 2018 | 2137062 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2022 | 35.5719 | -119.5985 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0082412 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850653 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | FUSE | 97639 | 20230614 | 1502 | 20230615 | 1042 | 2137086 | 1180 | Distribution Circuit | Animal | Other | 1 | 1180 | 35.4122 | -119.6072 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0082473 | OH | Sus | 31652357 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850685 | 1 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | T3186 | 20230614 | 2321 | 20230615 | 1426 | 2137336 | 905 | Distribution Circuit | Equipment Failure/Involved | Underground | 145 | 28237 | 35.3079 | -119.0094 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0082534 | UG | Sus | 35457759 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850735 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 16965 | 20230615 | 940 | 20230615 | 1615 | 2137570 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 395 | 35.2559 | -118.9322 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0082638 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850812 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MC FARLAND-1105 | 253181105 | TRANSFORMER | 516080581218 | 20230615 | 1358 | 20230615 | 1622 | 2137775 | 144 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 144 | 35.7244 | -119.3209 | No | Clear;32-90 F |  |  | 23-0082876 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1850897 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 7072 | 20230615 | 2051 | 20230616 | 153 | 2138034 | 302 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1813 | 35.7179 | -119.3835 | No | Clear;32-90 F |  |  | 23-0082957 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850946 | 1 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | JUMPER | HIGH SIDE JUMPERS 1 P N/O 13909 | 20230616 | 910 | 20230616 | 1754 | 2138331 | 524 | Distribution Circuit | 3rd Party | Vehicle | 13 | 6812 | 35.3612 | -118.9763 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0083068 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1851063 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1114 | 253371114 | FUSE | 20179 | 20230616 | 1412 | 20230616 | 1645 | 2138681 | 153 | Distribution Circuit | Company Initiated | Improper Construction | 43 | 6579 | 35.3726 | -118.9632 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0083229 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1851170 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2107 | 254572107 | FUSE | 17908 | 20230616 | 1519 | 20230617 | 45 | 2138743 | 566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4109 | 116014 | 35.3892 | -119.1633 | No | Clear;Above 90 | Cutout- fuse holder | Broken | 23-0083266 | OH | Sus | 45851493 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851185 | 1 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 15449 | 20230617 | 1030 | 20230617 | 1215 | 2139248 | 105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 3780 | 35.1363 | -119.4756 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0083363 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1851317 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1107 | 252931107 | INTERRUPTER | 216260 | 20230617 | 1444 | 20230617 | 1930 | 2139505 | 286 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 286 | 34.9863 | -118.944 | No | Clear;32-90 F |  |  | 23-0083427 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1851371 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1107 | 252931107 | TRANSFORMER | T892609 | 20230617 | 1801 | 20230617 | 1906 | 2139510 | 65 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 65 | 34.9863 | -118.9439 | No | Clear;32-90 F |  |  | 23-0083428 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1851372 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARNERAS-1103 | 252321103 | RECLOSER | 430670 | 20230617 | 1833 | 20230618 | 247 | 2139527 | 494 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 6916 | 35.5305 | -119.8089 | No | Clear;32-90 F |  |  | 23-0083424 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1851367 | 0 | EPSS Ckt | Y | 2023 | A B INST
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | T2640 | 20230617 | 2125 | 20230618 | 1247 | 2139605 | 903 | Distribution Circuit | Equipment Failure/Involved | Underground | 25 | 12862 | 35.3897 | -119.1377 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0083465 | UG | Sus | 35459760 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851408 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 14470 | 20230618 | 742 | 20230618 | 852 | 2139704 | 70 | Distribution Circuit | Animal | Squirrel | 21 | 1470 | 35.3221 | -119.0445 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0083487 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851431 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517261865819 | 20230618 | 1308 | 20230618 | 1501 | 2139808 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 226 | 35.3053 | -118.9188 | No | Clear;32-90 F | Secondary | Normal | 23-0083515 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851458 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 100000030185 | 20230618 | 1311 | 20230618 | 1406 | 2139805 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 55 | 35.0931 | -118.9501 | No | Clear;32-90 F | Fuse | Broken | 23-0083508 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851452 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA 1102 | 254211102 | RECLOSER | 3558 | 20230618 | 1726 | 20230618 | 1902 | 2139911 | 96 | Distribution Circuit | 3rd Party | Metallic Balloon | 192 | 18432 | 35.0639 | -119.4065 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0083530 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1851475 | 0 | EPSS Ckt | Y | 2023 | BC
KERN | KERN | TEJON-1107 | 252931107 | INTERRUPTER | 216260 | 20230618 | 2006 | 20230618 | 2133 | 2140019 | 87 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 87 | 34.9863 | -118.944 | No | Clear;32-90 F | Interrupter | Normal | 23-0083555 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1851499 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1107 | 252931107 | TRANSFORMER | T892609 | 20230618 | 2009 | 20230618 | 2118 | 2140022 | 69 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 69 | 34.9863 | -118.9439 | No | Clear;32-90 F |  |  | 23-0083554 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1851498 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 13787 | 20230619 | 821 | 20230619 | 1010 | 2140280 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 218 | 35.0926 | -118.9439 | No | Clear;32-90 F |  |  | 23-0083618 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1851611 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | JUMPER | WIRE DOWN NW/OF 18112 | 20230619 | 928 | 20230619 | 1520 | 2140452 | 352 | Distribution Circuit | Equipment Failure/Involved | Overhead | 115 | 1531 | 35.2582 | -118.8786 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083640 | OH | Sus | 45851772 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | Yes | Yes | 1851624 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEJON-1107 | 252931107 | TRANSFORMER | T892609 | 20230619 | 1228 | 20230619 | 1530 | 2140574 | 182 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 182 | 34.9863 | -118.9439 | No | Clear;32-90 F |  |  | 23-0083697 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1851667 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2109 | 254072109 | TRANSFORMER | T244374 | 20230620 | 712 | 20230620 | 1229 | 2140864 | 317 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 317 | 35.2916 | -119.0276 | No | Clear;32-90 F |  |  | 23-0083889 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1851909 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1102 | 254211102 | OCB | 1102/2 | 20230621 | 621 | 20230621 | 918 | 2141913 | 177 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 573 | 94581 | 35.1077 | -119.3972 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0084093 | OH | Sus | 31652938 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | Yes | No | 1852021 | 0 | EPSS Ckt | Y | 2023 | AB INST
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517102767773 | 20230621 | 1124 | 20230621 | 2024 | 2142267 | 540 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 540 | 35.3591 | -118.972 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0084373 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852210 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1102 | 254211102 | SWITCH | 1033 | 20230621 | 1545 | 20230621 | 1711 | 2142559 | 86 | Distribution Circuit | Company Initiated | Return Circuit Normal | 11 | 602 | 35.0766 | -119.4026 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0084093 | OH | Sus | 31652938 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1852219 | 0 | EPSS Ckt | N | 2023
KERN | KERN | KERN OIL-1109 | 252721109 | TRANSFORMER | 516868970050 | 20230622 | 616 | 20230622 | 721 | 2142834 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 585 | 35.4202 | -119.0516 | No | Clear;32-90 F | Fuse | Broken | 23-0084552 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852303 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2101 | 255322101 | TRANSFORMER | 100000013379 | 20230622 | 916 | 20230622 | 1952 | 2143016 | 636 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 636 | 35.2602 | -119.1815 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0084624 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852429 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517529762182 | 20230622 | 1000 | 20230622 | 1135 | 2143079 | 95 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 475 | 35.2059 | -118.8276 | No | Clear;32-90 F | Service conductor | Annealed | 23-0084610 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852420 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | TRANSFORMER | 516380775057 | 20230622 | 1014 | 20230622 | 1758 | 2142964 | 464 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 928 | 35.5562 | -119.2177 | No | Clear;32-90 F | Transformer | Leaking | 23-0084628 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852431 | 0 | Non-EPSS | N | 2023
KERN | KERN | SISQUOC-1102 | 182811102 | FUSE | 15497 | 20230622 | 1200 | 20230622 | 1533 | 2143223 | 213 | Distribution Circuit | Animal | Bird found | 3 | 478 | 35.1907 | -119.9531 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0084712 | OH | Sus | 31653165 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1852461 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 8888 | 20230622 | 1311 | 20230622 | 1410 | 2143241 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 649 | 35.3655 | -118.9626 | No | Clear;32-90 F |  |  | 23-0084747 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852471 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517502562245 | 20230622 | 1356 | 20230622 | 1456 | 2143284 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 360 | 35.2077 | -118.8366 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0084761 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852479 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 16241 | 20230622 | 1517 | 20230622 | 1750 | 2143331 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 612 | 35.4269 | -119.5169 | No | Clear;32-90 F |  |  | 23-0084846 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852502 | 1 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 515347275471 | 20230622 | 1647 | 20230622 | 2222 | 2143309 | 335 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 335 | 35.5647 | -119.5651 | No | Clear;32-90 F | Transformer | Arcing | 23-0084833 | OH | Sus | 45857172 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852497 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517150767995 | 20230622 | 1707 | 20230622 | 1839 | 2143410 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 368 | 35.365 | -118.9561 | No | Clear;32-90 F | Fuse | Broken | 23-0084852 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852507 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 15348 | 20230622 | 1931 | 20230623 | 512 | 2143716 | 581 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 22078 | 35.4156 | -119.0494 | No | Clear;32-90 F | Secondary | Broken | 23-0084899 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852568 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | RECLOSER | 3542 | 20230622 | 2210 | 20230623 | 216 | 2143650 | 246 | Distribution Circuit | Animal | Bird found | 124 | 30504 | 34.8725 | -119.4942 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0084884 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852549 | 0 | EPSS Ckt | N | 2023 | B C INST
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7442 | 20230623 | 622 | 20230623 | 858 | 2143740 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 520 | 35.5721 | -119.6094 | No | Clear;32-90 F |  |  | 23-0084945 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852617 | 1 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 517097060455 | 20230623 | 1241 | 20230623 | 1517 | 2144178 | 156 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 156 | 35.158 | -118.9718 | No | Clear;32-90 F |  |  | 23-0080821 | OH | Sus | 45647980 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1852727 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1103 | 252611103 | TRANSFORMER | 515981970683 | 20230623 | 1627 | 20230624 | 1712 | 2143915 | 1485 | Transformer only | 3rd Party | Customer Equipment | 1 | 1485 | 35.4348 | -119.3496 | No | Clear;32-90 F | Customer Equipment | Broken | 23-0085217 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1852755 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1104 | 252961104 | FUSE | 16002 | 20230624 | 312 | 20230624 | 515 | 2144486 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 133 | 16359 | 35.5907 | -119.3448 | No | Clear;32-90 F |  |  | 23-0085284 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852805 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | RECLOSER | 3301 | 20230624 | 531 | 20230624 | 728 | 2144515 | 117 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 242 | 12738 | 35.4424 | -118.9595 | No | Clear;32-90 F |  |  | 23-0085285 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852806 | 0 | EPSS Ckt | N | 2023 | SGF
KERN | KERN | TEJON-1107 | 252931107 | TRANSFORMER | T892609 | 20230624 | 856 | 20230624 | 1100 | 2144630 | 124 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 124 | 34.9863 | -118.9439 | No | Clear;32-90 F |  |  | 23-0085325 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1852877 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 15301 | 20230624 | 929 | 20230624 | 1415 | 2144653 | 286 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 6864 | 35.2523 | -118.9276 | No | Clear;32-90 F |  |  | 23-0085346 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852893 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20230624 | 1200 | 20230624 | 1515 | 2144881 | 195 | Distribution Circuit | Animal | Bird found | 131 | 25545 | 35.5605 | -118.9587 | No | Partly Cloudy;32-90 F | Recloser | Normal | 23-0085330 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852880 | 0 | EPSS Ckt | Y | 2023 | B- C- GRD- 50RLY
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 16397 | 20230624 | 1748 | 20230625 | 1056 | 2145060 | 1028 | Distribution Circuit | Equipment Failure/Involved | Underground | 97 | 49452 | 35.4905 | -119.2783 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0085372 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852913 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 17742 | 20230625 | 551 | 20230625 | 745 | 2145166 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 6840 | 35.3323 | -118.9899 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085403 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852950 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | T7215 | 20230625 | 920 | 20230625 | 1927 | 2145225 | 607 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2428 | 35.3323 | -118.9987 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0085419 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852969 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517040266758 | 20230625 | 1017 | 20230625 | 1926 | 2145279 | 549 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2745 | 35.3305 | -118.9927 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0085422 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852972 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514790370058 | 20230625 | 1120 | 20230626 | 1439 | 2145303 | 1639 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1639 | 35.4124 | -119.7491 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085433 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852982 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 18451 | 20230625 | 2312 | 20230626 | 108 | 2145556 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 619 | 35.6884 | -119.5088 | No | Clear;32-90 F |  |  | 23-0085471 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853025 | 1 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 58941 | 20230626 | 234 | 20230626 | 1103 | 2145569 | 509 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 125 | 63625 | 35.2231 | -119.0035 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0085473 | OH | Sus | 31653459 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | Yes | No | 1853029 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 13318 | 20230626 | 532 | 20230626 | 656 | 2145578 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 168 | 35.3543 | -118.9333 | No | Clear;32-90 F |  |  | 23-0085481 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853035 | 1 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | FUSE | 16929 | 20230626 | 1214 | 20230626 | 1705 | 2146083 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 291 | 35.6012 | -119.5818 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0085642 | OH | Sus | 45860726 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853214 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 517000067985 | 20230626 | 1258 | 20230626 | 1543 | 2146116 | 165 | Transformer only | 3rd Party | Fire- house or bldg. | 7 | 1155 | 35.3641 | -119.0066 | No | Clear;32-90 F | Service conductor | Burned Open | 23-0085776 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853265 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | TRANSFORMER | 515225176838 | 20230626 | 1327 | 20230626 | 2350 | 2145954 | 623 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 623 | 35.6013 | -119.6071 | No | Clear;32-90 F | Secondary | Broken | 23-0085683 | OH | Sus | 31653587 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853232 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 17658 | 20230626 | 1458 | 20230626 | 1643 | 2146269 | 105 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 4094 | 35.3068 | -119.0238 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0085761 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853253 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 16138 | 20230626 | 1802 | 20230627 | 1204 | 2146377 | 1082 | Distribution Circuit | Equipment Failure/Involved | Underground | 25 | 9990 | 35.3248 | -119.0029 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0085831 | UG | Sus | 35461575 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853288 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 10730 | 20230627 | 54 | 20230627 | 2025 | 2146516 | 1037 | Distribution Circuit | Equipment Failure/Involved | Underground | 55 | 54505 | 35.3217 | -119.0763 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0085866 | UG | Sus | 45860612 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853325 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20230627 | 1033 | 20230627 | 1325 | 2147072 | 117 | Distribution Circuit | Company Initiated | Personnel- company | 131 | 21579 | 35.5605 | -118.9587 | No | Clear;32-90 F |  |  | 23-0086034 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853504 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 16138 | 20230627 | 1204 | 20230628 | 403 | 2147020 | 959 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 3054 | 35.3248 | -119.0029 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0085831 | UG | Sus | 35461575 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853494 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | RECLOSER | 4765 | 20230627 | 1210 | 20230627 | 1854 | 2147038 | 404 | Distribution Circuit | 3rd Party | Other | 3751 | 287229 | 35.3175 | -119.034 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0086106 | OH | Sus | 31653801 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1853496 | 0 | Non-EPSS | N | 2023 | A- B- C
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 13787 | 20230627 | 1308 | 20230627 | 1437 | 2147077 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 119 | 35.0926 | -118.9439 | No | Clear;32-90 F |  |  | 23-0086157 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853506 | 1 | Non-EPSS | N | 2023
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 15070 | 20230627 | 1329 | 20230628 | 554 | 2147094 | 985 | Distribution Circuit | Animal | Other | 2 | 1149 | 35.1945 | -118.788 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0086259 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853526 | 1 | EPSS Ckt | N | 2023
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20230627 | 1832 | 20230627 | 1856 | 2147290 | 24 | Distribution Circuit | Company Initiated | Return Circuit Normal | 3 | 72 | 35.5593 | -118.9575 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0077547 | OH | Sus | 35272732 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1853542 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | MCKITTRICK-1101 | 252781101 | FUSE | 1685 | 20230628 | 318 | 20230628 | 611 | 2147411 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2249 | 35.3205 | -119.7371 | No | Clear;32-90 F |  |  | 23-0086360 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1853590 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 7189 | 20230628 | 352 | 20230628 | 1117 | 2147403 | 445 | Distribution Circuit | 3rd Party | Vehicle | 24 | 10680 | 35.4999 | -119.315 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0086369 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1853600 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20230628 | 941 | 20230628 | 1149 | 2147754 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 131 | 16714 | 35.5605 | -118.9587 | No | Clear;32-90 F |  |  | 23-0086486 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853764 | 0 | EPSS Ckt | Y | 2023 | SGF
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516632278255 | 20230628 | 1247 | 20230628 | 2050 | 2148102 | 483 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 483 | 35.6448 | -119.1344 | No | Clear;32-90 F |  |  | 23-0086876 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1853871 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20230628 | 1503 | 20230629 | 1554 | 2148225 | 1491 | Distribution Circuit | Animal | Other | 26 | 32518 | 35.5593 | -118.9575 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0086759 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1853843 | 0 | EPSS Ckt | Y | 2023 | A- B & PH OC INST
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516953162338 | 20230628 | 1543 | 20230628 | 1712 | 2148257 | 89 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 89 | 35.2085 | -119.0208 | No | Clear;32-90 F |  |  | 23-0086837 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1853856 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 7089 | 20230628 | 1557 | 20230628 | 2041 | 2148263 | 284 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1704 | 35.6306 | -119.2978 | No | Clear;32-90 F |  |  | 23-0086873 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853870 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517026568191 | 20230628 | 1729 | 20230628 | 1958 | 2148482 | 149 | Distribution Circuit | 3rd Party | Other | 10 | 1238 | 35.3695 | -118.998 | No | Clear;32-90 F | Service conductor | Normal | 23-0086881 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853877 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | SWITCH | 1239 | 20230629 | 1027 | 20230629 | 1548 | 2148884 | 321 | Distribution Circuit | 3rd Party | Vehicle | 35 | 4137 | 35.6452 | -119.2747 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0087061 | OH | Sus | 35463495 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854067 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 100000004212 | 20230629 | 1146 | 20230630 | 1016 | 2148616 | 1350 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1350 | 35.1229 | -119.1634 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0087133 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854093 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1106 | 253411106 | TRANSFORMER | 516853556170 | 20230629 | 1241 | 20230629 | 2114 | 2148820 | 513 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 513 | 35.0406 | -119.0538 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087183 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854105 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | TRANSFORMER | 517571156432 | 20230629 | 1551 | 20230630 | 223 | 2149118 | 632 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 632 | 35.0498 | -118.8113 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0087304 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854132 | 0 | EPSS Ckt | N | 2023
KERN | KERN | KERN POWER-2103 | 255262103 | TRANSFORMER | 516680368805 | 20230629 | 2016 | 20230630 | 11 | 2149321 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1410 | 35.3854 | -119.1145 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0087364 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854172 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | SWITCH | 1606 | 20230630 | 810 | 20230630 | 1418 | 2149595 | 368 | Distribution Circuit | 3rd Party | Vehicle | 55 | 3284 | 35.4998 | -119.1623 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0087445 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854293 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1107 | 253411107 | TRANSFORMER | 516507457213 | 20230630 | 1114 | 20230630 | 1602 | 2149863 | 288 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 288 | 35.0662 | -119.1665 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087616 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854380 | 0 | Non-EPSS | N | 2023
KERN | KERN | DEVILS DEN-1102 | 253451102 | TRANSFORMER | 514357881721 | 20230630 | 1254 | 20230630 | 1749 | 2149915 | 295 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 295 | 35.7308 | -119.9015 | No | Clear;Above 90 | Transformer | Failed/Faulted | 23-0087661 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854402 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | FUSE | 11050 | 20230630 | 1858 | 20230701 | 2013 | 2150249 | 1515 | Distribution Circuit | Equipment Failure/Involved | Underground | 122 | 38511 | 35.3323 | -119.0946 | No | Clear;Above 90 | Conductor- Underground | Deteriorated | 23-0087794 | UG | Sus | 31654089 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854459 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 4456 | 20230630 | 1954 | 20230630 | 2137 | 2150312 | 103 | Distribution Circuit | Animal | Bird found | 79 | 8137 | 35.5876 | -118.9581 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0087783 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1854448 | 0 | EPSS Ckt | Y | 2023 | N/A
KERN | KERN | 7TH STANDARD-2101 | 254582101 | FUSE | 18218 | 20230630 | 2039 | 20230701 | 1310 | 2150348 | 991 | Distribution Circuit | Equipment Failure/Involved | Underground | 60 | 19935 | 35.4146 | -119.1099 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0087833 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854501 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2103 | 255262103 | FUSE | 8883 | 20230630 | 2110 | 20230701 | 1527 | 2150385 | 1097 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 30018 | 35.3907 | -119.1154 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0087842 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854520 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 14427 | 20230630 | 2233 | 20230701 | 1736 | 2150454 | 1143 | Distribution Circuit | Equipment Failure/Involved | Underground | 32 | 15408 | 35.3741 | -119.1279 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0087844 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854522 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 18529 | 20230630 | 2303 | 20230701 | 1024 | 2150491 | 681 | Distribution Circuit | Equipment Failure/Involved | Underground | 97 | 66057 | 35.3812 | -119.1453 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0087838 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854515 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20230701 | 917 | 20230701 | 1653 | 2150690 | 456 | Distribution Circuit | Animal | Bird found | 130 | 33200 | 35.5605 | -118.9587 | No | Clear-Heat Wave;32-90 F | PT/CCVT | Burned/flashed | 23-0087867 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854563 | 0 | EPSS Ckt | Y | 2023 | A G INST
KERN | KERN | 7TH STANDARD-2102 | 254582102 | FUSE | 291707 | 20230701 | 1241 | 20230701 | 1745 | 2150798 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 318 | 35.4415 | -119.1414 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 23-0087926 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854584 | 1 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | RECLOSER | 2705 | 20230701 | 1304 | 20230701 | 2124 | 2150812 | 500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 8335 | 35.3617 | -119.291 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0087931 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | Yes | No | 1854587 | 0 | Non-EPSS | N | 2023 | A B SGF
KERN | KERN | TEMBLOR-1104 | 252551104 | OCB | 1104/2 | 20230701 | 1405 | 20230701 | 1421 | 2150859 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 1118 | 35.3831 | -119.6964 | No | Clear-Heat Wave;Above 90 | Recloser | Burned/flashed | 23-0087887 | OH | Sus | 44960863 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1854593 | 0 | EPSS Ckt | Y | 2023 | NONE
KERN | KERN | STOCKDALE-2106 | 254072106 | TRANSFORMER | 516926665897 | 20230701 | 1538 | 20230701 | 2228 | 2150928 | 410 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 4920 | 35.3061 | -119.0309 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 23-0087959 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854607 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517219768077 | 20230701 | 1720 | 20230701 | 1923 | 2151323 | 123 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1476 | 35.3674 | -118.933 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Contaminated | 23-0087997 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854642 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2106 | 254072106 | TRANSFORMER | T6252 | 20230701 | 1823 | 20230702 | 1457 | 2151171 | 1234 | Distribution Circuit | Equipment Failure/Involved | Underground | 59 | 23360 | 35.312 | -119.0275 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 23-0088016 | UG | Sus | 35463918 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854659 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | JUMPER | JUMPER 1 E/OF 17608 | 20230701 | 1827 | 20230701 | 2037 | 2151575 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1300 | 34.9053 | -119.5538 | No | Clear-Heat Wave;Above 90 | Jumper | Burned Open | 23-0088037 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1854678 | 1 | EPSS Ckt | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | T9714 | 20230701 | 1917 | 20230702 | 139 | 2151319 | 382 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 7640 | 35.2976 | -119.0041 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 23-0088021 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854663 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | T3957 | 20230701 | 2037 | 20230704 | 2112 | 2154317 | 4355 | Transformer only | 3rd Party | Vandalism | 2 | 8710 | 35.3966 | -119.0081 | No | Clear;Above 90 | Transformer (UG) | Normal | 23-0088809 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855217 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | TRANSFORMER | 517371570617 | 20230701 | 2228 | 20230702 | 902 | 2151666 | 634 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 634 | 35.4373 | -118.8832 | No | Clear;Above 90 | Transformer | Failed/Faulted | 23-0088076 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854715 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-1108 | 254071108 | FUSE | 6159 | 20230702 | 257 | 20230702 | 2012 | 2151770 | 1035 | Distribution Circuit | Equipment Failure/Involved | Underground | 103 | 92069 | 35.33 | -119.0432 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0088122 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854757 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | 516934869649 | 20230702 | 939 | 20230702 | 1228 | 2151988 | 169 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1521 | 35.4093 | -119.0295 | No | Clear;Above 90 | Service conductor | Arcing | 23-0088146 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854775 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517070468111 | 20230702 | 1348 | 20230702 | 1503 | 2152115 | 75 | Transformer only | Vegetation | Tree - fell into line | 16 | 1200 | 35.3675 | -118.9835 | No | Clear-Heat Wave;Above 90 | Service conductor | Broken- wire on ground | 23-0088185 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854812 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1102 | 254211102 | TRANSFORMER | 515789656609 | 20230702 | 1409 | 20230702 | 1950 | 2152488 | 341 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 341 | 35.0475 | -119.4066 | No | Clear;Above 90 | Transformer (OH) | Deteriorated | 23-0088229 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854850 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 77133 | 20230702 | 1607 | 20230702 | 1805 | 2152331 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 944 | 35.267 | -118.9058 | No | Clear;32-90 F |  |  | 23-0088209 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1854830 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2105 | 254072105 | TRANSFORMER | T8987 | 20230702 | 1804 | 20230703 | 118 | 2152340 | 434 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 10920 | 35.2995 | -119.0712 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 23-0088275 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854914 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516970666327 | 20230702 | 2258 | 20230703 | 17 | 2152877 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 1106 | 35.3181 | -119.0157 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0088287 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854925 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516970666327 | 20230703 | 243 | 20230703 | 947 | 2152939 | 424 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3392 | 35.3181 | -119.0157 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0088325 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854954 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516973366327 | 20230703 | 243 | 20230703 | 947 | 2152938 | 424 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2544 | 35.3181 | -119.0148 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0088328 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854956 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | FUSE | 13972 | 20230703 | 450 | 20230703 | 1415 | 2152969 | 565 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 1695 | 35.6338 | -118.9581 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0088303 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1854946 | 0 | EPSS Ckt | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 9369 | 20230703 | 834 | 20230703 | 958 | 2153088 | 84 | Distribution Circuit | Animal | Squirrel | 11 | 896 | 35.4415 | -118.945 | No | Clear;Above 90 | Fuse | Burned Open | 23-0088404 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1854998 | 1 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 100000017772 | 20230703 | 1027 | 20230703 | 1242 | 2153236 | 135 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 270 | 35.5905 | -119.6137 | No | Clear;Above 90 | Transformer | Normal | 23-0088502 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855032 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516522959821 | 20230703 | 1257 | 20230703 | 1620 | 2153385 | 203 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 203 | 35.1384 | -119.1635 | No | Clear;32-90 F | Jumper | Broken | 23-0088528 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855040 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1104 | 253951104 | TRANSFORMER | 517137568542 | 20230703 | 1927 | 20230704 | 1015 | 2153743 | 888 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 7992 | 35.38 | -118.9605 | No | Clear;Above 90 | Service conductor | Broken | 23-0088698 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855117 | 0 | Non-EPSS | N | 2023
KERN | KERN | CAL WATER-1103 | 255451103 | RECLOSER | 768902 | 20230703 | 1938 | 20230704 | 338 | 2153757 | 480 | Distribution Circuit | Equipment Failure/Involved | Underground | 2039 | 251833 | 35.4021 | -118.914 | No | Clear;Above 90 | Connector or Splice (UG) | Failed/Faulted | 23-0088665 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855083 | 0 | Non-EPSS | N | 2023 | A-GRD
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | T6025 | 20230704 | 40 | 20230704 | 329 | 2153653 | 6 | Transformer only | Equipment Failure/Involved | Underground | 16 | 128 | 35.3805 | -119.1594 | No | Clear;Above 90 | Service conductor | Burned/flashed | 23-0088663 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855080 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517044569075 | 20230704 | 706 | 20230704 | 811 | 2153950 | 65 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 1040 | 35.3929 | -118.992 | No | Clear;32-90 F |  |  | 23-0088729 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1855141 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 144657 | 20230704 | 1235 | 20230704 | 2011 | 2154081 | 456 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 47 | 21432 | 35.2638 | -119.0119 | No | Clear;32-90 F | Fuse | Burned Open | 23-0088756 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855162 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | OCB | 2104/2 | 20230704 | 2110 | 20230705 | 229 | 2154248 | 319 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 4498 | 487666 | 35.3885 | -119.0046 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0088778 | OH | Sus | 45869749 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | Yes | No | 1855186 | 0 | Non-EPSS | N | 2023 | ABC-GRD
KERN | KERN | COLUMBUS-1110 | 253951110 | TRANSFORMER | 517171768832 | 20230705 | 1321 | 20230705 | 1823 | 2154570 | 302 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 906 | 35.3877 | -118.9496 | No | Clear;Above 90 | Transformer (OH) | Deteriorated | 23-0089056 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855337 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1102 | 252611102 | SWITCH | 1442 | 20230705 | 1445 | 20230705 | 1906 | 2154764 | 261 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 7182 | 35.3545 | -119.4117 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 23-0089078 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855341 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | SWITCH | 18855BP | 20230705 | 1450 | 20230705 | 1653 | 2154733 | 123 | Distribution Circuit | 3rd Party | Vehicle | 17 | 2091 | 35.1365 | -119.1635 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0089097 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855344 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2105 | 254072105 | TRANSFORMER | T9332 | 20230706 | 14 | 20230706 | 1025 | 2155049 | 611 | Distribution Circuit | Equipment Failure/Involved | Underground | 85 | 17663 | 35.3029 | -119.0754 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0089195 | UG | Sus | 35465984 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855405 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 1703 | 20230706 | 830 | 20230706 | 1021 | 2155204 | 111 | Distribution Circuit | 3rd Party | Other | 1 | 111 | 35.559 | -118.9797 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0089278 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855460 | 0 | EPSS Ckt | Y | 2023 | A- C
KERN | KERN | CAL WATER-1102 | 255451102 | TRANSFORMER | 517418069636 | 20230706 | 1124 | 20230706 | 1300 | 2155409 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 192 | 35.4072 | -118.8666 | No | Clear;32-90 F | Fuse | Burned Open | 23-0089444 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855542 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 39390 | 20230706 | 1806 | 20230707 | 23 | 2155758 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1131 | 35.2383 | -118.95 | No | Clear;32-90 F | Insulator | Failed/Faulted | 23-0089590 | OH | Sus | 45872786 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855586 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1112 | 253701112 | FUSE | 8094 | 20230706 | 2349 | 20230707 | 1144 | 2155922 | 715 | Distribution Circuit | Equipment Failure/Involved | Underground | 201 | 66313 | 35.3477 | -119.0567 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0089637 | UG | Sus | 31654589 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855619 | 1 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1102 | 254501102 | OCB | 1102/2 | 20230707 | 914 | 20230707 | 1408 | 2156152 | 294 | Distribution Circuit | 3rd Party | Vehicle | 286 | 21809 | 35.6081 | -119.3255 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0089758 | OH | Sus | 31654624 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | Yes | No | 1855697 | 0 | Non-EPSS | N | 2023 | BC GRD TIME OC
KERN | KERN | WEEDPATCH-1101 | 252971101 | OCB | 1101/2 | 20230707 | 1009 | 20230707 | 1808 | 2156283 | 479 | Distribution Circuit | 3rd Party | Vehicle | 8 | 3832 | 35.2238 | -118.88 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0089844 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855725 | 0 | Non-EPSS | N | 2023 | BC PH TIME OC
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 684566 | 20230707 | 1221 | 20230707 | 1614 | 2156301 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1398 | 35.0707 | -119.9955 | No | Clear;32-90 F |  |  | 23-0089890 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855732 | 0 | EPSS Ckt | Y | 2023 | A
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 7120 | 20230707 | 1349 | 20230707 | 1553 | 2156370 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 3472 | 35.4407 | -119.3051 | No | Clear;Above 90 |  |  | 23-0089978 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855752 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 16097 | 20230707 | 1500 | 20230707 | 1540 | 2156420 | 40 | Distribution Circuit | Animal | Other | 2 | 80 | 35.7503 | -119.4776 | No | Clear;Above 90 | Fuse | Burned Open | 23-0089958 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1855747 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13445 | 20230707 | 1503 | 20230707 | 1555 | 2156418 | 52 | Distribution Circuit | Animal | Bird found | 41 | 2132 | 35.3649 | -118.9725 | No | Clear;Above 90 | Fuse | Burned Open | 23-0089982 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855754 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1103 | 254501103 | OCB | 1103/2 | 20230707 | 1626 | 20230708 | 1400 | 2156466 | 1294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 95 | 17650 | 35.6081 | -119.3255 | No | Clear;Above 90 | Crossarm- Wood | Broken- wire on ground | 23-0089983 | OH | Sus | 31654668 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | Yes | No | 1855755 | 0 | Non-EPSS | N | 2023 | A GRD TIM OC
KERN | KERN | 7TH STANDARD-2103 | 254582103 | FUSE | 7350 | 20230708 | 631 | 20230708 | 825 | 2156914 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 114 | 35.4705 | -119.1346 | No | Clear;32-90 F |  |  | 23-0090076 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855835 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | FUSE | 14947 | 20230708 | 2258 | 20230708 | 2338 | 2157469 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 293 | 35.407 | -119.0428 | No | Clear;32-90 F |  |  | 23-0090185 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855927 | 1 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8008 | 20230709 | 808 | 20230709 | 1108 | 2157586 | 180 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 14400 | 35.3491 | -119.0845 | No | Clear;32-90 F |  |  | 23-0090200 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855944 | 0 | Non-EPSS | N | 2023
KERN | KERN | COPUS-1102 | 253871102 | FUSE | 9060 | 20230709 | 928 | 20230709 | 1406 | 2157613 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1113 | 35.1223 | -119.2963 | No | Clear;32-90 F |  |  | 23-0090242 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855970 | 1 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1104 | 253651104 | RECLOSER | 1419 | 20230709 | 1534 | 20230709 | 2347 | 2157753 | 452 | Distribution Circuit | Equipment Failure/Involved | Underground | 1084 | 129200 | 35.5071 | -119.3117 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0090246 | UG | Sus | 45875868 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855973 | 0 | Non-EPSS | N | 2023 | B GRD
KERN | KERN | WESTPARK-1112 | 253701112 | FUSE | 8094 | 20230710 | 557 | 20230711 | 1320 | 2158073 | 1883 | Distribution Circuit | Equipment Failure/Involved | Underground | 201 | 152103 | 35.3477 | -119.0567 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0090308 | UG | Sus | 31654969 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856024 | 1 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1104 | 253651104 | RECLOSER | 1419 | 20230711 | 643 | 20230711 | 1207 | 2159314 | 324 | Distribution Circuit | 3rd Party | Vehicle | 1084 | 97794 | 35.5071 | -119.3117 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0090677 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856312 | 0 | Non-EPSS | N | 2023 | B C
KERN | KERN | BAKERSFIELD-1115 | 253371115 | TRANSFORMER | 516966168547 | 20230711 | 957 | 20230712 | 656 | 2159711 | 1259 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1259 | 35.3794 | -119.0182 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0090859 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856538 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1102 | 252961102 | SWITCH | 5888 | 20230711 | 958 | 20230711 | 1011 | 2159771 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 13 | 35.5883 | -119.3446 | No | Clear;32-90 F | Fuse | Normal | 23-0084980 | OH | Sus | 45604775 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1856491 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515580770618 | 20230711 | 1003 | 20230711 | 1328 | 2159720 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 205 | 35.4315 | -119.4842 | No | Clear;32-90 F | Fuse | Broken | 23-0090888 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856553 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 517121055610 | 20230711 | 1123 | 20230711 | 1201 | 2159717 | 38 | Transformer only | Animal | Bird found | 2 | 76 | 35.0262 | -118.9628 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0090835 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856525 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FAMOSO-1102 | 252461102 | FUSE | 7475 | 20230711 | 1321 | 20230711 | 1453 | 2159934 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1564 | 35.6416 | -119.1868 | No | Clear;Above 90 |  |  | 23-0090919 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856564 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514724480770 | 20230711 | 1611 | 20230711 | 1910 | 2160074 | 179 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 179 | 35.706 | -119.7792 | No | Clear;Above 90 | Fuse | Broken | 23-0091025 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856598 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | OCB | 1104/2 | 20230711 | 1644 | 20230711 | 1739 | 2160092 | 55 | Distribution Circuit | 3rd Party | Vehicle | 400 | 21683 | 35.3531 | -119.271 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0090998 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856586 | 0 | Non-EPSS | N | 2023 | A B TIME
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | T4447 | 20230711 | 1816 | 20230712 | 150 | 2159982 | 454 | Transformer only | Equipment Failure/Involved | Underground | 5 | 2270 | 35.3344 | -118.9111 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0091023 | UG | Sus | 45883119 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856597 | 0 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1101 | 253801101 | FUSE | 15900 | 20230711 | 1930 | 20230712 | 956 | 2160223 | 866 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1247 | 35.14 | -118.8499 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0091038 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856609 | 0 | EPSS Ckt | N | 2023
KERN | KERN | KERN OIL-1104 | 252721104 | TRANSFORMER | 516911074380 | 20230711 | 2019 | 20230712 | 657 | 2160195 | 638 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1276 | 35.5397 | -119.0394 | No | Clear;Above 90 | Transformer | Failed/Faulted | 23-0091035 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856605 | 0 | EPSS Ckt | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 13078 | 20230712 | 832 | 20230712 | 949 | 2160616 | 77 | Distribution Circuit | Animal | Bird found | 203 | 12554 | 35.3086 | -119.0002 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0091196 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856797 | 1 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 14573 | 20230712 | 933 | 20230713 | 200 | 2160662 | 967 | Distribution Circuit | Animal | Bird found | 2 | 1201 | 35.3691 | -119.4388 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0091375 | OH | Sus | 31655154 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856889 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1112 | 252901112 | TRANSFORMER | 515768377842 | 20230712 | 1116 | 20230713 | 435 | 2160742 | 1039 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 1039 | 35.6308 | -119.425 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0091472 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856910 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1105 | 253951105 | FUSE | 3134 | 20230712 | 1528 | 20230713 | 137 | 2161011 | 609 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 11055 | 35.4119 | -118.9588 | No | Clear;Above 90 | Conductor- Underground | Deteriorated | 23-0091483 | UG | Sus | 45884337 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856912 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | FUSE | 18158 | 20230712 | 1746 | 20230712 | 1900 | 2161125 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 888 | 35.3472 | -118.8693 | No | Clear;32-90 F |  |  | 23-0091519 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856927 | 1 | EPSS Ckt | N | 2023
KERN | KERN | SEMITROPIC-1110 | 252901110 | FUSE | 18434 | 20230713 | 808 | 20230713 | 1025 | 2161368 | 137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 640 | 35.6017 | -119.3936 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0091736 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857146 | 1 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8657 | 20230713 | 948 | 20230713 | 1225 | 2161414 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 19154 | 35.3531 | -119.0839 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0091660 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857040 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | 516455768681 | 20230713 | 1658 | 20230713 | 1736 | 2161919 | 38 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 190 | 35.3821 | -119.19 | No | Clear;Above 90 |  |  | 23-0092035 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857239 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | RECLOSER | 4810 | 20230713 | 1722 | 20230713 | 2238 | 2161938 | 316 | Distribution Circuit | 3rd Party | Vehicle | 3318 | 65386 | 35.2958 | -119.0059 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0092024 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857235 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | STOCKDALE-2107 | 254072107 | TRANSFORMER | T3048 | 20230714 | 725 | 20230715 | 1737 | 2162167 | 2020 | Distribution Circuit | Equipment Failure/Involved | Underground | 89 | 66392 | 35.3216 | -119.0768 | No | Clear;32-90 F | Service conductor | Deteriorated | 23-0092212 | UG | Sus | 45887552 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857443 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1105 | 253951105 | SWITCH | 6238 | 20230714 | 1229 | 20230714 | 1350 | 2162596 | 81 | Distribution Circuit | Company Initiated | Return Circuit Normal | 62 | 4239 | 35.4123 | -118.9547 | No | Clear;Above 90 | Conductor- Underground | Normal | 23-0083824 | UG | Sus | 35387233 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857507 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | OTHER | WIRE DOWN HOT 1 POLE N/OF CGC 517330066890 | 20230715 | 726 | 20230715 | 1557 | 2163239 | 511 | Distribution Circuit | Animal | Bird found | 108 | 20873 | 35.3352 | -118.8965 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0092545 | OH | Sus | 35468159 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | Yes | 1857632 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | OCB | 2115/2 | 20230715 | 807 | 20230717 | 509 | 2163544 | 2702 | Distribution Circuit | Equipment Failure/Involved | Underground | 146 | 160057 | 35.3165 | -119.0677 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Broken | 23-0092543 | UG | Sus | 45888247 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857699 | 0 | Non-EPSS | N | 2023 | C/GRD PHASE OC TIME
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515300472730 | 20230715 | 823 | 20230716 | 1640 | 2163299 | 1937 | Transformer only | Animal | Other | 1 | 1937 | 35.4876 | -119.5791 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0092658 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857702 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | 515560873949 | 20230715 | 840 | 20230715 | 1057 | 2163312 | 137 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 137 | 35.5228 | -119.4924 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0092586 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857671 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1108 | 253701108 | TRANSFORMER | 516960267251 | 20230715 | 1747 | 20230715 | 2215 | 2163715 | 268 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 2412 | 35.3437 | -119.0196 | No | Clear-Heat Wave;Above 90 |  |  | 23-0092705 | OH | Sus | 31655686 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857726 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2102 | 253142102 | RECLOSER | 195688 | 20230715 | 1816 | 20230716 | 852 | 2163737 | 876 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 18396 | 34.9379 | -119.4727 | No | Clear-Heat Wave;Above 90 |  |  | 23-0092696 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857721 | 0 | EPSS Ckt | Y | 2023 | C- SGF & 50 INST
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 10777 | 20230715 | 2000 | 20230716 | 1345 | 2163826 | 1019 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 14512 | 35.321 | -119.0678 | No | Clear;Above 90 | Transformer (UG) | Broken | 23-0092718 | UG | Sus | 35469220 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857737 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2108 | 254072108 | RECLOSER | 4265 | 20230715 | 2325 | 20230716 | 1717 | 2163939 | 1014 | Distribution Circuit | Equipment Failure/Involved | Underground | 1887 | 331032 | 35.3181 | -119.0826 | No | Partly Cloudy;32-90 F | Elbow | Failed/Faulted | 23-0092747 | UG | Sus | 45888823 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857765 | 0 | Non-EPSS | N | 2023 | AG
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 1703 | 20230716 | 842 | 20230716 | 2136 | 2164082 | 774 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 774 | 35.559 | -118.9797 | No | Partly Cloudy-Heat Wave;32-90 F | Customer Equipment | Failed/Faulted | 23-0092779 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857805 | 0 | EPSS Ckt | Y | 2023 | A & C
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 69452 | 20230716 | 944 | 20230716 | 2341 | 2164124 | 837 | Distribution Circuit | Equipment Failure/Involved | Underground | 34 | 28458 | 35.3647 | -119.0923 | No | Clear;Above 90 | Conductor- Underground | Burned/flashed | 23-0092795 | UG | Sus | 31655860 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857828 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 8069 | 20230716 | 1507 | 20230717 | 444 | 2164345 | 817 | Distribution Circuit | Equipment Failure/Involved | Underground | 130 | 50212 | 35.4159 | -119.0468 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Broken | 23-0092841 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857874 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | T324 | 20230716 | 1652 | 20230716 | 1738 | 2164189 | 46 | Transformer only | Equipment Failure/Involved | Underground | 18 | 828 | 35.3989 | -119.0159 | No | Clear-Heat Wave;Above 90 | Connector or Splice (UG) | Deteriorated | 23-0092828 | UG | Sus | 45888791 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857866 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517032165640 | 20230716 | 1654 | 20230716 | 2232 | 2164486 | 338 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 2704 | 35.2995 | -118.9951 | No | Heat Wave-Clear;Above 90 | Transformer | Broken | 23-0092893 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857915 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | T0083 | 20230716 | 1743 | 20230716 | 1833 | 2164545 | 50 | Transformer only | Unknown Cause | Patrol - found nothing | 21 | 1050 | 35.3627 | -118.9421 | No | Clear-Heat Wave;Above 90 |  |  | 23-0092891 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1857913 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1112 | 253491112 | TRANSFORMER | 516847074438 | 20230716 | 1831 | 20230716 | 2252 | 2164534 | 261 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 522 | 35.5406 | -119.0605 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 23-0092898 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857918 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1108 | 252081108 | TRANSFORMER | 515635859721 | 20230716 | 1848 | 20230716 | 1953 | 2164599 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 455 | 35.1322 | -119.4604 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092905 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857926 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1103 | 252081103 | TRANSFORMER | 515629260494 | 20230716 | 1914 | 20230716 | 2039 | 2164606 | 85 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 850 | 35.1534 | -119.4633 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092913 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857934 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1108 | 254071108 | TRANSFORMER | T0539 | 20230716 | 1946 | 20230717 | 1236 | 2164699 | 1005 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 30480 | 35.33 | -119.0424 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Broken | 23-0092935 | UG | Sus | 35468501 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857952 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2105 | 254072105 | TRANSFORMER | T8989 | 20230716 | 1956 | 20230717 | 308 | 2164734 | 432 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 5490 | 35.2976 | -119.0704 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0092963 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857977 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2105 | 255322105 | TRANSFORMER | T9365 | 20230716 | 1959 | 20230717 | 253 | 2164738 | 414 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 7038 | 35.3508 | -119.1166 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0092937 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857953 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 6269 | 20230717 | 5 | 20230717 | 1934 | 2164917 | 1169 | Distribution Circuit | Equipment Failure/Involved | Underground | 98 | 26656 | 35.4122 | -119.0625 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0092971 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857985 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2105 | 255322105 | OTHER | J959 TWD T9365 | 20230717 | 152 | 20230717 | 244 | 2164985 | 52 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 1456 | 35.3507 | -119.1155 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0092932 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857988 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7119 | 20230717 | 749 | 20230717 | 1115 | 2165081 | 206 | Distribution Circuit | Animal | Other | 6 | 1236 | 35.5719 | -119.5985 | No | Partly Cloudy-Heat Wave;Above 90 | Fuse | Burned Open | 23-0093108 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858148 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1106 | 253411106 | FUSE | 18554 | 20230717 | 1239 | 20230717 | 2340 | 2165456 | 661 | Distribution Circuit | 3rd Party | Vehicle | 1 | 661 | 35.0769 | -119.0916 | No | Partly Cloudy-Heat Wave;Above 90 | Conductor- Overhead | Normal | 23-0093176 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858186 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2108 | 254072108 | SWITCH | 10422 | 20230717 | 1353 | 20230717 | 1406 | 2164065 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 98 | 1274 | 35.3247 | -119.0915 | No | Clear;32-90 F | Connector or Splice (UG) | Normal | 23-0092543 | UG | Sus | 45888247 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1857799 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-2101 | 254682101 | TRANSFORMER | 514719579640 | 20230717 | 1355 | 20230718 | 240 | 2165656 | 765 | Transformer only | 3rd Party | Customer Equipment | 1 | 765 | 35.6754 | -119.7787 | No | Partly Cloudy-Heat Wave;Above 90 | Customer Equipment | Burned/flashed | 23-0093297 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858226 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517521262190 | 20230717 | 1459 | 20230718 | 358 | 2165828 | 779 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3895 | 35.2061 | -118.8305 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 23-0093357 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858241 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517521262217 | 20230717 | 1459 | 20230718 | 357 | 2165829 | 778 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 7780 | 35.2069 | -118.8305 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 23-0093360 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858244 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 9362 | 20230717 | 1731 | 20230717 | 1823 | 2165907 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 1664 | 35.3105 | -119.018 | No | Clear-Heat Wave;Above 90 |  |  | 23-0093401 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858265 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | RECLOSER | 3241 | 20230718 | 1005 | 20230718 | 1911 | 2166236 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 10431 | 35.6417 | -119.9035 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0093587 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858474 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 15931 | 20230718 | 1023 | 20230719 | 314 | 2166630 | 1011 | Distribution Circuit | 3rd Party | Vehicle | 4 | 4044 | 35.26 | -118.8785 | No | Clear;32-90 F | Transformer (OH) | On Ground | 23-0093673 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1858504 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514351079584 | 20230718 | 1137 | 20230718 | 2204 | 2167277 | 627 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 627 | 35.6722 | -119.9032 | No | Clear-Heat Wave;Above 90 | Fuse | Broken | 23-0093968 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858609 | 0 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 514086078492 | 20230718 | 1206 | 20230719 | 1 | 2166651 | 715 | Transformer only | Animal | Bird found | 1 | 715 | 35.6405 | -119.9924 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 23-0093822 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858536 | 0 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 515155973956 | 20230718 | 1347 | 20230719 | 240 | 2166758 | 773 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 773 | 35.521 | -119.6283 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093905 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858559 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1107 | 252721107 | FUSE | 13283 | 20230718 | 1533 | 20230718 | 1612 | 2166864 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 39 | 35.4558 | -119.0299 | No | Clear-Heat Wave;Above 90 | Crossarm- Wood | Broken | 23-0093895 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858552 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | RECLOSER | 152466 | 20230718 | 1553 | 20230718 | 2009 | 2166880 | 256 | Distribution Circuit | 3rd Party | Vehicle | 365 | 32240 | 35.6745 | -119.2399 | No | Clear-Heat Wave;Above 90 | Capacitor | Broken | 23-0093897 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858553 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514351379360 | 20230718 | 2120 | 20230719 | 440 | 2166548 | 440 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 440 | 35.667 | -119.9033 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Leaking | 23-0093950 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858591 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1102 | 253191102 | FUSE | 13356 | 20230718 | 2210 | 20230719 | 5 | 2167321 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 345 | 35.1215 | -118.8763 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0093951 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858593 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514375680140 | 20230718 | 2214 | 20230719 | 340 | 2167276 | 326 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 326 | 35.6874 | -119.8958 | No | Clear-Heat Wave;Above 90 | Bushing | Broken | 23-0093978 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858617 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | TRANSFORMER | 517804055610 | 20230719 | 839 | 20230720 | 100 | 2167638 | 981 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 981 | 35.0261 | -118.7332 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0094110 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858801 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517059567750 | 20230719 | 1211 | 20230719 | 2100 | 2167942 | 529 | Transformer only | Equipment Failure/Involved | Electrical Overload | 10 | 5290 | 35.3575 | -118.9869 | No | Clear;Above 90 | Transformer (OH) | Normal | 23-0094228 | OH | Sus | 45894093 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858853 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1103 | 252721103 | FUSE | 8068 | 20230719 | 1454 | 20230720 | 104 | 2168303 | 610 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 18300 | 35.4141 | -119.0507 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0094323 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1858901 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1102 | 253181102 | SWITCH | 1217 | 20230719 | 2339 | 20230720 | 321 | 2168463 | 222 | Distribution Circuit | 3rd Party | Vehicle | 25 | 5550 | 35.703 | -119.3683 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0094392 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858924 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1104 | 253651104 | FUSE | 16105 | 20230720 | 1137 | 20230721 | 112 | 2168872 | 815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 33415 | 35.5066 | -119.2805 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 23-0094664 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1859097 | 0 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | OCB | 1101/2 | 20230720 | 1251 | 20230720 | 1925 | 2168949 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 27579 | 35.6579 | -119.9968 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 23-0094713 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1859108 | 0 | EPSS Ckt | N | 2023 | SET A RLY- AC
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517056268959 | 20230720 | 1330 | 20230720 | 1439 | 2169025 | 69 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 828 | 35.3908 | -118.988 | No | Clear;Above 90 | Fuse | Broken | 23-0094807 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859138 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 517025355681 | 20230720 | 1438 | 20230721 | 500 | 2168988 | 862 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 862 | 35.0262 | -118.9945 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0094827 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859148 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | TRANSFORMER | T12298 | 20230721 | 548 | 20230721 | 757 | 2169518 | 129 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 129 | 35.3386 | -119.2251 | No | Clear;32-90 F |  |  | 23-0095035 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1859271 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1105 | 253911105 | FUSE | 16993 | 20230721 | 735 | 20230721 | 1521 | 2169675 | 466 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2330 | 35.2599 | -118.8428 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0095062 | OH | Sus | 31656114 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | Yes | No | 1859335 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | FUSE | 18158 | 20230721 | 957 | 20230721 | 1056 | 2169780 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 708 | 35.3472 | -118.8693 | No | Clear;32-90 F |  |  | 23-0095180 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859421 | 1 | EPSS Ckt | N | 2023
KERN | KERN | SEMITROPIC-1110 | 252901110 | FUSE | 18434 | 20230721 | 1057 | 20230721 | 1312 | 2169859 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 630 | 35.6017 | -119.3936 | No | Clear;Above 90 |  |  | 23-0095257 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859436 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 8412 | 20230721 | 1220 | 20230721 | 1312 | 2169952 | 52 | Distribution Circuit | Animal | Bird found | 85 | 4420 | 35.3287 | -119.0501 | No | Clear;Above 90 | Fuse | Burned Open | 23-0095281 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859448 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1107 | 253411107 | TRANSFORMER | 100000007432 | 20230721 | 1320 | 20230724 | 1347 | 2170001 | 4347 | Transformer only | Animal | Bird found | 1 | 4347 | 35.0581 | -119.1849 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0095304 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859453 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16172 | 20230721 | 1912 | 20230721 | 2053 | 2170298 | 101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 808 | 35.1513 | -119.071 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0095428 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859492 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2105 | 254072105 | TRANSFORMER | T8703 | 20230721 | 2313 | 20230722 | 1320 | 2170479 | 847 | Distribution Circuit | Equipment Failure/Involved | Underground | 79 | 23948 | 35.3023 | -119.0585 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0095484 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859543 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | OCB | 2101/2 | 20230722 | 611 | 20230722 | 849 | 2170598 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 19592 | 34.9276 | -119.6203 | No | Clear;32-90 F |  |  | 23-0095503 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859567 | 0 | EPSS Ckt | Y | 2023 | PH OC B GRD
KERN | KERN | ELK HILLS-1104 | 252441104 | OTHER | WIRE DOWN 4 SP S/E OF 9266 | 20230722 | 1209 | 20230722 | 1619 | 2170858 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 473 | 36587 | 35.2182 | -119.3895 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 23-0095562 | OH | Sus | 31656459 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | Yes | Yes | 1859661 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | RECLOSER | 1550 | 20230723 | 157 | 20230723 | 333 | 2171279 | 96 | Distribution Circuit | Animal | Other | 189 | 9396 | 35.5303 | -119.1693 | No | Partly Cloudy;32-90 F | Recloser | Burned/flashed | 23-0095651 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1859743 | 0 | Non-EPSS | N | 2023 | A- B- C
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 8961 | 20230723 | 648 | 20230723 | 1137 | 2171319 | 172 | Distribution Circuit | Equipment Failure/Involved | Underground | 233 | 46334 | 35.3105 | -119.0071 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0095663 | UG | Sus | 31656602 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859757 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRIP-SAVER | 16874 | 20230723 | 1634 | 20230723 | 2016 | 2171795 | 222 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 125 | 9132 | 35.3685 | -118.9654 | No | Partly Cloudy-Heat Wave;Above 90 | Secondary | Burned/flashed | 23-0095710 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859810 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516813563955 | 20230723 | 1804 | 20230723 | 2245 | 2171805 | 281 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 281 | 35.2527 | -119.0677 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0095717 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859818 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1106 | 253371106 | JUMPER | OJ 1 E/ OF CGC 517048668783 | 20230723 | 1823 | 20230724 | 237 | 2171878 | 494 | Distribution Circuit | Vegetation | Tree - branch fell on line | 192 | 19554 | 35.3858 | -118.9901 | No | Clear-Heat Wave;Above 90 | Secondary | Broken- wire on ground | 23-0095728 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859829 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514643281172 | 20230724 | 756 | 20230724 | 1019 | 2172161 | 143 | Transformer only | Animal | Other | 1 | 143 | 35.7168 | -119.8054 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0095906 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860020 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | T11646 | 20230724 | 941 | 20230724 | 958 | 2172185 | 17 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 17 | 35.204 | -119.09 | No | Clear;32-90 F |  |  | 23-0095891 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1860006 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1104 | 253551104 | FUSE | 7293 | 20230724 | 1520 | 20230724 | 2019 | 2172732 | 299 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 14 | 4186 | 35.79 | -119.4629 | No | Clear;Above 90 | Pole-Wood | Burned/flashed | 23-0096194 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1860117 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515628369524 | 20230724 | 2056 | 20230725 | 1051 | 2172915 | 835 | Transformer only | 3rd Party | Vehicle | 4 | 3340 | 35.4016 | -119.4682 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0096245 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860158 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1106 | 254071106 | TRANSFORMER | T0193 | 20230724 | 2338 | 20230725 | 40 | 2172958 | 62 | Transformer only | Equipment Failure/Involved | Underground | 23 | 1426 | 35.3185 | -119.0604 | No | Clear;32-90 F | Secondary | Broken | 23-0096257 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860166 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | OTHER | T12878 TWD T12879 | 20230725 | 152 | 20230725 | 249 | 2172991 | 57 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 1710 | 35.2825 | -119.0086 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0096133 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860173 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | JUMPER | OJ 2 N/OF 2469 | 20230725 | 534 | 20230725 | 654 | 2173046 | 80 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 8640 | 35.314 | -118.8965 | No | Clear;32-90 F | Jumper | Burned Open | 23-0096287 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1860185 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 14637 | 20230725 | 714 | 20230725 | 1012 | 2173083 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 6764 | 35.336 | -119.0151 | No | Clear;32-90 F | Jumper | Burned Open | 23-0096413 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1860364 | 1 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | OCB | 1101/2 | 20230725 | 1309 | 20230725 | 1826 | 2173575 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 367 | 23048 | 35.0891 | -118.9767 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0096544 | OH | Sus | 45900663 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1860398 | 0 | EPSS Ckt | N | 2023 | PH OC INSTA- GRD
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514508379107 | 20230725 | 1340 | 20230725 | 1620 | 2173602 | 160 | Transformer only | Animal | Other | 1 | 160 | 35.6587 | -119.8499 | No | Clear;Above 90 | Fuse | Failed/Faulted | 23-0096720 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860431 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1116 | 253371116 | OCB | 1116/2 | 20230725 | 1431 | 20230725 | 1532 | 2173642 | 61 | Distribution Circuit | 3rd Party | Metallic Balloon | 2735 | 166835 | 35.3886 | -119.0042 | No | Clear;Above 90 | Transformer (OH) | Normal | 23-0096622 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1860421 | 0 | Non-EPSS | N | 2023 | A B
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 15301 | 20230725 | 1736 | 20230725 | 2318 | 2173788 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 2181 | 35.2523 | -118.9276 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0096747 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860438 | 1 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | OCB | 1101/2 | 20230725 | 2047 | 20230725 | 2332 | 2173901 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 104 | 16805 | 35.6579 | -119.9968 | No | Clear;32-90 F |  |  | 23-0096776 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860456 | 0 | EPSS Ckt | N | 2023 | SET A
KERN | KERN | WESTPARK-1101 | 253701101 | FUSE | 8748 | 20230726 | 655 | 20230726 | 1501 | 2174035 | 486 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 486 | 35.3606 | -119.0092 | No | Clear;32-90 F | Customer Equipment | Broken | 23-0096844 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860508 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14955 | 20230726 | 1354 | 20230726 | 1441 | 2174534 | 47 | Distribution Circuit | 3rd Party | Metallic Balloon | 146 | 6042 | 35.4036 | -118.9766 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0097149 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1860729 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1101 | 253371101 | FUSE | 8638 | 20230726 | 1827 | 20230728 | 324 | 2174784 | 1977 | Distribution Circuit | Equipment Failure/Involved | Underground | 143 | 45897 | 35.3976 | -119.0039 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0097261 | UG | Sus | 35472778 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1860754 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 16865 | 20230727 | 936 | 20230727 | 1041 | 2175225 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 585 | 35.3776 | -118.9542 | No | Clear;32-90 F |  |  | 23-0097545 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1860977 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1103 | 252861103 | FUSE | 14011 | 20230727 | 1744 | 20230727 | 1937 | 2175727 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1695 | 35.4334 | -119.1896 | No | Clear;Above 90 | Anchor or Guy | Broken | 23-0097805 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861043 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 390355 | 20230728 | 618 | 20230728 | 757 | 2175941 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 4653 | 35.3569 | -119.0062 | No | Clear;32-90 F |  |  | 23-0097921 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861129 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRIP-SAVER | 13017 | 20230728 | 717 | 20230728 | 1206 | 2175961 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 36992 | 35.335 | -119.0029 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0097993 | OH | Sus | 31656994 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | Yes | No | 1861247 | 0 | Non-EPSS | N | 2023 | LINE-LINE
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 8939 | 20230728 | 904 | 20230728 | 1115 | 2176103 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1965 | 35.3636 | -118.9653 | No | Clear;32-90 F |  |  | 23-0098053 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861275 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 9725 | 20230729 | 337 | 20230729 | 458 | 2176887 | 81 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 566 | 35.3323 | -119.0028 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0098264 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861380 | 1 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1105 | 253951105 | FUSE | 3134 | 20230729 | 708 | 20230730 | 302 | 2176927 | 1194 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 24316 | 35.4119 | -118.9588 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 23-0098281 | UG | Sus | 35473359 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1861412 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | SWITCH | 16755 | 20230729 | 743 | 20230729 | 1119 | 2176943 | 216 | Distribution Circuit | Animal | Other | 19 | 4104 | 35.5496 | -118.9216 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0095802 | OH | Sus | 31646607 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1861399 | 0 | EPSS Ckt | N | 2023
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 16643 | 20230729 | 1809 | 20230729 | 2022 | 2177307 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 22610 | 35.4995 | -119.2805 | No | Clear;Above 90 |  |  | 23-0098371 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861505 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 14859 | 20230730 | 215 | 20230730 | 1415 | 2177506 | 720 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9243 | 35.4557 | -118.9199 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0098418 | OH | Sus | 31657540 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | Yes | No | 1861555 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SHAFTER-1104 | 253651104 | TRANSFORMER | MTR#1010332476 | 20230730 | 1255 | 20230730 | 1317 | 2177665 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 264 | 35.501 | -119.2757 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0098457 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861602 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516794863504 | 20230730 | 1753 | 20230731 | 17 | 2177911 | 384 | Transformer only | Environmental/External | Fire- Forest/Grass | 2 | 768 | 35.2401 | -119.0744 | No | Clear;32-90 F | Secondary | Broken- wire on object | 23-0098483 | OH | Sus | 31657564 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861621 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1110 | 253371110 | OTHER | BURNED OPEN CONNECTOR | 20230730 | 1937 | 20230730 | 2252 | 2177966 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1333 | 229411 | 35.3895 | -119.0148 | No | Partly Cloudy;Above 90 | Connector or Splice (OH) | Burned Open | 23-0098487 | OH | Sus | 45906250 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1861626 | 1 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1101 | 252081101 | TRANSFORMER | 515671660041 | 20230731 | 55 | 20230731 | 343 | 2178063 | 168 | Transformer only | Vegetation | Tree - branch fell on line | 13 | 2184 | 35.1413 | -119.4487 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0098528 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861666 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 14554 | 20230731 | 726 | 20230731 | 1058 | 2178152 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 636 | 35.2452 | -119.0386 | No | Clear;32-90 F |  |  | 23-0098660 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861823 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1101 | 252081101 | TRANSFORMER | 515671660041 | 20230731 | 955 | 20230731 | 1043 | 2178350 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 624 | 35.1413 | -119.4487 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0098625 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861807 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1103 | 254501103 | OCB | 1103/2 | 20230731 | 1043 | 20230731 | 1102 | 2178406 | 19 | Distribution Circuit | 3rd Party | Vehicle | 95 | 1805 | 35.6081 | -119.3255 | No | Partly Cloudy;32-90 F | Anchor or Guy | Normal | 23-0098662 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861824 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | KERN POWER-2103 | 255262103 | TRANSFORMER | 516764068756 | 20230731 | 1136 | 20230731 | 1948 | 2178405 | 492 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 492 | 35.3844 | -119.0864 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0098693 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861837 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 18388 | 20230731 | 1234 | 20230731 | 1935 | 2178537 | 421 | Distribution Circuit | Animal | Bird found | 8 | 1128 | 35.4634 | -119.1801 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 23-0098769 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861872 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 19031 | 20230731 | 1238 | 20230731 | 1340 | 2178544 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 3060 | 35.4133 | -119.0801 | No | Clear;Above 90 |  |  | 23-0098732 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861856 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516970666327 | 20230731 | 1730 | 20230731 | 1837 | 2178865 | 67 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 536 | 35.3181 | -119.0157 | No | Clear;Above 90 |  |  | 23-0098876 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1861902 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | 517365065035 | 20230731 | 2213 | 20230801 | 22 | 2179015 | 129 | Transformer only | 3rd Party | Customer Equipment | 3 | 387 | 35.2836 | -118.8832 | No | Clear;32-90 F | Metering Equipment | Burned/flashed | 23-0098921 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861936 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-1104 | 252771104 | OTHER | T12209 TWD T12210 | 20230731 | 2222 | 20230731 | 2345 | 2179016 | 83 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 1909 | 35.3509 | -118.9441 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0098782 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861929 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1104 | 252771104 | OTHER | T11762 TWD T11763 | 20230801 | 27 | 20230801 | 145 | 2179056 | 78 | Distribution Circuit | Equipment Failure/Involved | Underground | 53 | 4134 | 35.3502 | -118.946 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0098797 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1861937 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1105 | 252931105 | FUSE | 9921 | 20230801 | 508 | 20230801 | 728 | 2179092 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 840 | 35.0744 | -118.8845 | No | Clear;32-90 F |  |  | 23-0098957 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1861977 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1105 | 254561105 | FUSE | 17344 | 20230801 | 800 | 20230821 | 1940 | 2198315 | 29500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 29500 | 35.3188 | -119.3238 | No | Clear;32-90 F | Bushing | Broken | 23-0107129 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1867695 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2108 | 254072108 | TRANSFORMER | T7200 | 20230801 | 858 | 20230801 | 1328 | 2179300 | 270 | Transformer only | Equipment Failure/Involved | Underground | 16 | 4320 | 35.3245 | -119.0989 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0098988 | UG | Sus | 45907243 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862075 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1102 | 254211102 | JUMPER | #3 BLOWN JMPR | 20230801 | 1047 | 20230801 | 1734 | 2179475 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 407 | 35.0357 | -119.3759 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0099313 | OH | Sus | 45907545 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862209 | 1 | EPSS Ckt | N | 2023
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | 516457867897 | 20230801 | 1513 | 20230801 | 2214 | 2179575 | 421 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1263 | 35.3597 | -119.1891 | No | Clear;Above 90 | Conductor- Underground | Deteriorated | 23-0099243 | UG | Sus | 45907511 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862191 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | RECLOSER | 1647 | 20230801 | 1600 | 20230801 | 1642 | 2179737 | 42 | Distribution Circuit | 3rd Party | Vehicle | 60 | 2520 | 35.2092 | -119.2097 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0099282 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862201 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | POSO MOUNTAIN 2104 | 253642104 | OCB | 2104/2 | 20230801 | 1616 | 20230804 | 1523 | 2179748 | 4267 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 15 | 40347 | 35.5593 | -118.9576 | No | Partly Cloudy;Above 90 | Pole-Wood | Burned/flashed | 23-0099299 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862203 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | KERN OIL-1109 | 252721109 | TRANSFORMER | 516885469957 | 20230801 | 1820 | 20230802 | 352 | 2179905 | 572 | Transformer only | Vegetation | Tree - grew into line | 12 | 6864 | 35.4177 | -119.0461 | No | Clear;Above 90 | Transformer | Broken- wire on ground | 23-0099339 | OH | Sus | 45907664 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1862224 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1112 | 253491112 | JUMPER | BURNED OPEN JPR 2P W/O CGC 516815074056 | 20230801 | 1913 | 20230801 | 2052 | 2179921 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 4897 | 35.5301 | -119.0728 | No | Clear;Above 90 | Connector or Splice (OH) | Deteriorated | 23-0099342 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862229 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1105 | 252771105 | TRANSFORMER | 517181268457 | 20230802 | 17 | 20230802 | 143 | 2180029 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 860 | 35.3778 | -118.9458 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0099371 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862251 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 8939 | 20230802 | 647 | 20230802 | 810 | 2180146 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1245 | 35.3636 | -118.9653 | No | Clear;32-90 F |  |  | 23-0099428 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862292 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1108 | 252771108 | OTHER | J1326 TWD T11220 | 20230802 | 852 | 20230802 | 1005 | 2180274 | 73 | Distribution Circuit | Equipment Failure/Involved | Underground | 34 | 2482 | 35.3584 | -118.8997 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0099350 | UG | Sus | 35474181 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862363 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | TRIP-SAVER | 2455 | 20230802 | 1019 | 20230802 | 1608 | 2180469 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 270 | 44918 | 34.8582 | -118.8838 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0099624 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1862498 | 0 | EPSS Ckt | N | 2023 | #1 & #2 POS
KERN | KERN | MAGUNDEN-1105 | 252771105 | FUSE | 14853 | 20230802 | 1557 | 20230802 | 1707 | 2180816 | 70 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 68 | 4760 | 35.3726 | -118.927 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0099733 | OH | Sus | 45908503 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862530 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | SWITCH | 1785 | 20230802 | 1938 | 20230803 | 550 | 2180968 | 612 | Distribution Circuit | Environmental/External | Water | 2158 | 325210 | 35.401 | -119.0124 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0099787 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862550 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1104 | 252961104 | OCB | 1104/2 | 20230802 | 2053 | 20230803 | 1850 | 2181025 | 1317 | Distribution Circuit | 3rd Party | Vandalism | 1355 | 410975 | 35.6018 | -119.3261 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0099802 | UG | Sus | 31659001 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862563 | 0 | Non-EPSS | N | 2023 | PH OC- C GRD
KERN | KERN | COPUS-1103 | 253871103 | TRANSFORMER | 516265858243 | 20230803 | 847 | 20230804 | 1109 | 2181289 | 1582 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1582 | 35.0938 | -119.2492 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0099973 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862692 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | RECLOSER | 46960 | 20230803 | 952 | 20230803 | 1108 | 2181400 | 76 | Distribution Circuit | 3rd Party | Other | 8 | 608 | 35.4771 | -118.887 | No | Clear;32-90 F | Other | Normal | 23-0100015 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1862744 | 0 | EPSS Ckt | Y | 2023 | C
KERN | KERN | WASCO-1101 | 252961101 | OTHER | T14016 TWD T14017 | 20230803 | 1040 | 20230803 | 1137 | 2181483 | 57 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 1083 | 35.5817 | -119.3499 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0099994 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862773 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | FUSE | 7021 | 20230803 | 1733 | 20230803 | 2056 | 2181846 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1870 | 35.4412 | -119.6427 | No | Clear;32-90 F |  |  | 23-0100319 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1862891 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 2181 | 20230803 | 2031 | 20230804 | 1054 | 2181964 | 863 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 42838 | 35.5944 | -118.9585 | No | Clear;32-90 F |  |  | 23-0100317 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1862890 | 0 | EPSS Ckt | Y | 2023 | A C
KERN | KERN | SMYRNA-1102 | 253551102 | RECLOSER | 1183 | 20230804 | 704 | 20230804 | 1327 | 2182076 | 383 | Distribution Circuit | 3rd Party | Vehicle | 61 | 18347 | 35.7466 | -119.4343 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0100412 | OH | Sus | 31661900 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | Yes | No | 1862943 | 0 | Non-EPSS | N | 2023 | B C GRD
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 11011 | 20230804 | 1027 | 20230804 | 2230 | 2182338 | 723 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 16886 | 35.3243 | -119.0298 | No | Clear;32-90 F | Bushing | Failed/Faulted | 23-0100581 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1863105 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | FUSE | 18901 | 20230804 | 1157 | 20230804 | 1758 | 2182558 | 361 | Distribution Circuit | 3rd Party | Other | 2 | 705 | 35.5001 | -119.457 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0100742 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863151 | 1 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 15036 | 20230804 | 1746 | 20230805 | 1118 | 2182698 | 1052 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1221 | 34.984 | -118.8643 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100803 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863183 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 100000012402 | 20230804 | 1831 | 20230805 | 1239 | 2182717 | 1088 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1088 | 35.5249 | -119.6084 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100794 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863173 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 100000000370 | 20230804 | 1857 | 20230805 | 1138 | 2182723 | 1001 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1001 | 35.5072 | -119.5768 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100796 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863175 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 14371 | 20230805 | 50 | 20230805 | 328 | 2182812 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3315 | 35.2674 | -119.0354 | No | Clear;32-90 F |  |  | 23-0100834 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863217 | 1 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517152868420 | 20230806 | 12 | 20230806 | 1502 | 2183480 | 890 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 7120 | 35.3767 | -118.9554 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0100978 | OH | Sus | 35475381 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863381 | 0 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | FUSE | 7485 | 20230806 | 803 | 20230806 | 1030 | 2183515 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1470 | 35.6571 | -119.9211 | No | Clear;32-90 F |  |  | 23-0101006 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863416 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | RECLOSER | 4505 | 20230806 | 945 | 20230806 | 1029 | 2183566 | 44 | Distribution Circuit | 3rd Party | Vehicle | 95 | 4180 | 35.3541 | -118.9651 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0100979 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1863406 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 2181 | 20230806 | 1025 | 20230806 | 1456 | 2183578 | 271 | Distribution Circuit | 3rd Party | Customer Equipment | 50 | 13354 | 35.5944 | -118.9585 | No | Clear;32-90 F | Customer Equipment | Burned Open | 23-0101002 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863413 | 0 | EPSS Ckt | Y | 2023 | B G
KERN | KERN | CARNERAS-1103 | 252321103 | RECLOSER | 1584 | 20230806 | 1944 | 20230807 | 1827 | 2183824 | 1363 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 18948 | 35.5424 | -119.8074 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0101051 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1863450 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | KERN POWER-2103 | 255262103 | FUSE | 16274 | 20230807 | 654 | 20230807 | 932 | 2184045 | 158 | Distribution Circuit | Animal | Bird found | 12 | 1841 | 35.3857 | -119.1101 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0101170 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863626 | 1 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13912 | 20230807 | 916 | 20230807 | 1740 | 2184304 | 504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 5364 | 35.7015 | -119.69 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0101175 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863635 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 8491 | 20230807 | 924 | 20230807 | 1218 | 2184324 | 174 | Distribution Circuit | Animal | Squirrel | 30 | 5220 | 35.3251 | -119.0451 | No | Clear;32-90 F | Jumper | Broken | 23-0101189 | OH | Sus | 45915678 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863655 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17784 | 20230807 | 937 | 20230807 | 1028 | 2184344 | 51 | Distribution Circuit | Animal | Bird found | 211 | 10761 | 35.3447 | -119.0708 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0101204 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863666 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2103 | 255262103 | TRANSFORMER | 516764068756 | 20230807 | 1545 | 20230807 | 1635 | 2184854 | 50 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 50 | 35.3844 | -119.0864 | No | Clear;Above 90 |  |  | 23-0101415 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1863767 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2111 | 254072111 | INTERRUPTER | 4022 | 20230807 | 1914 | 20230807 | 2226 | 2185032 | 192 | Distribution Circuit | Equipment Failure/Involved | Underground | 259 | 49728 | 35.3213 | -119.0682 | No | Clear;Above 90 | Conductor- Underground | Broken | 23-0101455 | UG | Sus | 45916608 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863790 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | JUMPER | OJS 2 W/OF CGC# 515905970467 | 20230808 | 920 | 20230808 | 1134 | 2185409 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 268 | 35.4286 | -119.3761 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0101609 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1863959 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1104 | 252901104 | RECLOSER | 4549 | 20230808 | 1458 | 20230808 | 1911 | 2185914 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 1228 | 35.5994 | -119.4736 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0101848 | OH | Sus | 31662543 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864079 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | LAMONT-1102 | 253911102 | OTHER | WIRE DOWN 1 PHASE @ L&B POLE W/OF D4519 | 20230808 | 1908 | 20230809 | 216 | 2186151 | 392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 417 | 110948 | 35.2963 | -118.8786 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0101944 | OH | Sus | 45917814 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1864113 | 1 | EPSS Ckt | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 122865 | 20230808 | 2008 | 20230808 | 2240 | 2186128 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 912 | 35.34 | -119.1496 | No | Clear;32-90 F |  |  | 23-0101952 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1864120 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 17426 | 20230809 | 706 | 20230809 | 720 | 2186269 | 14 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 42 | 35.6016 | -119.2461 | No | Partly Cloudy;32-90 F |  |  | 23-0102010 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1864155 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 515615981820 | 20230809 | 1017 | 20230809 | 1903 | 2186568 | 526 | Transformer only | Animal | Bird found | 2 | 1052 | 35.739 | -119.4773 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0102378 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864412 | 0 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1103 | 253801103 | OCB | 1103/2 | 20230809 | 1424 | 20230810 | 205 | 2186823 | 701 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2103 | 35.1499 | -118.8788 | No | Clear;32-90 F | Conductor- Overhead | Annealed | 23-0102278 | OH | Sus | 31662796 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864390 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | BAKERSFIELD-2109 | 253372109 | OTHER | J4612 TWD T4518 | 20230809 | 1540 | 20230809 | 2104 | 2186879 | 324 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 324 | 35.3692 | -119.0057 | No | Clear;Above 90 | Transformer (UG) | Leaking | 23-0101703 | UG | Sus | 35475758 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864399 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 16358 | 20230809 | 1549 | 20230809 | 2204 | 2186874 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1500 | 35.5998 | -119.5002 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0102327 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864398 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | T10235 | 20230809 | 1937 | 20230809 | 2040 | 2187286 | 63 | Transformer only | Equipment Failure/Involved | Underground | 2 | 126 | 35.0753 | -118.9323 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0102498 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1864476 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 18315 | 20230809 | 2110 | 20230810 | 315 | 2187126 | 365 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 142 | 9450 | 35.4163 | -119.0434 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0102428 | OH | Sus | 31662861 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864431 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1105 | 253371105 | FUSE | 8835 | 20230809 | 2332 | 20230810 | 1334 | 2187191 | 842 | Distribution Circuit | 3rd Party | Vandalism | 1 | 842 | 35.3882 | -119.0244 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0102472 | UG | Sus | 31662823 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1864455 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | OCB | 1101/2 | 20230810 | 45 | 20230810 | 959 | 2187218 | 554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 13072 | 35.7178 | -119.4554 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0102473 | OH | Sus | 31662862 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1864456 | 0 | Non-EPSS | N | 2023 | B- GRD- 51RLY- SET-A
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 14637 | 20230810 | 825 | 20230810 | 1126 | 2187471 | 181 | Distribution Circuit | Animal | Bird found | 13 | 2290 | 35.336 | -119.0151 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0102698 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1864684 | 1 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | FUSE | 18714 | 20230810 | 1342 | 20230810 | 1549 | 2187888 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 127 | 35.6425 | -119.1337 | No | Partly Cloudy;32-90 F |  |  | 23-0102876 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864731 | 1 | Non-EPSS | N | 2023
KERN | KERN | FELLOWS-2104 | 254242104 | FUSE | 9132 | 20230810 | 1610 | 20230810 | 2155 | 2188034 | 345 | Distribution Circuit | Environmental/External | Lightning | 1 | 345 | 35.1946 | -119.5422 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0102960 | OH | Sus | 31662779 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864750 | 1 | EPSS Ckt | N | 2023
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 9771 | 20230810 | 1933 | 20230810 | 2059 | 2188195 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 430 | 35.2241 | -118.7509 | No | Clear;32-90 F |  |  | 23-0102996 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1864765 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | 517278965468 | 20230810 | 1942 | 20230810 | 2231 | 2188197 | 169 | Transformer only | 3rd Party | Other | 2 | 338 | 35.2962 | -118.9129 | No | Clear;32-90 F | Metering Equipment | Normal | 23-0103037 | OH | Sus | 31662989 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864802 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | FUSE | 15669 | 20230811 | 623 | 20230811 | 731 | 2188313 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 204 | 35.2246 | -118.8335 | No | Clear;32-90 F |  |  | 23-0103086 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1864827 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1110 | 253491110 | FUSE | 15881 | 20230811 | 1215 | 20230811 | 1235 | 2188649 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 20 | 35.4563 | -119.1096 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0103301 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864996 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | TRANSFORMER | 516492272731 | 20230811 | 1320 | 20230811 | 2146 | 2188690 | 506 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1012 | 35.4924 | -119.1797 | No | Clear;32-90 F | Transformer | Broken | 23-0103440 | OH | Sus | 35480302 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865048 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516955363082 | 20230811 | 1807 | 20230811 | 1940 | 2188910 | 93 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 93 | 35.2291 | -119.0204 | No | Clear;32-90 F | Service conductor | Broken | 23-0103505 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865076 | 0 | Non-EPSS | N | 2023
KERN | KERN | FELLOWS-2104 | 254242104 | JUMPER | BURNT VERT JMPRS 1P N/ OF CGC# 515538160220 | 20230811 | 2324 | 20230812 | 1112 | 2188991 | 708 | Distribution Circuit | Animal | Bird found | 1 | 708 | 35.1464 | -119.4925 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0103542 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865116 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | OTHER | 16540 | 20230812 | 1409 | 20230812 | 1838 | 2189231 | 269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 14526 | 35.3477 | -118.8707 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0103629 | OH | Sus | 31663142 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1865232 | 1 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517210367862 | 20230812 | 2007 | 20230812 | 2126 | 2189391 | 79 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 395 | 35.3615 | -118.9361 | No | Clear;32-90 F |  |  | 23-0103681 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1865271 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517028966039 | 20230813 | 43 | 20230813 | 215 | 2189470 | 92 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 276 | 35.3105 | -118.9962 | No | Clear;32-90 F |  |  | 23-0103702 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865296 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 16205 | 20230813 | 844 | 20230813 | 933 | 2189557 | 49 | Distribution Circuit | Animal | Bird found | 1 | 49 | 35.3589 | -118.9662 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0103724 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865325 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1103 | 252721103 | TRANSFORMER | 516960070484 | 20230813 | 937 | 20230813 | 1040 | 2189565 | 63 | Transformer only | Unknown Cause | Patrol - found nothing | 19 | 1197 | 35.4324 | -119.0207 | No | Clear;32-90 F |  |  | 23-0103732 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865335 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 8675 | 20230813 | 944 | 20230813 | 1332 | 2189568 | 228 | Distribution Circuit | Equipment Failure/Involved | Underground | 41 | 7896 | 35.3231 | -119.0278 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0103729 | UG | Sus | 45924825 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865331 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 7505 | 20230813 | 1846 | 20230813 | 2007 | 2189749 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 2701 | 35.5072 | -119.2733 | No | Clear;Above 90 |  |  | 23-0103789 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865369 | 1 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517503462198 | 20230813 | 1959 | 20230813 | 2246 | 2189808 | 167 | Transformer only | Vegetation | Tree - grew into line | 13 | 2171 | 35.2062 | -118.8366 | No | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0103819 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865401 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1109 | 253701109 | TRANSFORMER | 516924169430 | 20230813 | 2006 | 20230814 | 248 | 2189822 | 402 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2412 | 35.4032 | -119.0329 | No | Partly Cloudy-Lightning;Above 90 | Fuse | Failed/Faulted | 23-0103798 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865377 | 0 | Non-EPSS | N | 2023
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 9367 | 20230813 | 2013 | 20230814 | 59 | 2189827 | 286 | Distribution Circuit | Animal | Other | 13 | 3624 | 35.2092 | -118.8033 | No | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0103834 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865410 | 1 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1105 | 253911105 | TRANSFORMER | 517538463338 | 20230813 | 2055 | 20230814 | 1155 | 2189874 | 900 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1800 | 35.2375 | -118.8248 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0103827 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865405 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | FUSE | 15669 | 20230813 | 2209 | 20230814 | 202 | 2189892 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 699 | 35.2246 | -118.8335 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0103838 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865414 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516971166716 | 20230813 | 2239 | 20230814 | 349 | 2189820 | 310 | Transformer only | Vegetation | Tree - grew into line | 10 | 3100 | 35.329 | -119.0157 | No | Partly Cloudy;Above 90 | Conductor- Overhead | Arcing | 23-0103820 | OH | Sus | 45924849 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865402 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | TRANSFORMER | 516804167379 | 20230813 | 2308 | 20230813 | 2325 | 2189876 | 17 | Transformer only | Vegetation | Tree - grew into line | 8 | 136 | 35.3466 | -119.0726 | No | Partly Cloudy;32-90 F | Transformer | Normal | 23-0103822 | OH | Sus | 45925015 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865403 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | OCB | 1103/2 | 20230814 | 714 | 20230814 | 2230 | 2189991 | 916 | Distribution Circuit | 3rd Party | Vehicle | 201 | 49658 | 35.0891 | -118.9767 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0103853 | OH | Sus | 35480594 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1865427 | 0 | Non-EPSS | N | 2023 | AB TIME OC
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 516952364153 | 20230814 | 817 | 20230814 | 1548 | 2190050 | 451 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 451 | 35.2584 | -119.0213 | No | Clear;32-90 F |  |  | 23-0104209 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1865653 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13402 | 20230814 | 1143 | 20230814 | 1545 | 2190483 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1210 | 35.2389 | -118.8962 | No | Clear;32-90 F | Other | Broken | 23-0104029 | OH | Sus | 45926092 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1865611 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 14974 | 20230814 | 1405 | 20230814 | 1450 | 2190599 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 585 | 35.1775 | -118.9676 | No | Clear;32-90 F |  |  | 23-0104179 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865646 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1103 | 252611103 | SWITCH | 1129 | 20230814 | 1448 | 20230814 | 2110 | 2190640 | 382 | Distribution Circuit | 3rd Party | Vehicle | 31 | 11842 | 35.4409 | -119.4292 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0104041 | OH | Sus | 35480471 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1865644 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 13607 | 20230814 | 1525 | 20230814 | 1627 | 2190667 | 62 | Distribution Circuit | Vegetation | Tree - grew into line | 39 | 2418 | 35.3453 | -119.0729 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0104183 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1865647 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1108 | 253701108 | TRANSFORMER | 516939267245 | 20230814 | 1830 | 20230815 | 400 | 2190925 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 5841 | 35.3435 | -119.027 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0104277 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865683 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1110 | 252721110 | FUSE | 15281 | 20230814 | 1904 | 20230814 | 2003 | 2190913 | 59 | Distribution Circuit | 3rd Party | Metallic Balloon | 99 | 5841 | 35.4232 | -119.0203 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0104280 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865687 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1101 | 253701101 | RECLOSER | 4897 | 20230814 | 1957 | 20230815 | 223 | 2190943 | 386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1729 | 19502 | 35.3613 | -119.0308 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0104281 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865688 | 0 | Non-EPSS | N | 2023 | B & C
KERN | KERN | TEMBLOR-1104 | 252551104 | FUSE | 18599 | 20230815 | 1632 | 20230815 | 2016 | 2191932 | 224 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 224 | 35.4098 | -119.7157 | No | Clear;Above 90 |  |  | 23-0104788 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865988 | 1 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1105 | 253911105 | JUMPER | OJ #1 PHASE @ 13384 | 20230815 | 1722 | 20230815 | 1845 | 2192018 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1328 | 35.2395 | -118.8695 | No | Clear;32-90 F | Jumper | Broken | 23-0104804 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1865996 | 1 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 17950 | 20230815 | 1945 | 20230816 | 251 | 2192230 | 426 | Distribution Circuit | Equipment Failure/Involved | Underground | 141 | 60066 | 35.3307 | -119.1281 | No | Clear;Above 90 | Transformer (UG) | Leaking | 23-0104822 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866012 | 1 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1108 | 253701108 | TRANSFORMER | 516939267245 | 20230815 | 2049 | 20230816 | 141 | 2192169 | 292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4310 | 35.3435 | -119.027 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 23-0104810 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866001 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516976967750 | 20230815 | 2309 | 20230816 | 336 | 2192291 | 267 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 4005 | 35.3575 | -119.0143 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0104850 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866037 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 122865 | 20230816 | 736 | 20230816 | 846 | 2192422 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 420 | 35.34 | -119.1496 | No | Clear;32-90 F |  |  | 23-0104964 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866188 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 14757 | 20230816 | 754 | 20230816 | 1150 | 2192573 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1180 | 35.0018 | -118.8479 | No | Clear;32-90 F | Fuse | Burned Open | 23-0105058 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866258 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | TRANSFORMER | 516488166445 | 20230816 | 924 | 20230816 | 1034 | 2192672 | 70 | Transformer only | Animal | Other | 1 | 70 | 35.3201 | -119.1783 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0105010 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866229 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517307766811 | 20230816 | 1239 | 20230816 | 1259 | 2192898 | 20 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 100 | 35.3325 | -118.9038 | No | Clear;32-90 F | Fuse | Broken | 23-0105102 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866274 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2102 | 254582102 | TRANSFORMER | T11440 | 20230816 | 1448 | 20230816 | 2233 | 2192893 | 465 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 8835 | 35.4151 | -119.1192 | No | Partly Cloudy;Above 90 | Transformer (UG) | Broken | 23-0105181 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866295 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 1641 | 20230816 | 1548 | 20230817 | 1411 | 2193077 | 1343 | Distribution Circuit | Environmental/External | Lightning | 23 | 30295 | 34.8908 | -119.6045 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105328 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866365 | 1 | EPSS Ckt | N | 2023
KERN | KERN | SHAFTER-1104 | 253651104 | TRANSFORMER | J1650 TWD T11884 | 20230816 | 1653 | 20230816 | 1830 | 2193137 | 97 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 873 | 35.5042 | -119.2905 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0105173 | UG | Sus | 35481327 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866315 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | 516017573560 | 20230816 | 1653 | 20230816 | 2342 | 2193104 | 409 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 818 | 35.5143 | -119.3394 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105261 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866318 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | RECLOSER | 768638 | 20230816 | 1657 | 20230816 | 1840 | 2193144 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 5356 | 35.4378 | -119.6873 | No | Clear;32-90 F |  |  | 23-0105259 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866316 | 0 | Non-EPSS | Y | 2023 | BC
KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | 514926153199 | 20230816 | 1702 | 20230817 | 9 | 2193151 | 427 | Transformer only | Environmental/External | Lightning | 2 | 854 | 34.9499 | -119.6939 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105323 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866360 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | OCB | 2113/2 | 20230816 | 1915 | 20230816 | 2010 | 2193267 | 55 | Distribution Circuit | 3rd Party | Vehicle | 3751 | 191122 | 35.3165 | -119.0678 | No | Clear;Above 90 | Pole-Wood | Normal | 23-0105301 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866343 | 0 | Non-EPSS | N | 2023 | PH OC TIME
KERN | KERN | 7TH STANDARD-2102 | 254582102 | OTHER | T11213 TWD J1591 | 20230816 | 2045 | 20230816 | 2222 | 2193340 | 97 | Distribution Circuit | Equipment Failure/Involved | Underground | 48 | 4656 | 35.4156 | -119.1189 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0104223 | UG | Sus | 45926141 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866364 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2110 | 254072110 | TRANSFORMER | 516872466798 | 20230817 | 1737 | 20230817 | 1804 | 2194065 | 27 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 162 | 35.3309 | -119.0495 | No | Clear;Above 90 |  |  | 23-0105773 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866598 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | OTHER | J2692 TWD T14958 | 20230817 | 1744 | 20230817 | 1852 | 2194069 | 68 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 136 | 35.3391 | -118.9323 | No | Clear;Above 90 | Transformer (UG) | Leaking | 23-0105626 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866595 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | RECLOSER | 768638 | 20230817 | 1816 | 20230817 | 2139 | 2194101 | 203 | Distribution Circuit | Animal | Bird found | 52 | 10556 | 35.4378 | -119.6873 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0105776 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866599 | 0 | Non-EPSS | Y | 2023 | A AND C PHASE
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517261863888 | 20230817 | 1840 | 20230818 | 321 | 2194110 | 500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 4500 | 35.2515 | -118.918 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105781 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866603 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1101 | 253701101 | TRIP-SAVER | 15325 | 20230817 | 2230 | 20230817 | 2358 | 2194273 | 88 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 7480 | 35.3648 | -119.029 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0105846 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866657 | 0 | Non-EPSS | N | 2023 | B C
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516929668015 | 20230817 | 2235 | 20230818 | 1304 | 2194312 | 869 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 32153 | 35.3644 | -119.0306 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105850 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866661 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1109 | 253951109 | SWITCH | 5604 | 20230817 | 2300 | 20230818 | 114 | 2194279 | 134 | Distribution Circuit | Equipment Failure/Involved | Underground | 181 | 5996 | 35.3984 | -118.9303 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0105644 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866650 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7256 | 20230818 | 711 | 20230818 | 1424 | 2194449 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 5360 | 35.6023 | -119.5268 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0106036 | OH | Sus | 45933193 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1866826 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 18983 | 20230818 | 752 | 20230818 | 1753 | 2194612 | 601 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1202 | 35.3836 | -119.161 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0105944 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866751 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRIP-SAVER | 13017 | 20230818 | 802 | 20230818 | 904 | 2194517 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 128 | 7936 | 35.335 | -119.0029 | No | Clear;32-90 F |  |  | 23-0105963 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866779 | 0 | Non-EPSS | N | 2023 | 1 & 2
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | 516262680690 | 20230818 | 835 | 20230818 | 1400 | 2194808 | 325 | Transformer only | 3rd Party | Vehicle | 1 | 325 | 35.7106 | -119.2595 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106111 | OH | Sus | 31663970 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1866862 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1102 | 253181102 | OTHER | WIRE DOWN 5 E/ OF CGC 515916779415 | 20230818 | 1320 | 20230818 | 1617 | 2194969 | 177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 2070 | 35.6743 | -119.3671 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 23-0106149 | OH | Sus | 31663998 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | Yes | 1866883 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 4525 | 20230818 | 1933 | 20230818 | 2225 | 2195317 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3784 | 34.9716 | -118.9397 | No | Clear;32-90 F |  |  | 23-0106276 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866925 | 0 | EPSS Ckt | Y | 2023 | B PHASE AND GROUND
KERN | KERN | STOCKDALE-2106 | 254072106 | OCB | 2106/2 | 20230819 | 601 | 20230819 | 712 | 2195427 | 71 | Distribution Circuit | 3rd Party | Vehicle | 2709 | 192339 | 35.3165 | -119.068 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0106322 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866973 | 0 | Non-EPSS | N | 2023 | PH OC TIME
KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | 517147153503 | 20230819 | 851 | 20230819 | 959 | 2195531 | 68 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 68 | 34.9668 | -118.9535 | No | Clear;32-90 F |  |  | 23-0106341 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1867041 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CAL WATER-1102 | 255451102 | RECLOSER | 920714 | 20230819 | 1511 | 20230820 | 928 | 2195764 | 1097 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 31782 | 35.4216 | -118.8325 | No | Overcast-Lightning;32-90 F | Conductor- Overhead | Together | 23-0106401 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867075 | 0 | EPSS Ckt | Y | 2023 | B & C
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20230819 | 1512 | 20230820 | 935 | 2195765 | 1103 | Distribution Circuit | Environmental/External | Lightning | 130 | 143390 | 35.5605 | -118.9587 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0106402 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867076 | 0 | EPSS Ckt | Y | 2023 | SGF
KERN | KERN | KERN OIL-1106 | 252721106 | RECLOSER | 3301 | 20230819 | 1515 | 20230819 | 1735 | 2195766 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 242 | 17734 | 35.4424 | -118.9595 | No | Partly Cloudy;Above 90 |  |  | 23-0106403 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867077 | 0 | EPSS Ckt | Y | 2023 | A & C
KERN | KERN | LERDO-1110 | 253491110 | OCB | 1110/2 | 20230819 | 1544 | 20230820 | 252 | 2195782 | 668 | Distribution Circuit | Company Initiated | Improper Construction | 121 | 9428 | 35.5004 | -119.152 | No | Partly Cloudy;Above 90 | Conductor- Overhead | Contaminated | 23-0106413 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867083 | 0 | Non-EPSS | N | 2023 | A G PH OC TIME
KERN | KERN | BAKERSFIELD-1115 | 253371115 | FUSE | 41062 | 20230819 | 1557 | 20230819 | 1856 | 2195786 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3872 | 35.3772 | -119.013 | No | Overcast;Above 90 |  |  | 23-0106456 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867121 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 7505 | 20230819 | 1603 | 20230819 | 2229 | 2195791 | 386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 19300 | 35.5072 | -119.2733 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0106481 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867148 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1103 | 253651103 | OCB | 1103/2 | 20230819 | 1641 | 20230819 | 1719 | 2195838 | 38 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 233 | 8854 | 35.5138 | -119.3179 | No | Partly Cloudy-Lightning;32-90 F |  |  | 23-0106420 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867089 | 0 | Non-EPSS | N | 2023 | BC INST
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 934590 | 20230819 | 1700 | 20230820 | 1824 | 2195852 | 1507 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 36 | 50315 | 34.9828 | -119.7854 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0106421 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867090 | 0 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | SMYRNA-1104 | 253551104 | FUSE | 7293 | 20230819 | 1701 | 20230819 | 2015 | 2195855 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1812 | 35.79 | -119.4629 | No | Partly Cloudy-Lightning;32-90 F |  |  | 23-0106476 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867141 | 1 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1101 | 253181101 | FUSE | 556403 | 20230819 | 1712 | 20230819 | 1914 | 2195870 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1220 | 35.6889 | -119.2353 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0106465 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1867131 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1104 | 253141104 | FUSE | 9212 | 20230819 | 1817 | 20230821 | 1805 | 2196068 | 2868 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 25812 | 34.9275 | -119.6963 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0106441 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1867106 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 57521 | 20230819 | 1841 | 20230819 | 2320 | 2196152 | 279 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 558 | 35.4424 | -119.4839 | No | Overcast;32-90 F |  |  | 23-0106526 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867195 | 1 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRIP-SAVER | 14402 | 20230819 | 1902 | 20230819 | 2001 | 2196228 | 59 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 84 | 4931 | 35.3396 | -118.9309 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0106468 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867134 | 1 | Non-EPSS | N | 2023 | #2 TRIP
KERN | KERN | LERDO-1113 | 253491113 | FUSE | 15146 | 20230819 | 1908 | 20230820 | 1637 | 2196242 | 1289 | Distribution Circuit | Environmental/External | Lightning | 13 | 5801 | 35.5584 | -119.2046 | No | Overcast-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 23-0106543 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867215 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1116 | 253491116 | OTHER | WIRE DOWN @ L376 | 20230819 | 1924 | 20230820 | 1303 | 2196262 | 1059 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 26069 | 35.5431 | -119.1336 | No | Partly Cloudy-Lightning;32-90 F | Pole-Wood | Broken- wire on ground | 23-0106545 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1867217 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514697680949 | 20230819 | 1943 | 20230820 | 2150 | 2196290 | 1567 | Transformer only | Environmental/External | Lightning | 2 | 3134 | 35.7107 | -119.7876 | No | Overcast-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106567 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867240 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | OCB | 2103/2 | 20230819 | 2047 | 20230819 | 2230 | 2196367 | 103 | Distribution Circuit | Environmental/External | Lightning | 58 | 5819 | 35.3831 | -119.6964 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0106480 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1867147 | 0 | Non-EPSS | N | 2023 | ABC- GRD- INST OC
KERN | KERN | ANTELOPE-1101 | 252021101 | RECLOSER | 3609 | 20230819 | 2055 | 20230820 | 648 | 2196442 | 593 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 26685 | 35.6583 | -120.0132 | No | Partly Cloudy-Lightning;32-90 F |  |  | 23-0106485 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867152 | 0 | EPSS Ckt | Y | 2023 | A&C
KERN | KERN | BAKERSFIELD SUB | 25337 | OCB | 1700/2 | 20230819 | 2111 | 20230819 | 2151 | 2196482 | 40 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3689 | 147560 | 35.3886 | -119.0044 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0106489 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867156 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516924967751 | 20230819 | 2240 | 20230820 | 1831 | 2196591 | 1184 | Distribution Circuit | Vegetation | Tree - grew into line | 8 | 9445 | 35.3571 | -119.0322 | No | Partly Cloudy-Drizzle;32-90 F | Secondary | Normal | 23-0106516 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867185 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1112 | 253651112 | FUSE | 14702 | 20230819 | 2310 | 20230820 | 1354 | 2196597 | 884 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 12376 | 35.5725 | -119.3585 | No | Overcast;32-90 F | Crossarm- Wood | Burned/flashed | 23-0106522 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867191 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1105 | 252821105 | RECLOSER | 56702 | 20230820 | 16 | 20230820 | 1755 | 2196647 | 1059 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 7 | 6449 | 35.209 | -119.1467 | No | Clear-Lightning;32-90 F | Pole-Wood | Broken- wire on ground | 23-0106549 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1867220 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 8939 | 20230820 | 734 | 20230820 | 855 | 2196777 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1215 | 35.3636 | -118.9653 | No | Partly Cloudy;32-90 F |  |  | 23-0106588 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867267 | 0 | Non-EPSS | N | 2023
KERN | KERN | MCKITTRICK-1101 | 252781101 | OCB | 1101/2 | 20230820 | 924 | 20230821 | 202 | 2196840 | 998 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 154 | 20780 | 35.297 | -119.6266 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0106602 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1867277 | 0 | EPSS Ckt | N | 2023 | BC GRD
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20230820 | 1120 | 20230820 | 1346 | 2196920 | 146 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 130 | 18980 | 35.5605 | -118.9587 | No | Overcast;32-90 F |  |  | 23-0106625 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867294 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 8902 | 20230820 | 1216 | 20230820 | 1615 | 2196957 | 239 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 11950 | 35.3252 | -118.933 | No | Clear;32-90 F |  |  | 23-0106640 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867305 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 3855 | 20230820 | 1240 | 20230820 | 1334 | 2196969 | 54 | Distribution Circuit | Company Initiated | Coordination failure | 26 | 1404 | 35.3116 | -118.8251 | No | Overcast-Heavy Rain;32-90 F | Recloser | Normal | 23-0106639 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867303 | 0 | EPSS Ckt | Y | 2023 | B- GRD
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 4222 | 20230820 | 1243 | 20230821 | 1030 | 2196973 | 1307 | Distribution Circuit | Animal | Other | 64 | 10364 | 35.3258 | -118.804 | No | Overcast-Heavy Rain;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0106639 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867304 | 0 | EPSS Ckt | Y | 2023 | B- GRD
KERN | KERN | MAGUNDEN-1108 | 252771108 | RECLOSER | 250674 | 20230820 | 1306 | 20230820 | 1424 | 2196989 | 78 | Distribution Circuit | Animal | Other | 99 | 7722 | 35.3618 | -118.8954 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106644 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867309 | 0 | EPSS Ckt | Y | 2023 | A-B
KERN | KERN | MAGUNDEN-1108 | 252771108 | TRANSFORMER | 517497068282 | 20230820 | 1306 | 20230820 | 2220 | 2197174 | 554 | Transformer only | Animal | Other | 2 | 1108 | 35.3729 | -118.8407 | No | Overcast-Fog-Heavy Rain;32-90 F | Fuse | Failed/Faulted | 23-0106767 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867415 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ARVIN-1103 | 253801103 | OCB | 1103/2 | 20230820 | 1309 | 20230820 | 1437 | 2196991 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 105 | 9240 | 35.1499 | -118.8788 | No | Clear;32-90 F |  |  | 23-0106645 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867310 | 0 | Non-EPSS | N | 2023 | PH & GRD TIME OC
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 14733 | 20230820 | 1311 | 20230820 | 1408 | 2196990 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 1995 | 35.3061 | -119.0303 | No | Overcast-Rain;32-90 F |  |  | 23-0106663 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867323 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | OCB | 1103/2 | 20230820 | 1351 | 20230820 | 1821 | 2197017 | 270 | Distribution Circuit | Animal | Other | 328 | 41040 | 35.0198 | -118.9548 | No | Overcast-Fog-Heavy Rain;32-90 F | Jumper | Burned Open | 23-0106661 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867321 | 0 | EPSS Ckt | N | 2023 | PH-OC INST- GRD- B- SET-A
KERN | KERN | STOCKDALE-2110 | 254072110 | OCB | 2200/2 | 20230820 | 1427 | 20230820 | 1628 | 2197038 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3090 | 373890 | 35.3165 | -119.0679 | No | Overcast-Fog-Rain;32-90 F | Recloser | Failed/Faulted | 23-0106671 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1867328 | 0 | Non-EPSS | N | 2023 | A- B- C- GRD- 51RLY- SET-A- MA
KERN | KERN | LAMONT-1107 | 253911107 | RECLOSER | 1952 | 20230820 | 1439 | 20230821 | 1450 | 2197059 | 1451 | Distribution Circuit | Environmental/External | Lightning | 56 | 6841 | 35.3122 | -118.8786 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106673 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1867330 | 0 | Non-EPSS | N | 2023 | AB
KERN | KERN | OLD RIVER-1102 | 252821102 | OCB | 1102/2 | 20230820 | 1449 | 20230820 | 2249 | 2197063 | 480 | Distribution Circuit | Animal | Bird found | 451 | 124025 | 35.2083 | -119.101 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106676 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1867332 | 0 | Non-EPSS | N | 2023 | B- GRD & PH OC INST
KERN | KERN | LERDO-1112 | 253491112 | FUSE | 16367 | 20230820 | 1532 | 20230821 | 1210 | 2197121 | 1238 | Distribution Circuit | Animal | Other | 1 | 1651 | 35.4851 | -119.083 | No | Rain;32-90 F | Fuse | Normal | 23-0106713 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867361 | 1 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 14153 | 20230820 | 1536 | 20230821 | 1242 | 2197128 | 1266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 7596 | 35.3543 | -119.2343 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0106714 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867362 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 16072 | 20230820 | 1628 | 20230821 | 1345 | 2197154 | 1277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3610 | 35.72 | -119.8587 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106744 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867392 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 8491 | 20230820 | 1648 | 20230820 | 1733 | 2197170 | 45 | Distribution Circuit | Environmental/External | Lightning | 30 | 1350 | 35.3251 | -119.0451 | No | Overcast-Rain;32-90 F | Lightning Arrestor | Burned/flashed | 23-0106727 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867375 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2109 | 254072109 | FUSE | 17395 | 20230820 | 1739 | 20230821 | 736 | 2197206 | 837 | Distribution Circuit | Equipment Failure/Involved | Underground | 53 | 19551 | 35.3032 | -119.0265 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 23-0106733 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867381 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516997366688 | 20230820 | 1756 | 20230821 | 51 | 2197221 | 415 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4150 | 35.3283 | -119.0067 | No | Overcast-Heavy Rain-Fog;32-90 F | Crossarm- Wood | Broken | 23-0106728 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867376 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 8295 | 20230820 | 2116 | 20230820 | 2327 | 2197367 | 131 | Distribution Circuit | Animal | Bird found | 13 | 1703 | 35.38 | -118.9944 | No | Overcast-Fog-Rain;32-90 F | Cutout- fuse holder | Normal | 23-0106765 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867413 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1104 | 253551104 | FUSE | 7290 | 20230820 | 2150 | 20230821 | 1131 | 2197378 | 821 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4 | 3286 | 35.7792 | -119.4634 | No | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Burned/flashed | 23-0106794 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867445 | 1 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | SWITCH | 1999 | 20230820 | 2336 | 20230820 | 2345 | 2197425 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 262 | 2358 | 35.2231 | -119.0007 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0106676 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1867426 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1112 | 252901112 | FUSE | 87100 | 20230821 | 306 | 20230821 | 2137 | 2197487 | 1111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 7777 | 35.6304 | -119.4561 | No | Overcast-Drizzle;32-90 F | Insulator | Burned/flashed | 23-0107280 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1867778 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 15723 | 20230821 | 458 | 20230821 | 1518 | 2197517 | 620 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 5 | 3052 | 35.0934 | -118.9648 | No | Partly Cloudy-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106805 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1867456 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13476 | 20230821 | 633 | 20230821 | 754 | 2197573 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 7695 | 35.3649 | -118.9745 | No | Overcast;32-90 F |  |  | 23-0106850 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867485 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | RECLOSER | 330930 | 20230821 | 637 | 20230821 | 1132 | 2197576 | 295 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1179 | 25881 | 35.6743 | -119.2552 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0106817 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867469 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20230821 | 702 | 20230821 | 759 | 2197595 | 57 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 130 | 7410 | 35.5605 | -118.9587 | No | Partly Cloudy;32-90 F |  |  | 23-0106826 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867477 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | T15010 | 20230821 | 811 | 20230821 | 1533 | 2197665 | 442 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 442 | 34.983 | -118.9471 | No | Partly Cloudy-Fog-Drizzle-Strong Winds;32-90 F | Transformer (UG) | Leaking | 23-0106961 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867615 | 0 | EPSS Ckt | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 14372 | 20230821 | 940 | 20230821 | 1603 | 2197826 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1532 | 35.2668 | -119.0478 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0106998 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1867632 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1112 | 253701112 | TRANSFORMER | 516860667570 | 20230821 | 953 | 20230821 | 1849 | 2197961 | 536 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 4288 | 35.3521 | -119.0537 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0107006 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1867637 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | TRANSFORMER | 516540475870 | 20230821 | 1033 | 20230821 | 1518 | 2197950 | 285 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 570 | 35.5788 | -119.1647 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107007 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867638 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516958267048 | 20230821 | 1145 | 20230821 | 1535 | 2197900 | 230 | Transformer only | Vegetation | Tree - grew into line | 20 | 4600 | 35.3381 | -119.02 | No | Overcast;32-90 F | Transformer | Broken | 23-0107033 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867651 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1106 | 253371106 | TRANSFORMER | 100000126433 | 20230821 | 1157 | 20230821 | 1711 | 2198084 | 314 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1570 | 35.3894 | -118.9748 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0107042 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867654 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 14371 | 20230821 | 1215 | 20230821 | 1950 | 2197994 | 455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 28665 | 35.2674 | -119.0354 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0107052 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867661 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | T10235 | 20230821 | 1514 | 20230821 | 1730 | 2198400 | 136 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 272 | 35.0753 | -118.9323 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107206 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867727 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | 514938352660 | 20230821 | 1532 | 20230821 | 1854 | 2198416 | 202 | Transformer only | Animal | Other | 1 | 202 | 34.9345 | -119.6898 | No | Partly Cloudy;32-90 F | Transformer (OH) |  | 23-0107264 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867766 | 0 | EPSS Ckt | N | 2023
KERN | KERN | COLUMBUS-1109 | 253951109 | TRANSFORMER | T2477 | 20230821 | 1655 | 20230822 | 637 | 2198564 | 822 | Distribution Circuit | Equipment Failure/Involved | Underground | 61 | 10402 | 35.3998 | -118.9277 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0107254 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867756 | 0 | Non-EPSS | N | 2023
KERN | KERN | DEVILS DEN-1102 | 253451102 | TRANSFORMER | 514063281491 | 20230822 | 959 | 20230822 | 1125 | 2199149 | 86 | Transformer only | Animal | Other | 1 | 86 | 35.7237 | -120.0002 | No | Clear;32-90 F | Fuse | Burned Open | 23-0107543 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868014 | 0 | EPSS Ckt | N | 2023
KERN | KERN | RIO BRAVO-1101 | 252861101 | TRANSFORMER | 516225571902 | 20230822 | 1130 | 20230822 | 1145 | 2199222 | 15 | Transformer only | Vegetation | Tree - branch fell on line | 10 | 150 | 35.4692 | -119.2691 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0107557 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868022 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1106 | 253411106 | TRANSFORMER | 516682056277 | 20230822 | 1208 | 20230822 | 1222 | 2199187 | 14 | Transformer only | Animal | Other | 1 | 14 | 35.0412 | -119.109 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0107575 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868031 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514706280892 | 20230822 | 1252 | 20230822 | 2304 | 2199369 | 612 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 612 | 35.7093 | -119.7849 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0107610 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868050 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514711080863 | 20230822 | 1254 | 20230822 | 2137 | 2199296 | 523 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 523 | 35.7084 | -119.7831 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0107607 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868049 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1102 | 252961102 | TRANSFORMER | 516028176516 | 20230823 | 316 | 20230823 | 1010 | 2199745 | 414 | Transformer only | Equipment Failure/Involved | Overhead | 29 | 12006 | 35.5949 | -119.3372 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107840 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868151 | 0 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 513785579462 | 20230823 | 1314 | 20230823 | 1336 | 2200091 | 22 | Transformer only | Vegetation | Other ground vegetation | 1 | 22 | 35.666 | -120.0932 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0108150 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868366 | 0 | EPSS Ckt | N | 2023
KERN | KERN | COLUMBUS-1104 | 253951104 | SWITCH | 2299 | 20230823 | 1427 | 20230823 | 1838 | 2200273 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 262 | 65762 | 35.3832 | -118.9574 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0108198 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1868374 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1104 | 252081104 | OCB | 1104/2 | 20230823 | 1501 | 20230823 | 1533 | 2200346 | 32 | Distribution Circuit | Animal | Bird found | 2474 | 79168 | 35.1363 | -119.4822 | No | Clear;32-90 F | Insulator | Normal | 23-0108235 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868380 | 0 | Non-EPSS | N | 2023 | PH A B GRD
KERN | KERN | TAFT-1108 | 252081108 | TRANSFORMER | 515647559663 | 20230823 | 1838 | 20230824 | 125 | 2200481 | 407 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 5291 | 35.1304 | -119.4568 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0108311 | OH | Sus | 45938144 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1868412 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516711959526 | 20230824 | 849 | 20230824 | 1138 | 2201002 | 169 | Transformer only | Animal | Other | 1 | 169 | 35.1293 | -119.1006 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0108607 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868689 | 0 | Non-EPSS | N | 2023
KERN | KERN | DEVILS DEN-1102 | 253451102 | TRANSFORMER | 514297781088 | 20230824 | 907 | 20230824 | 1209 | 2201040 | 182 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 182 | 35.7128 | -119.921 | No | Clear;32-90 F | Fuse | Broken | 23-0108629 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868697 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | 514929353167 | 20230824 | 938 | 20230824 | 1134 | 2201146 | 116 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 116 | 34.9487 | -119.6931 | No | Clear;32-90 F |  |  | 23-0108600 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1868685 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514508379107 | 20230824 | 1241 | 20230824 | 1254 | 2201303 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 13 | 35.6587 | -119.8499 | No | Clear;Above 90 | Connector or Splice (OH) | Arcing | 23-0108657 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868706 | 0 | Non-EPSS | N | 2023
KERN | KERN | WELLFIELD-1102 | 254291102 | TRANSFORMER | 517697261760 | 20230824 | 1301 | 20230824 | 1451 | 2201364 | 110 | Transformer only | Animal | Other | 1 | 110 | 35.196 | -118.7713 | No | Clear;32-90 F | Transformer (OH) |  | 23-0108730 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868740 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WELLFIELD-1102 | 254291102 | TRANSFORMER | 517699462099 | 20230824 | 1303 | 20230825 | 423 | 2201368 | 920 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 920 | 35.2038 | -118.7703 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0108714 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868734 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BLACKWELL-2101 | 254682101 | FUSE | 7314 | 20230825 | 59 | 20230829 | 1223 | 2201731 | 6444 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 25776 | 35.5938 | -119.7626 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108880 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1868845 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | JUMPER | 18400 | 20230825 | 814 | 20230825 | 1132 | 2201889 | 198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 198 | 35.6453 | -119.2503 | No | Clear;32-90 F | Jumper | Burned Open | 23-0109083 | OH | Sus | 45941066 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1869018 | 1 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1108 | 252721108 | JUMPER | BURNT OPEN CENTER PHASE JUMPER @ 8974 | 20230825 | 856 | 20230825 | 1011 | 2201951 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2357 | 39011 | 35.4484 | -119.031 | No | Clear;32-90 F | Jumper | Burned Open | 23-0109007 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1868995 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1107 | 253371107 | TRANSFORMER | 516965068238 | 20230825 | 1602 | 20230825 | 1651 | 2202375 | 49 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 245 | 35.3709 | -119.0184 | No | Clear;Above 90 |  |  | 23-0109290 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1869093 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1107 | 253371107 | TRANSFORMER | 516966168238 | 20230825 | 1602 | 20230825 | 1652 | 2202376 | 50 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 200 | 35.3709 | -119.0181 | No | Clear;Above 90 |  |  | 23-0109292 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1869095 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | 516170673020 | 20230825 | 1705 | 20230825 | 2027 | 2202435 | 202 | Transformer only | 3rd Party | Vehicle | 3 | 606 | 35.4995 | -119.2871 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0109315 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869117 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 517000167647 | 20230825 | 1809 | 20230826 | 949 | 2202500 | 935 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 6055 | 35.3546 | -119.0069 | No | Clear;Above 90 | Secondary | Annealed | 23-0109312 | OH | Sus | 31664941 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869110 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | 516170673020 | 20230825 | 2247 | 20230826 | 900 | 2202583 | 613 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1839 | 35.4995 | -119.2871 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109329 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869133 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516675864230 | 20230826 | 813 | 20230826 | 1434 | 2202651 | 381 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 381 | 35.2598 | -119.1145 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109373 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869200 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | TRANSFORMER | 517288554920 | 20230826 | 1137 | 20230826 | 1213 | 2202840 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 144 | 35.0063 | -118.9065 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0109405 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1869225 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | FUSE | 241697 | 20230826 | 1841 | 20230826 | 2050 | 2202984 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 258 | 35.6158 | -119.6998 | No | Clear;32-90 F |  |  | 23-0109459 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1869267 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | OCB | 1106/2 | 20230826 | 2040 | 20230827 | 347 | 2203029 | 427 | Distribution Circuit | 3rd Party | Vehicle | 1742 | 397069 | 35.2971 | -118.8618 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0109462 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1869271 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 8486 | 20230826 | 2204 | 20230828 | 148 | 2203048 | 1664 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 88673 | 35.3212 | -119.0095 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0109481 | UG | Sus | 45942020 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869291 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1101 | 253181101 | OTHER | 1 & 3 PHASES BURNED OPEN | 20230827 | 344 | 20230827 | 1325 | 2203098 | 581 | Distribution Circuit | 3rd Party | Vehicle | 32 | 17649 | 35.6816 | -119.2297 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0109485 | OH | Sus | 35484361 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1869300 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | T25654 | 20230827 | 1259 | 20230827 | 1310 | 2203329 | 11 | Transformer only | Equipment Failure/Involved | Underground | 1 | 11 | 35.4988 | -119.5245 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0109515 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869333 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2102 | 254572102 | TRANSFORMER | T7444 | 20230827 | 1405 | 20230827 | 1420 | 2203119 | 15 | Transformer only | Equipment Failure/Involved | Underground | 11 | 165 | 35.3695 | -119.1591 | No | Clear;32-90 F | Secondary | Burned Open | 23-0109531 | UG | Sus | 45942062 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1869338 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517032265972 | 20230827 | 1727 | 20230828 | 833 | 2203413 | 906 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 11778 | 35.3086 | -118.995 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0109556 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869348 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | TRANSFORMER | 517389555293 | 20230828 | 958 | 20230828 | 1155 | 2203935 | 117 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 117 | 35.0163 | -118.8728 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0109712 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1869549 | 0 | EPSS Ckt | N | 2023
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516968470025 | 20230828 | 1002 | 20230828 | 1115 | 2203927 | 73 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 73 | 35.4198 | -119.0179 | No | Clear;32-90 F |  |  | 23-0109746 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1869574 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1105 | 254071105 | TRANSFORMER | 516888566001 | 20230828 | 1039 | 20230828 | 1353 | 2203991 | 194 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 194 | 35.309 | -119.0434 | No | Clear;32-90 F |  |  | 23-0109844 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1869627 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | TRANSFORMER | 516391274725 | 20230828 | 1107 | 20230828 | 1428 | 2204023 | 201 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 201 | 35.548 | -119.2136 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109775 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869590 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516969470025 | 20230828 | 1114 | 20230828 | 1132 | 2203928 | 18 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 162 | 35.4198 | -119.0175 | No | Clear;32-90 F |  |  | 23-0109745 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1869573 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 18299 | 20230828 | 1147 | 20230829 | 239 | 2204064 | 892 | Distribution Circuit | 3rd Party | Vehicle | 6 | 5352 | 35.0765 | -118.9681 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0109788 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1869603 | 0 | EPSS Ckt | N | 2023
KERN | KERN | CHARCA-1106 | 254501106 | JUMPER | 17146 | 20230828 | 1320 | 20230828 | 1540 | 2204191 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 140 | 35.6012 | -119.3301 | No | Clear;32-90 F | Jumper | Broken | 23-0109852 | OH | Sus | 45943410 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1869629 | 1 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | OCB | 1101/2 | 20230829 | 103 | 20230829 | 1701 | 2204523 | 958 | Distribution Circuit | 3rd Party | Vehicle | 3598 | 776379 | 35.3618 | -118.924 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0110003 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1869691 | 0 | Non-EPSS | N | 2023 | A GRD
KERN | KERN | STOCKDALE-2107 | 254072107 | RECLOSER | 4163 | 20230829 | 256 | 20230829 | 506 | 2204536 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 662 | 79319 | 35.326 | -119.0745 | No | Clear;32-90 F |  |  | 23-0110007 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869697 | 0 | Non-EPSS | N | 2023 | B GRD
KERN | KERN | SMYRNA-1104 | 253551104 | FUSE | 515709681811 | 20230829 | 823 | 20230829 | 1500 | 2204775 | 397 | Distribution Circuit | Animal | Other | 1 | 397 | 35.7392 | -119.4463 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0110180 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869901 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2111 | 254072111 | SWITCH | 6607 | 20230829 | 858 | 20230829 | 1541 | 2204815 | 403 | Distribution Circuit | Equipment Failure/Involved | Underground | 79 | 11509 | 35.3411 | -119.0549 | No | Clear;32-90 F | Elbow | Broken | 23-0110025 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1869845 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516651077979 | 20230829 | 944 | 20230829 | 1405 | 2204875 | 261 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 261 | 35.6373 | -119.1279 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0110247 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869927 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517259263930 | 20230830 | 421 | 20230830 | 637 | 2205560 | 136 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 272 | 35.2532 | -118.9189 | No | Clear;32-90 F |  |  | 23-0110565 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1870067 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13951 | 20230830 | 642 | 20230830 | 1650 | 2205584 | 608 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 12830 | 35.3693 | -118.9742 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0110598 | OH | Sus | 31666003 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1870101 | 1 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 16027 | 20230830 | 905 | 20230830 | 1233 | 2205755 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1040 | 35.5794 | -119.4742 | No | Clear;32-90 F |  |  | 23-0110790 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1870236 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | TRANSFORMER | 517041569189 | 20230830 | 1413 | 20230830 | 1509 | 2206122 | 56 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 560 | 35.397 | -118.9931 | No | Clear;Above 90 |  |  | 23-0110924 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1870272 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515506579332 | 20230830 | 1737 | 20230830 | 2025 | 2206321 | 168 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 168 | 35.6701 | -119.5135 | No | Clear;Above 90 | Transformer | Deteriorated | 23-0110986 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870289 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514734569418 | 20230830 | 1803 | 20230830 | 2345 | 2206374 | 342 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 342 | 35.3948 | -119.7678 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111002 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870302 | 0 | EPSS Ckt | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | T25654 | 20230831 | 817 | 20230831 | 1018 | 2206640 | 121 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 121 | 35.4988 | -119.5245 | No | Clear;32-90 F |  |  | 23-0111135 | OH | Sus | 45947399 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1870450 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | JUMPER | VERT JMPRS 1P N/ OF L554 | 20230831 | 838 | 20230831 | 1159 | 2206759 | 201 | Distribution Circuit | 3rd Party | Vehicle | 1 | 201 | 35.6701 | -119.5089 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0111113 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1870427 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517027865683 | 20230831 | 842 | 20230831 | 2019 | 2206791 | 697 | Transformer only | Vegetation | Tree - grew into line | 14 | 9758 | 35.3007 | -118.9964 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0111263 | OH | Sus | 45947309 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1870563 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRANSFORMER | 516114570858 | 20230831 | 916 | 20230831 | 1335 | 2207080 | 259 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 259 | 35.4399 | -119.3051 | No | Clear;Above 90 | Fuse | Broken | 23-0111344 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870590 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517349362513 | 20230831 | 1213 | 20230831 | 1443 | 2207090 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 300 | 35.214 | -118.8879 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0111397 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870600 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1102 | 254501102 | RECLOSER | 345544 | 20230831 | 1425 | 20230831 | 1538 | 2207203 | 73 | Distribution Circuit | 3rd Party | Vehicle | 78 | 5694 | 35.6305 | -119.3338 | No | Clear;Above 90 | Insulator | Broken- wire on object | 23-0111389 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | Yes | Yes | 1870599 | 0 | Non-EPSS | N | 2023 | C
KERN | KERN | TEMBLOR-1104 | 252551104 | OCB | 1104/2 | 20230831 | 1948 | 20230831 | 2355 | 2207397 | 247 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 6720 | 35.3831 | -119.6964 | No | Clear-Strong Winds;32-90 F |  |  | 23-0111532 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1870631 | 0 | EPSS Ckt | Y | 2023 | BC INST SET A RLY
KERN | KERN | COLUMBUS-1106 | 253951106 | TRANSFORMER | 517158669306 | 20230831 | 2340 | 20230901 | 1156 | 2207476 | 736 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 5152 | 35.4006 | -118.9541 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111573 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870671 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1106 | 253951106 | TRANSFORMER | 517154569271 | 20230901 | 12 | 20230901 | 1156 | 2207478 | 704 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 4224 | 35.3997 | -118.9554 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111571 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870669 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1106 | 253951106 | TRANSFORMER | 517151769270 | 20230901 | 22 | 20230901 | 1156 | 2207483 | 694 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 5552 | 35.3996 | -118.9564 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111570 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870668 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1106 | 253951106 | TRANSFORMER | 517156469284 | 20230901 | 43 | 20230901 | 1156 | 2207477 | 673 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 5384 | 35.4 | -118.9548 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111572 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870670 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20230901 | 212 | 20230901 | 229 | 2207485 | 17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4558 | 31996 | 35.3885 | -119.0046 | No | Clear;32-90 F | Transformer (OH) | Arcing | 23-0111575 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1870674 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | TEMBLOR-1104 | 252551104 | OCB | 1104/2 | 20230901 | 1926 | 20230902 | 110 | 2208192 | 344 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 13480 | 35.3831 | -119.6964 | No | Partly Cloudy;32-90 F |  |  | 23-0112006 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1870855 | 0 | EPSS Ckt | Y | 2023 | ABC INST SET A RLY
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 55553 | 20230901 | 2157 | 20230902 | 539 | 2208245 | 462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 28644 | 35.325 | -119.0175 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0112027 | OH | Sus | 35486300 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870880 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1101 | 253371101 | FUSE | 14197 | 20230901 | 2213 | 20230902 | 103 | 2208246 | 170 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 170 | 35.3979 | -118.9984 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0112017 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1870868 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | RECLOSER | 2436 | 20230901 | 2232 | 20230902 | 1924 | 2208259 | 1252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 37431 | 34.9844 | -118.9227 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0112030 | OH | Sus | 35486217 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1870883 | 0 | Non-EPSS | N | 2023 | AC
KERN | KERN | WEEDPATCH-1101 | 252971101 | RECLOSER | 4574 | 20230902 | 7 | 20230902 | 1452 | 2208269 | 885 | Distribution Circuit | 3rd Party | Vehicle | 56 | 25738 | 35.2087 | -118.8811 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 23-0112034 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | Yes | No | 1870891 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 517121055610 | 20230902 | 1326 | 20230903 | 1115 | 2208704 | 1309 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2618 | 35.0262 | -118.9628 | No | Partly Cloudy;32-90 F |  |  | 23-0112123 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1870957 | 0 | EPSS Ckt | N | 2023
KERN | KERN | KERN OIL-1110 | 252721110 | FUSE | 12013 | 20230902 | 1609 | 20230902 | 1914 | 2208795 | 185 | Distribution Circuit | Equipment Failure/Involved | Underground | 150 | 27750 | 35.4272 | -119.0304 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 23-0112151 | UG | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1870966 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | T6607 | 20230903 | 335 | 20230903 | 557 | 2208965 | 142 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 142 | 35.0871 | -119.38 | No | Partly Cloudy;32-90 F |  |  | 23-0112205 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1871016 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | RECLOSER | 4151 | 20230903 | 745 | 20230903 | 842 | 2209004 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 697 | 39729 | 35.346 | -119.0737 | No | Overcast;32-90 F |  |  | 23-0112207 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871018 | 0 | Non-EPSS | N | 2023 | C GRD
KERN | KERN | RENFRO-2103 | 254572103 | OCB | 2103/2 | 20230904 | 915 | 20230904 | 1427 | 2209318 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1893 | 135404 | 35.3871 | -119.1643 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112310 | OH | Sus | 45953210 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1871109 | 0 | Non-EPSS | N | 2023 | B & GRD
KERN | KERN | STOCKDALE-1110 | 254071110 | FUSE | 16973 | 20230904 | 1407 | 20230904 | 2149 | 2209454 | 462 | Distribution Circuit | 3rd Party | Vehicle | 141 | 40518 | 35.3251 | -119.0307 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0112362 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871139 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | TRANSFORMER | 516849969746 | 20230904 | 2039 | 20230904 | 2240 | 2209584 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 121 | 35.4119 | -119.0579 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0112404 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871163 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1102 | 254501102 | FUSE | 7184 | 20230905 | 110 | 20230905 | 240 | 2209629 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 840 | 35.6669 | -119.3293 | No | Clear;32-90 F |  |  | 23-0112419 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871178 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | OCB | 1106/2 | 20230905 | 138 | 20230905 | 346 | 2209635 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 229 | 23471 | 35.718 | -119.4554 | No | Clear;32-90 F |  |  | 23-0112418 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871177 | 0 | Non-EPSS | N | 2023 | AC TIME OC
KERN | KERN | TUPMAN-1103 | 254561103 | FUSE | 16220 | 20230905 | 301 | 20230905 | 730 | 2209677 | 269 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1435 | 35.3675 | -119.2526 | No | Clear;32-90 F |  |  | 23-0112447 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871194 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | TRANSFORMER | 516812167431 | 20230905 | 1000 | 20230905 | 1130 | 2209930 | 90 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 180 | 35.3481 | -119.07 | No | Clear;32-90 F | Fuse | Broken | 23-0112590 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871357 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | FUSE | 15686 | 20230905 | 2100 | 20230905 | 2350 | 2210419 | 170 | Distribution Circuit | 3rd Party | Vehicle | 5 | 850 | 35.1943 | -119.1109 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0112829 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871402 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 8985 | 20230906 | 125 | 20230906 | 339 | 2210525 | 134 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 268 | 35.3706 | -119.002 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0112877 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871425 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | 516151372771 | 20230906 | 738 | 20230906 | 1623 | 2210588 | 525 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 525 | 35.4926 | -119.293 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0112935 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871448 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517040168154 | 20230906 | 752 | 20230907 | 1120 | 2210606 | 1648 | Transformer only | 3rd Party | Other | 4 | 6592 | 35.3689 | -118.9932 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0112951 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871458 | 0 | Non-EPSS | N | 2023
KERN | KERN | MARICOPA-1102 | 254211102 | JUMPER | OJ 1 E/ OF CGC 515812857096 | 20230906 | 756 | 20230906 | 1330 | 2210595 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 7682 | 35.061 | -119.399 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0112944 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871451 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ELK HILLS-1104 | 252441104 | FUSE | 18964 | 20230907 | 539 | 20230907 | 800 | 2211387 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1317 | 35.1842 | -119.4288 | No | Clear;32-90 F |  |  | 23-0113439 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871733 | 1 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1103 | 252861103 | OCB | 1103/2 | 20230907 | 900 | 20230907 | 918 | 2211588 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 2592 | 35.442 | -119.2606 | No | Clear;32-90 F | Jumper | Broken | 23-0113521 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871827 | 0 | Non-EPSS | N | 2023 | A- B- TIME
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 515164473676 | 20230907 | 950 | 20230908 | 1035 | 2211684 | 1485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1589 | 35.5132 | -119.6261 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0113805 | OH | Sus | 35487361 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871955 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 515280373520 | 20230907 | 950 | 20230908 | 1155 | 2211685 | 1565 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1565 | 35.51 | -119.5868 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0113847 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871963 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | TRANSFORMER | 517305870985 | 20230907 | 1034 | 20230908 | 1300 | s1871892 | 1586 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1586 | 35.4474 | -118.9044 | No | Clear;32-90 F | Secondary | Broken | 23-0113594 | OH | Sus | 31667951 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871892 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 18451 | 20230907 | 1214 | 20230908 | 554 | 2211814 | 1060 | Distribution Circuit | 3rd Party | Vehicle | 9 | 3726 | 35.6884 | -119.5088 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0113704 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1871928 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 8652 | 20230907 | 1235 | 20230908 | 1150 | 2211831 | 1395 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 13739 | 35.4088 | -119.0813 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0113718 | UG | Sus | 45960500 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871933 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 9725 | 20230907 | 1651 | 20230907 | 1928 | 2212054 | 157 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 677 | 35.3323 | -119.0028 | No | Clear;Above 90 | Transformer (UG) | Leaking | 23-0113803 | UG | Sus | 35487245 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871959 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1114 | 253371114 | FUSE | 20179 | 20230907 | 2347 | 20230908 | 57 | 2212303 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 95 | 6650 | 35.3726 | -118.9632 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0113906 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871995 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | JUMPER | #2 JUMPER BURNT OPEN | 20230908 | 322 | 20230908 | 558 | 2212362 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 3120 | 35.4425 | -119.4749 | No | Clear;32-90 F | Jumper | Burned Open | 23-0113937 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1872004 | 1 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 13289 | 20230908 | 647 | 20230908 | 815 | 2212390 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 5808 | 35.3833 | -119.2166 | No | Clear;32-90 F |  |  | 23-0113984 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872029 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1102 | 252961102 | FUSE | 7599 | 20230908 | 653 | 20230908 | 855 | 2212389 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 5368 | 35.5993 | -119.3495 | No | Clear;32-90 F |  |  | 23-0114039 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872099 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 43373 | 20230908 | 713 | 20230908 | 907 | 2212403 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 114 | 35.4205 | -119.4471 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0113964 | OH | Sus | 45963519 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872020 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1102 | 252971102 | RECLOSER | 4106 | 20230908 | 1102 | 20230908 | 1112 | 2212369 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1016 | 10160 | 35.1946 | -118.8367 | No | Clear;32-90 F | Jumper | Deteriorated | 23-0114134 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872164 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | SEMITROPIC-1110 | 252901110 | FUSE | 7602 | 20230908 | 1139 | 20230908 | 1246 | 2212749 | 67 | Distribution Circuit | Animal | Bird found | 141 | 7207 | 35.6014 | -119.3537 | No | Clear;32-90 F | Fuse | Normal | 23-0114178 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872181 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7292 | 20230908 | 1618 | 20230908 | 1836 | 2213105 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2070 | 35.7609 | -119.5625 | No | Clear;Above 90 | Conductor- Overhead | Together | 23-0114330 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872239 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 966142 | 20230908 | 1732 | 20230908 | 2029 | 2213176 | 177 | Distribution Circuit | 3rd Party | Customer Equipment | 6 | 1062 | 35.3141 | -118.8298 | No | Clear;32-90 F | Other | Failed/Faulted | 23-0114315 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872232 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | ANTELOPE-1101 | 252021101 | FUSE | 7078 | 20230908 | 1843 | 20230909 | 1224 | 2213208 | 1061 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3183 | 35.6586 | -120.0555 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114340 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1872244 | 0 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | JUMPER | OJ @ LINE & BUCK @ CGC #515254177914 | 20230908 | 1858 | 20230909 | 1805 | 2213900 | 1387 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1387 | 35.6302 | -119.5981 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 23-0114497 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872436 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 69452 | 20230909 | 519 | 20230909 | 641 | 2213343 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 2788 | 35.3647 | -119.0923 | Yes | Clear;32-90 F |  |  | 23-0114383 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1872289 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | T11646 | 20230909 | 859 | 20230909 | 918 | 2213404 | 19 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 19 | 35.204 | -119.09 | Yes | Clear;32-90 F |  |  | 23-0114411 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872353 | 0 | Non-EPSS | N | 2023
KERN | KERN | WELLFIELD-1104 | 254291104 | SWITCH | 3406 | 20230909 | 1149 | 20230909 | 1415 | 2213698 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1752 | 35.2368 | -118.7766 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0114400 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872396 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1106 | 252081106 | FUSE | 847825 | 20230909 | 1652 | 20230909 | 1838 | 2213978 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 106 | 35.1467 | -119.471 | Yes | Partly Cloudy;Above 90 |  |  | 23-0114540 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872474 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | OTHER | J2105 TWD T13210 | 20230909 | 1824 | 20230909 | 1925 | 2214009 | 61 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 610 | 35.3902 | -119.1833 | Yes | Partly Cloudy;Above 90 | Transformer (UG) | Leaking | 23-0114517 | UG | Sus | 35487550 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872466 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | OTHER | J2106 TWD T13212 | 20230909 | 1941 | 20230909 | 2023 | 2214226 | 42 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 462 | 35.389 | -119.1833 | Yes | Partly Cloudy;Above 90 | Transformer (UG) | Leaking | 23-0114557 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872493 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 390355 | 20230909 | 2001 | 20230909 | 2138 | 2214301 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 4656 | 35.3569 | -119.0062 | Yes | Partly Cloudy;Above 90 |  |  | 23-0114576 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872510 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 7296 | 20230909 | 2035 | 20230910 | 1133 | 2214028 | 898 | Distribution Circuit | 3rd Party | Vehicle | 9 | 8082 | 35.7028 | -119.7613 | Yes | Partly Cloudy;Above 90 | Pole-Wood | Broken | 23-0114577 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872511 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 16382 | 20230909 | 2156 | 20230910 | 1655 | 2214340 | 1139 | Distribution Circuit | 3rd Party | Vehicle | 3 | 3417 | 35.6671 | -119.2584 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0114590 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1872529 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1103 | 252861103 | FUSE | 14011 | 20230911 | 816 | 20230911 | 1045 | 2215189 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2235 | 35.4334 | -119.1896 | No | Clear;32-90 F |  |  | 23-0114917 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872945 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1106 | 252901106 | TRANSFORMER | 515857075455 | 20230911 | 1014 | 20230911 | 1745 | 2215423 | 451 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 451 | 35.5658 | -119.394 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115030 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873005 | 0 | Non-EPSS | N | 2023
KERN | KERN | WELLFIELD-1102 | 254291102 | OCB | 1102/2 | 20230911 | 1022 | 20230911 | 1035 | 2215437 | 13 | Distribution Circuit | Equipment Failure/Involved | Overhead | 173 | 2249 | 35.2249 | -118.7784 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0114858 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872932 | 0 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | KERN OIL-1109 | 252721109 | TRANSFORMER | 516904069955 | 20230911 | 1220 | 20230912 | 301 | 2215565 | 881 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 27001 | 35.4176 | -119.0398 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0115082 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873018 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13895 | 20230911 | 1309 | 20230912 | 320 | 2215610 | 851 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 3 | 2834 | 35.7322 | -119.8033 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0115108 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873028 | 1 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20230911 | 1400 | 20230911 | 1539 | 2215650 | 99 | Distribution Circuit | 3rd Party | Customer Equipment | 32 | 3168 | 35.6271 | -118.9849 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0115075 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1873016 | 0 | EPSS Ckt | Y | 2023 | A & B INST
KERN | KERN | RENFRO-2105 | 254572105 | OTHER | T10711 TWD T10712 | 20230911 | 1919 | 20230911 | 2056 | 2215989 | 97 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 6596 | 35.4047 | -119.1377 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0115219 | UG | Sus | 35487867 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873097 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1109 | 254071109 | FUSE | 8765 | 20230911 | 2345 | 20230912 | 49 | 2216061 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 1088 | 35.3061 | -119.0534 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0115279 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1873131 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1106 | 254501106 | OTHER | J876 TWD J804 | 20230912 | 727 | 20230912 | 951 | 2216176 | 144 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 3540 | 35.5833 | -119.3404 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0115254 | UG | Sus | 35488099 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873154 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13400 | 20230912 | 810 | 20230912 | 1121 | 2216245 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 955 | 35.2306 | -118.8966 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115328 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873174 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1102 | 254501102 | OCB | 1102/2 | 20230912 | 1131 | 20230912 | 1500 | 2216623 | 209 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 284 | 16623 | 35.6081 | -119.3255 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0115461 | OH | Sus | 31668471 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1873347 | 0 | Non-EPSS | N | 2023 | C & GRD TIME
KERN | KERN | KERN OIL-1109 | 252721109 | OCB | 1109/2 | 20230912 | 1243 | 20230912 | 2108 | 2216703 | 397 | Distribution Circuit | Equipment Failure/Involved | Underground | 1895 | 649279 | 35.4407 | -119.0203 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0115518 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873375 | 0 | Non-EPSS | N | 2023 | C GRD 51
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 13153 | 20230913 | 615 | 20230913 | 725 | 2217271 | 70 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 63 | 4410 | 35.3448 | -119.0042 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0115853 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873519 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2109 | 254072109 | FUSE | 8889 | 20230913 | 630 | 20230913 | 920 | 2217586 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 850 | 35.2947 | -119.0339 | No | Clear;32-90 F |  |  | 23-0115940 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1873664 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 14824 | 20230913 | 1455 | 20230913 | 1530 | 2218051 | 35 | Distribution Circuit | Animal | Bird found | 87 | 3045 | 35.3853 | -118.999 | No | Clear;Above 90 | Transformer (OH) | Normal | 23-0116245 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1873769 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 100000016943 | 20230914 | 739 | 20230914 | 1523 | 2218683 | 464 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 464 | 35.3774 | -119.3412 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0116575 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874035 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 16917 | 20230914 | 831 | 20230914 | 1212 | 2218551 | 221 | Distribution Circuit | Animal | Squirrel | 2 | 442 | 35.4564 | -119.3143 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0116635 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874054 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 13889 | 20230914 | 1710 | 20230915 | 315 | 2219121 | 605 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2420 | 35.2747 | -118.8785 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0116861 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1874103 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 264429 | 20230914 | 1811 | 20230915 | 307 | 2219131 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 536 | 35.7306 | -119.4459 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0116866 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874107 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517014567532 | 20230914 | 1839 | 20230914 | 1949 | 2219143 | 70 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 350 | 35.3517 | -119.0018 | No | Clear;Above 90 |  |  | 23-0116894 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1874120 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 14128 | 20230915 | 902 | 20230915 | 1250 | 2219544 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 228 | 35.3532 | -118.9763 | No | Clear;32-90 F | Lightning Arrestor | Broken | 23-0117217 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874373 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 75683 | 20230915 | 1027 | 20230915 | 1130 | 2219763 | 63 | Distribution Circuit | 3rd Party | Vehicle | 11 | 693 | 35.267 | -118.9176 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0117167 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874357 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2105 | 254072105 | TRANSFORMER | T505126 | 20230915 | 1030 | 20230915 | 1115 | 2219764 | 45 | Transformer only | Equipment Failure/Involved | Underground | 3 | 135 | 35.3076 | -119.067 | No | Clear;32-90 F | Secondary | Broken | 23-0117115 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874345 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1105 | 254071105 | FUSE | 9543 | 20230916 | 748 | 20230916 | 940 | 2220372 | 112 | Distribution Circuit | Animal | Squirrel | 38 | 4256 | 35.3171 | -119.0583 | No | Clear;32-90 F | Jumper | Burned Open | 23-0117405 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1874501 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516923866314 | 20230916 | 1307 | 20230916 | 1400 | 2220651 | 53 | Transformer only | 3rd Party | Metallic Balloon | 3 | 159 | 35.3183 | -119.0319 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0117473 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874553 | 0 | Non-EPSS | N | 2023
KERN | KERN | SCE TEHACHAPI-1101 | 258131101 | OCB | 1101/2 | 20230916 | 2104 | 20230917 | 254 | 2220809 | 350 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1050 | 35.1976 | -118.7007 | No | Clear;32-90 F |  |  | 23-0117499 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874577 | 0 | Non-EPSS | N | 2023 | SCE RELAY
KERN | KERN | STOCKDALE-2113 | 254072113 | OTHER | J1366 TWD T10728 | 20230916 | 2306 | 20230917 | 44 | 2220836 | 98 | Distribution Circuit | 3rd Party | Vehicle | 1 | 98 | 35.3178 | -119.0395 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0117497 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874588 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516908267682 | 20230917 | 541 | 20230917 | 653 | 2220869 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 432 | 35.3552 | -119.0378 | No | Clear;32-90 F | Fuse | Broken | 23-0117522 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874603 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | FUSE | 7427 | 20230917 | 646 | 20230917 | 1658 | 2220916 | 612 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 6120 | 35.3838 | -119.3233 | No | Partly Cloudy;32-90 F |  |  | 23-0117569 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874649 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 9163 | 20230917 | 822 | 20230917 | 1415 | 2220953 | 353 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2118 | 35.3529 | -119.9873 | No | Overcast;32-90 F |  |  | 23-0117554 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874633 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WEEDPATCH-1102 | 252971102 | OTHER | J96549 TWD T237439 | 20230917 | 1509 | 20230917 | 1647 | 2221044 | 98 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 1862 | 35.185 | -118.8417 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0117542 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874635 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1106 | 253411106 | TRANSFORMER | 517079058120 | 20230917 | 1658 | 20230917 | 1735 | 2221083 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 37 | 35.0934 | -118.9772 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0117570 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874650 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WEEDPATCH-1102 | 252971102 | OTHER | T14435 TWD T14434 | 20230917 | 1725 | 20230917 | 1952 | 2221088 | 147 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 2352 | 35.1878 | -118.8366 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0117546 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874651 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1102 | 252971102 | OTHER | J1322 TWD T10567 | 20230917 | 2355 | 20230918 | 208 | 2221150 | 133 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 4655 | 35.1941 | -118.8398 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0117555 | UG | Sus | 35489462 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874674 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1102 | 252971102 | OTHER | T14324 TWD T14325 | 20230918 | 230 | 20230918 | 322 | 2221158 | 52 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 1456 | 35.1872 | -118.8382 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0117544 | UG | Sus | 35489362 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874677 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1102 | 252971102 | OTHER | T14307 TWD T14308 | 20230918 | 1328 | 20230918 | 1628 | 2221704 | 180 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 4680 | 35.1892 | -118.8344 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0117830 | UG | Sus | 35489474 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874913 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1116 | 253491116 | OTHER | WIRE DOWN 1 SP N/OF 49515 | 20230918 | 1348 | 20230918 | 2242 | 2221731 | 534 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 22108 | 35.5716 | -119.1156 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0117878 | OH | Sus | 31669495 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | Yes | Yes | 1874927 | 1 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T11957 TWD T11958 | 20230918 | 1424 | 20230918 | 1532 | 2221755 | 68 | Distribution Circuit | Equipment Failure/Involved | Underground | 79 | 5372 | 35.4094 | -119.1288 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0117809 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874929 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-2103 | 252552103 | RECLOSER | 768638 | 20230918 | 1525 | 20230918 | 1718 | 2221837 | 113 | Distribution Circuit | Animal | Other | 52 | 5876 | 35.4378 | -119.6873 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0117923 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874945 | 0 | Non-EPSS | N | 2023 | B C
KERN | KERN | LAMONT-1105 | 253911105 | TRANSFORMER | 517542563365 | 20230918 | 1754 | 20230919 | 200 | 2221921 | 486 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 486 | 35.2383 | -118.8239 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117983 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1874961 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516785064445 | 20230919 | 1142 | 20230919 | 1210 | 2222437 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 35.2668 | -119.0777 | No | Clear;32-90 F | Fuse | Broken | 23-0118208 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875225 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 7547 | 20230919 | 1840 | 20230920 | 110 | 2222768 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3900 | 35.6019 | -119.2644 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0118433 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875291 | 0 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1101 | 253801101 | OTHER | T14948 TWD T14949 | 20230919 | 1854 | 20230919 | 2116 | 2222774 | 142 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 4118 | 35.1916 | -118.8278 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0118283 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875295 | 0 | EPSS Ckt | N | 2023
KERN | KERN | RENFRO-2107 | 254572107 | FUSE | 18668 | 20230920 | 538 | 20230920 | 2126 | 2222874 | 948 | Distribution Circuit | Equipment Failure/Involved | Underground | 67 | 63516 | 35.4154 | -119.1454 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0118546 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875360 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 14376 | 20230920 | 835 | 20230920 | 930 | 2223062 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 1485 | 35.2668 | -119.0302 | No | Clear;32-90 F |  |  | 23-0118651 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1875527 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17784 | 20230920 | 1145 | 20230920 | 1252 | 2223365 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 4708 | 35.3447 | -119.0708 | No | Clear;32-90 F |  |  | 23-0118768 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875592 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | T5974 | 20230920 | 1305 | 20230921 | 255 | 2223439 | 830 | Transformer only | 3rd Party | Vandalism | 1 | 830 | 35.3513 | -119.0024 | No | Clear;32-90 F | Transformer | Leaking | 23-0118868 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875620 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1107 | 253411107 | TRANSFORMER | 516467857587 | 20230920 | 1438 | 20230920 | 2321 | 2223481 | 523 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 523 | 35.0765 | -119.1814 | No | Clear;32-90 F | Transformer | Broken | 23-0118877 | OH | Sus | 31669313 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875625 | 0 | Non-EPSS | N | 2023
KERN | KERN | NORCO-1101 | 254691101 | OCB | 1101/2 | 20230920 | 1801 | 20230921 | 621 | 2223682 | 740 | Distribution Circuit | Animal | Bird found | 100 | 43699 | 35.2855 | -119.309 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0118956 | OH | Sus | 45985827 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1875651 | 0 | Non-EPSS | N | 2023 | AG TIME
KERN | KERN | STOCKDALE-2113 | 254072113 | OCB | 2113/2 | 20230920 | 2014 | 20230920 | 2115 | 2223717 | 61 | Distribution Circuit | 3rd Party | Metallic Balloon | 3714 | 226554 | 35.3165 | -119.0678 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118971 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1875656 | 0 | Non-EPSS | N | 2023 | PH OC
KERN | KERN | FAMOSO-1101 | 252461101 | FUSE | 18714 | 20230921 | 1003 | 20230921 | 1511 | 2224048 | 308 | Distribution Circuit | 3rd Party | Vehicle | 1 | 308 | 35.6425 | -119.1337 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0119260 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1875770 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1106 | 253411106 | TRANSFORMER | 517052758650 | 20230921 | 1526 | 20230922 | 215 | 2224176 | 649 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 649 | 35.1078 | -118.9861 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0119452 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875820 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WEEDPATCH-1102 | 252971102 | FUSE | 13131 | 20230921 | 1837 | 20230921 | 2050 | 2224267 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 887 | 35.1943 | -118.8793 | No | Clear;32-90 F |  |  | 23-0119462 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875828 | 1 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1101 | 252961101 | TRANSFORMER | 515991875607 | 20230921 | 2119 | 20230922 | 935 | 2224317 | 736 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1472 | 35.5697 | -119.3493 | No | Clear;32-90 F | Service conductor | Failed/Faulted | 23-0119510 | UG | Sus | 45986852 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875859 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1108 | 254071108 | SWITCH | 3886 | 20230921 | 2155 | 20230922 | 454 | s1875869 | 419 | Distribution Circuit | 3rd Party | Vehicle | 28 | 11732 | 35.3323 | -119.0369 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0119456 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875869 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | RECLOSER | 88892 | 20230921 | 2256 | 20230922 | 15 | 2224356 | 79 | Distribution Circuit | 3rd Party | Metallic Balloon | 2011 | 158869 | 35.3657 | -118.9447 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0119506 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1875855 | 0 | Non-EPSS | N | 2023 | AB
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRANSFORMER | 513813268759 | 20230922 | 1613 | 20230922 | 2034 | 2225009 | 261 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 522 | 35.3721 | -120.0763 | No | Clear;32-90 F |  |  | 23-0119966 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1876126 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WESTPARK SUB | 25370 | OCB | 1200/2 | 20230923 | 714 | 20230923 | 1230 | 2225214 | 316 | Distribution Circuit | 3rd Party | Vehicle | 808 | 27262 | 35.374 | -119.0404 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0119996 | OH | Sus | 35490910 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1876155 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 13231 | 20230923 | 740 | 20230923 | 900 | 2225221 | 80 | Distribution Circuit | Animal | Bird found | 17 | 1360 | 35.354 | -118.9925 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0120018 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876204 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRIP-SAVER | 9360 | 20230923 | 1545 | 20230923 | 1824 | 2225507 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1431 | 35.1659 | -119.1101 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0120070 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1876232 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | LERDO-1116 | 253491116 | OCB | 1116/2 | 20230924 | 1735 | 20230924 | 1810 | 2225961 | 35 | Distribution Circuit | 3rd Party | Vehicle | 105 | 3675 | 35.5004 | -119.1518 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0120142 | OH | Sus | 35491024 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876330 | 0 | Non-EPSS | N | 2023 | A & B INST
KERN | KERN | KERN OIL-1106 | 252721106 | OCB | 1106/2 | 20230924 | 1759 | 20230924 | 2011 | 2225965 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 826 | 109032 | 35.4407 | -119.0204 | No | Clear;32-90 F |  |  | 23-0120164 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1876331 | 0 | EPSS Ckt | N | 2023 | ABC
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 7371 | 20230924 | 1923 | 20230924 | 2311 | 2225983 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1369 | 35.3841 | -119.4482 | No | Clear;32-90 F |  |  | 23-0120187 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876351 | 1 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 13289 | 20230925 | 714 | 20230925 | 1251 | 2226133 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 7330 | 35.3833 | -119.2166 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0120285 | OH | Sus | 45989206 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876510 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRIP-SAVER | 13017 | 20230925 | 813 | 20230925 | 957 | 2226214 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 128 | 13312 | 35.335 | -119.0029 | No | Clear;32-90 F |  |  | 23-0120317 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876562 | 0 | Non-EPSS | N | 2023 | A & B
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515872857327 | 20230925 | 916 | 20230925 | 1344 | 2226365 | 268 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 268 | 35.0674 | -119.3795 | No | Clear;32-90 F |  |  | 23-0120480 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1876636 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517128368083 | 20230925 | 1047 | 20230925 | 1120 | 2226515 | 33 | Transformer only | Equipment Failure/Involved | Electrical Overload | 10 | 330 | 35.3673 | -118.9637 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0120351 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1876582 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | FUSE | 14715 | 20230926 | 1023 | 20230926 | 1138 | 2227533 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 375 | 35.526 | -119.4747 | No | Clear;32-90 F |  |  | 23-0120934 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876956 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1104 | 253551104 | TRANSFORMER | 515684783000 | 20230926 | 1024 | 20230926 | 1226 | 2227184 | 122 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 122 | 35.7721 | -119.4553 | No | Clear;32-90 F | Connector- Bolted | Arcing | 23-0120870 | OH | Sus | 45990037 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876940 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2101 | 254572101 | SWITCH | 767322 | 20230926 | 1524 | 20230926 | 1603 | 2227809 | 39 | Distribution Circuit | Company Initiated | Improper Construction | 88 | 3432 | 35.3542 | -119.1802 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0109792 | UG | Sus | 35341975 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1877007 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRIP-SAVER | 3527 | 20230926 | 1534 | 20230926 | 1933 | 2227824 | 239 | Distribution Circuit | Animal | Bird found | 210 | 50190 | 35.3482 | -120.0054 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0121175 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877038 | 0 | EPSS Ckt | N | 2023 | AC
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517537162280 | 20230926 | 1547 | 20230927 | 237 | 2227840 | 650 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3900 | 35.2087 | -118.825 | No | Clear;32-90 F | Transformer | Leaking | 23-0121119 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877015 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2101 | 254572101 | SWITCH | 767322 | 20230926 | 1633 | 20230926 | 1654 | 2227883 | 21 | Distribution Circuit | Company Initiated | Improper Construction | 87 | 1827 | 35.3542 | -119.1802 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0109792 | UG | Sus | 35341975 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1877021 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1106 | 254201106 | JUMPER | WIRE DOWN #1 PHASE | 20230926 | 1753 | 20230926 | 1944 | 2227934 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 5010 | 35.6449 | -119.4912 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0121180 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | Yes | No | 1877045 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1104 | 252081104 | TRANSFORMER | 515613359850 | 20230926 | 2220 | 20230927 | 910 | 2228079 | 650 | Transformer only | 3rd Party | Fire- house or bldg. | 19 | 12350 | 35.1355 | -119.4681 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0121226 | OH | Sus | 31670501 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877083 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1104 | 252081104 | TRANSFORMER | 515610059810 | 20230926 | 2324 | 20230927 | 841 | 2228105 | 557 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3899 | 35.1346 | -119.4692 | No | Clear;32-90 F | Secondary | Broken | 23-0121234 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877085 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 122865 | 20230926 | 2357 | 20230927 | 47 | 2228113 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 300 | 35.34 | -119.1496 | No | Clear;32-90 F |  |  | 23-0121236 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877086 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1104 | 252901104 | TRANSFORMER | 515617275451 | 20230927 | 1041 | 20230927 | 1312 | 2228525 | 151 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 151 | 35.5642 | -119.4742 | No | Clear;32-90 F |  |  | 23-0121564 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1877338 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 8450 | 20230927 | 1501 | 20230928 | 400 | 2228736 | 779 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 779 | 35.3175 | -119.0337 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0121697 | UG | Sus | 45992438 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877355 | 1 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | SWITCH | 5252 | 20230927 | 1650 | 20230927 | 1947 | 2228854 | 177 | Distribution Circuit | 3rd Party | Vandalism | 10 | 546 | 35.3744 | -118.934 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0121578 | UG | Sus | 35491858 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1877364 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516393962415 | 20230928 | 1058 | 20230928 | 1839 | 2229212 | 461 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 922 | 35.2094 | -119.2082 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0122055 | OH | Sus | 31670513 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877614 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | T7128 | 20230928 | 1217 | 20230928 | 2045 | 2229552 | 508 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 4434 | 35.3734 | -119.1391 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0122167 | UG | Sus | 35492504 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877656 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 100000028157 | 20230928 | 1233 | 20230928 | 1417 | 2229561 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 104 | 35.0624 | -119.0382 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0122203 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877663 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | JUMPER | WIRE DOWN 1 E/OF L200 | 20230928 | 1418 | 20230928 | 2221 | 2229751 | 483 | Distribution Circuit | 3rd Party | Vehicle | 116 | 22774 | 35.2525 | -118.8899 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0122258 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1877693 | 1 | EPSS Ckt | N | 2023
KERN | KERN | WESTPARK-1107 | 253701107 | SWITCH | 11841 | 20230929 | 4 | 20230929 | 253 | 2229957 | 169 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 1007 | 35.3755 | -119.0436 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0122276 | UG | Sus | 35492378 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1877744 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | SWITCH | 5585 | 20230929 | 52 | 20230929 | 330 | 2229967 | 158 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 698 | 35.3759 | -118.9362 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0122292 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1877748 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2102 | 255262102 | SWITCH | 58270 | 20230929 | 1254 | 20230929 | 1318 | 2230489 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 816 | 35.3659 | -119.0921 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0122609 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1877952 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | TRIP-SAVER | 16222 | 20230929 | 1818 | 20230929 | 2005 | 2230675 | 107 | Distribution Circuit | 3rd Party | Customer Equipment | 10 | 737 | 35.3545 | -119.2435 | No | Clear;32-90 F | Customer Equipment | Burned/flashed | 23-0122761 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877992 | 0 | Non-EPSS | N | 2023 | A- C
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | 517400367356 | 20230929 | 2038 | 20230929 | 2144 | 2230815 | 66 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 66 | 35.3476 | -118.8729 | No | Clear;32-90 F |  |  | 23-0122775 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1878004 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WESTPARK-1108 | 253701108 | FUSE | 20213 | 20230929 | 2131 | 20230929 | 2243 | 2230811 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 103 | 7416 | 35.3468 | -119.0251 | No | Partly Cloudy;32-90 F |  |  | 23-0122789 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1878017 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517276866075 | 20230930 | 1001 | 20230930 | 1102 | 2231490 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 122 | 35.3126 | -118.9148 | No | Clear;32-90 F |  |  | 23-0122921 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1878176 | 0 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1101 | 252021101 | FUSE | 18375 | 20230930 | 1124 | 20230930 | 1605 | 2231555 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2504 | 35.6729 | -120.0455 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0122970 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1878211 | 1 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-1106 | 254071106 | FUSE | 14064 | 20230930 | 1707 | 20230930 | 1758 | 2231794 | 41 | Distribution Circuit | 3rd Party | Metallic Balloon | 36 | 1476 | 35.3364 | -119.0434 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0123023 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1878248 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | OCB | 2101/2 | 20231001 | 508 | 20231001 | 1104 | 2232015 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 52070 | 35.5593 | -118.9574 | No | Partly Cloudy;32-90 F | Insulator | Burned/flashed | 23-0123069 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1878299 | 0 | EPSS Ckt | Y | 2023 | PH OC INST GRD
KERN | KERN | STOCKDALE-1108 | 254071108 | OCB | 1108/2 | 20231001 | 727 | 20231001 | 1156 | 2232029 | 269 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1254 | 13232 | 35.3164 | -119.0681 | No | Overcast-Rain;32-90 F | Conductor- Underground | Burned/flashed | 23-0123073 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1878306 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20231001 | 739 | 20231001 | 828 | 2232069 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 925 | 45325 | 35.3885 | -119.0046 | No | Overcast-Rain;32-90 F |  |  | 23-0123074 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878307 | 0 | Non-EPSS | N | 2023 | A B
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8008 | 20231001 | 814 | 20231001 | 915 | 2232081 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 4880 | 35.3491 | -119.0845 | No | Overcast-Drizzle;32-90 F |  |  | 23-0123083 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878316 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20231001 | 1423 | 20231001 | 1608 | 2232208 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1155 | 35.4767 | -119.5887 | No | Clear;32-90 F |  |  | 23-0123116 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878356 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 516105269583 | 20231001 | 1610 | 20231001 | 1856 | 2232236 | 166 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 332 | 35.4045 | -119.3077 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0123126 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1878365 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1103 | 254561103 | RECLOSER | 1190 | 20231002 | 507 | 20231002 | 1336 | 2232394 | 509 | Distribution Circuit | 3rd Party | Vehicle | 391 | 37103 | 35.3835 | -119.2471 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0123176 | OH | Sus | 35492907 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1878406 | 0 | Non-EPSS | N | 2023 | B & grd
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20231002 | 1459 | 20231002 | 1822 | 2233055 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 26390 | 35.5605 | -118.9587 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0123423 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1878635 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16172 | 20231003 | 953 | 20231003 | 1713 | 2233622 | 440 | Distribution Circuit | 3rd Party | Vehicle | 8 | 2904 | 35.1513 | -119.071 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0123765 | OH | Sus | 31671282 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1878934 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2101 | 254582101 | SWITCH | 158160 | 20231003 | 1002 | 20231003 | 1012 | 2233673 | 8 | Distribution Circuit | Company Initiated | Improper Construction | 239 | 1912 | 35.4447 | -119.119 | No | Clear;32-90 F | Switch (UG) | Normal | 23-0115400 | UG | Sus | 35349183 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1878931 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | TRANSFORMER | 516391274738 | 20231003 | 1143 | 20231003 | 1810 | 2233604 | 387 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 774 | 35.5476 | -119.2136 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0123816 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1878941 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1105 | 253181105 | FUSE | 7468 | 20231003 | 1448 | 20231003 | 2208 | 2233904 | 440 | Distribution Circuit | 3rd Party | Other | 17 | 7480 | 35.7202 | -119.2942 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0123999 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1878992 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1105 | 253911105 | FUSE | 16997 | 20231003 | 1450 | 20231003 | 1548 | 2233906 | 58 | Distribution Circuit | Animal | Bird found | 1 | 58 | 35.2383 | -118.8322 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0124003 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878993 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2109 | 254072109 | RECLOSER | 4718 | 20231003 | 1655 | 20231004 | 306 | 2233986 | 611 | Distribution Circuit | 3rd Party | Vehicle | 2625 | 132184 | 35.2863 | -119.0389 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0124035 | OH | Sus | 35493531 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879003 | 0 | Non-EPSS | N | 2023 | C GRD
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7097 | 20231003 | 1811 | 20231004 | 353 | 2234102 | 582 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2910 | 35.5211 | -119.5463 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0124065 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1879027 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1108 | 254071108 | FUSE | 8109 | 20231004 | 554 | 20231004 | 637 | 2234180 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 731 | 35.3353 | -119.0517 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0124145 | OH | Sus | 45998950 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879084 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1108 | 253391108 | FUSE | 8034 | 20231004 | 659 | 20231004 | 1014 | 2234192 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 195 | 35.3809 | -119.0631 | No | Clear;32-90 F |  |  | 23-0124302 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879280 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517029368337 | 20231004 | 1221 | 20231004 | 1702 | 2234667 | 281 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1967 | 35.3738 | -118.9969 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0124444 | OH | Sus | 31671404 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1879350 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 18451 | 20231004 | 1738 | 20231004 | 1908 | 2234944 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 810 | 35.6884 | -119.5088 | No | Clear;32-90 F |  |  | 23-0124637 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1879390 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | OCB | 2115/2 | 20231005 | 445 | 20231007 | 350 | 2235216 | 2825 | Distribution Circuit | Equipment Failure/Involved | Underground | 4354 | 436787 | 35.3165 | -119.0677 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0124702 | UG | Sus | 31671604 | CENTRAL VALLEY | OCT | Multi-Fault | 0 | No | No | No | 1879437 | 0 | Non-EPSS | N | 2023 | A- C- GRD
KERN | KERN | FRUITVALE-1108 | 253391108 | SWITCH | 1425 | 20231005 | 533 | 20231005 | 1416 | 2235224 | 523 | Distribution Circuit | 3rd Party | Vehicle | 32 | 16736 | 35.3831 | -119.0653 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0124703 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879438 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1101 | 252961101 | TRANSFORMER | 515992376103 | 20231005 | 743 | 20231005 | 919 | 2235317 | 96 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 192 | 35.5834 | -119.3493 | No | Clear;32-90 F |  |  | 23-0124776 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1879545 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | 516038873480 | 20231005 | 848 | 20231005 | 1324 | 2235435 | 276 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 276 | 35.5119 | -119.3316 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0124799 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879597 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | RECLOSER | 4409 | 20231005 | 901 | 20231006 | 112 | 2235462 | 971 | Distribution Circuit | 3rd Party | Vehicle | 116 | 20686 | 35.2807 | -118.8786 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0124780 | OH | Sus | 35494149 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | No | No | 1879566 | 0 | EPSS Ckt | N | 2023 | ABC
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515508579990 | 20231005 | 931 | 20231005 | 1132 | 2235527 | 121 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 121 | 35.6884 | -119.5128 | No | Clear;32-90 F |  |  | 23-0124873 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1879635 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1103 | 254561103 | TRANSFORMER | 516308168923 | 20231005 | 952 | 20231005 | 1314 | 2235550 | 202 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 202 | 35.3875 | -119.2395 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0124940 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879669 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2106 | 254072106 | JUMPER | 2844 #2 PHASE | 20231005 | 2109 | 20231005 | 2326 | 2236142 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 7809 | 35.314 | -119.0205 | No | Clear;32-90 F |  |  | 23-0125139 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879764 | 1 | Non-EPSS | N | 2023
KERN | KERN | ARVIN-1101 | 253801101 | SWITCH | 3182 | 20231005 | 2302 | 20231006 | 320 | 2236140 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 516 | 35.1395 | -118.8537 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0125114 | OH | Sus | 35494105 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879762 | 0 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 7072 | 20231006 | 546 | 20231006 | 1031 | 2236252 | 285 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2565 | 35.7179 | -119.3835 | No | Clear;32-90 F |  |  | 23-0125360 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1879962 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 16924 | 20231006 | 826 | 20231006 | 1205 | 2236360 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 438 | 35.4237 | -119.2876 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0125209 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879853 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1102 | 253371102 | TRANSFORMER | 517021868897 | 20231006 | 1010 | 20231006 | 1816 | 2236663 | 486 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3402 | 35.3888 | -118.9994 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0125529 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880032 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1108 | 253701108 | TRANSFORMER | 516964267477 | 20231007 | 724 | 20231007 | 1047 | 2237364 | 203 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 1015 | 35.3499 | -119.0185 | No | Clear;32-90 F |  |  | 23-0125718 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1880206 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1104 | 254541104 | FUSE | 7149 | 20231007 | 812 | 20231007 | 1129 | 2237632 | 197 | Distribution Circuit | 3rd Party | Vehicle | 2 | 394 | 35.4861 | -119.4034 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0125723 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1880209 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1105 | 254071105 | FUSE | 9543 | 20231007 | 1246 | 20231007 | 1357 | 2237680 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1800 | 35.3171 | -119.0583 | No | Clear;32-90 F |  |  | 23-0125745 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880223 | 1 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | OTHER | T10014 TWD T10015 | 20231007 | 1720 | 20231007 | 1925 | 2237856 | 125 | Distribution Circuit | Equipment Failure/Involved | Underground | 84 | 10500 | 35.2885 | -119.0151 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0125729 | UG | Sus | 35494684 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880244 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1110 | 252901110 | FUSE | 7112 | 20231008 | 441 | 20231008 | 1858 | 2238107 | 857 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 16716 | 35.5911 | -119.3536 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 23-0125835 | UG | Sus | 35494880 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1880296 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13418 | 20231009 | 732 | 20231009 | 847 | 2238582 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 68 | 5100 | 35.3691 | -118.9991 | No | Clear;32-90 F |  |  | 23-0125968 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880507 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 16249 | 20231009 | 842 | 20231009 | 1112 | 2238664 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 4500 | 35.4009 | -119.472 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0125952 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880478 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516710361425 | 20231009 | 907 | 20231009 | 1107 | 2238740 | 120 | Transformer only | Vegetation | Other ground vegetation | 1 | 120 | 35.1833 | -119.1008 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0126058 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880614 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1110 | 252721110 | TRANSFORMER | 516961070106 | 20231009 | 1010 | 20231009 | 1539 | 2238859 | 329 | Transformer only | Unknown Cause | Patrol - found nothing | 21 | 6909 | 35.422 | -119.0203 | No | Partly Cloudy;32-90 F |  |  | 23-0126029 | OH | Sus | 31672002 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880605 | 0 | Non-EPSS | N | 2023
KERN | KERN | FELLOWS-2104 | 254242104 | TRANSFORMER | 515558459734 | 20231009 | 1240 | 20231009 | 1502 | 2238861 | 142 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 142 | 35.1326 | -119.4865 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 23-0126110 | OH | Sus | 46004046 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880646 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | FUSE | 17005 | 20231009 | 1331 | 20231009 | 2004 | 2239062 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3433 | 34.9417 | -118.9316 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0126116 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880648 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WESTPARK-1108 | 253701108 | JUMPER | JMPRS 1/W/OF CGC# 516924767380 | 20231009 | 1715 | 20231009 | 1846 | 2239251 | 91 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1638 | 35.3472 | -119.0322 | No | Partly Cloudy;32-90 F | Bushing | Broken | 23-0126229 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880688 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 390355 | 20231009 | 1855 | 20231009 | 2033 | 2239359 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 4704 | 35.3569 | -119.0062 | No | Clear;32-90 F |  |  | 23-0126273 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1880712 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516978970563 | 20231010 | 710 | 20231010 | 900 | 2239550 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 330 | 35.4347 | -119.0144 | No | Clear;32-90 F | Fuse | Broken | 23-0126405 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880865 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 15546 | 20231010 | 731 | 20231010 | 947 | 2239575 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1132 | 35.3749 | -118.9964 | No | Clear;32-90 F |  |  | 23-0126445 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880930 | 1 | Non-EPSS | N | 2023
KERN | KERN | BLACKWELL-1102 | 254681102 | FUSE | 7483 | 20231010 | 1535 | 20231010 | 2154 | 2240129 | 379 | Distribution Circuit | 3rd Party | Vehicle | 1 | 379 | 35.6362 | -119.8891 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0126696 | OH | Sus | 35495624 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881018 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 8483 | 20231011 | 120 | 20231011 | 406 | 2240347 | 166 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 166 | 35.3518 | -118.9849 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0126807 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881073 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1106 | 253371106 | TRANSFORMER | 517073169118 | 20231011 | 413 | 20231011 | 1049 | 2240362 | 396 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 4356 | 35.3953 | -118.9824 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0126814 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881078 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | OTHER | T14456 TWD T14457 | 20231011 | 1549 | 20231011 | 1700 | 2241163 | 71 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 355 | 35.2342 | -119.0773 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0126930 | UG | Sus | 35495863 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881382 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA SUB | 25314 | OTHER | TAFT-CUYAMA #1 170KV LINE | 20231011 | 1847 | 20231011 | 2222 | 2241284 | 215 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 542 | 115429 | 34.9277 | -119.6204 | No | Clear;32-90 F |  |  | 23-0127245 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881401 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | OTHER | J1444 TWD T83829 | 20231013 | 37 | 20231013 | 207 | 2242265 | 90 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 810 | 35.3469 | -118.974 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0127434 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881752 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 14438 | 20231013 | 1005 | 20231013 | 1140 | 2242465 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 95 | 35.3541 | -118.9623 | No | Overcast;32-90 F |  |  | 23-0127956 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881925 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 17307 | 20231013 | 1228 | 20231013 | 1540 | 2242684 | 190 | Distribution Circuit | Equipment Failure/Involved | Underground | 91 | 17290 | 35.2672 | -118.9031 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0128036 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881962 | 0 | Non-EPSS | N | 2023
KERN | KERN | ANTELOPE-1102 | 252021102 | FUSE | 7172 | 20231013 | 1411 | 20231013 | 1605 | 2242800 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 608 | 35.6568 | -119.9747 | No | Clear;32-90 F |  |  | 23-0128165 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882005 | 1 | EPSS Ckt | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | RECLOSER | 46960 | 20231013 | 1453 | 20231013 | 1707 | 2242823 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1072 | 35.4768 | -118.887 | No | Clear;32-90 F |  |  | 23-0128159 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882002 | 0 | EPSS Ckt | Y | 2023 | C SGF
KERN | KERN | FAMOSO-1101 | 252461101 | RECLOSER | 2686 | 20231013 | 1706 | 20231013 | 2337 | 2242900 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 39100 | 35.6313 | -119.1355 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0128187 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882009 | 0 | Non-EPSS | N | 2023 | BC
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 516099169660 | 20231014 | 827 | 20231014 | 954 | 2243215 | 87 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 87 | 35.4067 | -119.3097 | No | Clear;32-90 F |  |  | 23-0128268 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1882157 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1101 | 253191101 | OCB | 1101/2 | 20231014 | 837 | 20231014 | 1029 | 2243229 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 86 | 9632 | 35.0921 | -118.878 | No | Clear;32-90 F |  |  | 23-0128259 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882117 | 0 | EPSS Ckt | N | 2023 | C & B INST
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 16916 | 20231014 | 1243 | 20231014 | 2224 | 2243389 | 581 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 8 | 4648 | 35.443 | -119.3054 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0128320 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882186 | 1 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516972467823 | 20231014 | 1415 | 20231014 | 1855 | 2243463 | 279 | Transformer only | Equipment Failure/Involved | Overhead | 32 | 8921 | 35.3594 | -119.0161 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0128318 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882185 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1113 | 253491113 | SWITCH | 1313 | 20231015 | 906 | 20231015 | 1202 | 2243690 | 176 | Distribution Circuit | 3rd Party | Vehicle | 24 | 4224 | 35.5586 | -119.2007 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0128392 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882258 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 14631 | 20231016 | 848 | 20231016 | 1050 | 2244210 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 2978 | 35.3466 | -119.0075 | No | Clear;32-90 F |  |  | 23-0128629 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882495 | 1 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 9369 | 20231016 | 1004 | 20231016 | 1105 | 2244388 | 61 | Distribution Circuit | Animal | Squirrel | 11 | 651 | 35.4415 | -118.945 | No | Clear;32-90 F | Fuse | Burned Open | 23-0128651 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882505 | 1 | EPSS Ckt | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 13053 | 20231016 | 1415 | 20231016 | 1541 | 2244632 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1548 | 35.3981 | -119.1811 | No | Clear;32-90 F |  |  | 23-0128855 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882572 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2112 | 254072112 | RECLOSER | 1466 | 20231016 | 2245 | 20231017 | 104 | 2244907 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4577 | 595163 | 35.2878 | -119.0745 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0128927 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882618 | 0 | Non-EPSS | N | 2023 | B GRD
KERN | KERN | STOCKDALE-2115 | 254072115 | SWITCH | 1737 | 20231017 | 1304 | 20231017 | 1313 | 2245436 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 4577 | 41193 | 35.3123 | -119.0746 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128927 | OH | Sus | 46017636 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1882892 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1105 | 253951105 | FUSE | 2508 | 20231017 | 1630 | 20231017 | 1642 | 2245599 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 168 | 35.4198 | -118.9499 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0129310 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882924 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OTHER | J300 TWD T2034 | 20231017 | 2035 | 20231018 | 42 | 2245719 | 247 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 247 | 35.6166 | -119.6594 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0129285 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882937 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | RECLOSER | 3459 | 20231017 | 2300 | 20231018 | 1350 | 2245758 | 890 | Distribution Circuit | 3rd Party | Vehicle | 2880 | 427971 | 35.3755 | -118.9941 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0129379 | OH | Sus | 35503030 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882956 | 0 | Non-EPSS | N | 2023 | B C TIME
KERN | KERN | FRUITVALE-1105 | 253391105 | OCB | 1105/2 | 20231018 | 1201 | 20231018 | 1335 | 2246170 | 94 | Distribution Circuit | 3rd Party | Metallic Balloon | 1 | 94 | 35.3777 | -119.0928 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0129643 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1883174 | 0 | Non-EPSS | N | 2023 | AB PH OC INST SET A RLY
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 966142 | 20231018 | 1602 | 20231018 | 2243 | 2246358 | 401 | Distribution Circuit | 3rd Party | Customer Equipment | 6 | 2406 | 35.3141 | -118.8298 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0129803 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883221 | 0 | EPSS Ckt | N | 2023 | A GRD 51 TIME
KERN | KERN | RIO BRAVO-1101 | 252861101 | FUSE | 7569 | 20231018 | 1719 | 20231019 | 258 | 2246414 | 579 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2316 | 35.4781 | -119.2597 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0129864 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1883237 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 18310 | 20231018 | 1725 | 20231019 | 359 | 2246420 | 634 | Distribution Circuit | 3rd Party | Vehicle | 84 | 53256 | 35.3175 | -119.0063 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0129856 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1883232 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | OTHER | 15066 | 20231018 | 2104 | 20231019 | 1040 | 2246559 | 816 | Distribution Circuit | 3rd Party | Vehicle | 5 | 4020 | 35.3326 | -118.8799 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0129902 | OH | Sus | 31673311 | CENTRAL VALLEY | OCT | Open Circuit | 0 | No | Yes | Yes | 1883251 | 1 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | 516344679685 | 20231019 | 725 | 20231019 | 854 | 2246707 | 89 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 623 | 35.6837 | -119.2314 | No | Clear;32-90 F |  |  | 23-0130040 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1883331 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | 517258664186 | 20231020 | 1101 | 20231020 | 1250 | 2247591 | 109 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 109 | 35.2597 | -118.9192 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0130582 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1883659 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7285 | 20231020 | 2057 | 20231021 | 1535 | 2247918 | 1118 | Distribution Circuit | 3rd Party | Vehicle | 8 | 8948 | 35.4569 | -119.4382 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0130823 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883730 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 7207 | 20231021 | 1018 | 20231021 | 1200 | 2248193 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 918 | 35.7192 | -119.4193 | No | Clear;32-90 F |  |  | 23-0130900 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1883859 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1101 | 252961101 | FUSE | 14563 | 20231021 | 1211 | 20231021 | 1333 | 2248287 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 948 | 35.587 | -119.3129 | No | Clear;32-90 F |  |  | 23-0130918 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1883885 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 18245 | 20231021 | 1830 | 20231021 | 2057 | 2248434 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 1960 | 35.2581 | -118.9054 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0130944 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1883908 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1104 | 253951104 | FUSE | 13046 | 20231021 | 2157 | 20231022 | 28 | 2248512 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 9966 | 35.392 | -118.9665 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0130968 | OH | Sus | 31673680 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883930 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1104 | 253951104 | FUSE | 13047 | 20231022 | 406 | 20231022 | 432 | 2248701 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 1716 | 35.3912 | -118.9661 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0130968 | OH | Sus | 31673680 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883953 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 1703 | 20231022 | 631 | 20231022 | 800 | 2248740 | 89 | Distribution Circuit | Animal | Bird found | 1 | 89 | 35.559 | -118.9797 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0130997 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883965 | 0 | EPSS Ckt | Y | 2023 | B
KERN | KERN | MCKITTRICK-1101 | 252781101 | RECLOSER | 3092 | 20231022 | 2100 | 20231022 | 2310 | 2249314 | 130 | Distribution Circuit | Animal | Bird found | 45 | 2880 | 35.3071 | -119.6225 | No | Partly Cloudy;32-90 F | Bushing | Burned/flashed | 23-0131119 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884078 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20231023 | 457 | 20231023 | 1228 | 2249438 | 451 | Distribution Circuit | 3rd Party | Customer Equipment | 32 | 14432 | 35.6271 | -118.9849 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0131136 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884098 | 0 | EPSS Ckt | Y | 2023 | A- GRD & INST
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 2101/2 | 20231023 | 531 | 20231024 | 1052 | 2249447 | 1761 | Distribution Circuit | 3rd Party | Customer Equipment | 115 | 27258 | 35.5593 | -118.9574 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0131139 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884100 | 0 | EPSS Ckt | Y | 2023 | A- GRD- INST
KERN | KERN | OLD RIVER-1101 | 252821101 | RECLOSER | 3570 | 20231023 | 536 | 20231023 | 2344 | 2249453 | 1088 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 15232 | 35.179 | -119.1461 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0131140 | OH | Sus | 46028751 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1884102 | 0 | Non-EPSS | N | 2023 | A- B
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRIP-SAVER | 13017 | 20231023 | 553 | 20231023 | 1105 | 2249452 | 312 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 127 | 39624 | 35.335 | -119.0029 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0131153 | OH | Sus | 31673729 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1884112 | 1 | Non-EPSS | N | 2023 | A-GRD
KERN | KERN | MAGUNDEN-1108 | 252771108 | FUSE | 8902 | 20231023 | 620 | 20231023 | 918 | 2249463 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 8900 | 35.3252 | -118.933 | No | Clear;32-90 F |  |  | 23-0131237 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | No | No | 1884277 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 8178 | 20231023 | 708 | 20231023 | 852 | 2249484 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 7377 | 35.3142 | -119.0169 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 23-0131239 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884278 | 1 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1103 | 254561103 | TRANSFORMER | 516434969106 | 20231023 | 737 | 20231023 | 1406 | 2249502 | 389 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 389 | 35.3925 | -119.197 | No | Overcast-Heavy Rain-Fog;32-90 F | Transformer | Deteriorated | 23-0131200 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884181 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14390 | 20231023 | 745 | 20231023 | 1445 | 2249509 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 26880 | 35.3978 | -118.971 | No | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken | 23-0131323 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884323 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 7549 | 20231023 | 821 | 20231023 | 1607 | 2249574 | 466 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 5592 | 35.6018 | -119.2414 | No | Overcast;32-90 F | Crossarm- Wood | Burned/flashed | 23-0131291 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1884304 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1101 | 252861101 | FUSE | 18130 | 20231023 | 838 | 20231023 | 1905 | 2250060 | 627 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 8 | 5016 | 35.4854 | -119.2531 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0131475 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1884362 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1103 | 254541103 | TRANSFORMER | 515686974804 | 20231023 | 938 | 20231023 | 1320 | 2249739 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 444 | 35.5467 | -119.4509 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0131390 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884342 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1109 | 253701109 | RECLOSER | 1508 | 20231023 | 1003 | 20231023 | 1036 | 2249782 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1496 | 49368 | 35.3968 | -119.0431 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0131248 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1884284 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | LAMONT-1104 | 253911104 | OCB | 1104/2 | 20231023 | 1042 | 20231023 | 2047 | 2249826 | 605 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 432 | 73520 | 35.2971 | -118.8619 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0131282 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1884302 | 0 | EPSS Ckt | N | 2023 | B&C
KERN | KERN | WEEDPATCH-1101 | 252971101 | FUSE | 13129 | 20231023 | 1110 | 20231023 | 1518 | 2249867 | 248 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1736 | 35.2078 | -118.896 | No | Clear;32-90 F |  |  | 23-0131491 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1884364 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 16865 | 20231023 | 1123 | 20231023 | 2101 | 2249904 | 578 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 9 | 5202 | 35.3776 | -118.9542 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0131525 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1884371 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | T0083 | 20231023 | 1124 | 20231023 | 1516 | 2249873 | 232 | Transformer only | 3rd Party | Other | 21 | 4872 | 35.3627 | -118.9421 | No | Partly Cloudy;32-90 F | Customer Equipment | Burned Open | 23-0131500 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884368 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517199361135 | 20231023 | 1758 | 20231023 | 2019 | 2250174 | 141 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 282 | 35.1761 | -118.9382 | No | Clear;32-90 F | Fuse | Broken | 23-0131578 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884391 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516681668579 | 20231025 | 1410 | 20231025 | 1428 | 2251519 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 108 | 35.3791 | -119.1139 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0132462 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885007 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 15352 | 20231025 | 1417 | 20231025 | 1935 | 2251720 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 20034 | 35.4177 | -119.0495 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0132504 | OH | Sus | 31674127 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1885015 | 1 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 14899 | 20231025 | 1559 | 20231025 | 1640 | 2251782 | 41 | Distribution Circuit | 3rd Party | Metallic Balloon | 99 | 4059 | 35.3498 | -119.0433 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0132571 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885030 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 282557 | 20231025 | 1910 | 20231025 | 2112 | 2251877 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 231 | 28182 | 34.9474 | -119.6881 | No | Clear;32-90 F |  |  | 23-0132603 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885040 | 0 | EPSS Ckt | Y | 2023 | B & C
KERN | KERN | WASCO-1101 | 252961101 | FUSE | 55611 | 20231026 | 924 | 20231026 | 1239 | 2252335 | 195 | Distribution Circuit | 3rd Party | Vehicle | 1 | 195 | 35.5799 | -119.3128 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0132769 | OH | Sus | 31674241 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885251 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 9583 | 20231026 | 1205 | 20231026 | 2103 | 2252504 | 538 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 3784 | 35.3963 | -119.0744 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0132899 | UG | Sus | 35507593 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885342 | 1 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1106 | 253701106 | TRANSFORMER | 516912068498 | 20231026 | 1239 | 20231026 | 1338 | 2252531 | 59 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 5 | 295 | 35.3778 | -119.0367 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0132888 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1885337 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 648357 | 20231026 | 1320 | 20231026 | 1719 | 2252559 | 239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1594 | 35.4166 | -119.4829 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0132997 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885386 | 1 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 20256 | 20231027 | 1356 | 20231027 | 1413 | 2253452 | 17 | Distribution Circuit | Company Initiated | Return Circuit Normal | 9 | 144 | 35.3968 | -119.0758 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0132899 | UG | Sus | 35507593 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1885680 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | SWITCH | 1915 | 20231027 | 1818 | 20231028 | 220 | 2253562 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 2422 | 82442 | 35.343 | -119.0799 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0133423 | OH | Sus | 46033400 | CENTRAL VALLEY | OCT | Force Out | 0 | No | Yes | No | 1885708 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 15213 | 20231028 | 810 | 20231028 | 917 | 2254008 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 268 | 34.993 | -118.9008 | No | Clear;32-90 F |  |  | 23-0133501 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885820 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1103 | 253411103 | FUSE | 9062 | 20231028 | 1800 | 20231028 | 1925 | 2254436 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 425 | 35.0307 | -119.1357 | No | Clear;32-90 F |  |  | 23-0133602 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885894 | 0 | EPSS Ckt | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 14543 | 20231028 | 2249 | 20231029 | 44 | 2254533 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 156 | 17940 | 35.2307 | -119.0749 | No | Clear;32-90 F |  |  | 23-0133641 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885925 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2105 | 255322105 | FUSE | 14473 | 20231029 | 741 | 20231029 | 941 | 2254672 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 248 | 23964 | 35.325 | -119.1133 | No | Clear;32-90 F |  |  | 23-0133667 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885952 | 1 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 16247 | 20231029 | 802 | 20231029 | 1142 | 2254685 | 220 | Distribution Circuit | Animal | Bird found | 20 | 4400 | 35.3986 | -119.4831 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0133688 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885979 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1112 | 253491112 | RECLOSER | 4323 | 20231029 | 1149 | 20231029 | 1234 | 2254880 | 45 | Distribution Circuit | Animal | Bird found | 124 | 5580 | 35.5151 | -119.0819 | No | Clear;32-90 F | Booster | Burned/flashed | 23-0133694 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1885982 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 17587 | 20231029 | 1657 | 20231029 | 2300 | 2255007 | 363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 441 | 35.2091 | -119.1713 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0133734 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886027 | 1 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 7077 | 20231030 | 959 | 20231030 | 1209 | 2255593 | 130 | Distribution Circuit | Animal | Bird found | 3 | 390 | 35.7319 | -119.7786 | No | Clear-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0133996 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1886262 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1102 | 253181102 | FUSE | 16079 | 20231030 | 1224 | 20231030 | 1425 | 2255764 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 484 | 35.6889 | -119.2853 | No | Clear;32-90 F |  |  | 23-0134078 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1886298 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 14753 | 20231030 | 1402 | 20231031 | 245 | 2256103 | 763 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3815 | 35.016 | -118.922 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0134152 | OH | Sus | 31674719 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1886334 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 8886 | 20231030 | 1600 | 20231030 | 1654 | 2256018 | 54 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 1372 | 35.3296 | -119.0745 | No | Clear;32-90 F | Elbow | Broken | 23-0134025 | UG | Sus | 46037093 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1886314 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1116 | 253491116 | FUSE | 53115 | 20231030 | 1636 | 20231030 | 1734 | 2256047 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 58 | 35.5842 | -119.1157 | No | Clear;32-90 F |  |  | 23-0134132 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886325 | 1 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 9369 | 20231031 | 911 | 20231031 | 1436 | 2256466 | 325 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3468 | 35.4415 | -118.945 | No | Clear;32-90 F |  |  | 23-0134314 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886602 | 1 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 3855 | 20231031 | 941 | 20231031 | 1345 | 2256518 | 244 | Distribution Circuit | 3rd Party | Vehicle | 90 | 8200 | 35.3116 | -118.8251 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0134261 | OH | Sus | 31674751 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1886531 | 0 | EPSS Ckt | Y | 2023 | B- C
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 622728 | 20231101 | 21 | 20231101 | 1048 | 2257005 | 627 | Distribution Circuit | 3rd Party | Metallic Balloon | 54 | 33858 | 35.0056 | -119.808 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0134482 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1886684 | 0 | EPSS Ckt | Y | 2023 | A & C
KERN | KERN | LERDO-1116 | 253491116 | OCB | 1116/2 | 20231102 | 745 | 20231103 | 1359 | 2258001 | 1814 | Distribution Circuit | 3rd Party | Vehicle | 147 | 29309 | 35.5004 | -119.1518 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0135011 | OH | Sus | 31675122 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1887041 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517285965828 | 20231102 | 1035 | 20231102 | 1054 | 2258181 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 19 | 35.3062 | -118.9108 | No | Clear;32-90 F | Fuse | Broken | 23-0135161 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887216 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | RECLOSER | 4678 | 20231102 | 1052 | 20231102 | 1131 | 2258313 | 39 | Distribution Circuit | 3rd Party | Vehicle | 1432 | 55848 | 35.277 | -119.0213 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0135158 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887218 | 0 | Non-EPSS | N | 2023 | C GRD
KERN | KERN | OLD RIVER-1102 | 252821102 | JUMPER | BURNED OPEN CENTER PHASE JPR | 20231102 | 1055 | 20231102 | 1554 | 2258311 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 8073 | 35.208 | -119.0216 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0135260 | OH | Sus | 46045817 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1887256 | 1 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1106 | 254501106 | OCB | 1106/2 | 20231102 | 2205 | 20231103 | 1151 | 2258706 | 826 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1720 | 229018 | 35.6081 | -119.3254 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0135413 | OH | Sus | 31675139 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1887320 | 0 | Non-EPSS | N | 2023 | B GRD TIME
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | JUMPER | OJ 2SP E/OF 1609 | 20231103 | 538 | 20231103 | 754 | 2258759 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 204 | 17770 | 35.0955 | -118.98 | No | Clear;32-90 F | Jumper | Burned Open | 23-0127329 | OH | Sus | 31544661 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1887340 | 1 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1102 | 252461102 | TRANSFORMER | 516525377006 | 20231103 | 810 | 20231103 | 957 | 2258837 | 107 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 107 | 35.6101 | -119.1697 | No | Partly Cloudy;32-90 F |  |  | 23-0135552 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1887519 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1102 | 252931102 | FUSE | 16727 | 20231103 | 822 | 20231103 | 1119 | 2258815 | 177 | Distribution Circuit | 3rd Party | Vandalism | 1 | 177 | 35.0077 | -118.9502 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0135473 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1887365 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TAFT-1103 | 252081103 | FUSE | 15429 | 20231104 | 1008 | 20231104 | 1327 | 2259913 | 199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 9828 | 35.1554 | -119.457 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0135885 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887769 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | RECLOSER | 4409 | 20231104 | 2115 | 20231104 | 2121 | 2260260 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 116 | 696 | 35.2807 | -118.8786 | No | Clear;32-90 F |  |  | 23-0135947 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1887820 | 0 | EPSS Ckt | N | 2023 | B C
KERN | KERN | SHAFTER-1102 | 253651102 | TRANSFORMER | 516197474476 | 20231105 | 327 | 20231105 | 801 | 2260293 | 274 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 274 | 35.5397 | -119.278 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0135978 | OH | Sus | 46047960 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887858 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 14753 | 20231105 | 804 | 20231105 | 939 | 2260385 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 317 | 35.016 | -118.922 | No | Partly Cloudy;32-90 F |  |  | 23-0135994 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887892 | 1 | EPSS Ckt | N | 2023
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRANSFORMER | 513762268835 | 20231105 | 1055 | 20231105 | 1524 | 2260454 | 269 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 538 | 35.3735 | -120.0931 | No | Clear;32-90 F | Transformer | Normal | 23-0136014 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887913 | 0 | EPSS Ckt | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 17676 | 20231106 | 605 | 20231106 | 743 | 2261019 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 4018 | 35.3176 | -119.0046 | No | Clear;32-90 F |  |  | 23-0136128 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1888016 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 14152 | 20231106 | 1137 | 20231106 | 1338 | 2261644 | 121 | Distribution Circuit | Animal | Other | 2 | 242 | 35.3326 | -119.2528 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0136340 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1888231 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 14799 | 20231106 | 1150 | 20231106 | 1656 | 2261659 | 306 | Distribution Circuit | 3rd Party | Vehicle | 9 | 2754 | 35.2596 | -119.0026 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0136302 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | Yes | No | 1888216 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 100000024400 | 20231106 | 1433 | 20231106 | 1615 | 2261815 | 102 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 102 | 35.1515 | -119.0216 | No | Clear;32-90 F |  |  | 23-0136426 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1888254 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1103 | 253411103 | FUSE | 9062 | 20231106 | 1648 | 20231106 | 1825 | 2261923 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 485 | 35.0307 | -119.1357 | No | Clear;32-90 F |  |  | 23-0136457 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1888267 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517285966540 | 20231107 | 628 | 20231107 | 1442 | 2262269 | 494 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 1482 | 35.325 | -118.9112 | No | Clear;32-90 F | Transformer | Normal | 23-0136632 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888503 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13484 | 20231107 | 654 | 20231107 | 756 | 2262277 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 2542 | 35.3648 | -118.9765 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0136581 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888368 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | OCB | 1107/2 | 20231107 | 953 | 20231108 | 210 | 2262739 | 977 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1139 | 42557 | 35.2971 | -118.8618 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0136649 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | No | No | 1888523 | 0 | Non-EPSS | N | 2023 | ABCG INST
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517082568536 | 20231107 | 1007 | 20231107 | 1233 | 2262763 | 146 | Transformer only | Company Initiated | Personnel- company | 17 | 2482 | 35.3797 | -118.9791 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0136702 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888550 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1108 | 252771108 | FUSE | 9592 | 20231107 | 1120 | 20231107 | 1316 | 2262825 | 116 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 32 | 3712 | 35.337 | -118.9142 | No | Clear;32-90 F |  |  | 23-0136761 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888594 | 0 | EPSS Ckt | N | 2023
KERN | KERN | MAGUNDEN-1108 | 252771108 | FUSE | 15063 | 20231107 | 1144 | 20231107 | 1254 | 2262868 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 2335 | 35.3507 | -118.9133 | No | Partly Cloudy;32-90 F |  |  | 23-0136743 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888580 | 1 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | 517558066302 | 20231107 | 1645 | 20231107 | 1746 | 2263126 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 61 | 35.3192 | -118.8182 | No | Partly Cloudy;32-90 F |  |  | 23-0136873 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1888644 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ELK HILLS-1104 | 252441104 | RECLOSER | 4306 | 20231108 | 101 | 20231108 | 1802 | 2263269 | 1021 | Distribution Circuit | 3rd Party | Vehicle | 474 | 165922 | 35.2282 | -119.3774 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0136912 | OH | Sus | 31675477 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1888687 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | STOCKDALE-2115 | 254072115 | FUSE | 10800 | 20231108 | 244 | 20231108 | 1529 | 2263290 | 536 | Distribution Circuit | Equipment Failure/Involved | Underground | 41 | 18772 | 35.3357 | -119.0915 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0136915 | UG | Sus | 35510353 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888693 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 16359 | 20231108 | 829 | 20231108 | 1234 | 2263430 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 490 | 35.4422 | -119.5107 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0137003 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888859 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516550361584 | 20231108 | 934 | 20231108 | 1039 | 2263742 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 65 | 35.1871 | -119.1553 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0137051 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888897 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 516998354202 | 20231108 | 1139 | 20231108 | 1916 | 2264152 | 457 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 457 | 34.9869 | -119.0023 | No | Clear;32-90 F |  |  | 23-0137114 | OH | Sus | 46051079 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1888937 | 0 | EPSS Ckt | N | 2023
KERN | KERN | COLUMBUS-1104 | 253951104 | TRIP-SAVER | 8058 | 20231108 | 2045 | 20231108 | 2151 | 2264628 | 66 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 6006 | 35.3866 | -118.968 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0137275 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1889017 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 14586 | 20231109 | 807 | 20231109 | 1215 | 2264826 | 248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 248 | 35.5245 | -119.5672 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0137375 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889097 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517008868665 | 20231109 | 1130 | 20231109 | 1835 | 2265025 | 425 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 425 | 35.3828 | -119.0039 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0137506 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889279 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7119 | 20231109 | 1315 | 20231110 | 1022 | 2266210 | 1267 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 6335 | 35.5719 | -119.5985 | No | Clear;32-90 F |  |  | 23-0137867 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1889581 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-1101 | 252771101 | OCB | 1101/2 | 20231109 | 1845 | 20231109 | 2026 | 2265495 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3590 | 306546 | 35.3618 | -118.924 | No | Partly Cloudy;32-90 F |  |  | 23-0137651 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1889345 | 0 | Non-EPSS | N | 2023 | AC PH OC INST
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516666468686 | 20231110 | 1550 | 20231110 | 1619 | 2266414 | 29 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 319 | 35.382 | -119.1191 | No | Clear;32-90 F |  |  | 23-0137997 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889640 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1103 | 252971103 | FUSE | 15961 | 20231110 | 2331 | 20231111 | 323 | 2266529 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 7192 | 35.2054 | -118.8305 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0138031 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1889671 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | OCB | 2104/2 | 20231111 | 851 | 20231111 | 1846 | 2266648 | 595 | Distribution Circuit | 3rd Party | Other | 3818 | 333528 | 35.3194 | -119.1291 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0138057 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1889714 | 0 | Non-EPSS | N | 2023 | C & GRD TIME OC
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 12541 | 20231111 | 2157 | 20231112 | 509 | 2266951 | 432 | Distribution Circuit | 3rd Party | Vehicle | 82 | 12522 | 35.3485 | -118.9495 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0138158 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889816 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | OCB | 1106/2 | 20231112 | 1022 | 20231112 | 1155 | 2267110 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 9832 | 35.3531 | -119.2709 | No | Clear;32-90 F |  |  | 23-0138191 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1889865 | 0 | Non-EPSS | N | 2023 | B- C- INST
KERN | KERN | COLUMBUS-1106 | 253951106 | FUSE | 8665 | 20231112 | 1527 | 20231112 | 1615 | 2267271 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 864 | 35.3977 | -118.9408 | No | Clear;32-90 F | Fuse | Burned Open | 23-0138220 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1889893 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20231113 | 930 | 20231113 | 959 | 2267706 | 29 | Distribution Circuit | Company Initiated | Personnel- company | 51 | 1479 | 35.5605 | -118.9587 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0138358 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1890117 | 0 | EPSS Ckt | Y | 2023 | A- C- GRD
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 88627 | 20231113 | 934 | 20231113 | 1655 | 2267757 | 441 | Distribution Circuit | 3rd Party | Vehicle | 339 | 11257 | 35.4422 | -119.4595 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0138380 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890136 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1101 | 253701101 | RECLOSER | 4897 | 20231113 | 1137 | 20231113 | 1250 | 2267835 | 73 | Distribution Circuit | 3rd Party | Metallic Balloon | 1729 | 120259 | 35.3613 | -119.0308 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0138424 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890163 | 0 | Non-EPSS | N | 2023 | A B GRD
KERN | KERN | RENFRO-2102 | 254572102 | FUSE | 19898 | 20231113 | 1551 | 20231113 | 1650 | s1890228 | 59 | Distribution Circuit | Animal | Other | 4 | 236 | 35.3875 | -119.1545 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0138565 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890228 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 14684 | 20231113 | 1616 | 20231113 | 1802 | 2268101 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1272 | 35.2091 | -119.249 | No | Clear;32-90 F |  |  | 23-0138581 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890240 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 9866 | 20231113 | 1733 | 20231114 | 900 | 2268137 | 927 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 5269 | 35.208 | -119.0216 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 23-0138584 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890242 | 1 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 14684 | 20231114 | 347 | 20231114 | 642 | 2268538 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1401 | 35.2091 | -119.249 | No | Clear;32-90 F |  |  | 23-0138637 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890283 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1103 | 253411103 | FUSE | 9062 | 20231114 | 1323 | 20231114 | 1640 | 2269124 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 985 | 35.0307 | -119.1357 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0138916 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890515 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WESTPARK-1102 | 253701102 | TRANSFORMER | 516948068352 | 20231114 | 1828 | 20231114 | 1905 | 2269275 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 111 | 35.3739 | -119.0246 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0139046 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890542 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | OCB | 1106/2 | 20231115 | 641 | 20231115 | 812 | 2269425 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 13099 | 35.3531 | -119.2709 | No | Clear;32-90 F |  |  | 23-0139106 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1890586 | 0 | Non-EPSS | N | 2023 | A B C INST
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 8613 | 20231115 | 647 | 20231115 | 940 | 2269433 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 346 | 35.1868 | -119.0745 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0139205 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890739 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | RECLOSER | 4164 | 20231115 | 828 | 20231116 | 206 | 2269515 | 1058 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 5602 | 35.0595 | -118.978 | No | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0139157 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1890638 | 0 | EPSS Ckt | N | 2023 | ABC
KERN | KERN | LAKEVIEW-1103 | 253411103 | FUSE | 9062 | 20231115 | 952 | 20231115 | 1213 | 2269691 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 705 | 35.0307 | -119.1357 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0139210 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890741 | 0 | EPSS Ckt | N | 2023
KERN | KERN | COLUMBUS-1110 | 253951110 | TRANSFORMER | 517167468732 | 20231115 | 1102 | 20231115 | 1729 | 2269732 | 387 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 1161 | 35.385 | -118.9509 | No | Partly Cloudy;32-90 F | Transformer | Together | 23-0139312 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890795 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1110 | 253951110 | TRANSFORMER | 517169068732 | 20231115 | 1102 | 20231115 | 1728 | 2269784 | 386 | Transformer only | Vegetation | Tree - bark fell into line | 4 | 1544 | 35.385 | -118.9504 | No | Partly Cloudy;32-90 F | Transformer | Together | 23-0139333 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890807 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 91893 | 20231115 | 1152 | 20231115 | 1306 | 2269824 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1332 | 35.3628 | -118.95 | No | Overcast-Rain;32-90 F |  |  | 23-0139363 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890816 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 15690 | 20231115 | 1220 | 20231115 | 1550 | 2269857 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2520 | 35.2079 | -119.0746 | No | Clear;32-90 F |  |  | 23-0139559 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890872 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1104 | 253951104 | FUSE | 8118 | 20231115 | 1251 | 20231115 | 1816 | 2269899 | 325 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 23075 | 35.3828 | -118.956 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0139619 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890898 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1109 | 253701109 | FUSE | 17796 | 20231115 | 1300 | 20231115 | 1521 | 2269936 | 141 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 5358 | 35.4131 | -119.0334 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0139451 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890844 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516601068850 | 20231115 | 1320 | 20231115 | 1732 | 2269876 | 252 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 504 | 35.3864 | -119.1415 | No | Strong Winds-Rain-Overcast;32-90 F | Transformer | Broken- wire on ground | 23-0139409 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1890833 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2115 | 254072115 | RECLOSER | 2858 | 20231115 | 1321 | 20231115 | 1412 | 2269958 | 51 | Distribution Circuit | Vegetation | Tree - fell into line | 581 | 29631 | 35.2981 | -119.0919 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0139379 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890821 | 0 | Non-EPSS | N | 2023 | A & B
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517041469114 | 20231115 | 1344 | 20231115 | 2328 | 2269992 | 584 | Transformer only | Vegetation | Tree - fell into line | 12 | 7008 | 35.395 | -118.993 | No | Strong Winds-Rain-Overcast;32-90 F | Transformer | Broken | 23-0139570 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890877 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1102 | 253191102 | OCB | 1102/2 | 20231115 | 1406 | 20231115 | 1822 | 2270026 | 256 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 11008 | 35.0921 | -118.8779 | No | Overcast-Strong Winds;32-90 F |  |  | 23-0139439 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1890843 | 0 | Non-EPSS | N | 2023 | A B & C
KERN | KERN | ARVIN-1103 | 253801103 | OCB | 1103/2 | 20231115 | 1533 | 20231116 | 324 | 2270074 | 711 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 30348 | 35.1499 | -118.8788 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0139528 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | Yes | No | 1890861 | 0 | Non-EPSS | N | 2023 | PH OC TIME PHA & GRD OC TIME
KERN | KERN | STOCKDALE-2113 | 254072113 | RECLOSER | 4765 | 20231115 | 1540 | 20231116 | 720 | 2270088 | 940 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3747 | 659072 | 35.3175 | -119.034 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0139542 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1890867 | 0 | Non-EPSS | N | 2023 | ABC
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 18177 | 20231115 | 1542 | 20231115 | 1610 | 2270085 | 28 | Distribution Circuit | 3rd Party | Kite | 143 | 4004 | 35.4051 | -119.0311 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0139573 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890878 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 822793 | 20231115 | 1549 | 20231115 | 1948 | 2270127 | 239 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2149 | 35.2413 | -119.0214 | No | Clear;32-90 F |  |  | 23-0139649 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890917 | 1 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 37032 | 20231115 | 1606 | 20231115 | 1853 | 2270137 | 167 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 3899 | 35.2524 | -118.9664 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0139635 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890909 | 1 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516967766489 | 20231115 | 1722 | 20231115 | 1755 | 2270271 | 33 | Transformer only | Vegetation | Tree - grew into line | 4 | 132 | 35.3227 | -119.0174 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0139616 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890897 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | 517278464432 | 20231115 | 1736 | 20231115 | 1941 | 2270348 | 125 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 1375 | 35.2667 | -118.9128 | No | Clear;32-90 F |  |  | 23-0139654 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1890920 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 516852064468 | 20231115 | 1738 | 20231115 | 2317 | 2270112 | 339 | Transformer only | Vegetation | Tree - fell into line | 2 | 678 | 35.2669 | -119.0551 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0139608 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890891 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1110 | 254071110 | FUSE | 16978 | 20231115 | 1836 | 20231115 | 1941 | 2270406 | 65 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 6305 | 35.3251 | -119.0295 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0139620 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890899 | 0 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 13064 | 20231115 | 1945 | 20231116 | 115 | 2270186 | 330 | Distribution Circuit | 3rd Party | Other | 49 | 16170 | 35.3045 | -118.9941 | No | Overcast;32-90 F | Secondary | Broken- wire on ground | 23-0139641 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890912 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516938869497 | 20231115 | 2049 | 20231115 | 2341 | 2269948 | 172 | Transformer only | Vegetation | Tree - fell into line | 13 | 2236 | 35.405 | -119.0281 | No | Overcast-Rain-Strong Winds;32-90 F | Secondary | Normal | 23-0139534 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890862 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1101 | 253371101 | TRANSFORMER | 517011469209 | 20231115 | 2054 | 20231116 | 621 | 2270464 | 567 | Transformer only | Equipment Failure/Involved | Underground | 1 | 567 | 35.3974 | -119.0032 | No | Overcast;32-90 F | Transformer | Deteriorated | 23-0139692 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890950 | 0 | Non-EPSS | N | 2023
KERN | KERN | RIO BRAVO-1101 | 252861101 | FUSE | 7572 | 20231115 | 2143 | 20231116 | 245 | 2270470 | 300 | Distribution Circuit | 3rd Party | Vehicle | 40 | 11720 | 35.4563 | -119.2622 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0139680 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890944 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516963266495 | 20231116 | 36 | 20231116 | 255 | 2270492 | 139 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 556 | 35.3227 | -119.0182 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0139738 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890964 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1106 | 253411106 | FUSE | 18579 | 20231116 | 146 | 20231116 | 1201 | 2270552 | 615 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 615 | 35.0949 | -119.0919 | No | Strong Winds | Other | Broken | 23-0139739 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890965 | 0 | EPSS Ckt | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 18555 | 20231116 | 420 | 20231116 | 915 | 2270562 | 295 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1180 | 35.1078 | -118.9839 | No | Partly Cloudy;32-90 F |  |  | 23-0139741 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890967 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1110 | 252721110 | OTHER | J1137 TWD T9879 | 20231116 | 1545 | 20231116 | 1810 | 2270994 | 145 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 10875 | 35.4321 | -119.0266 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0139962 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891100 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 87257 | 20231117 | 554 | 20231117 | 708 | 2271217 | 74 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 41 | 3034 | 35.3103 | -119.0247 | No | Clear;32-90 F | Fuse | Burned Open | 23-0140262 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891166 | 0 | Non-EPSS | N | 2023
KERN | KERN | MCKITTRICK-1101 | 252781101 | FUSE | 1686 | 20231117 | 1002 | 20231117 | 1355 | 2271478 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1554 | 35.3126 | -119.7144 | No | Clear;32-90 F |  |  | 23-0140579 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891384 | 1 | EPSS Ckt | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516872762485 | 20231117 | 1301 | 20231117 | 1403 | 2271612 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 62 | 35.2124 | -119.048 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0140586 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1891386 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 2771 | 20231117 | 1812 | 20231117 | 1822 | 2271872 | 10 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 459 | 4590 | 35.2234 | -119.1004 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0140696 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891420 | 0 | Non-EPSS | N | 2023 | NA
KERN | KERN | GOOSE LAKE-1103 | 254201103 | RECLOSER | 56686 | 20231117 | 1921 | 20231118 | 432 | 2271912 | 551 | Distribution Circuit | 3rd Party | Vehicle | 73 | 7033 | 35.5424 | -119.6191 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0140703 | OH | Sus | 35511968 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | Yes | No | 1891425 | 0 | Non-EPSS | N | 2023 | A- B- C- GRD
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 55239 | 20231117 | 2024 | 20231117 | 2030 | 2271928 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 42 | 35.3541 | -119.0029 | No | Overcast;32-90 F | Anchor or Guy | Bent or Twisted | 23-0140707 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891428 | 0 | Non-EPSS | N | 2023
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 7507 | 20231118 | 801 | 20231118 | 1115 | 2272251 | 194 | Distribution Circuit | Animal | Bird found | 3 | 582 | 35.7172 | -119.7615 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0140850 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891555 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 7409 | 20231118 | 813 | 20231118 | 1000 | 2272265 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 642 | 35.6594 | -119.5075 | No | Partly Cloudy;32-90 F |  |  | 23-0140824 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891535 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1110 | 252721110 | OTHER | J1137 TWD T9879 | 20231118 | 823 | 20231118 | 858 | 2272286 | 35 | Distribution Circuit | Company Initiated | Return Circuit Normal | 75 | 2625 | 35.4321 | -119.0266 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0140785 | UG | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1891511 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 55239 | 20231118 | 848 | 20231118 | 944 | 2272300 | 56 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 392 | 35.3541 | -119.0029 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0140707 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891518 | 0 | Non-EPSS | N | 2023
KERN | KERN | WASCO-1101 | 252961101 | FUSE | 1169 | 20231118 | 1637 | 20231118 | 1832 | 2272903 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1304 | 35.5753 | -119.3495 | No | Overcast;32-90 F |  |  | 23-0140947 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891622 | 1 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | JUMPER | 18299 #3 LD-SIDE JUMPER | 20231118 | 1802 | 20231118 | 2033 | 2273036 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 906 | 35.0766 | -118.9681 | No | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 23-0140978 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1891649 | 0 | EPSS Ckt | N | 2023
KERN | KERN | FELLOWS-2103 | 254242103 | OCB | 2103/2 | 20231118 | 2150 | 20231118 | 2223 | 2273337 | 33 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 190 | 6270 | 35.1948 | -119.5861 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0141025 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891696 | 0 | EPSS Ckt | N | 2023 | N/A
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7292 | 20231119 | 1613 | 20231119 | 1755 | 2273645 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1021 | 35.7609 | -119.5625 | No | Clear;32-90 F |  |  | 23-0141126 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891791 | 1 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516957769706 | 20231119 | 1707 | 20231119 | 1807 | 2273659 | 60 | Transformer only | 3rd Party | Metallic Balloon | 6 | 360 | 35.411 | -119.0216 | No | Partly Cloudy;32-90 F | Jumper | Burned/flashed | 23-0141130 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891794 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | RECLOSER | 4151 | 20231119 | 2258 | 20231120 | 155 | 2273755 | 177 | Distribution Circuit | Equipment Failure/Involved | Underground | 1367 | 64435 | 35.346 | -119.0737 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0141164 | UG | Sus | 31676767 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891824 | 0 | Non-EPSS | N | 2023 | A-GRD
KERN | KERN | MARICOPA-1101 | 254211101 | FUSE | 16489 | 20231120 | 818 | 20231120 | 1114 | 2274234 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 352 | 35.0676 | -119.367 | No | Clear;32-90 F |  |  | 23-0141320 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891959 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516961266835 | 20231120 | 1457 | 20231120 | 1649 | 2274334 | 112 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 224 | 35.3323 | -119.019 | No | Clear;32-90 F | Jumper | Broken | 23-0141491 | OH | Sus | 46063005 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891995 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 18635 | 20231121 | 939 | 20231121 | 1039 | 2274960 | 60 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1 | 60 | 35.4823 | -119.1795 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0141740 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892154 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1110 | 253701110 | TRANSFORMER | 516965567957 | 20231121 | 953 | 20231121 | 2340 | 2274980 | 827 | Transformer only | Animal | Bird found | 9 | 7443 | 35.3632 | -119.0182 | No | Clear;32-90 F | Jumper | Burned/flashed | 23-0141862 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892193 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1102 | 253181102 | FUSE | 15988 | 20231121 | 1414 | 20231122 | 105 | 2275223 | 651 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1953 | 35.6886 | -119.3484 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0141963 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1892209 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | T7118 | 20231122 | 50 | 20231122 | 110 | 2275447 | 20 | Transformer only | Equipment Failure/Involved | Underground | 16 | 320 | 35.3805 | -119.1398 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0142129 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892289 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515714881569 | 20231122 | 1104 | 20231122 | 1726 | 2275638 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 382 | 35.7323 | -119.4448 | No | Clear;32-90 F | Jumper | Broken | 23-0142318 | OH | Sus | 46063689 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892357 | 0 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1103 | 252461103 | TRANSFORMER | 516722376990 | 20231122 | 1351 | 20231122 | 1447 | 2275798 | 56 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 56 | 35.6106 | -119.1031 | No | Partly Cloudy;32-90 F |  |  | 23-0142413 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1892381 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 14149 | 20231122 | 2244 | 20231122 | 2253 | 2276000 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 7 | 63 | 35.3695 | -119.0031 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0135073 | OH | Sus | 45927731 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1892426 | 0 | Non-EPSS | N | 2023
KERN | KERN | CARNERAS-1102 | 252321102 | FUSE | 16619 | 20231123 | 646 | 20231123 | 908 | 2276038 | 142 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 710 | 35.5416 | -119.7789 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0142495 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892433 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE-2102 | 254762102 | FUSE | 11450 | 20231124 | 453 | 20231124 | 648 | 2276348 | 115 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 47 | 5405 | 35.3589 | -119.0613 | No | Clear;32-90 F |  |  | 23-0142593 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892527 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13417 | 20231124 | 1244 | 20231124 | 1333 | 2276596 | 49 | Distribution Circuit | Animal | Bird found | 10 | 490 | 35.3721 | -118.9991 | No | Clear;32-90 F | Fuse | Burned Open | 23-0142656 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892572 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-1105 | 254071105 | TRANSFORMER | T5427 | 20231125 | 840 | 20231126 | 440 | 2276910 | 1200 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 17046 | 35.3008 | -119.0395 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0142752 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892656 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517318066811 | 20231125 | 1203 | 20231125 | 1453 | 2277018 | 170 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 850 | 35.3326 | -118.9004 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0142809 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892680 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2103 | 255262103 | TRANSFORMER | T8971 | 20231125 | 1636 | 20231125 | 1756 | 2277017 | 80 | Transformer only | Equipment Failure/Involved | Underground | 21 | 1680 | 35.3908 | -119.0991 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0142847 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892695 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517079167895 | 20231125 | 2322 | 20231125 | 2342 | 2277216 | 20 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 220 | 35.3617 | -118.9805 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0142869 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892714 | 0 | Non-EPSS | N | 2023
KERN | KERN | WEEDPATCH-1106 | 252971106 | RECLOSER | 205044 | 20231126 | 242 | 20231126 | 1039 | 2277235 | 477 | Distribution Circuit | 3rd Party | Vehicle | 18 | 8586 | 35.2221 | -118.9323 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0142875 | OH | Sus | 31677160 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1892720 | 0 | Non-EPSS | N | 2023 | A B C
KERN | KERN | KERN OIL-1103 | 252721103 | TRANSFORMER | 516960070499 | 20231126 | 1033 | 20231126 | 1846 | 2277427 | 493 | Transformer only | Equipment Failure/Involved | Overhead | 34 | 16762 | 35.4328 | -119.0207 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142941 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892773 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1103 | 253651103 | RECLOSER | 1197 | 20231126 | 1543 | 20231127 | 153 | 2277489 | 610 | Distribution Circuit | 3rd Party | Vehicle | 73 | 18087 | 35.5291 | -119.2963 | No | Overcast;32-90 F | Capacitor | Broken- wire on ground | 23-0142940 | OH | Sus | 31677243 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1892771 | 0 | Non-EPSS | N | 2023 | C PHASE & GRD
KERN | KERN | WASCO-1101 | 252961101 | SWITCH | 1301 | 20231127 | 205 | 20231127 | 212 | 2277598 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 7 | 35.5581 | -119.331 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0142940 | OH | Sus | 31677243 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1892806 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 17676 | 20231127 | 626 | 20231127 | 727 | 2277649 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 2501 | 35.3176 | -119.0046 | No | Clear;32-90 F |  |  | 23-0142991 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892825 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2103 | 255262103 | FUSE | 13270 | 20231127 | 701 | 20231127 | 1015 | 2277660 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 194 | 35.3916 | -119.0834 | No | Clear;32-90 F |  |  | 23-0143061 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892991 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15044 | 20231128 | 207 | 20231128 | 323 | 2278525 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1368 | 35.3472 | -118.9138 | No | Clear;32-90 F |  |  | 23-0143317 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1893130 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | OTHER | WIRE DOWN 4 N/OF 18855 | 20231128 | 423 | 20231128 | 1120 | 2278540 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 7089 | 35.1372 | -119.1635 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0143329 | OH | Sus | 46069710 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893144 | 1 | Non-EPSS | N | 2023
KERN | KERN | KERN POWER-2103 | 255262103 | FUSE | 13270 | 20231128 | 912 | 20231128 | 1145 | 2278669 | 153 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 153 | 35.3916 | -119.0834 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0143364 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893201 | 0 | Non-EPSS | N | 2023
KERN | KERN | 7TH STANDARD-2101 | 254582101 | OTHER | T505505 TWD T106990 | 20231128 | 937 | 20231128 | 1040 | 2278866 | 63 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 378 | 35.4519 | -119.1082 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0143316 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893321 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 516955058820 | 20231128 | 1239 | 20231128 | 1445 | 2279019 | 126 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 126 | 35.1123 | -119.0189 | No | Clear;32-90 F |  |  | 23-0143551 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1893384 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13484 | 20231128 | 1530 | 20231128 | 1605 | 2279134 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 1435 | 35.3648 | -118.9765 | No | Clear;32-90 F |  |  | 23-0143586 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893390 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 7100 | 20231128 | 1639 | 20231129 | 149 | 2279264 | 550 | Distribution Circuit | 3rd Party | Vehicle | 13 | 7150 | 35.4915 | -119.206 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0143622 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893411 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1102 | 254501102 | OTHER | 7521 | 20231129 | 717 | 20231129 | 1244 | 2279410 | 327 | Distribution Circuit | 3rd Party | Customer Equipment | 17 | 5559 | 35.6524 | -119.3338 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0143750 | OH | Sus | 31677176 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893626 | 1 | Non-EPSS | N | 2023
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516624277848 | 20231129 | 1601 | 20231129 | 1706 | 2280156 | 65 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 65 | 35.6337 | -119.1372 | No | Clear;32-90 F |  |  | 23-0144000 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1893761 | 0 | Non-EPSS | N | 2023
KERN | KERN | FELLOWS-2104 | 254242104 | OCB | 2104/2 | 20231130 | 36 | 20231130 | 530 | 2280323 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 130 | 31508 | 35.1948 | -119.5861 | No | Partly Cloudy;32-90 F |  |  | 23-0144073 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1893805 | 0 | EPSS Ckt | N | 2023 | 51(TIME) SET A TGT
KERN | KERN | ROSEDALE-1101 | 254761101 | JUMPER | FB N/OF 968435 | 20231130 | 828 | 20231130 | 1040 | 2280484 | 132 | Distribution Circuit | 3rd Party | Vehicle | 4 | 528 | 35.4007 | -119.0743 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0144078 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893878 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 14694 | 20231130 | 1001 | 20231130 | 1226 | 2280842 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1160 | 35.5578 | -119.4564 | No | Clear;32-90 F |  |  | 23-0144291 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1894048 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 16998 | 20231201 | 1356 | 20231201 | 1735 | 2281622 | 219 | Distribution Circuit | Equipment Failure/Involved | Underground | 37 | 8103 | 35.2425 | -118.9146 | No | Clear;32-90 F | Transformer (UG) | Contaminated | 23-0144763 | UG | Sus | 46077484 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1894400 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 713123 | 20231203 | 1641 | 20231203 | 1903 | s1894699 | 142 | Distribution Circuit | Animal | Bird found | 7 | 994 | 35.3545 | -119.1975 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0145054 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1894699 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517057168376 | 20231204 | 110 | 20231204 | 211 | 2282932 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 854 | 35.3751 | -118.9876 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0145083 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1894726 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | OCB | 2104/2 | 20231204 | 645 | 20231204 | 730 | 2283088 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 612 | 27540 | 35.3885 | -119.0046 | No | Partly Cloudy;32-90 F |  |  | 23-0145090 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1894744 | 0 | Non-EPSS | N | 2023 | A- B- C
KERN | KERN | BAKERSFIELD-2104 | 253372104 | JUMPER | FBS 2P N/E OF DELAWARE AND MARIPOSA | 20231204 | 1154 | 20231204 | 1346 | 2283503 | 112 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 31 | 3472 | 35.3442 | -119.0042 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 23-0145216 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1894975 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | SWITCH | 10548 | 20231204 | 1155 | 20231204 | 1205 | 2283514 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 12 | 120 | 35.3597 | -119.066 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0128690 | UG | Sus | 44377188 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1894982 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2102 | 253142102 | FUSE | 18660 | 20231205 | 801 | 20231205 | 1057 | 2284022 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2288 | 34.9398 | -119.5933 | No | Clear;32-90 F |  |  | 23-0145513 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1895315 | 0 | EPSS Ckt | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | FUSE | 13996 | 20231205 | 853 | 20231205 | 1030 | 2284119 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 8924 | 35.4078 | -119.026 | No | Clear;32-90 F |  |  | 23-0145504 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895289 | 0 | Non-EPSS | N | 2023
KERN | KERN | SHAFTER-1104 | 253651104 | RECLOSER | 1419 | 20231205 | 953 | 20231206 | 33 | 2284245 | 880 | Distribution Circuit | Equipment Failure/Involved | Underground | 1089 | 279855 | 35.5071 | -119.3117 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0145495 | UG | Sus | 46079263 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895279 | 0 | Non-EPSS | N | 2023 | C-GRD
KERN | KERN | COLUMBUS-1106 | 253951106 | FUSE | 8226 | 20231205 | 1611 | 20231206 | 545 | 2284612 | 814 | Distribution Circuit | 3rd Party | Vandalism | 1 | 814 | 35.3961 | -118.9696 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 23-0145665 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1895377 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1108 | 253701108 | FUSE | 8131 | 20231205 | 1727 | 20231206 | 657 | 2284653 | 810 | Distribution Circuit | 3rd Party | Vandalism | 1 | 810 | 35.3518 | -119.017 | No | Clear;32-90 F | Secondary | Broken | 23-0145679 | UG | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1895388 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517256066073 | 20231206 | 824 | 20231206 | 959 | 2284871 | 95 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 570 | 35.3129 | -118.921 | No | Clear;32-90 F | Fuse | Broken | 23-0145828 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895579 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516844560730 | 20231206 | 1042 | 20231206 | 1325 | 2285120 | 163 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 163 | 35.1612 | -119.0567 | No | Clear;32-90 F |  |  | 23-0145928 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1895655 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 4113 | 20231206 | 1639 | 20231206 | 1948 | 2285411 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 6426 | 35.312 | -118.843 | No | Clear;32-90 F |  |  | 23-0146003 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1895683 | 0 | EPSS Ckt | Y | 2023 | AB
KERN | KERN | KERN OIL-1103 | 252721103 | TRANSFORMER | 516969770493 | 20231206 | 2033 | 20231207 | 149 | 2285574 | 316 | Transformer only | Vegetation | Tree - grew into line | 6 | 1896 | 35.4327 | -119.0174 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0146046 | OH | Sus | 46080123 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895713 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1107 | 252721107 | TRANSFORMER | T14955 | 20231207 | 735 | 20231207 | 1056 | 2285793 | 201 | Transformer only | Equipment Failure/Involved | Underground | 1 | 201 | 35.4399 | -119.0776 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0146089 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895758 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | T0084 | 20231207 | 941 | 20231207 | 1045 | 2286013 | 64 | Transformer only | Equipment Failure/Involved | Underground | 26 | 1664 | 35.3628 | -118.943 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0146129 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1895889 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | JUMPER | OJS 1 W/OF MTR# 1004075684 | 20231207 | 1007 | 20231207 | 1616 | 2286060 | 369 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2214 | 35.3862 | -119.1943 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0146144 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1895905 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | RECLOSER | 573054 | 20231207 | 1202 | 20231207 | 1248 | 2286215 | 45 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 1325 | 35.5736 | -119.6899 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0146210 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1895956 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 13027 | 20231207 | 1341 | 20231207 | 2225 | 2286291 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 524 | 35.2676 | -118.8517 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0146307 | OH | Sus | 46082146 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896009 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 8837 | 20231208 | 716 | 20231208 | 1259 | 2286657 | 343 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2744 | 35.2589 | -119.1283 | No | Clear;32-90 F |  |  | 23-0146430 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896200 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | TRANSFORMER | 515468550048 | 20231208 | 733 | 20231208 | 1838 | 2286978 | 665 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1007 | 34.8694 | -119.5121 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0146467 | OH | Sus | 31678538 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896236 | 0 | EPSS Ckt | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 901387 | 20231208 | 936 | 20231208 | 1132 | 2286923 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 928 | 35.229 | -119.0029 | No | Clear;32-90 F |  |  | 23-0146504 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896260 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 967375 | 20231208 | 1118 | 20231208 | 1322 | 2287020 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1364 | 35.1018 | -119.0391 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0146484 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1896246 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 16961 | 20231208 | 1236 | 20231208 | 1547 | 2287129 | 191 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 573 | 35.2962 | -118.9217 | No | Clear;32-90 F |  |  | 23-0146572 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896298 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | OCB | 1101/2 | 20231209 | 1612 | 20231210 | 334 | 2288061 | 682 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 16349 | 35.7178 | -119.4554 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0146671 | OH | Sus | 46083327 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1896508 | 0 | Non-EPSS | N | 2023 | B GRD TIME 51
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 4113 | 20231209 | 1635 | 20231209 | 1855 | 2288071 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 4760 | 35.312 | -118.843 | No | Clear;32-90 F |  |  | 23-0146673 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896509 | 0 | EPSS Ckt | Y | 2023 | AB
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 210155 | 20231209 | 1737 | 20231209 | 2230 | 2288100 | 293 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 4 | 971 | 35.6742 | -119.5264 | No | Partly Cloudy;32-90 F | Transformer (UG) | Burned/flashed | 23-0146690 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896527 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | RECLOSER | 92790 | 20231210 | 537 | 20231210 | 703 | 2288226 | 86 | Distribution Circuit | 3rd Party | Vehicle | 1619 | 139234 | 35.3531 | -118.9851 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0146723 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896561 | 0 | Non-EPSS | N | 2023 | B & C
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515845368594 | 20231210 | 900 | 20231210 | 955 | 2288284 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 55 | 35.3767 | -119.3946 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0146735 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1896579 | 0 | Non-EPSS | N | 2023
KERN | KERN | MAGUNDEN-2108 | 252772108 | JUMPER | OJ 2 E/OF L738 | 20231210 | 1047 | 20231210 | 1345 | 2288336 | 178 | Distribution Circuit | 3rd Party | Vehicle | 2 | 356 | 35.3395 | -118.9876 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0146745 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1896604 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516758562317 | 20231210 | 1637 | 20231210 | 1845 | 2288491 | 128 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 384 | 35.2078 | -119.0857 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0146768 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896626 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516756562315 | 20231210 | 1637 | 20231210 | 1845 | 2288463 | 128 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 128 | 35.2078 | -119.0864 | No | Clear;32-90 F |  |  | 23-0146769 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1896627 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 4113 | 20231210 | 1647 | 20231210 | 1748 | 2288467 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 2074 | 35.312 | -118.843 | No | Partly Cloudy;32-90 F |  |  | 23-0146763 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896619 | 0 | EPSS Ckt | Y | 2023 | A B
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517395265987 | 20231211 | 844 | 20231211 | 1117 | 2288702 | 153 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 153 | 35.3098 | -118.874 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0146870 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896870 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20231211 | 1056 | 20231211 | 1601 | 2289197 | 305 | Distribution Circuit | 3rd Party | Metallic Balloon | 25 | 7119 | 35.5593 | -118.9575 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0146864 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896864 | 0 | EPSS Ckt | Y | 2023 | PH OC INST
KERN | KERN | CHARCA-1102 | 254501102 | FUSE | 7521 | 20231212 | 921 | 20231212 | 1237 | 2289879 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3332 | 35.6524 | -119.3338 | No | Clear;32-90 F |  |  | 23-0147072 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1897203 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1112 | 253491112 | FUSE | 18640 | 20231212 | 935 | 20231212 | 1325 | 2289910 | 230 | Distribution Circuit | Animal | Bird found | 2 | 460 | 35.4993 | -119.0998 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0147087 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1897213 | 0 | Non-EPSS | N | 2023
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | 516475169086 | 20231212 | 1018 | 20231212 | 1048 | 2289792 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 30 | 35.3924 | -119.1833 | No | Clear;32-90 F | Fuse | Broken | 23-0147048 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897168 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1106 | 252901106 | FUSE | 15174 | 20231212 | 1505 | 20231212 | 2015 | 2290158 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 620 | 35.5507 | -119.421 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0147098 | OH | Sus | 31678967 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1897222 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | TRANSFORMER | 516433578294 | 20231212 | 1539 | 20231212 | 1948 | 2290182 | 249 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 498 | 35.6455 | -119.2007 | No | Clear;32-90 F |  |  | 23-0147132 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1897246 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7292 | 20231213 | 701 | 20231213 | 1012 | 2290892 | 191 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2674 | 35.7609 | -119.5625 | No | Clear;32-90 F |  |  | 23-0147229 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1897499 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1103 | 254561103 | SWITCH | 110703 | 20231213 | 1114 | 20231213 | 1502 | 2290910 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 228 | 35.3723 | -119.2253 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0147232 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1897509 | 0 | Non-EPSS | N | 2023
KERN | KERN | CHARCA-1106 | 254501106 | TRANSFORMER | 516041775447 | 20231213 | 1418 | 20231213 | 1916 | 2291138 | 298 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 596 | 35.5656 | -119.3325 | No | Clear;32-90 F |  |  | 23-0147284 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1897566 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2104 | 255322104 | OTHER | J1264 TWD T10337 | 20231214 | 826 | 20231214 | 1049 | 2291575 | 143 | Distribution Circuit | Equipment Failure/Involved | Underground | 48 | 6864 | 35.3468 | -119.1322 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0147330 | UG | Sus | 35517345 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1897693 | 0 | Non-EPSS | N | 2023
KERN | KERN | TAFT-1106 | 252081106 | TRANSFORMER | 515698560525 | 20231214 | 1948 | 20231214 | 2002 | 2292101 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 28 | 35.1547 | -119.4392 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0147495 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897922 | 0 | Non-EPSS | N | 2023
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 100000124748 | 20231214 | 2000 | 20231215 | 152 | 2292144 | 352 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 352 | 35.115 | -119.0043 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0147497 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1897925 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20231215 | 1018 | 20231215 | 1728 | 2292498 | 430 | Distribution Circuit | 3rd Party | Other | 25 | 10165 | 35.5593 | -118.9575 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0147560 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898151 | 0 | EPSS Ckt | Y | 2023 | SET A INST OC
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 9868 | 20231216 | 137 | 20231216 | 455 | 2292937 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 924 | 35.2377 | -118.995 | No | Clear;32-90 F |  |  | 23-0147628 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898254 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | 517167264454 | 20231216 | 709 | 20231216 | 1249 | 2292976 | 340 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 680 | 35.2675 | -118.9499 | No | Clear;32-90 F | Secondary | Together | 23-0147637 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898301 | 0 | EPSS Ckt | N | 2023
KERN | KERN | ELK HILLS-1104 | 252441104 | FUSE | 7335 | 20231217 | 23 | 20231217 | 215 | 2293425 | 112 | Distribution Circuit | 3rd Party | Vandalism | 474 | 50043 | 35.2078 | -119.4081 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0147715 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1898441 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 13231 | 20231217 | 702 | 20231217 | 948 | 2293468 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2822 | 35.354 | -118.9925 | No | Clear;32-90 F |  |  | 23-0147742 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898491 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | RECLOSER | 3459 | 20231217 | 742 | 20231217 | 2149 | 2293480 | 847 | Distribution Circuit | 3rd Party | Vehicle | 894 | 488718 | 35.3755 | -118.9941 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0147733 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1898461 | 0 | Non-EPSS | N | 2023 | AB TIME OC
KERN | KERN | WEEDPATCH-1101 | 252971101 | TRANSFORMER | 517514562469 | 20231217 | 1338 | 20231217 | 1438 | 2293595 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 300 | 35.2142 | -118.8327 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0147755 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898504 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1103 | 254561103 | FUSE | 13287 | 20231217 | 1416 | 20231217 | 1525 | 2293735 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 690 | 35.368 | -119.2343 | No | Clear;32-90 F |  |  | 23-0147770 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898519 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 7409 | 20231217 | 1432 | 20231217 | 1608 | 2293741 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 384 | 35.6594 | -119.5075 | No | Partly Cloudy;32-90 F |  |  | 23-0147769 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898517 | 1 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20231217 | 1528 | 20231217 | 1715 | 2293786 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 785 | 35.4767 | -119.5887 | No | Clear;32-90 F |  |  | 23-0147778 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898529 | 1 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | FUSE | 9942 | 20231217 | 1811 | 20231217 | 2021 | 2293901 | 130 | Distribution Circuit | Company Initiated | Improper Construction | 21 | 2709 | 35.5547 | -118.9017 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0147789 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1898540 | 0 | EPSS Ckt | N | 2023
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OCB | 2104/2 | 20231217 | 2108 | 20231218 | 24 | 2293939 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 720 | 73440 | 35.6018 | -119.5799 | No | Overcast;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0147809 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898567 | 0 | Non-EPSS | N | 2023 | C
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 100000017935 | 20231217 | 2337 | 20231218 | 415 | 2293969 | 278 | Transformer only | Animal | Other | 1 | 278 | 35.5837 | -119.6132 | No | Overcast;32-90 F | Transformer (OH) |  | 23-0147829 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898590 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15061 | 20231218 | 748 | 20231218 | 850 | 2294189 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1240 | 35.3107 | -118.9167 | No | Clear;32-90 F |  |  | 23-0147869 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898653 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1105 | 254561105 | FUSE | 8695 | 20231218 | 1031 | 20231218 | 1230 | 2294420 | 119 | Distribution Circuit | Animal | Bird found | 2 | 238 | 35.327 | -119.3323 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0147908 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898716 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1106 | 253551106 | RECLOSER | 4550 | 20231218 | 1852 | 20231219 | 1345 | 2295066 | 1133 | Distribution Circuit | 3rd Party | Other | 52 | 50252 | 35.7078 | -119.4371 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 23-0147976 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898785 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7291 | 20231219 | 629 | 20231219 | 1425 | 2295317 | 476 | Distribution Circuit | Animal | Other | 6 | 2831 | 35.7173 | -119.5798 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Broken | 23-0148081 | OH | Sus | 46095437 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898942 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1105 | 253911105 | FUSE | 16994 | 20231219 | 1115 | 20231219 | 1521 | 2295640 | 246 | Distribution Circuit | 3rd Party | Vehicle | 1 | 246 | 35.2454 | -118.8428 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0148092 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898955 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1104 | 252901104 | TRANSFORMER | 515447476273 | 20231219 | 1415 | 20231220 | 40 | 2295801 | 625 | Transformer only | Animal | Bird found | 1 | 625 | 35.5864 | -119.5313 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 23-0148139 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899001 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | RECLOSER | 3542 | 20231219 | 1450 | 20231219 | 1903 | 2295847 | 253 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 31372 | 34.8725 | -119.4942 | No | Overcast;32-90 F |  |  | 23-0148122 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898984 | 0 | EPSS Ckt | Y | 2023 | BC
KERN | KERN | SMYRNA-1102 | 253551102 | SWITCH | 89047 | 20231219 | 1501 | 20231219 | 1713 | 2295855 | 132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 132 | 35.743 | -119.3479 | No | Overcast;32-90 F | Customer Equipment | Failed/Faulted | 23-0148123 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898985 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1109 | 252721109 | SWITCH | 15671 | 20231220 | 750 | 20231221 | 223 | 2296236 | 1113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 129 | 99343 | 35.4198 | -119.0545 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0148214 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899088 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1102 | 253181102 | FUSE | 91875 | 20231220 | 1159 | 20231220 | 1429 | 2296533 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 750 | 35.703 | -119.3837 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Normal | 23-0148273 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899203 | 0 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1105 | 252821105 | TRANSFORMER | 516523861673 | 20231220 | 1535 | 20231220 | 1602 | 2296587 | 27 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 27 | 35.1897 | -119.1636 | No | Clear;32-90 F |  |  | 23-0148293 | OH | Sus | 46098112 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1899229 | 0 | Non-EPSS | N | 2023
KERN | KERN | KERN OIL-1106 | 252721106 | OCB | 1106/2 | 20231220 | 1759 | 20231221 | 1214 | 2296934 | 1095 | Distribution Circuit | Equipment Failure/Involved | Overhead | 827 | 853045 | 35.4407 | -119.0204 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 23-0148419 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1899378 | 0 | EPSS Ckt | N | 2023 | A-B-C
KERN | KERN | MAGUNDEN-1108 | 252771108 | RECLOSER | 250674 | 20231220 | 1800 | 20231220 | 2033 | 2296946 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 15606 | 35.3618 | -118.8954 | No | Clear;32-90 F |  |  | 23-0148322 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899260 | 0 | EPSS Ckt | Y | 2023 | A- C
KERN | KERN | WESTPARK-1112 | 253701112 | FUSE | 14916 | 20231220 | 1917 | 20231220 | 1953 | 2297013 | 36 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 1224 | 35.3483 | -119.0524 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Arcing | 23-0148332 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899273 | 0 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1103 | 253951103 | OCB | 1103/2 | 20231220 | 1934 | 20231221 | 1058 | 2297046 | 924 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1683 | 104664 | 35.3985 | -118.9399 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 23-0148338 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1899279 | 0 | Non-EPSS | N | 2023 | A B C INST
KERN | KERN | BLACKWELL-2101 | 254682101 | RECLOSER | 1104 | 20231220 | 1939 | 20231223 | 1247 | 2297063 | 3908 | Distribution Circuit | Animal | Other | 8 | 30935 | 35.6176 | -119.7429 | No | Overcast-Rain;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0148339 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 1899282 | 0 | Non-EPSS | N | 2023 | B- C & GRD
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 4169 | 20231220 | 1949 | 20231221 | 503 | 2297026 | 554 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 554 | 35.2375 | -119.1008 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0148340 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899283 | 0 | Non-EPSS | N | 2023 | N/A
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 15206 | 20231220 | 2009 | 20231221 | 1045 | 2297085 | 876 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4 | 3504 | 35.3679 | -118.9955 | No | Overcast-Drizzle;32-90 F | Bushing | Burned/flashed | 23-0148345 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899291 | 0 | Non-EPSS | N | 2023
KERN | KERN | ROSEDALE SUB | 25476 | OCB | 1102/2 | 20231220 | 2046 | 20231221 | 136 | 2297098 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1432 | 196579 | 35.3774 | -119.0777 | No | Overcast-Drizzle;32-90 F | Switch (OH) | Burned/flashed | 23-0148348 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899297 | 0 | Non-EPSS | N | 2023 | GRD OC PH OC TIME
KERN | KERN | BAKERSFIELD-2104 | 253372104 | SWITCH | 1600 | 20231220 | 2104 | 20231221 | 228 | 2297113 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 567 | 55058 | 35.3291 | -119.0029 | No | Overcast;32-90 F | Crossarm- Wood | Burned/flashed | 23-0148364 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899314 | 0 | Non-EPSS | N | 2023
KERN | KERN | LERDO-1112 | 253491112 | RECLOSER | 4323 | 20231220 | 2136 | 20231221 | 1155 | 2297135 | 859 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 53299 | 35.5151 | -119.0819 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0148388 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1899341 | 0 | Non-EPSS | N | 2023 | A- B- C
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 8902 | 20231220 | 2201 | 20231221 | 245 | 2297167 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 14200 | 35.3252 | -118.933 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0148410 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899366 | 0 | Non-EPSS | N | 2023
KERN | KERN | SEMITROPIC-1112 | 252901112 | FUSE | 87100 | 20231220 | 2204 | 20231221 | 1242 | 2297173 | 878 | Distribution Circuit | Animal | Other | 7 | 6146 | 35.6304 | -119.4561 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Normal | 23-0148495 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899491 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20231220 | 2208 | 20231221 | 32 | 2297137 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4551 | 243807 | 35.3885 | -119.0046 | No | Overcast-Rain;32-90 F |  |  | 23-0148392 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899345 | 0 | Non-EPSS | N | 2023 | SET A CB TRIP
KERN | KERN | WESTPARK-1110 | 253701110 | OCB | 1110/2 | 20231220 | 2228 | 20231221 | 825 | 2297192 | 597 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2858 | 580117 | 35.374 | -119.0403 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0148393 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899346 | 0 | Non-EPSS | N | 2023 | A B
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20231220 | 2241 | 20231220 | 2252 | 2297202 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 32 | 352 | 35.6271 | -118.9849 | No | Overcast;32-90 F |  |  | 23-0148394 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899347 | 0 | EPSS Ckt | Y | 2023 | C
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13909 | 20231221 | 50 | 20231221 | 1053 | 2297226 | 603 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 13 | 7839 | 35.361 | -118.9763 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 23-0148407 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899363 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1102 | 253181102 | FUSE | 15154 | 20231221 | 235 | 20231221 | 958 | 2297288 | 443 | Distribution Circuit | 3rd Party | Thrown Object | 37 | 16391 | 35.6897 | -119.2941 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0148423 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899382 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20231221 | 240 | 20231221 | 958 | 2297290 | 438 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4551 | 472702 | 35.3885 | -119.0046 | No | Overcast;32-90 F | Insulator | Failed/Faulted | 23-0148414 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899372 | 0 | Non-EPSS | N | 2023 | A C
KERN | KERN | FELLOWS-2104 | 254242104 | OCB | 2104/2 | 20231221 | 252 | 20231221 | 846 | 2297299 | 354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 4956 | 35.1948 | -119.5861 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 23-0148416 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1899375 | 0 | EPSS Ckt | N | 2023 | A/B TIME OC
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 2181 | 20231221 | 300 | 20231221 | 1048 | 2297301 | 468 | Distribution Circuit | 3rd Party | Customer Equipment | 50 | 23400 | 35.5944 | -118.9585 | No | Overcast;32-90 F | Customer Equipment | Burned Open | 23-0148418 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899377 | 0 | EPSS Ckt | Y | 2023 | B- GRD
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 8902 | 20231221 | 312 | 20231221 | 1231 | 2297303 | 553 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 27650 | 35.3252 | -118.933 | No | Clear;32-90 F | Insulator | Failed/Faulted | 23-0148424 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1899383 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2110 | 254072110 | TRANSFORMER | 516876166646 | 20231221 | 346 | 20231221 | 1626 | 2297311 | 760 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3040 | 35.3267 | -119.0482 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148428 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899389 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 14733 | 20231221 | 419 | 20231221 | 1853 | 2297329 | 874 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 7368 | 35.3061 | -119.0303 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148431 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899391 | 0 | Non-EPSS | N | 2023
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 14884 | 20231221 | 508 | 20231222 | 1115 | 2297332 | 1807 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 7297 | 35.307 | -119.2285 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148520 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899515 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 13437 | 20231221 | 518 | 20231221 | 828 | 2297266 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 3800 | 35.3611 | -118.9833 | No | Overcast-Fog-Drizzle;32-90 F | Cutout- fuse holder | Arcing | 23-0148427 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899387 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-1104 | 252551104 | TRIP-SAVER | 14233 | 20231221 | 536 | 20231226 | 1808 | 2297503 | 7952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 71568 | 35.3678 | -119.7357 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148480 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1899473 | 0 | EPSS Ckt | N | 2023 | NONE
KERN | KERN | TEJON-1103 | 252931103 | RECLOSER | 984740 | 20231221 | 704 | 20231221 | 1011 | 2297354 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 5618 | 35.018 | -118.8467 | No | Overcast-Strong Winds;32-90 F |  |  | 23-0148434 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899396 | 0 | EPSS Ckt | N | 2023 | C
KERN | KERN | WESTPARK-1110 | 253701110 | FUSE | 13946 | 20231221 | 837 | 20231221 | 844 | 2297447 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 191 | 1337 | 35.3609 | -119.012 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0148393 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1899413 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 645327 | 20231221 | 917 | 20231221 | 1008 | 2297508 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 1683 | 35.3151 | -119.0062 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0148456 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899439 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1102 | 253181102 | FUSE | 15984 | 20231221 | 1052 | 20231221 | 1128 | 2297608 | 36 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 36 | 35.6884 | -119.3209 | No | Overcast-Fog;32-90 F |  |  | 23-0148466 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1899452 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13476 | 20231221 | 1213 | 20231221 | 1406 | 2297700 | 113 | Distribution Circuit | Animal | Bird found | 95 | 10735 | 35.3649 | -118.9745 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0148494 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899490 | 0 | Non-EPSS | N | 2023
KERN | KERN | CUYAMA-2101 | 253142101 | RECLOSER | 3533 | 20231221 | 1334 | 20231221 | 1710 | 2297762 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 203 | 43848 | 34.9277 | -119.5952 | No | Overcast-Strong Winds;32-90 F | Capacitor | Burned/flashed | 23-0148485 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899481 | 0 | EPSS Ckt | N | 2023 | SGF
KERN | KERN | COLUMBUS-1105 | 253951105 | TRANSFORMER | 517332470797 | 20231221 | 1437 | 20231221 | 2136 | 2297814 | 419 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 838 | 35.4417 | -118.895 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 23-0148508 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899504 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2109 | 254072109 | RECLOSER | 4718 | 20231221 | 1511 | 20231222 | 835 | 2297836 | 1044 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2626 | 373750 | 35.2863 | -119.0389 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0148501 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 1899497 | 0 | Non-EPSS | N | 2023 | BC GRD
KERN | KERN | STOCKDALE-1109 | 254071109 | OCB | 1109/2 | 20231221 | 1524 | 20231221 | 2231 | 2297858 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1607 | 179979 | 35.3164 | -119.0682 | No | Overcast-Rain;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0148505 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899501 | 0 | Non-EPSS | N | 2023 | A & B
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517100068083 | 20231221 | 1845 | 20231222 | 1156 | 2297959 | 1031 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 7217 | 35.3676 | -118.9731 | No | Partly Cloudy-Fog;32-90 F | Cutout- fuse holder | Arcing | 23-0148518 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899514 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1102 | 253701102 | FUSE | 13798 | 20231221 | 2320 | 20231222 | 129 | 2298063 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1032 | 35.3727 | -119.0259 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Broken | 23-0148560 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1899563 | 1 | Non-EPSS | N | 2023
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | MTR#1009986565 | 20231222 | 816 | 20231222 | 1230 | 2298168 | 254 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 508 | 35.1726 | -119.0914 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0148594 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899649 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1105 | 252931105 | OCB | 1105/2 | 20231222 | 827 | 20231222 | 1552 | 2298177 | 445 | Distribution Circuit | Animal | Other | 98 | 38170 | 35.0198 | -118.9547 | No | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Normal | 23-0148582 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899631 | 0 | Non-EPSS | N | 2023 | A B INST
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 516105869518 | 20231222 | 912 | 20231222 | 1218 | 2298235 | 186 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 372 | 35.4028 | -119.3075 | No | Overcast-Fog;32-90 F |  |  | 23-0148587 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1899641 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1102 | 253701102 | SWITCH | 13797 | 20231222 | 1035 | 20231222 | 1202 | 2298323 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 261 | 35.3725 | -119.026 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Broken | 23-0148560 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899636 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517100068083 | 20231222 | 1444 | 20231222 | 1507 | 2298487 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 161 | 35.3676 | -118.9731 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0148604 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899659 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1105 | 252931105 | OCB | 1105/2 | 20231222 | 1653 | 20231222 | 1713 | 2298556 | 20 | Distribution Circuit | Equipment Failure/Involved | Substation | 98 | 1960 | 35.0198 | -118.9547 | No | Partly Cloudy-Fog;32-90 F | Circuit Breaker | Malfunctioning | 23-0148582 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899671 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 37032 | 20231222 | 1819 | 20231222 | 2033 | 2298589 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 3128 | 35.2524 | -118.9664 | No | Clear;32-90 F |  |  | 23-0148615 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899675 | 1 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1105 | 253951105 | TRANSFORMER | 517332470797 | 20231222 | 1828 | 20231223 | 1345 | 2298592 | 1157 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 2314 | 35.4417 | -118.895 | No | Overcast;32-90 F | Transformer | Broken | 23-0148653 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899716 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 310879 | 20231223 | 736 | 20231223 | 1210 | 2298816 | 274 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 548 | 35.4776 | -119.5877 | No | Clear;32-90 F |  |  | 23-0148665 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899731 | 1 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20231223 | 837 | 20231223 | 1126 | 2298698 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1859 | 35.4767 | -119.5887 | No | Clear;32-90 F |  |  | 23-0148660 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899726 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1105 | 253701105 | TRANSFORMER | T739616 | 20231223 | 959 | 20231223 | 1343 | 2298731 | 224 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 1792 | 35.3561 | -119.0603 | No | Clear;32-90 F |  |  | 23-0148672 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1899737 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1105 | 253551105 | RECLOSER | 98496 | 20231223 | 1013 | 20231223 | 1443 | 2298744 | 270 | Distribution Circuit | 3rd Party | Vehicle | 15 | 1096 | 35.79 | -119.3924 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 23-0148648 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899722 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20231224 | 1234 | 20231226 | 1500 | 2299155 | 3026 | Distribution Circuit | Animal | Other | 21 | 43925 | 35.5593 | -118.9575 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0148753 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899824 | 0 | EPSS Ckt | Y | 2023 | OH
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20231225 | 954 | 20231225 | 1154 | 2299418 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 880 | 35.4767 | -119.5887 | No | Clear;32-90 F |  |  | 23-0148823 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899894 | 1 | Non-EPSS | N | 2023
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 17256 | 20231225 | 1034 | 20231225 | 1500 | 2299435 | 266 | Distribution Circuit | Animal | Bird found | 6 | 741 | 35.2742 | -119.0028 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0148824 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899895 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 8461 | 20231225 | 1037 | 20231225 | 1602 | 2299437 | 325 | Distribution Circuit | Animal | Squirrel | 2 | 650 | 35.3456 | -119.0795 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0148831 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899902 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1118 | 253371118 | FUSE | 8322 | 20231225 | 1210 | 20231225 | 1400 | 2299459 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 7590 | 35.4006 | -119.012 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0148826 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899897 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 310879 | 20231225 | 1603 | 20231225 | 1714 | 2299517 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 189 | 35.4776 | -119.5877 | No | Clear;32-90 F |  |  | 23-0148837 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899908 | 1 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-1106 | 253371106 | OTHER | OJ N/E OF 15022 | 20231225 | 2159 | 20231226 | 1004 | 2299565 | 725 | Distribution Circuit | 3rd Party | Vehicle | 17 | 12325 | 35.3902 | -118.9826 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0148854 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1899925 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEVIS-2105 | 255322105 | FUSE | 12135 | 20231225 | 2338 | 20231226 | 1606 | 2299583 | 988 | Distribution Circuit | Equipment Failure/Involved | Underground | 111 | 56589 | 35.3492 | -119.1141 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 23-0148857 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899929 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17784 | 20231226 | 820 | 20231226 | 928 | 2299659 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 211 | 14348 | 35.3447 | -119.0708 | No | Clear;32-90 F |  |  | 23-0148868 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899967 | 0 | Non-EPSS | N | 2023
KERN | KERN | SAN BERNARD-1101 | 253191101 | FUSE | 9841 | 20231226 | 1204 | 20231227 | 130 | 2299787 | 650 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 4657 | 35.018 | -118.8467 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148883 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900000 | 1 | EPSS Ckt | N | 2023
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7292 | 20231226 | 1731 | 20231226 | 1813 | 2300064 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 392 | 35.7609 | -119.5625 | No | Partly Cloudy;32-90 F |  |  | 23-0148915 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900033 | 1 | Non-EPSS | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 63081 | 20231226 | 2032 | 20231226 | 2146 | 2300172 | 74 | Distribution Circuit | Animal | Bird found | 1 | 74 | 35.3107 | -118.903 | No | Clear;32-90 F | Fuse | Burned Open | 23-0148939 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900061 | 0 | Non-EPSS | N | 2023
KERN | KERN | LAKEVIEW-1102 | 253411102 | RECLOSER | 3548 | 20231227 | 55 | 20231227 | 758 | 2300257 | 423 | Distribution Circuit | 3rd Party | Vehicle | 40 | 7302 | 35.0944 | -119.1296 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0148945 | OH | Sus | 31680305 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900066 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | CHARCA-1103 | 254501103 | RECLOSER | 4333 | 20231227 | 724 | 20231227 | 1324 | 2300376 | 360 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 4214 | 35.6018 | -119.2551 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0148966 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1900092 | 0 | Non-EPSS | N | 2023 | C SGF
KERN | KERN | STOCKDALE-2114 | 254072114 | TRANSFORMER | T0108 | 20231227 | 739 | 20231227 | 1051 | 2300382 | 192 | Transformer only | Equipment Failure/Involved | Underground | 4 | 768 | 35.3593 | -119.0733 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0148968 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900094 | 0 | Non-EPSS | N | 2023
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20231227 | 742 | 20231227 | 1802 | 2300386 | 620 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 10206 | 35.5593 | -118.9575 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148969 | OH | Sus | 46101879 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1900095 | 0 | EPSS Ckt | Y | 2023 | PH OC INST
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517042567567 | 20231227 | 839 | 20231227 | 1332 | 2300476 | 293 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1172 | 35.3529 | -118.9924 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0148991 | OH | Sus | 46102079 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900157 | 0 | Non-EPSS | N | 2023
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 5901 | 20231227 | 1003 | 20231228 | 337 | 2300572 | 1054 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 12 | 6411 | 35.3402 | -119.0549 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0149000 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900167 | 0 | Non-EPSS | N | 2023
KERN | KERN | WESTPARK-1102 | 253701102 | SWITCH | 5687 | 20231227 | 1330 | 20231227 | 1352 | 2300752 | 22 | Distribution Circuit | Company Initiated | Return Circuit Normal | 5 | 110 | 35.3727 | -119.0292 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 23-0148560 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1900181 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514681368091 | 20231227 | 1654 | 20231228 | 948 | 2300754 | 1014 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1014 | 35.3571 | -119.7852 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0149037 | OH | Sus | 31680274 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900210 | 0 | EPSS Ckt | N | 2023
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | MTR#1010421571 | 20231229 | 934 | 20231229 | 1101 | 2301799 | 87 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 87 | 35.4227 | -119.7656 | No | Clear;32-90 F |  |  | 23-0149205 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1900496 | 0 | EPSS Ckt | N | 2023
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 7575 | 20231229 | 1133 | 20231229 | 1151 | 2301892 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 126 | 35.4999 | -119.2191 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0004794 | OH | Sus | 35350444 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900501 | 0 | Non-EPSS | N | 2023
KERN | KERN | MIDWAY-1102 | 252611102 | RECLOSER | 1482 | 20231229 | 1317 | 20231229 | 2235 | 2302005 | 558 | Distribution Circuit | 3rd Party | Vehicle | 103 | 21669 | 35.3665 | -119.4477 | No | Clear;32-90 F | Pole-Wood | On Ground | 23-0149226 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900523 | 0 | Non-EPSS | N | 2023 | A & B
KERN | KERN | RIO BRAVO-1103 | 252861103 | OCB | 1103/2 | 20231229 | 2117 | 20231230 | 2010 | 2302282 | 1373 | Distribution Circuit | 3rd Party | Vehicle | 151 | 21536 | 35.442 | -119.2606 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0149282 | OH | Sus | 35520400 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900584 | 0 | Non-EPSS | N | 2023 | NONE
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 653595 | 20231230 | 723 | 20231230 | 917 | 2302461 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 836 | 35.1433 | -118.9677 | No | Clear;32-90 F |  |  | 23-0149336 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900644 | 1 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | OTHER | WIRE DOWN 1/N/OF 79732 | 20231230 | 941 | 20231231 | 434 | 2302560 | 1133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 9522 | 35.6591 | -119.5177 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0149356 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1900665 | 1 | Non-EPSS | N | 2023
KERN | KERN | COLUMBUS-1110 | 253951110 | TRANSFORMER | 517147568730 | 20231230 | 1013 | 20231230 | 1115 | 2302623 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 372 | 35.3849 | -118.9576 | No | Overcast-Drizzle;32-90 F | Secondary | Annealed | 23-0149348 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900657 | 0 | Non-EPSS | N | 2023
KERN | KERN | GANSO-1104 | 254541104 | FUSE | 17094 | 20231230 | 1041 | 20231230 | 1808 | 2302654 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1341 | 35.486 | -119.4211 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0149371 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1900683 | 0 | Non-EPSS | N | 2023
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 17613 | 20231230 | 1208 | 20231230 | 1306 | 2302759 | 58 | Distribution Circuit | 3rd Party | Metallic Balloon | 26 | 1508 | 35.4196 | -119.0666 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0149373 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900685 | 0 | Non-EPSS | N | 2023
KERN | KERN | TEJON-1105 | 252931105 | OCB | 1105/2 | 20231230 | 1621 | 20231230 | 1858 | 2302924 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 15386 | 35.0198 | -118.9547 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0149393 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900705 | 0 | Non-EPSS | N | 2023 | SET A-PH OC TIME A B
KERN | KERN | LAMONT-1104 | 253911104 | SWITCH | 2144 | 20231231 | 152 | 20231231 | 207 | 2303062 | 15 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 285 | 35.3392 | -118.8354 | No | Partly Cloudy-Fog;32-90 F | Jumper | Burned Open | 23-0149446 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900761 | 1 | EPSS Ckt | N | 2023
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 44281 | 20231231 | 658 | 20231231 | 1713 | 2303105 | 615 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3690 | 35.3107 | -118.9041 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0149453 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1900770 | 0 | Non-EPSS | N | 2023
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 53339 | 20231231 | 736 | 20231231 | 950 | 2303112 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 670 | 35.6597 | -119.5177 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0149457 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1900775 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | SWITCH | 1876 | 20231231 | 1048 | 20231231 | 1157 | 2303193 | 69 | Distribution Circuit | 3rd Party | Metallic Balloon | 894 | 61686 | 35.3708 | -118.966 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0149469 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900788 | 0 | Non-EPSS | N | 2023
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20231231 | 1203 | 20231231 | 1333 | 2303214 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 990 | 35.4767 | -119.5887 | No | Clear;32-90 F |  |  | 23-0149485 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900806 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | SWITCH | 1869 | 20231231 | 1248 | 20231231 | 1302 | 2303224 | 14 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1976 | 27664 | 35.3733 | -118.9815 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0149482 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900802 | 0 | Non-EPSS | N | 2023
KERN | KERN | BAKERSFIELD-2106 | 253372106 | JUMPER | 13953 | 20231231 | 1400 | 20231231 | 1805 | 2303251 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2205 | 35.3679 | -118.9742 | No | Clear;32-90 F | Jumper | Burned Open | 23-0149494 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900815 | 0 | Non-EPSS | N | 2023
KERN | KERN | MC FARLAND-1104 | 253181104 | TRANSFORMER | 516324479341 | 20240101 | 6 | 20240101 | 118 | 2303413 | 72 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 1152 | 35.6737 | -119.2387 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0005734 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1900846 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1107 | 252461107 | OCB | 1107/2 | 20240101 | 844 | 20240101 | 852 | 2304155 | 8 | Distribution Circuit | 3rd Party | Vehicle | 98 | 784 | 35.6054 | -119.2033 | No | Overcast-Fog;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0005766 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | Yes | No | 1900874 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | MC FARLAND-1105 | 253181105 | TRANSFORMER | 516213381226 | 20240101 | 1410 | 20240101 | 1624 | 2304309 | 134 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 402 | 35.7252 | -119.2764 | No | Partly Cloudy;32-90 F |  |  | 24-0005810 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1900912 | 1 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 310879 | 20240102 | 759 | 20240102 | 944 | 2304546 | 105 | Distribution Circuit | Animal | Other | 3 | 280 | 35.4776 | -119.5877 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0005955 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901044 | 1 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7456 | 20240102 | 823 | 20240102 | 1140 | 2304575 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 788 | 35.4705 | -119.5648 | No | Overcast-Fog;32-90 F |  |  | 24-0006012 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901064 | 1 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 310879 | 20240102 | 1552 | 20240102 | 1732 | 2305039 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 267 | 35.4776 | -119.5877 | No | Clear;32-90 F |  |  | 24-0006200 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901107 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517049666531 | 20240102 | 1738 | 20240103 | 240 | 2305137 | 542 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4878 | 35.324 | -118.9893 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0006207 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901110 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1102 | 252961102 | FUSE | 14599 | 20240102 | 2104 | 20240103 | 1107 | 2305480 | 843 | Distribution Circuit | 3rd Party | Vehicle | 175 | 16329 | 35.6013 | -119.3381 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0006270 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901165 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 16914 | 20240103 | 845 | 20240103 | 1605 | 2305997 | 440 | Distribution Circuit | 3rd Party | Vehicle | 40 | 4316 | 35.4782 | -119.2962 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 24-0006385 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901301 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1109 | 253951109 | FUSE | 8668 | 20240103 | 909 | 20240103 | 949 | 2306157 | 40 | Distribution Circuit | Animal | Bird found | 18 | 720 | 35.3977 | -118.9383 | No | Overcast-Fog;32-90 F | Fuse | Burned Open | 24-0006401 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901309 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1102 | 253181102 | FUSE | 15989 | 20240103 | 1056 | 20240103 | 1222 | 2306303 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 86 | 35.6886 | -119.3572 | No | Partly Cloudy;32-90 F |  |  | 24-0006488 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901356 | 1 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516931367749 | 20240103 | 1532 | 20240103 | 1548 | 2306335 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 128 | 35.3571 | -119.03 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0006521 | OH | Sus | 31681000 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901365 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7119 | 20240103 | 1551 | 20240104 | 920 | 2306994 | 1049 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 4198 | 35.5719 | -119.5985 | No | Partly Cloudy;32-90 F |  |  | 24-0006793 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901570 | 1 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 18465 | 20240104 | 911 | 20240104 | 949 | 2306915 | 38 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 38 | 35.7578 | -119.4131 | No | Clear;32-90 F | Customer Equipment | Leaking | 24-0006757 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1901520 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514742570428 | 20240104 | 1122 | 20240104 | 1215 | 2307110 | 53 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 53 | 35.4227 | -119.7656 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0006920 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1901616 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-1105 | 252771105 | FUSE | 15258 | 20240104 | 1603 | 20240104 | 1720 | 2307332 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 4928 | 35.3687 | -118.9296 | No | Partly Cloudy;32-90 F |  |  | 24-0007070 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901647 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 2771 | 20240104 | 2102 | 20240105 | 545 | 2307476 | 523 | Distribution Circuit | 3rd Party | Vehicle | 459 | 64953 | 35.2234 | -119.1004 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0007117 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1901672 | 0 | Non-EPSS | N | 2024 | B & GRD
KERN | KERN | ROSEDALE-2102 | 254762102 | TRANSFORMER | 516796368175 | 20240105 | 1151 | 20240106 | 349 | 2307937 | 958 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 958 | 35.3688 | -119.0756 | No | Clear;32-90 F | Jumper | Broken | 24-0007457 | OH | Sus | 46131904 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901881 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | OCB | 1103/2 | 20240105 | 1157 | 20240106 | 1157 | 2307943 | 1440 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1684 | 146744 | 35.3985 | -118.9399 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0007373 | UG | Sus | 31681087 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901862 | 0 | Non-EPSS | N | 2024 | A & GRD
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17784 | 20240105 | 1530 | 20240105 | 1650 | 2308105 | 80 | Distribution Circuit | Animal | Bird found | 211 | 16880 | 35.3447 | -119.0708 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0007483 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901889 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2109 | 254072109 | FUSE | 17657 | 20240106 | 758 | 20240106 | 838 | 2308421 | 40 | Distribution Circuit | Animal | Bird found | 38 | 1520 | 35.3032 | -119.0256 | No | Clear;32-90 F | Fuse | Burned Open | 24-0007568 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901958 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | MTR#1009999998 | 20240106 | 832 | 20240106 | 1208 | 2308442 | 216 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 216 | 35.4098 | -119.7215 | No | Clear;32-90 F |  |  | 24-0007615 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1901998 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 866991 | 20240106 | 1012 | 20240106 | 1355 | 2308566 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 223 | 35.1222 | -118.9588 | No | Clear;32-90 F |  |  | 24-0007638 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902017 | 1 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | 515825074121 | 20240106 | 1053 | 20240106 | 1613 | 2308593 | 320 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 320 | 35.5289 | -119.404 | No | Partly Cloudy;32-90 F |  |  | 24-0007662 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1902033 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1102 | 253651102 | FUSE | 7535 | 20240106 | 1059 | 20240106 | 1533 | 2308617 | 274 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 8220 | 35.5298 | -119.278 | No | Partly Cloudy;32-90 F |  |  | 24-0007642 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1902020 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1101 | 252971101 | TRANSFORMER | MTR#1008604678 | 20240106 | 1123 | 20240106 | 1221 | 2308523 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 290 | 35.2142 | -118.8327 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0007618 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902001 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | FUSE | 15957 | 20240106 | 1213 | 20240106 | 1247 | 2308652 | 34 | Distribution Circuit | 3rd Party | Metallic Balloon | 99 | 3366 | 35.2087 | -118.8242 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0007626 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1902008 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1106 | 253951106 | TRANSFORMER | 517113469405 | 20240106 | 1552 | 20240106 | 1742 | 2308865 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1323 | 35.4035 | -118.9691 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0007660 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902032 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-1101 | 254761101 | TRANSFORMER | T7526 | 20240106 | 1716 | 20240106 | 1752 | 2308939 | 36 | Transformer only | Unknown Cause | Patrol - found nothing | 12 | 432 | 35.406 | -119.0705 | No | Partly Cloudy;32-90 F |  |  | 24-0007673 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1902044 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20240106 | 1936 | 20240107 | 252 | 2308984 | 432 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2876 | 341508 | 35.3885 | -119.0046 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0007680 | OH | Sus | 31681160 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1902051 | 0 | Non-EPSS | N | 2024 | A & B
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 9998 | 20240107 | 27 | 20240107 | 108 | 2309001 | 41 | Distribution Circuit | 3rd Party | Metallic Balloon | 36 | 1476 | 35.3213 | -119.0207 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0007717 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902090 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | FUSE | 14923 | 20240107 | 557 | 20240107 | 814 | 2309094 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 548 | 34.8344 | -118.8615 | No | Overcast-Snow-Strong Winds;Below 32 F |  |  | 24-0007732 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902105 | 1 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 11035 | 20240107 | 709 | 20240107 | 937 | 2309101 | 148 | Distribution Circuit | Animal | Bird found | 5 | 690 | 35.3175 | -119.0204 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0007740 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902115 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1109 | 254071109 | RECLOSER | 2526 | 20240107 | 1446 | 20240107 | 1629 | 2309263 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1060 | 81208 | 35.2974 | -119.0566 | No | Overcast;32-90 F |  |  | 24-0007770 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902132 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 15006 | 20240107 | 1630 | 20240107 | 1808 | 2309294 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 686 | 35.4194 | -119.0306 | No | Clear;32-90 F |  |  | 24-0007779 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902141 | 1 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1101 | 253191101 | OCB | 1101/2 | 20240107 | 2050 | 20240108 | 525 | 2309376 | 515 | Distribution Circuit | 3rd Party | Vehicle | 86 | 6189 | 35.0921 | -118.878 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0007786 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902148 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | 516481569018 | 20240108 | 907 | 20240108 | 1334 | 2309492 | 267 | Transformer only | 3rd Party | Vehicle | 1 | 267 | 35.3908 | -119.1814 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0007842 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902191 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1103 | 252721103 | TRANSFORMER | 516926669956 | 20240108 | 1116 | 20240108 | 1901 | 2309836 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 30 | 13950 | 35.4178 | -119.0322 | No | Clear;32-90 F | Secondary | Broken | 24-0007994 | OH | Sus | 31681158 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902374 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 9447 | 20240108 | 1238 | 20240108 | 1302 | 2309781 | 24 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 24 | 35.3129 | -119.0692 | No | Clear;32-90 F | Metering Equipment | Broken | 24-0008015 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902380 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRANSFORMER | 514027666217 | 20240108 | 1853 | 20240109 | 215 | 2310181 | 442 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 442 | 35.3033 | -120.0025 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0008214 | OH | Sus | 31681171 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902429 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 18561 | 20240109 | 552 | 20240109 | 750 | 2310260 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 590 | 35.2311 | -118.7886 | No | Partly Cloudy;32-90 F |  |  | 24-0008290 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1902481 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1105 | 253371105 | JUMPER | OJ 1/W/OF 16273 | 20240109 | 1254 | 20240109 | 1905 | 2310867 | 371 | Distribution Circuit | 3rd Party | Metallic Balloon | 514 | 60612 | 35.3849 | -119.0223 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0008485 | OH | Sus | 46134939 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1902686 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1109 | 254071109 | RECLOSER | 2526 | 20240109 | 1517 | 20240109 | 1614 | 2310979 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1060 | 51810 | 35.2974 | -119.0566 | No | Clear;32-90 F | PT/CCVT | Deteriorated | 24-0008608 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Multi-Fault | 0 | No | No | No | 1902702 | 0 | Non-EPSS | N | 2024 | B C GRD
KERN | KERN | STOCKDALE-1109 | 254071109 | TRANSFORMER | 516844666055 | 20240109 | 2300 | 20240110 | 509 | 2311255 | 369 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 369 | 35.3105 | -119.0581 | No | Partly Cloudy;32-90 F | Switch (OH) | Broken | 24-0008707 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902770 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | 516956769590 | 20240110 | 654 | 20240110 | 1021 | 2311314 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1035 | 35.4078 | -119.0221 | No | Overcast;32-90 F | Fuse | Broken | 24-0008891 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902940 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | TRANSFORMER | 516657068967 | 20240110 | 750 | 20240110 | 1941 | 2311353 | 711 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 6399 | 35.3898 | -119.1224 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0008843 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902879 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2101 | 255262101 | FUSE | 20068 | 20240110 | 1109 | 20240111 | 345 | 2311669 | 996 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 5463 | 35.3887 | -119.0955 | No | Overcast;32-90 F | Switch (UG) | Failed/Faulted | 24-0009042 | UG | Sus | 35523001 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | No | No | 1903018 | 0 | Non-EPSS | N | 2024
KERN | KERN | BLACKWELL-2101 | 254682101 | TRANSFORMER | 514719579640 | 20240110 | 1118 | 20240111 | 608 | 2311679 | 1130 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1130 | 35.6754 | -119.7787 | No | Clear;32-90 F | Other | Broken | 24-0008955 | OH | Sus | 46139853 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902988 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1110 | 253951110 | TRANSFORMER | 517180168525 | 20240110 | 1139 | 20240111 | 51 | 2311685 | 792 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 5544 | 35.3796 | -118.9462 | No | Overcast;32-90 F | Transformer | Deteriorated | 24-0008984 | OH | Sus | 31681438 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903003 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | 516172272887 | 20240110 | 1357 | 20240111 | 142 | 2311825 | 703 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 5624 | 35.4958 | -119.2866 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0009239 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903047 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 16067 | 20240110 | 1415 | 20240110 | 2235 | 2311859 | 500 | Distribution Circuit | 3rd Party | Vehicle | 6 | 3000 | 35.5722 | -119.4738 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0009118 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903032 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | FUSE | 9942 | 20240110 | 1545 | 20240111 | 1054 | 2311932 | 1149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 16086 | 35.5547 | -118.9017 | No | Clear;32-90 F |  |  | 24-0009265 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903051 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 883676 | 20240111 | 117 | 20240111 | 419 | 2312558 | 182 | Distribution Circuit | Animal | Other | 7 | 1214 | 35.7753 | -119.5181 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0009402 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903155 | 1 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 16913 | 20240111 | 151 | 20240111 | 658 | 2312582 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1843 | 35.4818 | -119.2962 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0009411 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903163 | 1 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516681668579 | 20240111 | 202 | 20240111 | 527 | 2312594 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1230 | 35.3791 | -119.1139 | No | Partly Cloudy-Drizzle;32-90 F | Fuse | Broken | 24-0009414 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903166 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | FUSE | 9267 | 20240111 | 207 | 20240111 | 414 | 2312588 | 127 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 61 | 7709 | 35.2969 | -119.3767 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0009401 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903154 | 1 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1105 | 252931105 | FUSE | 13741 | 20240111 | 841 | 20240111 | 1108 | 2312751 | 147 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 147 | 35.0712 | -118.8818 | No | Overcast-Strong Winds;32-90 F | Transformer (UG) | Leaking | 24-0009484 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903226 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1103 | 253871103 | SWITCH | 95739 | 20240111 | 1028 | 20240111 | 1040 | 2312981 | 12 | Distribution Circuit | Animal | Other | 1 | 12 | 35.1336 | -119.2479 | No | Overcast-Strong Winds;32-90 F | Cutout- fuse holder | Normal | 24-0009594 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903360 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | TRANSFORMER | T5805 | 20240112 | 1940 | 20240112 | 2143 | 2314329 | 123 | Transformer only | Equipment Failure/Involved | Underground | 14 | 1722 | 35.3915 | -119.1251 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0010355 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903694 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1109 | 254071109 | FUSE | 20086 | 20240113 | 751 | 20240113 | 833 | 2314474 | 42 | Distribution Circuit | Animal | Bird found | 19 | 784 | 35.2961 | -119.0544 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0010422 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903756 | 1 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515721271795 | 20240113 | 1039 | 20240113 | 1049 | 2314571 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 30 | 35.4646 | -119.4381 | No | Clear;32-90 F | Fuse | Broken | 24-0010443 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903780 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1103 | 255451103 | INTERRUPTER | 81176 | 20240114 | 1410 | 20240114 | 1533 | 2315450 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 10292 | 35.4074 | -118.8923 | No | Clear;32-90 F |  |  | 24-0010710 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1903987 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1113 | 253491113 | FUSE | 15142 | 20240116 | 119 | 20240116 | 339 | 2316066 | 140 | Distribution Circuit | Animal | Bird found | 3 | 467 | 35.5294 | -119.2047 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Normal | 24-0010860 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904111 | 1 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2102 | 254582102 | RECLOSER | 1499 | 20240116 | 547 | 20240116 | 803 | 2316073 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2720 | 35.4418 | -119.1812 | No | Partly Cloudy-Fog;32-90 F | Recloser | Malfunctioning | 24-0010862 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1904112 | 0 | Non-EPSS | N | 2024 | none
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 16866 | 20240116 | 653 | 20240116 | 906 | 2316081 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 11571 | 35.3537 | -118.9942 | No | Overcast-Fog;32-90 F |  |  | 24-0010936 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1904241 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7260 | 20240116 | 904 | 20240116 | 1301 | 2316239 | 237 | Distribution Circuit | Animal | Other | 3 | 790 | 35.4712 | -119.5279 | No | Partly Cloudy-Fog;32-90 F | Fuse | Burned Open | 24-0011109 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904315 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | INTERRUPTER | 12588 | 20240116 | 911 | 20240117 | 59 | 2316275 | 948 | Distribution Circuit | Equipment Failure/Involved | Underground | 503 | 92812 | 35.3545 | -119.0901 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0010941 | UG | Sus | 46155875 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904254 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1103 | 255451103 | INTERRUPTER | 81176 | 20240116 | 1335 | 20240116 | 1410 | 2316615 | 35 | Distribution Circuit | Equipment Failure/Involved | Underground | 124 | 4340 | 35.4074 | -118.8923 | No | Overcast;32-90 F | Interrupter | Malfunctioning | 24-0011163 | UG | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1904333 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517062267011 | 20240116 | 1615 | 20240116 | 1712 | 2316630 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 114 | 35.3377 | -118.9854 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned Open | 24-0011287 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904356 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517168868372 | 20240116 | 1814 | 20240116 | 2048 | 2316839 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 616 | 35.3754 | -118.9501 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0011317 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904379 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517167268372 | 20240116 | 1927 | 20240116 | 1937 | 2316873 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 160 | 35.3754 | -118.9506 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0011319 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904381 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | TRANSFORMER | 516646268652 | 20240116 | 2021 | 20240116 | 2033 | 2316872 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 60 | 35.3809 | -119.1258 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0011323 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1904383 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | RECLOSER | 4107 | 20240117 | 1129 | 20240117 | 2206 | 2317616 | 637 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 7328 | 35.3327 | -119.3061 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0011609 | OH | Sus | 46160914 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1904634 | 0 | Non-EPSS | N | 2024 | B & GRD
KERN | KERN | SMYRNA-1106 | 253551106 | OCB | 1106/2 | 20240117 | 1621 | 20240118 | 302 | 2317927 | 641 | Distribution Circuit | 3rd Party | Aircraft- crop dusting | 229 | 15810 | 35.718 | -119.4554 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0011839 | OH | Sus | 31681816 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1904676 | 0 | Non-EPSS | N | 2024 | SET A RLY- A B C TIME 51
KERN | KERN | MAGUNDEN-1108 | 252771108 | TRANSFORMER | 517332168112 | 20240117 | 1808 | 20240117 | 2341 | 2317926 | 333 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 666 | 35.3686 | -118.8959 | No | Clear;32-90 F | Cutout- fuse holder | Arcing | 24-0011883 | OH | Sus | 31681968 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904685 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | FUSE | 8695 | 20240118 | 758 | 20240118 | 855 | 2318231 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 114 | 35.327 | -119.3323 | No | Clear;32-90 F |  |  | 24-0012029 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904768 | 1 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1106 | 252441106 | TRANSFORMER | 516315063745 | 20240118 | 924 | 20240118 | 1134 | 2318318 | 130 | Transformer only | Animal | Bird found | 1 | 130 | 35.2454 | -119.2351 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0012145 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904812 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 7265 | 20240118 | 1025 | 20240118 | 1347 | 2318394 | 202 | Distribution Circuit | 3rd Party | Vehicle | 6 | 1212 | 35.5726 | -119.2595 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0012117 | OH | Sus | 46164602 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1904805 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 100000006186 | 20240118 | 1301 | 20240119 | 112 | 2318330 | 731 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 731 | 35.1655 | -118.932 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0012196 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904833 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7291 | 20240118 | 1626 | 20240119 | 1303 | 2318956 | 1237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 6662 | 35.7173 | -119.5798 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0012511 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | No | No | 1904995 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | 517266164402 | 20240118 | 1630 | 20240118 | 1738 | 2318637 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 476 | 35.2656 | -118.9167 | No | Clear;32-90 F | Fuse | Broken | 24-0012379 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904862 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517459264960 | 20240118 | 1648 | 20240118 | 1827 | 2318647 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 99 | 35.2818 | -118.8524 | No | Overcast;32-90 F | Fuse | Broken | 24-0012391 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904867 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | OCB | 1103/2 | 20240118 | 1920 | 20240119 | 19 | s1904880 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 9568 | 35.3985 | -118.9399 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0012316 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1904880 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | MAGUNDEN-1108 | 252771108 | TRANSFORMER | 517336368080 | 20240119 | 840 | 20240119 | 1028 | 2318923 | 108 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 108 | 35.3678 | -118.8946 | No | Clear;32-90 F |  |  | 24-0012570 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1905067 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516767563351 | 20240119 | 938 | 20240119 | 1321 | 2319038 | 223 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 223 | 35.2361 | -119.0833 | No | Clear;32-90 F | Fuse | Broken | 24-0012668 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905102 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2108 | 254072108 | TRANSFORMER | T5621 | 20240119 | 1035 | 20240119 | 1409 | 2318935 | 214 | Transformer only | Unknown Cause | Patrol - not conducted | 9 | 1926 | 35.3271 | -119.1033 | No | Partly Cloudy;32-90 F |  |  | 24-0012576 | OH | Sus | 46165444 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1905069 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1114 | 253491114 | OCB | 1114/2 | 20240119 | 1740 | 20240120 | 653 | 2319385 | 793 | Distribution Circuit | 3rd Party | Vehicle | 37 | 10398 | 35.5004 | -119.1519 | No | Partly Cloudy;32-90 F | Switch (OH) | Broken | 24-0012791 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905130 | 0 | Non-EPSS | N | 2024 | A B SET A & PH OC INST
KERN | KERN | RIO BRAVO-1104 | 252861104 | OCB | 1104/2 | 20240119 | 1855 | 20240119 | 2204 | 2319421 | 189 | Distribution Circuit | 3rd Party | Vehicle | 29 | 5481 | 35.442 | -119.2608 | No | Overcast;32-90 F | Pole - Tower- steel | Broken- wire on ground | 24-0012799 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Multi-Fault | 0 | No | Yes | No | 1905136 | 0 | Non-EPSS | N | 2024 | BC GRD TIME
KERN | KERN | BAKERSFIELD-1102 | 253371102 | TRANSFORMER | 517029668622 | 20240119 | 2211 | 20240120 | 2 | 2319493 | 111 | Transformer only | Unknown Cause | Patrol - found nothing | 15 | 1665 | 35.3817 | -118.997 | No | Overcast;32-90 F |  |  | 24-0012848 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1905183 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1105 | 253181105 | FUSE | 18371 | 20240119 | 2345 | 20240120 | 250 | 2319500 | 185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 925 | 35.7177 | -119.3208 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0012844 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905180 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1110 | 253371110 | FUSE | 8813 | 20240120 | 252 | 20240120 | 1610 | 2319943 | 798 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 15162 | 35.3909 | -119.0084 | No | Overcast;32-90 F | Secondary | Broken | 24-0012965 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905264 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 2825 | 20240120 | 1533 | 20240120 | 1855 | 2320019 | 202 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 8780 | 35.3541 | -119.0675 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 24-0012991 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905277 | 1 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1104 | 253181104 | OCB | 1104/2 | 20240120 | 2335 | 20240121 | 202 | 2320235 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1531 | 225057 | 35.6882 | -119.2769 | No | Overcast-Fog;32-90 F | Other | Broken | 24-0013035 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905308 | 0 | Non-EPSS | N | 2024 | AB PH OC
KERN | KERN | TEJON-1105 | 252931105 | OCB | 1105/2 | 20240121 | 57 | 20240121 | 1258 | 2320247 | 721 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 42158 | 35.0198 | -118.9547 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 24-0013042 | OH | Sus | 31682200 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905315 | 0 | Non-EPSS | N | 2024 | AB PH OC INS
KERN | KERN | CAL WATER-1103 | 255451103 | INTERRUPTER | 81176 | 20240121 | 1315 | 20240121 | 1413 | 2320451 | 58 | Distribution Circuit | Equipment Failure/Involved | Underground | 124 | 7192 | 35.4074 | -118.8923 | No | Overcast;32-90 F | Interrupter | Malfunctioning | 24-0013108 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905368 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | FUSE | 9942 | 20240122 | 345 | 20240123 | 1304 | 2320898 | 1999 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 27986 | 35.5547 | -118.9017 | No | Clear;32-90 F |  |  | 24-0013233 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905463 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | OCB | 1104/2 | 20240122 | 512 | 20240122 | 541 | 2320916 | 29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 401 | 5905 | 35.3531 | -119.271 | No | Clear;32-90 F | Recloser | Failed/Faulted | 24-0013195 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Multi-Fault | 0 | No | No | No | 1905444 | 0 | Non-EPSS | N | 2024 | BC GRD TIME OC
KERN | KERN | TUPMAN-1104 | 254561104 | OCB | 1104/2 | 20240122 | 614 | 20240122 | 629 | s1905851 | 15 | Distribution Circuit | Equipment Failure/Involved | Overhead | 401 | 6015 | 35.3531 | -119.271 | No | Clear;32-90 F | Recloser | Failed/Faulted | 24-0013195 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905851 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | BAKERSFIELD-1105 | 253371105 | TRANSFORMER | 516956968781 | 20240122 | 941 | 20240122 | 1151 | 2321205 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 520 | 35.3853 | -119.0218 | No | Partly Cloudy-Rain;32-90 F | Fuse | Broken | 24-0013417 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905574 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARNERAS-1103 | 252321103 | TRANSFORMER | 514685375511 | 20240122 | 950 | 20240122 | 1407 | 2321219 | 257 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 257 | 35.5618 | -119.7884 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0013469 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905593 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CAL WATER-1103 | 255451103 | SWITCH | 19366 | 20240122 | 1029 | 20240122 | 1221 | 2321184 | 112 | Distribution Circuit | Equipment Failure/Involved | Underground | 428 | 24832 | 35.4088 | -118.8887 | No | Overcast-Drizzle;32-90 F | Interrupter | Malfunctioning | 24-0013207 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905525 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | SWITCH | 1204 | 20240122 | 1744 | 20240122 | 2357 | 2321716 | 373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 8206 | 35.7175 | -119.4785 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0013598 | OH | Sus | 35525575 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905635 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | OCB | 1102/2 | 20240123 | 1955 | 20240124 | 257 | 2322629 | 422 | Distribution Circuit | 3rd Party | Vehicle | 173 | 13228 | 35.2249 | -118.7784 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0014113 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905906 | 0 | EPSS Ckt | N | 2024 | NONE
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515639269506 | 20240124 | 741 | 20240124 | 931 | 2322811 | 110 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 1100 | 35.401 | -119.4645 | No | Overcast-Fog;32-90 F |  |  | 24-0014289 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1906036 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 14507 | 20240124 | 1012 | 20240124 | 1108 | 2323012 | 56 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 75 | 35.4538 | -118.9495 | No | Overcast;32-90 F |  |  | 24-0014357 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906060 | 1 | EPSS Ckt | N | 2024
KERN | KERN | TAFT-1103 | 252081103 | FUSE | 9149 | 20240125 | 755 | 20240125 | 851 | 2323678 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 112 | 35.1523 | -119.4828 | No | Partly Cloudy;32-90 F |  |  | 24-0014921 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906298 | 1 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1102 | 253801102 | SWITCH | 2076 | 20240125 | 1030 | 20240125 | 2221 | 2323979 | 711 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 12087 | 35.1579 | -118.8794 | No | Clear;32-90 F | Capacitor | Burned/flashed | 24-0014937 | OH | Sus | 35526303 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1906366 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | T85013 | 20240125 | 1055 | 20240125 | 1250 | 2324003 | 115 | Transformer only | 3rd Party | Other | 1 | 115 | 35.6938 | -119.2418 | No | Partly Cloudy;32-90 F | Customer Equipment | Broken | 24-0015147 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906403 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | TRANSFORMER | T0473 | 20240125 | 1630 | 20240125 | 1721 | 2324225 | 51 | Transformer only | Equipment Failure/Involved | Underground | 11 | 561 | 35.4017 | -118.946 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0015323 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906443 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7119 | 20240125 | 1653 | 20240127 | 1444 | 2324288 | 2751 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 11010 | 35.5719 | -119.5985 | No | Clear;32-90 F |  |  | 24-0015330 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906450 | 1 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1105 | 253951105 | TRANSFORMER | T1976 | 20240125 | 2011 | 20240125 | 2048 | 2324393 | 37 | Transformer only | Equipment Failure/Involved | Underground | 9 | 333 | 35.4091 | -118.943 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0015339 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1906457 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1101 | 252961101 | FUSE | 1169 | 20240125 | 2315 | 20240126 | 235 | 2324433 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3400 | 35.5753 | -119.3495 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0015378 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1906496 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1107 | 253371107 | OCB | 1107/2 | 20240126 | 130 | 20240126 | 136 | 2324449 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 698 | 4188 | 35.3886 | -119.0044 | No | Partly Cloudy-Fog;32-90 F | Capacitor | Broken | 24-0015392 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1906502 | 0 | Non-EPSS | N | 2024 | NA
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 11178 | 20240127 | 905 | 20240127 | 2324 | 2325480 | 859 | Distribution Circuit | Equipment Failure/Involved | Underground | 478 | 31772 | 35.3253 | -119.0641 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0015847 | UG | Sus | 35526556 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906845 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 15690 | 20240127 | 957 | 20240127 | 1407 | 2325519 | 250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 3250 | 35.2079 | -119.0746 | No | Clear;32-90 F |  |  | 24-0015858 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1906852 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517137468135 | 20240130 | 840 | 20240130 | 1139 | 2327966 | 179 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 179 | 35.3687 | -118.9609 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0016665 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907531 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516767463399 | 20240130 | 1914 | 20240131 | 247 | 2328569 | 453 | Transformer only | 3rd Party | Vehicle | 2 | 906 | 35.2374 | -119.0833 | No | Clear;32-90 F | Transformer | Broken | 24-0016908 | OH | Sus | 31682868 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907592 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | TRANSFORMER | 517544362837 | 20240131 | 137 | 20240131 | 322 | 2328763 | 105 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 735 | 35.2244 | -118.8228 | No | Clear;32-90 F |  |  | 24-0017003 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1907663 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | T7157 | 20240131 | 838 | 20240131 | 858 | 2329075 | 20 | Transformer only | Equipment Failure/Involved | Underground | 14 | 280 | 35.3927 | -119.1374 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0017082 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1907740 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | TRANSFORMER | 517216972760 | 20240131 | 1012 | 20240201 | 52 | 2329352 | 880 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 880 | 35.4951 | -118.9356 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0017320 | OH | Sus | 46175813 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907888 | 1 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1115 | 253371115 | OCB | 1115/2 | 20240131 | 1126 | 20240131 | 1356 | 2329490 | 150 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 848 | 123303 | 35.3887 | -119.0043 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0017242 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1907861 | 0 | Non-EPSS | N | 2024 | A- C- INST 50
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 13221 | 20240131 | 1144 | 20240131 | 1620 | 2329514 | 276 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 111 | 30636 | 35.3541 | -119.0017 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0017428 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1907928 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 9681 | 20240131 | 1206 | 20240131 | 1603 | 2329591 | 237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 4268 | 35.2378 | -118.9626 | No | Clear;32-90 F |  |  | 24-0017513 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907957 | 1 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | JUMPER | OPEN JUMPER @ CGC 517107562323 | 20240131 | 1308 | 20240131 | 1816 | 2329732 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3362 | 35.2085 | -118.9672 | No | Clear;32-90 F | Jumper | Broken | 24-0017434 | OH | Sus | 46175926 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1907930 | 1 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 14548 | 20240131 | 1400 | 20240131 | 2200 | 2329898 | 480 | Distribution Circuit | 3rd Party | Vehicle | 2 | 960 | 35.1942 | -119.0745 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0017446 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1907935 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1105 | 252931105 | FUSE | 9964 | 20240131 | 1434 | 20240131 | 2355 | 2329860 | 561 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1683 | 35.0454 | -118.9356 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0017726 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908122 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13342 | 20240131 | 1434 | 20240131 | 1947 | 2330145 | 313 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1878 | 35.0476 | -119.0296 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0017633 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908039 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | OCB | 2101/2 | 20240131 | 1509 | 20240131 | 1814 | 2329913 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 296 | 54760 | 34.9276 | -119.6203 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0017457 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1907936 | 0 | EPSS Ckt | N | 2024 | AB
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7292 | 20240131 | 1609 | 20240131 | 1948 | 2330011 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2045 | 35.7609 | -119.5625 | No | Overcast-Drizzle;32-90 F |  |  | 24-0017607 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1908023 | 1 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1110 | 253951110 | TRANSFORMER | 517159968823 | 20240131 | 1624 | 20240131 | 2102 | 2330009 | 278 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1112 | 35.3875 | -118.9536 | No | Clear;32-90 F | Secondary | Broken | 24-0017594 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1908010 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | JUMPER | BURNED OPEN JMPR 1 N/OF 14636 | 20240131 | 1654 | 20240131 | 1754 | 2330041 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 1260 | 35.3359 | -119.0166 | No | Clear;32-90 F | Jumper | Burned Open | 24-0017566 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1907983 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516978770346 | 20240131 | 1917 | 20240201 | 307 | 2330796 | 470 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 7454 | 35.4287 | -119.0145 | No | Clear-Strong Winds;32-90 F | Secondary | Together | 24-0017767 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908166 | 0 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1102 | 253191102 | OCB | 1102/2 | 20240131 | 1918 | 20240131 | 2055 | s1908378 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 4171 | 35.0921 | -118.8779 | No | Overcast-Strong Winds;32-90 F |  |  | 24-0017617 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1908378 | 0 | Non-EPSS | N | 2024 | FORCE OUT
KERN | KERN | LERDO-1112 | 253491112 | RECLOSER | 4323 | 20240131 | 2009 | 20240201 | 158 | 2330400 | 349 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 125 | 43625 | 35.5151 | -119.0819 | No | Partly Cloudy;32-90 F |  |  | 24-0017644 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | No | No | 1908048 | 0 | Non-EPSS | N | 2024 | A B C
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15062 | 20240131 | 2015 | 20240201 | 424 | 2330414 | 489 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 36409 | 35.3325 | -118.9142 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017721 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1908115 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 16407 | 20240131 | 2034 | 20240131 | 2234 | 2330440 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 4440 | 35.2608 | -118.9146 | No | Clear;32-90 F |  |  | 24-0017705 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908099 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1106 | 252771106 | FUSE | 14785 | 20240131 | 2134 | 20240201 | 403 | 2330386 | 389 | Distribution Circuit | Vegetation | Tree - grew into line | 15 | 5835 | 35.3834 | -118.939 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0017682 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1908078 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1105 | 252931105 | FUSE | 9964 | 20240201 | 40 | 20240201 | 916 | 2330711 | 516 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1548 | 35.0454 | -118.9356 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0017761 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1908160 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | FUSE | 13207 | 20240201 | 456 | 20240201 | 602 | 2330799 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 69 | 4554 | 35.3798 | -119.1173 | No | Overcast;32-90 F |  |  | 24-0017775 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908171 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 16241 | 20240201 | 514 | 20240201 | 701 | 2330808 | 107 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 428 | 35.4269 | -119.5169 | No | Overcast-Rain;32-90 F |  |  | 24-0017789 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908181 | 1 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1106 | 252441106 | RECLOSER | 556750 | 20240201 | 1117 | 20240207 | 1303 | 2331280 | 8746 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 39 | 51731 | 35.2376 | -119.3129 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 24-0017987 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908295 | 0 | Non-EPSS | N | 2024 | B & C
KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | 517473052410 | 20240201 | 1232 | 20240201 | 2230 | 2331363 | 598 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 598 | 34.9352 | -118.8438 | No | Rain-Overcast;32-90 F | Jumper | Broken | 24-0018218 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908360 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517048367615 | 20240201 | 1419 | 20240201 | 1509 | 2331418 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 550 | 35.3543 | -118.9902 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0018201 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908357 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514540681685 | 20240201 | 1423 | 20240201 | 2145 | 2331471 | 442 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 442 | 35.7312 | -119.8407 | No | Overcast-Drizzle;32-90 F | Service conductor | Broken | 24-0018369 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908437 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | FUSE | 15422 | 20240201 | 1549 | 20240201 | 2200 | 2331997 | 371 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1732 | 35.4261 | -118.8193 | No | Overcast-Fog-Lightning;Below 32 F |  |  | 24-0018371 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908440 | 1 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516961367768 | 20240201 | 1611 | 20240201 | 2244 | 2331683 | 393 | Transformer only | Environmental/External | Lightning | 16 | 6288 | 35.358 | -119.0196 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018313 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908388 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1103 | 253651103 | FUSE | 79677 | 20240201 | 1612 | 20240202 | 125 | 2331684 | 553 | Distribution Circuit | Environmental/External | Lightning | 27 | 12981 | 35.5216 | -119.3137 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018324 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1908394 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516958067774 | 20240201 | 1617 | 20240202 | 109 | 2331693 | 532 | Transformer only | Environmental/External | Lightning | 16 | 8512 | 35.3585 | -119.0207 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018297 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908379 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516961467787 | 20240201 | 1619 | 20240202 | 452 | 2331699 | 753 | Transformer only | Environmental/External | Lightning | 7 | 5271 | 35.3584 | -119.0196 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 24-0018322 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908392 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 12587 | 20240201 | 1628 | 20240202 | 14 | 2331714 | 466 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 23766 | 35.3545 | -119.0784 | No | Overcast-Rain;32-90 F |  |  | 24-0018381 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908442 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 14865 | 20240201 | 1640 | 20240201 | 1959 | 2331935 | 199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 994 | 35.3613 | -118.9665 | No | Overcast-Rain-Lightning;32-90 F |  |  | 24-0018337 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908404 | 1 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516962467822 | 20240201 | 1648 | 20240202 | 257 | 2331746 | 609 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3654 | 35.3593 | -119.0195 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 24-0018340 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908407 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1106 | 254071106 | SWITCH | 10009 | 20240201 | 1708 | 20240201 | 1719 | 2331822 | 11 | Distribution Circuit | 3rd Party | Vehicle | 129 | 1419 | 35.3215 | -119.0521 | No | Overcast-Drizzle-Lightning;32-90 F | Pole-Wood | Broken | 24-0017921 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1908376 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516961467858 | 20240201 | 1715 | 20240202 | 39 | 2331831 | 444 | Transformer only | Environmental/External | Lightning | 8 | 3552 | 35.3604 | -119.0195 | No | Overcast-Drizzle-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018345 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908414 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516961367763 | 20240201 | 1733 | 20240202 | 433 | 2331687 | 660 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 660 | 35.3578 | -119.0196 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 24-0018310 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908385 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | SWITCH | 17207 | 20240201 | 1803 | 20240202 | 251 | 2331855 | 525 | Distribution Circuit | 3rd Party | Vehicle | 299 | 156939 | 35.3252 | -119.0562 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0017921 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1908384 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516961467807 | 20240201 | 1859 | 20240201 | 2333 | 2331920 | 274 | Transformer only | Environmental/External | Lightning | 3 | 822 | 35.359 | -119.0195 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018330 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908399 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517384467336 | 20240202 | 416 | 20240202 | 912 | 2332107 | 296 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 296 | 35.3472 | -118.8779 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018399 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908460 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 7547 | 20240202 | 748 | 20240202 | 935 | 2332185 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 714 | 35.6019 | -119.2644 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0018516 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908580 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1106 | 254071106 | SWITCH | 10009 | 20240202 | 957 | 20240202 | 1005 | s1908637 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 129 | 1032 | 35.3215 | -119.0521 | No | Overcast-Drizzle-Lightning;32-90 F | Pole-Wood | Normal | 24-0017921 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1908637 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1101 | 252861101 | FUSE | 96337 | 20240202 | 1105 | 20240202 | 2202 | 2332457 | 657 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1314 | 35.4997 | -119.2678 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0018606 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1908606 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517161967757 | 20240202 | 1249 | 20240202 | 1348 | 2332576 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 177 | 35.3581 | -118.9525 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0018720 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908643 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | FUSE | 9267 | 20240202 | 1747 | 20240202 | 1939 | 2333202 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 6798 | 35.2969 | -119.3767 | No | Partly Cloudy;32-90 F |  |  | 24-0018854 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908713 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | RECLOSER | 90940 | 20240203 | 149 | 20240203 | 1648 | 2333379 | 890 | Distribution Circuit | 3rd Party | Vehicle | 952 | 267218 | 35.2671 | -118.9006 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0018891 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1908751 | 0 | Non-EPSS | N | 2024 | B & GRD
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 16809 | 20240203 | 734 | 20240203 | 900 | 2333424 | 86 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 30 | 2580 | 35.3843 | -119.0105 | No | Overcast;32-90 F | Secondary | Burned/flashed | 24-0018911 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1908809 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 16365 | 20240203 | 1122 | 20240203 | 1357 | 2333724 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 930 | 35.6011 | -119.4558 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 24-0018946 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1908848 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-2102 | 254762102 | OTHER | T7581 TWD T6990 | 20240203 | 1234 | 20240203 | 1743 | 2333667 | 309 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 309 | 35.3663 | -119.0604 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0018930 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1908842 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 16365 | 20240203 | 1401 | 20240203 | 1447 | 2333732 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 184 | 35.6011 | -119.4558 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0018948 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908854 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 14532 | 20240203 | 1534 | 20240203 | 1756 | s1908867 | 142 | Distribution Circuit | Animal | Bird found | 57 | 8094 | 35.3509 | -119.1546 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0018969 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1908867 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1111 | 253491111 | OTHER | WIRE DOWN @ CGC #516289073012 | 20240203 | 2010 | 20240204 | 332 | 2333899 | 442 | Distribution Circuit | 3rd Party | Vehicle | 166 | 21839 | 35.4997 | -119.2477 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0018977 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | Yes | 1908870 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 565211 | 20240204 | 335 | 20240204 | 1014 | 2334308 | 399 | Distribution Circuit | 3rd Party | Gun Shot | 37 | 14763 | 35.2305 | -119.0213 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019121 | OH | Sus | 31683344 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909008 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15041 | 20240204 | 411 | 20240204 | 733 | 2334336 | 202 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 22 | 4444 | 35.3054 | -118.9145 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019222 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909113 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | RECLOSER | 1497 | 20240204 | 514 | 20240204 | 724 | 2334450 | 130 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 3510 | 35.4022 | -119.5185 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0019143 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909030 | 0 | Non-EPSS | N | 2024 | B & C
KERN | KERN | TEMBLOR-1104 | 252551104 | FUSE | 17872 | 20240204 | 658 | 20240205 | 1619 | 2338923 | 2001 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 9343 | 35.3975 | -119.7532 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0022427 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912074 | 1 | EPSS Ckt | N | 2024
KERN | KERN | CUYAMA-2102 | 253142102 | OTHER | WIRE DOWN @ CGC 515458552566 | 20240204 | 720 | 20240204 | 2212 | 2335358 | 892 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 37457 | 34.935 | -119.5243 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019288 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | Yes | 1909176 | 1 | EPSS Ckt | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | JUMPER | 14680 #1 JUMPER | 20240204 | 756 | 20240204 | 1107 | 2335963 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1528 | 35.2234 | -119.1027 | Yes | Clear;32-90 F | Jumper | Burned Open | 24-0019356 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1909238 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | RECLOSER | 3776 | 20240204 | 800 | 20240204 | 1712 | s1910669 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 27600 | 35.1108 | -119.1095 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0019264 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910669 | 0 | Non-EPSS | N | 2024 | AC
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 13094 | 20240204 | 804 | 20240204 | 1725 | 2335186 | 561 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2708 | 35.1206 | -118.9324 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019381 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1909265 | 1 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1104 | 253141104 | FUSE | 9212 | 20240204 | 807 | 20240208 | 1147 | 2335231 | 5980 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 53820 | 34.9275 | -119.6963 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019584 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909455 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 16320 | 20240204 | 823 | 20240204 | 1648 | 2335336 | 505 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 168 | 84840 | 35.2549 | -118.9151 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0019414 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909295 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | JUMPER | 13090 #3 SS JUMPER | 20240204 | 838 | 20240204 | 1805 | 2335531 | 564 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 5640 | 35.1222 | -118.9675 | Yes | Clear;32-90 F | Jumper | Burned Open | 24-0019535 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1909406 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 57521 | 20240204 | 853 | 20240204 | 1549 | 2335755 | 416 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1248 | 35.4424 | -119.4839 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0020233 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910060 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1106 | 252771106 | OCB | 1880 | 20240204 | 854 | 20240206 | 1855 | 2335763 | 3446 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1618 | 1215978 | 35.3764 | -118.915 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019333 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1909216 | 0 | Non-EPSS | N | 2024 | A- B- C
KERN | KERN | MAGUNDEN-1106 | 252771106 | OTHER | NG CABLE BET 11138 & T6595 | 20240204 | 854 | 20240205 | 2054 | 2336065 | 2160 | Distribution Circuit | Equipment Failure/Involved | Underground | 65 | 140400 | 35.3993 | -118.9209 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Underground | Deteriorated | 24-0021474 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1911893 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 9452 | 20240204 | 904 | 20240206 | 1828 | 2335912 | 3444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 30996 | 34.9843 | -118.8731 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022487 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1912124 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 684566 | 20240204 | 905 | 20240206 | 1337 | 2335967 | 3152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 18912 | 35.0707 | -119.9955 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0019332 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909239 | 0 | EPSS Ckt | N | 2024 | BC
KERN | KERN | SHAFTER-1102 | 253651102 | FUSE | 727727 | 20240204 | 916 | 20240205 | 2115 | 2336116 | 2159 | Distribution Circuit | Animal | Other | 2 | 4318 | 35.5292 | -119.2516 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Fuse | Burned Open | 24-0022779 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1912415 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1103 | 253651103 | FUSE | 79677 | 20240204 | 916 | 20240204 | 1022 | 2336113 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 1782 | 35.5216 | -119.3137 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0019490 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909363 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | RECLOSER | 1609 | 20240204 | 920 | 20240205 | 135 | 2336240 | 975 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 9810 | 35.0955 | -118.9818 | Yes | Overcast-Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0019395 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909280 | 0 | Non-EPSS | N | 2024 | B & C
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 16471 | 20240204 | 929 | 20240205 | 53 | 2336329 | 924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 259 | 34744 | 35.3179 | -119.1402 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019452 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909327 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 8694 | 20240204 | 934 | 20240205 | 209 | 2338113 | 995 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 8955 | 35.2236 | -119.2072 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019595 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909465 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 87257 | 20240204 | 934 | 20240204 | 1858 | 2336381 | 564 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 41 | 23124 | 35.3103 | -119.0247 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0020806 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910625 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | 517240451120 | 20240204 | 936 | 20240206 | 1535 | 2336838 | 3239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3239 | 34.9019 | -118.922 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0022600 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912230 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | FUSE | 9267 | 20240204 | 937 | 20240205 | 330 | 2336420 | 1073 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 65128 | 35.2969 | -119.3767 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0021438 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911273 | 1 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 16652 | 20240204 | 943 | 20240206 | 1534 | 2337664 | 3231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3231 | 34.9918 | -118.9659 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0021151 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910976 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13338 | 20240204 | 948 | 20240204 | 1912 | 2336598 | 562 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 5058 | 35.0765 | -119.0204 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020842 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910660 | 0 | EPSS Ckt | N | 2024
KERN | KERN | COLUMBUS-1104 | 253951104 | FUSE | 8056 | 20240204 | 953 | 20240204 | 1251 | 2336659 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 19936 | 35.3921 | -118.9676 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019520 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909395 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 16034 | 20240204 | 1004 | 20240204 | 1801 | 2336936 | 477 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 5247 | 35.2381 | -119.0995 | Yes | Overcast;32-90 F |  |  | 24-0020645 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910464 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1109 | 253951109 | FUSE | 9465 | 20240204 | 1010 | 20240205 | 524 | 2336946 | 1152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 29952 | 35.3871 | -118.9357 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021463 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911298 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | FUSE | 17565 | 20240204 | 1011 | 20240204 | 1145 | 2337002 | 94 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 1254 | 35.4046 | -118.9489 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019620 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1909483 | 1 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 7540 | 20240204 | 1013 | 20240206 | 1232 | 2336992 | 3019 | Distribution Circuit | Environmental/External | Water | 12 | 19717 | 35.4637 | -119.3144 | Yes | Overcast;32-90 F | Pole-Wood | Broken | 24-0021757 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911513 | 1 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1103 | 255451103 | RECLOSER | 768902 | 20240204 | 1019 | 20240204 | 1310 | 2337085 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2067 | 303017 | 35.4021 | -118.914 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0019485 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1909357 | 0 | Non-EPSS | N | 2024 | A B C
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 14773 | 20240204 | 1022 | 20240206 | 330 | 2337124 | 2468 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 32084 | 35.0174 | -118.9087 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0021923 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1911654 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | JUMPER | 517095869408 | 20240204 | 1023 | 20240204 | 1544 | 2337146 | 321 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 21816 | 35.4035 | -118.9749 | Yes | Clear-Strong Winds;32-90 F | Jumper | Burned Open | 24-0020190 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1910015 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 16158 | 20240204 | 1024 | 20240205 | 109 | 2337170 | 885 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 91 | 80535 | 35.3439 | -119.0747 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0021279 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911111 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | JUMPER | OJS 3 SPANS SOUTH OF CGC 517207268013 | 20240204 | 1025 | 20240205 | 1344 | 2337183 | 1639 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 24585 | 35.3652 | -118.9371 | Yes | Clear-Strong Winds;32-90 F | Secondary | Deteriorated | 24-0021658 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1911444 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | RECLOSER | 286542 | 20240204 | 1026 | 20240206 | 353 | 2337237 | 2487 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 37305 | 35.0245 | -118.7714 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019503 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1909376 | 0 | EPSS Ckt | N | 2024 | SGF
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 7139 | 20240204 | 1027 | 20240205 | 1740 | 2337219 | 1873 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 13111 | 35.3701 | -119.3996 | Yes | Clear;32-90 F |  |  | 24-0022594 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1912222 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 15164 | 20240204 | 1029 | 20240207 | 1505 | 2337238 | 4596 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 13788 | 35.5284 | -119.5484 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0024369 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1913541 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1101 | 252861101 | RECLOSER | 2638 | 20240204 | 1032 | 20240204 | 1231 | 2337279 | 119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 942 | 112098 | 35.4642 | -119.2611 | Yes | Overcast-Strong Winds;32-90 F | Anchor or Guy | Broken | 24-0019502 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1909385 | 0 | Non-EPSS | N | 2024 | B-GRD
KERN | KERN | TUPMAN-1103 | 254561103 | FUSE | 13287 | 20240204 | 1038 | 20240204 | 1814 | 2337386 | 456 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 4560 | 35.368 | -119.2343 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020028 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909860 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1103 | 252461103 | RECLOSER | 3652 | 20240204 | 1048 | 20240205 | 912 | 2337580 | 1344 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 110 | 147840 | 35.6023 | -119.1425 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0019534 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1909405 | 0 | Non-EPSS | N | 2024 | A B C
KERN | KERN | OLD RIVER-1102 | 252821102 | RECLOSER | 3310 | 20240204 | 1050 | 20240207 | 128 | 2336945 | 3758 | Distribution Circuit | Equipment Failure/Involved | Overhead | 352 | 198966 | 35.2085 | -119.0417 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0019539 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1909410 | 0 | Non-EPSS | N | 2024 | SGF
KERN | KERN | FAMOSO-1101 | 252461101 | FUSE | 18711 | 20240204 | 1057 | 20240205 | 1653 | 2337696 | 1796 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 19756 | 35.6353 | -119.1245 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022455 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1912095 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516961566675 | 20240204 | 1058 | 20240205 | 1826 | 2354930 | 1888 | Transformer only | Vegetation | Tree - fell into line | 12 | 22650 | 35.3278 | -119.0189 | Yes | Clear;32-90 F | Secondary | Normal | 24-0021142 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910966 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1101 | 253371101 | OCB | 1101/2 | 20240204 | 1059 | 20240204 | 1217 | 2337731 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 937 | 73086 | 35.3885 | -119.0044 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0019561 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909429 | 0 | Non-EPSS | N | 2024 | A & B
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7119 | 20240204 | 1102 | 20240208 | 1154 | 2337746 | 5812 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 34872 | 35.5719 | -119.5985 | Yes | Overcast;32-90 F | Fuse | Burned Open | 24-0026249 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1915119 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | FUSE | 16099 | 20240204 | 1103 | 20240206 | 654 | 2337782 | 2631 | Distribution Circuit | Environmental/External | Water | 4 | 10513 | 35.6014 | -119.6175 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Deteriorated | 24-0022854 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912489 | 1 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 17608 | 20240204 | 1108 | 20240205 | 1145 | 2338283 | 1477 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 14770 | 34.9053 | -119.5547 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0021864 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911600 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | TRIP-SAVER | 2455 | 20240204 | 1109 | 20240205 | 1257 | 2337880 | 1548 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 271 | 419508 | 34.8582 | -118.8838 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0021836 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911581 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | RENFRO-2101 | 254572101 | RECLOSER | 134422 | 20240204 | 1110 | 20240204 | 2308 | 2337901 | 718 | Distribution Circuit | Vegetation | Tree - fell into line | 1688 | 967347 | 35.3688 | -119.1867 | Yes | Overcast-Strong Winds;32-90 F | Switch (OH) | Normal | 24-0019571 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909440 | 0 | Non-EPSS | N | 2024 | B & C
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 517000067738 | 20240204 | 1115 | 20240204 | 2043 | 2337963 | 568 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 7952 | 35.357 | -119.0065 | Yes | Strong Winds-Clear;32-90 F | Transformer | Contaminated | 24-0020552 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910375 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 42873 | 20240204 | 1115 | 20240204 | 1843 | 2337973 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3584 | 35.38 | -119.1813 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020299 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910128 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1104 | 253391104 | FUSE | 16660 | 20240204 | 1121 | 20240204 | 1732 | 2338038 | 371 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 10759 | 35.4227 | -119.0746 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020607 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910427 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | FUSE | 15963 | 20240204 | 1126 | 20240204 | 1730 | 2338091 | 364 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 21840 | 35.2018 | -118.8241 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0020586 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910408 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 7575 | 20240204 | 1132 | 20240205 | 1025 | 2338154 | 1373 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 8242 | 35.4999 | -119.2191 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0021763 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1911518 | 1 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 16751 | 20240204 | 1138 | 20240204 | 2213 | 2341181 | 635 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 8142 | 35.0595 | -119.0268 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020474 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910299 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 18146 | 20240204 | 1145 | 20240206 | 1302 | 2354415 | 2955 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 14775 | 35.3835 | -119.2032 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021167 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1910992 | 0 | Non-EPSS | N | 2024
KERN | KERN | BLACKWELL-2101 | 254682101 | FUSE | 526889 | 20240204 | 1150 | 20240205 | 2000 | 2357791 | 1930 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1930 | 35.6157 | -119.7151 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021580 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1911393 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1110 | 253951110 | FUSE | 14191 | 20240204 | 1150 | 20240204 | 1313 | 2335380 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 1826 | 35.3836 | -118.9494 | Yes | Overcast-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0019611 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909478 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 14918 | 20240204 | 1153 | 20240204 | 2150 | 2338771 | 597 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 11343 | 35.3467 | -119.0437 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021153 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910978 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 9835 | 20240204 | 1200 | 20240204 | 2327 | 2338754 | 687 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 81 | 55647 | 35.3725 | -119.1108 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021272 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911104 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 17531 | 20240204 | 1200 | 20240205 | 1030 | 2338756 | 1350 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 23700 | 35.2307 | -119.0922 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020083 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1909911 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2103 | 254242103 | FUSE | 16518 | 20240204 | 1205 | 20240205 | 1641 | 2338812 | 1716 | Distribution Circuit | 3rd Party | Other | 78 | 77778 | 35.2481 | -119.5952 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020852 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1910671 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8150 | 20240204 | 1205 | 20240205 | 1805 | 2361525 | 1800 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 34200 | 35.3518 | -119.0758 | Yes | Clear;32-90 F |  |  | 24-0022558 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1912184 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1103 | 254561103 | FUSE | 13291 | 20240204 | 1205 | 20240204 | 1724 | 2338871 | 319 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 7337 | 35.3963 | -119.2153 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020258 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910087 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517171367830 | 20240204 | 1207 | 20240204 | 2210 | 2338823 | 603 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 3618 | 35.3605 | -118.9492 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021225 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911053 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | OCB | 1102/2 | 20240204 | 1208 | 20240205 | 248 | 2340201 | 880 | Distribution Circuit | Equipment Failure/Involved | Overhead | 311 | 80250 | 35.0891 | -118.9767 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020014 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909848 | 0 | Non-EPSS | N | 2024 | BC
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516695064435 | 20240204 | 1210 | 20240204 | 2342 | 2339361 | 692 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 6228 | 35.2656 | -119.1075 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0019923 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1909756 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 16318 | 20240204 | 1212 | 20240205 | 429 | 2338818 | 977 | Distribution Circuit | 3rd Party | Other | 105 | 24735 | 35.2556 | -118.9138 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0019697 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909551 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2105 | 255322105 | OCB | 2105/2 | 20240204 | 1212 | 20240204 | 2030 | 2338901 | 498 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2979 | 333791 | 35.3194 | -119.1291 | Yes | Partly Cloudy-Strong Winds;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0019750 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1909598 | 0 | Non-EPSS | N | 2024 | AB & C
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 18451 | 20240204 | 1213 | 20240205 | 1518 | 2338910 | 1625 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 14625 | 35.6884 | -119.5087 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0022277 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911930 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | TRIP-SAVER | 4059 | 20240204 | 1216 | 20240205 | 1455 | 2354829 | 1599 | Distribution Circuit | Equipment Failure/Involved | Overhead | 178 | 182200 | 35.4359 | -118.9498 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021122 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1910945 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 91109 | 20240204 | 1222 | 20240204 | 2302 | 2339078 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 44135 | 35.3786 | -119.1899 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019941 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909772 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1104 | 252961104 | RECLOSER | 1269 | 20240204 | 1225 | 20240204 | 2015 | 2339119 | 470 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 620 | 291400 | 35.5929 | -119.3404 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0019745 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1909593 | 0 | Non-EPSS | N | 2024 | A B C
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 4525 | 20240204 | 1226 | 20240206 | 126 | 2339232 | 2220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 48840 | 34.9719 | -118.9397 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019774 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1909620 | 0 | EPSS Ckt | N | 2024 | ABC
KERN | KERN | MC FARLAND-1102 | 253181102 | FUSE | 15992 | 20240204 | 1228 | 20240205 | 1415 | 2339134 | 1547 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 12376 | 35.7104 | -119.366 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0022172 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911850 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2104 | 255322104 | RECLOSER | 4401 | 20240204 | 1236 | 20240204 | 1259 | 2338261 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2058 | 47334 | 35.3395 | -119.1281 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019706 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909565 | 0 | Non-EPSS | N | 2024 | FORCE OUT
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 122865 | 20240204 | 1236 | 20240204 | 2023 | 2336706 | 467 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2802 | 35.34 | -119.1496 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0020987 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910809 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | TRANSFORMER | 517183172635 | 20240204 | 1239 | 20240205 | 1538 | 2356595 | 1619 | Transformer only | Vegetation | Other ground vegetation | 1 | 1619 | 35.4918 | -118.9463 | Yes | Partly Cloudy-Strong Winds;32-90 F | Transformer (OH) | Burned/flashed | 24-0022309 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911962 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-1108 | 252771108 | FUSE | 15342 | 20240204 | 1239 | 20240207 | 55 | 2339278 | 3616 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 18080 | 35.3691 | -118.8547 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021815 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1911562 | 0 | EPSS Ckt | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | RECLOSER | 274456 | 20240204 | 1253 | 20240206 | 1616 | 2339658 | 3083 | Distribution Circuit | Environmental/External | Water | 9 | 27747 | 35.2366 | -119.5996 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019790 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1909635 | 0 | EPSS Ckt | N | 2024 | A-GRD
KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | 517168050770 | 20240204 | 1253 | 20240206 | 2142 | 2342614 | 3409 | Transformer only | Environmental/External | Water | 1 | 3409 | 34.8887 | -118.9491 | Yes | Strong Winds-Overcast-Heavy Rain;32-90 F | Transformer | Normal | 24-0022317 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911970 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN OIL-1110 | 252721110 | TRANSFORMER | 516911670216 | 20240204 | 1317 | 20240205 | 204 | 2356329 | 767 | Transformer only | Vegetation | Tree - fell into line | 11 | 8437 | 35.4249 | -119.0373 | Yes | Overcast-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0021421 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911256 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | RECLOSER | 1103/2 | 20240204 | 1321 | 20240204 | 2213 | 2338904 | 532 | Distribution Circuit | Equipment Failure/Involved | Overhead | 283 | 64740 | 35.442 | -119.2606 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019854 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909692 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 16268 | 20240204 | 1330 | 20240204 | 1645 | 2340075 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 650 | 35.209 | -119.1416 | Yes | Clear;32-90 F |  |  | 24-0020473 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910298 | 1 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1103 | 252861103 | TRANSFORMER | 516416170962 | 20240204 | 1336 | 20240205 | 1200 | 2348118 | 1344 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4032 | 35.4435 | -119.2038 | Yes | Overcast-Strong Winds;32-90 F | Secondary | Broken | 24-0020577 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910400 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1104 | 253651104 | RECLOSER | 1419 | 20240204 | 1337 | 20240204 | 2114 | 2342446 | 457 | Distribution Circuit | 3rd Party | Other | 1093 | 438427 | 35.5071 | -119.3117 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020726 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910546 | 0 | Non-EPSS | N | 2024 | AB
KERN | KERN | RENFRO-2107 | 254572107 | RECLOSER | 515188 | 20240204 | 1340 | 20240204 | 1453 | 2340371 | 73 | Distribution Circuit | Vegetation | Tree - fell into line | 2977 | 217321 | 35.4016 | -119.1632 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019988 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1909822 | 0 | Non-EPSS | N | 2024 | ABC
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 93603 | 20240204 | 1352 | 20240204 | 1950 | 2341165 | 358 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 358 | 35.0763 | -119.0305 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0020887 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910706 | 1 | EPSS Ckt | N | 2024
KERN | KERN | KERN POWER-2103 | 255262103 | FUSE | 16276 | 20240204 | 1407 | 20240204 | 2212 | 2341005 | 485 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 44620 | 35.3842 | -119.1101 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0021176 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911001 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1102 | 252961102 | JUMPER | OJS 1P W/OF 684627 | 20240204 | 1413 | 20240204 | 2225 | 2354990 | 492 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 86196 | 35.5865 | -119.3512 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Jumper | Broken | 24-0021166 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1910991 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 517107057649 | 20240204 | 1413 | 20240204 | 2037 | 2341180 | 384 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 1152 | 35.0799 | -118.9676 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0020998 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1910820 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | TRANSFORMER | 517036769042 | 20240204 | 1415 | 20240204 | 1754 | 2341696 | 219 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 3504 | 35.393 | -118.9946 | Yes | Strong Winds-Overcast;32-90 F | Cutout- fuse holder | Broken | 24-0020005 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1909839 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | WIRE DOWN HOT @ CGC #516532169028 | 20240204 | 1425 | 20240205 | 2040 | 2355376 | 1815 | Transformer only | Equipment Failure/Involved | Overhead | 105 | 190575 | 35.3909 | -119.1643 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021281 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | Yes | 1911113 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1106 | 252931106 | OCB | 1106/2 | 20240204 | 1427 | 20240205 | 1932 | 2341835 | 1745 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 99018 | 35.0198 | -118.9547 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020032 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909863 | 0 | Non-EPSS | N | 2024 | BC
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 79649 | 20240204 | 1439 | 20240204 | 2126 | 2354414 | 407 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 4337 | 35.3837 | -119.1989 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0021080 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910902 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | SWITCH | 19241 | 20240204 | 1459 | 20240204 | 1921 | 2336687 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 349 | 35526 | 35.3665 | -119.1102 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019987 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909821 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 16261 | 20240204 | 1501 | 20240204 | 1842 | 2342504 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2431 | 35.2456 | -119.1078 | Yes | Clear;32-90 F |  |  | 24-0020788 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910607 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | RECLOSER | 957534 | 20240204 | 1505 | 20240205 | 1429 | 2340795 | 1404 | Distribution Circuit | Vegetation | Tree - fell into line | 1244 | 201724 | 35.3981 | -119.1212 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020104 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909933 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | TEVIS-2104 | 255322104 | SWITCH | 19079 | 20240204 | 1507 | 20240205 | 342 | 2342199 | 755 | Distribution Circuit | Equipment Failure/Involved | Overhead | 176 | 55624 | 35.3398 | -119.1451 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019706 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909893 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 18961 | 20240204 | 1520 | 20240205 | 515 | 2337533 | 835 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 5010 | 35.2381 | -119.07 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0020140 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909969 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | FUSE | 17005 | 20240204 | 1554 | 20240206 | 245 | 2344902 | 2090 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 10450 | 34.9417 | -118.9316 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022640 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1912271 | 1 | EPSS Ckt | N | 2024
KERN | KERN | SHAFTER-1103 | 253651103 | RECLOSER | 1195 | 20240204 | 1555 | 20240205 | 1823 | 2345093 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 102239 | 35.529 | -119.3313 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020285 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910114 | 0 | Non-EPSS | N | 2024 | A C
KERN | KERN | SMYRNA-1101 | 253551101 | OCB | 1101/2 | 20240204 | 1607 | 20240207 | 1847 | 2346141 | 4480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 156258 | 35.7178 | -119.4554 | Yes | Overcast-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0020357 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1910185 | 0 | Non-EPSS | N | 2024 | B GRD TIME
KERN | KERN | TUPMAN-1103 | 254561103 | JUMPER | WIRE DOWN 1 SP @ L1083 | 20240204 | 1621 | 20240205 | 1220 | 2346140 | 1029 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 85222 | 35.4053 | -119.2268 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020740 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | Yes | 1910560 | 1 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1104 | 253181104 | TRANSFORMER | 516323178324 | 20240204 | 1706 | 20240205 | 1622 | 2348040 | 1396 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1396 | 35.6458 | -119.2381 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0021856 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911595 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13393 | 20240204 | 1722 | 20240204 | 2348 | 2348740 | 386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1287 | 35.1939 | -118.9675 | Yes | Clear;32-90 F | Jumper | Burned Open | 24-0020721 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910541 | 1 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1101 | 253191101 | SWITCH | 2268 | 20240204 | 1723 | 20240206 | 911 | 2361184 | 2388 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 14328 | 35.0819 | -118.875 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0022443 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1912087 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MARICOPA-1102 | 254211102 | RECLOSER | 3558 | 20240204 | 1731 | 20240205 | 936 | 2349269 | 965 | Distribution Circuit | Vegetation | Tree - branch fell on line | 192 | 185280 | 35.0639 | -119.4065 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020589 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910411 | 0 | EPSS Ckt | N | 2024 | B & C
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 18025 | 20240204 | 1734 | 20240205 | 1435 | 2347611 | 1261 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 5044 | 35.7103 | -119.437 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0022197 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911869 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17784 | 20240204 | 1742 | 20240204 | 2315 | 2349481 | 333 | Distribution Circuit | Animal | Bird found | 70 | 23398 | 35.3447 | -119.0708 | Yes | Overcast-Strong Winds;32-90 F | Transformer (OH) | Normal | 24-0021261 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911093 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1104 | 252771104 | FUSE | 15422 | 20240204 | 1756 | 20240206 | 930 | 2363534 | 2374 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 11084 | 35.4261 | -118.8193 | Yes | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0023048 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912618 | 1 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 639921 | 20240204 | 1838 | 20240205 | 707 | 2351075 | 749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 22657 | 35.2306 | -119.1018 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021136 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1910959 | 0 | Non-EPSS | N | 2024 | ABC
KERN | KERN | SAN BERNARD-1104 | 253191104 | SWITCH | 2092 | 20240204 | 1913 | 20240206 | 229 | 2361909 | 1876 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 68988 | 35.0928 | -118.8802 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0022614 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1912274 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 16651 | 20240204 | 1949 | 20240206 | 1742 | 2353214 | 2753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 16518 | 34.9939 | -118.9667 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Burned/flashed | 24-0022355 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1912007 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516997067738 | 20240204 | 2059 | 20240204 | 2133 | 2354280 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 408 | 35.3571 | -119.0075 | Yes | Overcast-Drizzle;32-90 F | Secondary | Broken | 24-0021035 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1910858 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | SWITCH | 4838 | 20240204 | 2204 | 20240206 | 1428 | 2355056 | 2424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2482 | 35.2313 | -119.5983 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 24-0021186 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1911012 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | RECLOSER | 3351 | 20240204 | 2257 | 20240205 | 1902 | 2347648 | 1205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 32535 | 35.3836 | -119.1615 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0021245 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1911076 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | RIO BRAVO-1102 | 252861102 | JUMPER | BURNT OJ 1 N/OF 7129 W PH | 20240204 | 2307 | 20240205 | 1551 | 2357816 | 1004 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 23033 | 35.4985 | -119.2777 | Yes | Partly Cloudy-Fog;32-90 F | Jumper | Burned Open | 24-0021824 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1911571 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | JUMPER | OPEN JUMPERS N/OF CGC#516460367900 | 20240205 | 319 | 20240206 | 252 | 2356501 | 1413 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1413 | 35.3599 | -119.1881 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0021487 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911323 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | 516460367900 | 20240205 | 503 | 20240206 | 252 | 2356881 | 1309 | Transformer only | Vegetation | Tree - bark fell into line | 2 | 2618 | 35.3599 | -119.1881 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0021679 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911459 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 423605 | 20240205 | 658 | 20240205 | 1322 | 2357287 | 384 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 5760 | 35.4199 | -119.243 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0022041 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911753 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13394 | 20240205 | 725 | 20240206 | 1530 | 2359640 | 1925 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 12793 | 35.2085 | -118.9672 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0022163 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911841 | 1 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 16036 | 20240205 | 804 | 20240205 | 1349 | 2357775 | 345 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1725 | 35.2271 | -119.1015 | No | Clear;32-90 F |  |  | 24-0022047 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911758 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1101 | 252861101 | OCB | 1101/2 | 20240205 | 934 | 20240206 | 1238 | 2357411 | 1624 | Distribution Circuit | Environmental/External | Water | 1019 | 15218 | 35.442 | -119.2606 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0021706 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1911476 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 18304 | 20240205 | 1141 | 20240205 | 1831 | 2361641 | 410 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 820 | 35.0582 | -118.9759 | No | Overcast-Drizzle;32-90 F |  |  | 24-0022590 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912218 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | 517558066302 | 20240205 | 1144 | 20240205 | 1933 | 2359335 | 469 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 469 | 35.3192 | -118.8182 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 24-0022664 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912299 | 0 | EPSS Ckt | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516740763183 | 20240205 | 1157 | 20240206 | 1800 | 2359427 | 1803 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 5409 | 35.2314 | -119.0923 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0022242 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911906 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 15036 | 20240205 | 1229 | 20240206 | 1700 | 2362272 | 1711 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2367 | 34.984 | -118.8643 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0022792 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912427 | 1 | EPSS Ckt | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 515847569922 | 20240205 | 1358 | 20240206 | 851 | 2360141 | 1133 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1133 | 35.4138 | -119.3942 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0022618 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912245 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1109 | 253951109 | FUSE | 11136 | 20240205 | 1419 | 20240205 | 1430 | 2360325 | 11 | Distribution Circuit | Equipment Failure/Involved | Underground | 94 | 1034 | 35.3983 | -118.9217 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 24-0021474 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1911888 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516393462635 | 20240205 | 1448 | 20240206 | 1625 | 2360406 | 1537 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4611 | 35.2152 | -119.2083 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0022331 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911984 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 516993162131 | 20240205 | 1459 | 20240206 | 512 | 2360457 | 853 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1706 | 35.2027 | -119.0075 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0022730 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912365 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 516926058180 | 20240205 | 1924 | 20240206 | 1601 | 2360234 | 1237 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3711 | 35.0935 | -119.0287 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0022663 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912298 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 9451 | 20240205 | 2023 | 20240205 | 2041 | 2362034 | 18 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 72 | 34.9843 | -118.8945 | No | Overcast;32-90 F |  |  | 24-0022700 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912334 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | SWITCH | 2109 | 20240205 | 2244 | 20240205 | 2309 | 2362572 | 25 | Distribution Circuit | Company Initiated | Return Circuit Normal | 33 | 825 | 35.0141 | -118.9087 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0020032 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1912464 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13392 | 20240206 | 151 | 20240206 | 539 | 2362733 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1217 | 35.1869 | -118.9673 | No | Clear;32-90 F |  |  | 24-0022914 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912548 | 1 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517109063950 | 20240206 | 219 | 20240206 | 820 | 2362732 | 361 | Transformer only | Vegetation | Tree - palm frond fell into line | 4 | 1444 | 35.253 | -118.9688 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0022989 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912578 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2103 | 255262103 | RECLOSER | 2487 | 20240206 | 538 | 20240207 | 32 | 2362996 | 1124 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1208 | 124435 | 35.3833 | -119.0996 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0022916 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1912550 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | MTR#1009411856 | 20240206 | 908 | 20240206 | 1408 | 2363531 | 300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 300 | 35.2669 | -119.0384 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0023045 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1912615 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | JUMPER | OJ 1 N/OF 516754763479 | 20240206 | 1007 | 20240208 | 100 | 2363794 | 2333 | Distribution Circuit | Environmental/External | Water | 2 | 4666 | 35.2399 | -119.0883 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023147 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1912680 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1103 | 254501103 | TRANSFORMER | 516299975877 | 20240206 | 1031 | 20240206 | 1407 | 2363429 | 216 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 216 | 35.5784 | -119.2455 | No | Overcast-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0023220 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912727 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1106 | 252931106 | SWITCH | 18423 | 20240206 | 1209 | 20240207 | 1535 | 2364240 | 1646 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1646 | 34.9844 | -118.9245 | No | Overcast-Fog;32-90 F | Metering Equipment | Failed/Faulted | 24-0024360 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913535 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1106 | 252931106 | TRANSFORMER | 517418653502 | 20240206 | 1222 | 20240206 | 1230 | 2364285 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 8 | 34.9672 | -118.8618 | No | Overcast-Fog;32-90 F | Bushing | Arcing | 24-0023333 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1912809 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517031265823 | 20240206 | 1420 | 20240206 | 2159 | 2364692 | 459 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 13905 | 35.3045 | -118.9953 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0023481 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1912913 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1106 | 253551106 | TRANSFORMER | 516045380991 | 20240206 | 1440 | 20240206 | 1450 | 2364720 | 10 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 10 | 35.7181 | -119.3326 | No | Overcast;32-90 F |  |  | 24-0023514 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1912936 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | FUSE | 8135 | 20240206 | 1638 | 20240207 | 354 | 2365158 | 676 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 8788 | 35.3612 | -119.0282 | No | Overcast-Drizzle;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0023666 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913067 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 8928 | 20240206 | 1650 | 20240206 | 1843 | 2365246 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1130 | 35.3486 | -119.0477 | No | Overcast-Drizzle;32-90 F | Jumper | Bent or Twisted | 24-0023773 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913155 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 18843 | 20240206 | 1940 | 20240207 | 419 | 2365703 | 519 | Distribution Circuit | 3rd Party | Vehicle | 11 | 5709 | 35.2092 | -118.8064 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0023758 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1913170 | 0 | EPSS Ckt | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 16329 | 20240207 | 144 | 20240207 | 1337 | 2366027 | 713 | Distribution Circuit | Equipment Failure/Involved | Underground | 203 | 98407 | 35.2958 | -119.0087 | No | Partly Cloudy-Fog-Rain;32-90 F | Elbow | Burned/flashed | 24-0023933 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913294 | 1 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 485677 | 20240207 | 550 | 20240207 | 940 | 2366112 | 230 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 690 | 35.3323 | -119.2244 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0023945 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1913304 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1101 | 253371101 | FUSE | 14340 | 20240207 | 843 | 20240207 | 1001 | 2366352 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 1560 | 35.393 | -119.002 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Arcing | 24-0024010 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1913329 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13341 | 20240207 | 1224 | 20240207 | 1438 | 2367194 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 402 | 35.0473 | -119.0115 | No | Partly Cloudy;32-90 F |  |  | 24-0024412 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1913559 | 0 | EPSS Ckt | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 14205 | 20240207 | 1348 | 20240207 | 1429 | 2367542 | 41 | Distribution Circuit | Company Initiated | Return Circuit Normal | 34 | 985 | 35.2311 | -119.256 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0017987 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1913530 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1103 | 253411103 | SWITCH | 3594 | 20240207 | 1510 | 20240207 | 1700 | 2367806 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 3520 | 35.0559 | -119.1359 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0024419 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1913564 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | SWITCH | 787651 | 20240207 | 1726 | 20240207 | 1852 | 2368212 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 86 | 35.3717 | -119.3323 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0024560 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1913637 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | TRANSFORMER | 515274551810 | 20240207 | 1938 | 20240208 | 1546 | 2368706 | 1208 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2416 | 34.9132 | -119.5773 | No | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0025155 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1914183 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 8927 | 20240207 | 2015 | 20240207 | 2116 | 2368304 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 385 | 23485 | 35.3473 | -119.048 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | On Ground | 24-0024593 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1913664 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | SWITCH | 4079 | 20240208 | 30 | 20240208 | 421 | 2369053 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 32571 | 35.3616 | -118.9244 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0024698 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1914350 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | OCB | 2104/2 | 20240208 | 728 | 20240208 | 1100 | 2369870 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 612 | 129744 | 35.3885 | -119.0046 | No | Overcast;32-90 F |  |  | 24-0025988 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1915092 | 0 | Non-EPSS | N | 2024 | ABC 51
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 9163 | 20240208 | 1356 | 20240209 | 1357 | 2370300 | 1441 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 4323 | 35.3529 | -119.9873 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0026347 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915171 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | RECLOSER | 952122 | 20240208 | 1638 | 20240208 | 1704 | 2370613 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 1924 | 34.9145 | -119.5954 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0026486 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915226 | 0 | EPSS Ckt | N | 2024 | NONE
KERN | KERN | RENFRO-2101 | 254572101 | JUMPER | OJS 1 W/OF CGC# 516452368198 | 20240208 | 1806 | 20240209 | 231 | 2370790 | 505 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2020 | 35.3678 | -119.1912 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0026542 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915268 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1104 | 252771104 | OTHER | J2718 TWD T14998 | 20240208 | 2150 | 20240209 | 12 | 2371035 | 142 | Transformer only | Equipment Failure/Involved | Underground | 18 | 2556 | 35.3794 | -118.9056 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 24-0026559 | UG | Sus | 35529033 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915455 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 67539 | 20240208 | 2205 | 20240209 | 444 | 2371038 | 399 | Distribution Circuit | 3rd Party | Vehicle | 154 | 61446 | 35.3499 | -118.9852 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0026759 | OH | Sus | 31683437 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1915471 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 14798 | 20240208 | 2212 | 20240209 | 1355 | 2371044 | 943 | Distribution Circuit | 3rd Party | Vehicle | 8 | 7548 | 35.2089 | -119.0121 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0026761 | OH | Sus | 35530000 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915473 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 16578 | 20240209 | 150 | 20240209 | 1021 | 2371113 | 511 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 21462 | 35.3728 | -119.1633 | No | Overcast;32-90 F | Elbow | Failed/Faulted | 24-0026793 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915497 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1110 | 253951110 | FUSE | 14176 | 20240209 | 356 | 20240209 | 1027 | 2371096 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 25806 | 35.3903 | -118.9569 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Arcing | 24-0026789 | OH | Sus | 46184322 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915492 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1113 | 253491113 | TRANSFORMER | 516391274738 | 20240209 | 851 | 20240209 | 1055 | 2371208 | 124 | Transformer only | 3rd Party | Other | 2 | 248 | 35.5476 | -119.2136 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken | 24-0026867 | OH | Sus | 31683811 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915528 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 516967958674 | 20240209 | 1114 | 20240209 | 1720 | 2371620 | 366 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 366 | 35.1083 | -119.0141 | No | Clear;32-90 F | Fuse | Broken | 24-0027158 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915682 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1104 | 253181104 | JUMPER | OJS 2 N/OF CGC# 516338477431 | 20240209 | 1450 | 20240210 | 1303 | 2371888 | 1333 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1333 | 35.6236 | -119.2324 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0027088 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915640 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | FUSE | 9783 | 20240209 | 1458 | 20240210 | 17 | 2371922 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2236 | 35.3263 | -118.7808 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0027094 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915644 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | 516418568080 | 20240209 | 1754 | 20240210 | 651 | 2372232 | 777 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1554 | 35.3645 | -119.2023 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0027192 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915706 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | TRANSFORMER | 517224074840 | 20240209 | 1807 | 20240209 | 2040 | 2372248 | 153 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 153 | 35.5533 | -118.9337 | No | Clear;32-90 F | Metering Equipment | Failed/Faulted | 24-0027214 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915727 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 16854 | 20240209 | 1903 | 20240209 | 2238 | 2372322 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 86 | 18490 | 35.3213 | -119.0456 | No | Clear;32-90 F |  |  | 24-0027269 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915779 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | JUMPER | 2469 | 20240210 | 1639 | 20240210 | 1739 | 2372910 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 6540 | 35.3122 | -118.8965 | No | Clear;32-90 F | Jumper | Burned Open | 24-0027441 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1915881 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | SWITCH | 20141 | 20240210 | 1742 | 20240210 | 2030 | 2372949 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 236 | 10273 | 35.3337 | -118.9321 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0027439 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915888 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1104 | 253951104 | TRANSFORMER | 517151668482 | 20240210 | 2137 | 20240210 | 2245 | 2373041 | 68 | Transformer only | 3rd Party | Metallic Balloon | 17 | 1156 | 35.3784 | -118.9557 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0027551 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915989 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 16193 | 20240210 | 2353 | 20240211 | 132 | 2373061 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 4653 | 35.2742 | -118.9145 | No | Clear;32-90 F |  |  | 24-0027556 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915993 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1108 | 252081108 | JUMPER | BURNED OJ 6P W/OF CGC 515671859397 | 20240211 | 941 | 20240212 | 1108 | 2373170 | 1527 | Distribution Circuit | 3rd Party | Vandalism | 1 | 1527 | 35.1235 | -119.4522 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027601 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | Yes | No | 1916029 | 1 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1104 | 253551104 | RECLOSER | 704492 | 20240212 | 745 | 20240212 | 913 | 2373618 | 88 | Distribution Circuit | Animal | Bird found | 6 | 528 | 35.7882 | -119.5794 | No | Fog;32-90 F | Conductor- Overhead | Normal | 24-0027740 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1916129 | 0 | Non-EPSS | N | 2024 | B C TIME
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514798771607 | 20240212 | 917 | 20240212 | 1733 | 2373766 | 496 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 496 | 35.4551 | -119.7473 | No | Clear;32-90 F | Fuse | Broken | 24-0028075 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916309 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SHAFTER-1104 | 253651104 | FUSE | 16105 | 20240212 | 919 | 20240212 | 1102 | 2373773 | 103 | Distribution Circuit | 3rd Party | Other | 41 | 4223 | 35.5066 | -119.2805 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0027859 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1916240 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | TRANSFORMER | 516273070395 | 20240212 | 930 | 20240212 | 1049 | 2373790 | 79 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 79 | 35.4276 | -119.2518 | No | Clear;32-90 F | Fuse | Broken | 24-0027856 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916239 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 517194958771 | 20240212 | 937 | 20240212 | 1000 | 2373659 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 23 | 35.1112 | -118.939 | No | Clear;32-90 F | Fuse | Burned Open | 24-0027825 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916226 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | FUSE | 7111 | 20240212 | 1228 | 20240212 | 1248 | 2374032 | 20 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 108 | 2160 | 35.3984 | -119.2976 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0027922 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1916259 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 18173 | 20240212 | 1237 | 20240212 | 2045 | 2374044 | 488 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 8664 | 35.4091 | -119.0193 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0027952 | OH | Sus | 31683973 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916268 | 1 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516812463370 | 20240212 | 1447 | 20240212 | 1808 | 2374196 | 201 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 603 | 35.2367 | -119.0686 | No | Clear;32-90 F | Fuse | Broken | 24-0028086 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916316 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | INTERRUPTER | 12588 | 20240213 | 349 | 20240214 | 1251 | 2374509 | 1982 | Distribution Circuit | Equipment Failure/Involved | Underground | 503 | 140339 | 35.3545 | -119.0901 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0028136 | UG | Sus | 31684075 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916364 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7285 | 20240213 | 844 | 20240213 | 1457 | 2374693 | 373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2985 | 35.4569 | -119.4382 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken | 24-0028255 | OH | Sus | 46190326 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916509 | 1 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | RECLOSER | 815842 | 20240213 | 929 | 20240213 | 940 | 2374887 | 11 | Distribution Circuit | Company Initiated | Operating error | 2791 | 30701 | 35.3786 | -119.1274 | No | Partly Cloudy;32-90 F | Relay | Normal | 24-0002251 | OH | Sus | 45904782 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1916497 | 0 | Non-EPSS | N | 2024 | SGF
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 9861 | 20240214 | 42 | 20240214 | 359 | 2375740 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1576 | 35.2026 | -119.0879 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0028639 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1916669 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1102 | 253651102 | RECLOSER | 66660 | 20240214 | 522 | 20240214 | 754 | 2375783 | 152 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 10336 | 35.5151 | -119.2782 | No | Partly Cloudy-Fog;32-90 F | Capacitor | Failed/Faulted | 24-0028643 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | No | No | 1916677 | 0 | Non-EPSS | N | 2024 | A B C SGF
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | T848457 | 20240214 | 609 | 20240214 | 1657 | 2375792 | 648 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 648 | 35.4913 | -119.2871 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0028777 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1916828 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1106 | 253371106 | FUSE | 14453 | 20240214 | 1552 | 20240215 | 313 | 2376511 | 681 | Distribution Circuit | Equipment Failure/Involved | Overhead | 137 | 93297 | 35.3913 | -118.9832 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0029114 | OH | Sus | 31684254 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1916901 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | OTHER | J1840 TWD T12372 | 20240214 | 1623 | 20240214 | 1737 | 2376547 | 74 | Distribution Circuit | Equipment Failure/Involved | Underground | 43 | 3182 | 35.3818 | -119.149 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0028801 | UG | Sus | 35531512 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1916910 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | TRIP-SAVER | 13071 | 20240214 | 2324 | 20240215 | 431 | 2376715 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 168 | 51576 | 35.3024 | -119.0028 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0029239 | OH | Sus | 31684290 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1916956 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | LAMONT-1107 | 253911107 | OCB | 1107/2 | 20240215 | 430 | 20240215 | 1633 | 2376869 | 723 | Distribution Circuit | 3rd Party | Vandalism | 1143 | 149972 | 35.2971 | -118.8618 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0029274 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1916995 | 0 | Non-EPSS | N | 2024 | A- B- C
KERN | KERN | BAKERSFIELD-1110 | 253371110 | FUSE | 14936 | 20240215 | 854 | 20240215 | 940 | 2377007 | 46 | Distribution Circuit | 3rd Party | Metallic Balloon | 121 | 5566 | 35.3897 | -119.0144 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0029391 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1917063 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | TRANSFORMER | 517294171305 | 20240215 | 1053 | 20240215 | 1415 | 2377157 | 202 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 202 | 35.4557 | -118.909 | No | Overcast;32-90 F |  |  | 24-0029599 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1917106 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | 517381665918 | 20240215 | 1211 | 20240215 | 2312 | 2377232 | 661 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 661 | 35.3082 | -118.8786 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0029624 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917117 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ARVIN-1103 | 253801103 | FUSE | 747533 | 20240216 | 1341 | 20240216 | 1655 | 2378292 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1940 | 35.1292 | -118.9323 | No | Clear;32-90 F |  |  | 24-0030073 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1917412 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514935169147 | 20240217 | 843 | 20240217 | 1340 | 2378732 | 297 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 297 | 35.3881 | -119.6998 | No | Clear;32-90 F | Jumper | Broken | 24-0030218 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917511 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | RECLOSER | 4713 | 20240217 | 856 | 20240217 | 941 | 2378742 | 45 | Distribution Circuit | Animal | Bird found | 806 | 36270 | 35.3304 | -119.0745 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0030151 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917480 | 0 | Non-EPSS | N | 2024 | B GRD
KERN | KERN | LAMONT-1107 | 253911107 | RECLOSER | 1913 | 20240217 | 947 | 20240218 | 41 | 2378780 | 894 | Distribution Circuit | 3rd Party | Vehicle | 741 | 218752 | 35.3127 | -118.9144 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0030159 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1917490 | 0 | Non-EPSS | N | 2024 | A- B- C
KERN | KERN | GANSO-1104 | 254541104 | FUSE | 17080 | 20240217 | 1301 | 20240217 | 1600 | 2378903 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 955 | 35.5007 | -119.4392 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0030245 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917529 | 1 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRIP-SAVER | 7273 | 20240217 | 2000 | 20240217 | 2135 | 2379240 | 95 | Distribution Circuit | Animal | Other | 187 | 17742 | 35.4202 | -119.3387 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0030319 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917599 | 1 | Non-EPSS | N | 2024 | N/A
KERN | KERN | PANAMA-2101 | 253422101 | RECLOSER | 1393 | 20240218 | 24 | 20240218 | 35 | 2379316 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 347 | 3817 | 35.2647 | -119.0215 | No | Clear;32-90 F | Woodpin | Broken | 24-0030356 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1917635 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | 517275064881 | 20240218 | 56 | 20240218 | 1649 | 2379361 | 953 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 953 | 35.2797 | -118.9137 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0030361 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917640 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1105 | 253551105 | TRANSFORMER | 515951582891 | 20240218 | 508 | 20240219 | 1023 | 2379383 | 1755 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1755 | 35.77 | -119.3655 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030372 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917649 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | JUMPER | FB 1 E/OF 68241 | 20240218 | 828 | 20240218 | 1157 | 2379445 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2090 | 35.2597 | -119.0361 | No | Clear;32-90 F | Woodpin | Burned/flashed | 24-0030356 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1917657 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | FUSE | 17872 | 20240218 | 1103 | 20240218 | 1342 | 2379528 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 742 | 35.3975 | -119.7532 | No | Clear;32-90 F |  |  | 24-0030447 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917694 | 1 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 14637 | 20240218 | 1246 | 20240218 | 1327 | 2379604 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 519 | 35.336 | -119.0151 | No | Clear;32-90 F |  |  | 24-0030444 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917691 | 1 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 15164 | 20240219 | 310 | 20240219 | 450 | 2380272 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 200 | 35.5284 | -119.5484 | No | Overcast;32-90 F |  |  | 24-0030610 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917850 | 1 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1102 | 252971102 | FUSE | 95359 | 20240219 | 605 | 20240219 | 1335 | 2380357 | 450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 900 | 35.1947 | -118.8262 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030680 | OH | Sus | 31684687 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1917906 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | OCB | 1102/2 | 20240219 | 725 | 20240219 | 836 | 2380427 | 71 | Distribution Circuit | Animal | Bird found | 416 | 29536 | 35.2971 | -118.8619 | No | Clear;32-90 F | Recloser | Burned/flashed | 24-0030639 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1917874 | 0 | EPSS Ckt | N | 2024 | RLY TRIP TARGET
KERN | KERN | LERDO-1111 | 253491111 | TRANSFORMER | 516492073139 | 20240219 | 842 | 20240219 | 1302 | 2380476 | 260 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 260 | 35.5035 | -119.1806 | No | Overcast-Rain;32-90 F | Fuse | Broken | 24-0030848 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918028 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13476 | 20240220 | 845 | 20240220 | 920 | 2382582 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 93 | 3255 | 35.3649 | -118.9745 | No | Partly Cloudy;32-90 F |  |  | 24-0031276 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918367 | 0 | Non-EPSS | N | 2024
KERN | KERN | MARICOPA-1102 | 254211102 | FUSE | 18607 | 20240220 | 1341 | 20240221 | 1432 | 2383040 | 1491 | Distribution Circuit | 3rd Party | Vandalism | 3 | 4473 | 35.1002 | -119.4225 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0031621 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1918475 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517005766652 | 20240220 | 1512 | 20240221 | 28 | 2383396 | 556 | Distribution Circuit | 3rd Party | Vehicle | 1 | 556 | 35.3274 | -119.004 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 24-0031685 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1918515 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2102 | 253142102 | FUSE | 9028 | 20240220 | 1802 | 20240222 | 950 | 2383363 | 2388 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4693 | 34.935 | -119.5249 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Burned/flashed | 24-0031680 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918512 | 1 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517005766652 | 20240221 | 620 | 20240221 | 705 | 2383579 | 45 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 45 | 35.3274 | -119.004 | No | Overcast-Fog;32-90 F |  |  | 24-0031835 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1918609 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2102 | 254572102 | OTHER | T12667 TWD T12668 | 20240221 | 833 | 20240221 | 949 | 2383880 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 2128 | 35.3576 | -119.1449 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0031228 | UG | Sus | 35532527 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1918730 | 0 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1104 | 253191104 | TRANSFORMER | 517309557960 | 20240221 | 1155 | 20240221 | 2218 | 2384201 | 623 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 623 | 35.0887 | -118.9004 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 24-0032179 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918839 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 13065 | 20240221 | 1342 | 20240221 | 1434 | 2384374 | 52 | Distribution Circuit | Animal | Bird found | 41 | 2132 | 35.3036 | -118.9941 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0032192 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918844 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 18498 | 20240221 | 1356 | 20240221 | 1703 | 2384378 | 187 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 187 | 35.3599 | -119.1989 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0032148 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1918830 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 516922556590 | 20240222 | 752 | 20240222 | 1441 | 2384889 | 409 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 409 | 35.0525 | -119.0293 | No | Partly Cloudy;32-90 F | Other | Failed/Faulted | 24-0031345 | OH | Sus | 46126699 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1918970 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEJON-1105 | 252931105 | RECLOSER | 95130 | 20240222 | 801 | 20240223 | 127 | 2384864 | 1046 | Distribution Circuit | 3rd Party | Vehicle | 37 | 11650 | 35.0307 | -118.934 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0032419 | OH | Sus | 31684885 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1918957 | 0 | Non-EPSS | N | 2024 | ABC-GRD TIME OC
KERN | KERN | TEVIS-2101 | 255322101 | TRANSFORMER | 516475864520 | 20240222 | 831 | 20240222 | 1428 | 2384936 | 357 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 357 | 35.267 | -119.1815 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0032434 | OH | Sus | 46193558 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1918984 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1111 | 253491111 | TRANSFORMER | 516329272478 | 20240222 | 1740 | 20240222 | 1926 | 2385627 | 106 | Transformer only | 3rd Party | Other | 1 | 106 | 35.4852 | -119.2342 | No | Clear;32-90 F | Other | On Ground | 24-0032814 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919251 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | OCB | 1105/2 | 20240223 | 751 | 20240224 | 400 | 2385870 | 1209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 30603 | 35.3531 | -119.271 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0033012 | OH | Sus | 46194676 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1919396 | 0 | Non-EPSS | N | 2024 | ABC-GRD TIME OC
KERN | KERN | RENFRO-2101 | 254572101 | OTHER | T12201 TWD T12202 | 20240223 | 1208 | 20240223 | 1329 | 2386269 | 81 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 1458 | 35.3682 | -119.1779 | No | Overcast;32-90 F | Transformer (UG) | Deteriorated | 24-0033193 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1919598 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | TRANSFORMER | 516975466430 | 20240223 | 1340 | 20240223 | 1926 | 2386279 | 346 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2768 | 35.321 | -119.0141 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0033313 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919621 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 13466 | 20240224 | 805 | 20240224 | 901 | 2386683 | 56 | Distribution Circuit | Animal | Bird found | 31 | 1736 | 35.31 | -119.0303 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0033461 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919742 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1107 | 252721107 | SWITCH | 3871 | 20240224 | 1726 | 20240224 | 2247 | 2387042 | 321 | Distribution Circuit | 3rd Party | Vehicle | 1 | 321 | 35.456 | -119.0738 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0033515 | OH | Sus | 35533509 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1919793 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 15545 | 20240225 | 343 | 20240225 | 1330 | 2387232 | 587 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 15966 | 35.3751 | -118.9973 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0033584 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1919854 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7260 | 20240225 | 1055 | 20240225 | 1725 | 2387381 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1301 | 35.4712 | -119.5279 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0033638 | OH | Sus | 31685080 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919900 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516955766914 | 20240225 | 1111 | 20240225 | 1249 | 2387388 | 98 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 784 | 35.3343 | -119.0216 | No | Clear;32-90 F | Fuse | Broken | 24-0033629 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919893 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 390355 | 20240225 | 1241 | 20240225 | 1424 | 2387418 | 103 | Distribution Circuit | Animal | Bird found | 48 | 4944 | 35.3569 | -119.0062 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0033640 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1919902 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 16097 | 20240226 | 104 | 20240226 | 405 | 2387658 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 543 | 35.7503 | -119.4776 | No | Partly Cloudy;32-90 F |  |  | 24-0033695 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1919945 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17784 | 20240226 | 1009 | 20240226 | 1109 | 2388027 | 60 | Distribution Circuit | Animal | Bird found | 211 | 12660 | 35.3447 | -119.0708 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0033835 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1920155 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1103 | 252081103 | FUSE | 9198 | 20240226 | 1345 | 20240227 | 1117 | 2388243 | 1292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 7752 | 35.1516 | -119.4195 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0034097 | OH | Sus | 46200051 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1920226 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | OTHER | T11732 TWD T11733 | 20240226 | 1351 | 20240226 | 1455 | 2388254 | 64 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 1728 | 35.3771 | -119.1968 | No | Overcast;32-90 F | Transformer (UG) | Deteriorated | 24-0033824 | UG | Sus | 35533756 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1920196 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | SWITCH | 12374 | 20240226 | 2004 | 20240226 | 2244 | 2388482 | 160 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 4640 | 35.3789 | -119.1774 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0033845 | UG | Sus | 35533805 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1920234 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1110 | 254071110 | OCB | 2200/2 | 20240226 | 2010 | 20240227 | 1625 | 2388494 | 1215 | Distribution Circuit | 3rd Party | Vehicle | 1349 | 57982 | 35.3165 | -119.0679 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0034119 | OH | Sus | 35534001 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1920237 | 0 | Non-EPSS | N | 2024 | A/C TIME
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 16039 | 20240226 | 2319 | 20240227 | 153 | 2388579 | 154 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 2702 | 35.3803 | -119.181 | No | Overcast;32-90 F | Transformer (UG) | Broken | 24-0033979 | UG | Sus | 46199961 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1920253 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | 516409168730 | 20240227 | 930 | 20240227 | 1053 | 2388891 | 83 | Transformer only | Animal | Other | 1 | 83 | 35.3823 | -119.2056 | No | Overcast;32-90 F | Transformer (OH) |  | 24-0034327 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920480 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1103 | 253651103 | FUSE | 16851 | 20240227 | 933 | 20240227 | 1224 | 2388962 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1197 | 35.529 | -119.3588 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0034296 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1920469 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 228405 | 20240227 | 1124 | 20240228 | 238 | 2389034 | 914 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2742 | 35.5582 | -119.6365 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0034453 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920515 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | TRANSFORMER | 517318055303 | 20240227 | 1311 | 20240227 | 1455 | 2389166 | 104 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 104 | 35.0164 | -118.8953 | No | Partly Cloudy;32-90 F |  |  | 24-0034529 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1920531 | 0 | EPSS Ckt | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | OTHER | J65874 TWD T60478 | 20240227 | 1710 | 20240227 | 1828 | 2389323 | 78 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 78 | 35.6145 | -119.6593 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0034366 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1920541 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | 517558066302 | 20240227 | 1951 | 20240227 | 2356 | 2389467 | 245 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 245 | 35.3192 | -118.8182 | No | Clear;32-90 F |  |  | 24-0034648 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1920600 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | TRANSFORMER | 516807667431 | 20240227 | 2006 | 20240227 | 2100 | 2389471 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 744 | 35.348 | -119.0714 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0034617 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1920565 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1104 | 252721104 | SWITCH | 9699 | 20240228 | 850 | 20240228 | 1103 | 2389779 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 133 | 35.5736 | -119.0373 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0034663 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1920705 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAMONT-1105 | 253911105 | TRANSFORMER | 517620564670 | 20240228 | 1457 | 20240228 | 2025 | 2390243 | 328 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 328 | 35.2744 | -118.7979 | No | Clear;32-90 F | Fuse | Burned Open | 24-0035174 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920903 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517408665623 | 20240229 | 755 | 20240229 | 1150 | 2390635 | 235 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 470 | 35.3 | -118.8695 | No | Clear;32-90 F |  |  | 24-0035469 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1921099 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 8927 | 20240229 | 900 | 20240229 | 1408 | 2390733 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 385 | 15035 | 35.3473 | -119.048 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0035276 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1921024 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | JUMPER | BROKEN JMPRS @ 16695 | 20240229 | 907 | 20240229 | 1420 | 2390838 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 313 | 35.2236 | -119.2088 | No | Clear;32-90 F | Jumper | Broken | 24-0035461 | OH | Sus | 46201014 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1921094 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1103 | 252861103 | FUSE | 14011 | 20240301 | 314 | 20240301 | 530 | 2391736 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2040 | 35.4334 | -119.1896 | Yes | Clear;32-90 F |  |  | 24-0035835 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921259 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 18401 | 20240301 | 858 | 20240301 | 1330 | 2391875 | 272 | Distribution Circuit | 3rd Party | Gun Shot | 3 | 396 | 35.6307 | -119.2754 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0035983 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921286 | 1 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1109 | 253951109 | TRANSFORMER | T3309 | 20240301 | 1024 | 20240301 | 1511 | 2391945 | 287 | Transformer only | Equipment Failure/Involved | Underground | 20 | 5740 | 35.3982 | -118.9274 | Yes | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0036231 | UG | Sus | 46202026 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921366 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1101 | 252021101 | RECLOSER | 3609 | 20240301 | 1052 | 20240301 | 1253 | 2391982 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 4859 | 35.6583 | -120.0132 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0036022 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921295 | 0 | EPSS Ckt | N | 2024 | GRD SFG
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516979562460 | 20240301 | 1120 | 20240301 | 2255 | 2392001 | 695 | Transformer only | 3rd Party | Vehicle | 1 | 695 | 35.2123 | -119.012 | Yes | Clear;32-90 F | Transformer | Broken | 24-0036068 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921308 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | RECLOSER | 2676 | 20240301 | 1927 | 20240302 | 154 | 2392979 | 387 | Distribution Circuit | 3rd Party | Vehicle | 159 | 38034 | 35.4854 | -119.2803 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0036397 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1921462 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516891267388 | 20240302 | 545 | 20240302 | 1415 | 2394383 | 510 | Transformer only | 3rd Party | Vehicle | 3 | 1530 | 35.3472 | -119.0433 | No | Overcast;32-90 F | Transformer (OH) | Broken | 24-0036685 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921729 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13447 | 20240302 | 844 | 20240302 | 1818 | 2394562 | 574 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 76342 | 35.365 | -118.9703 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036791 | OH | Sus | 31685466 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921810 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 45902 | 20240303 | 601 | 20240303 | 654 | 2395758 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 106 | 35.2305 | -118.9144 | No | Clear;32-90 F |  |  | 24-0037117 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922059 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | OCB | 1109/2 | 20240303 | 832 | 20240303 | 1333 | 2395842 | 301 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1896 | 278393 | 35.4407 | -119.0203 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0037145 | OH | Sus | 31685471 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1922076 | 0 | Non-EPSS | N | 2024 | B & C
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 16621 | 20240303 | 1401 | 20240303 | 1622 | 2396192 | 141 | Distribution Circuit | 3rd Party | Metallic Balloon | 14 | 1974 | 35.4855 | -119.2829 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0037242 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922156 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1105 | 253551105 | TRANSFORMER | 515778881273 | 20240304 | 945 | 20240304 | 955 | 2396550 | 10 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 20 | 35.725 | -119.4237 | No | Partly Cloudy;32-90 F |  |  | 24-0037465 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922288 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517329466475 | 20240304 | 1607 | 20240305 | 215 | 2397011 | 608 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 608 | 35.3233 | -118.8965 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0037878 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922462 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 18859 | 20240304 | 2046 | 20240304 | 2210 | 2397176 | 84 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 2772 | 35.3735 | -119.1988 | No | Partly Cloudy;32-90 F | Transformer (UG) | Deteriorated | 24-0037788 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1922374 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 18401 | 20240305 | 720 | 20240305 | 815 | 2397336 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 110 | 35.6307 | -119.2754 | No | Fog;32-90 F |  |  | 24-0037980 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922511 | 1 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 14548 | 20240305 | 1031 | 20240305 | 1152 | 2397684 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 108 | 35.1942 | -119.0745 | No | Clear;32-90 F |  |  | 24-0038165 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922601 | 1 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515486769271 | 20240305 | 1220 | 20240305 | 1831 | 2397658 | 371 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 371 | 35.394 | -119.5151 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0038181 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922613 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 698593 | 20240305 | 1502 | 20240305 | 1645 | 2397858 | 103 | Distribution Circuit | 3rd Party | Metallic Balloon | 111 | 11433 | 35.4129 | -119.3207 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0038352 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922649 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2103 | 255322103 | FUSE | 18232 | 20240305 | 1510 | 20240305 | 1529 | 2397865 | 19 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 38 | 35.355 | -119.1279 | No | Clear;32-90 F |  |  | 24-0038306 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922640 | 0 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2102 | 254582102 | OTHER | J1823 TWD T12390 | 20240305 | 1540 | 20240305 | 1710 | 2397894 | 90 | Distribution Circuit | Equipment Failure/Involved | Underground | 25 | 2250 | 35.4231 | -119.125 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0038157 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1922646 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | 515825773709 | 20240306 | 918 | 20240306 | 1319 | 2398223 | 241 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 241 | 35.5174 | -119.4033 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0038630 | OH | Sus | 46203859 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922911 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 516926758152 | 20240306 | 955 | 20240306 | 1020 | 2398309 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 25 | 35.0935 | -119.0293 | No | Clear;32-90 F | Service conductor | Broken | 24-0038605 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1922886 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1106 | 254071106 | FUSE | 9608 | 20240306 | 1129 | 20240306 | 1255 | 2398476 | 86 | Distribution Circuit | 3rd Party | Metallic Balloon | 1 | 86 | 35.325 | -119.0528 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0038761 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922943 | 1 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1103 | 253801103 | FUSE | 18549 | 20240306 | 1152 | 20240307 | 156 | 2398499 | 844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 844 | 35.1292 | -118.914 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0038732 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922936 | 1 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-2102 | 254762102 | SWITCH | 10532 | 20240306 | 1219 | 20240306 | 1229 | 2398517 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 16 | 160 | 35.3595 | -119.0636 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 24-0032150 | UG | Sus | 35506607 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1922941 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | FUSE | 116471 | 20240306 | 1247 | 20240307 | 1855 | 2398550 | 1808 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1808 | 35.3257 | -119.3228 | No | Clear;32-90 F |  |  | 24-0039534 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923327 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 55512 | 20240306 | 1410 | 20240306 | 1515 | 2398616 | 65 | Distribution Circuit | Animal | Bird found | 2 | 130 | 34.9275 | -119.5442 | No | Overcast;32-90 F | Cutout- fuse holder | Normal | 24-0038892 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922976 | 0 | EPSS Ckt | N | 2024
KERN | KERN | COPUS-1103 | 253871103 | OCB | 1103/2 | 20240306 | 1548 | 20240307 | 1735 | 2398693 | 1547 | Distribution Circuit | Animal | Other | 63 | 69133 | 35.0934 | -119.2787 | No | Overcast;32-90 F | Regulator | Burned/flashed | 24-0038902 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922979 | 0 | Non-EPSS | N | 2024 | A- GRD- TIME 51
KERN | KERN | STOCKDALE-2108 | 254072108 | TRANSFORMER | T4006 | 20240306 | 1605 | 20240306 | 1753 | 2398704 | 108 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 1080 | 35.3206 | -119.0818 | No | Overcast-Rain;32-90 F |  |  | 24-0038953 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1922998 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1101 | 252821101 | FUSE | 9140 | 20240306 | 2021 | 20240307 | 1955 | 2398845 | 1414 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 12726 | 35.1796 | -119.0834 | No | Clear;32-90 F |  |  | 24-0039555 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923346 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1101 | 252971101 | FUSE | 8893 | 20240306 | 2205 | 20240306 | 2341 | 2398840 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 7872 | 35.2109 | -118.8315 | No | Overcast;32-90 F | Insulator | Broken | 24-0039009 | OH | Sus | 31685872 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923050 | 0 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1101 | 253801101 | FUSE | 13329 | 20240306 | 2315 | 20240307 | 143 | 2398885 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 592 | 35.1303 | -118.8507 | No | Clear;32-90 F |  |  | 24-0039029 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923064 | 0 | EPSS Ckt | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516954562870 | 20240307 | 303 | 20240307 | 920 | 2398931 | 377 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 377 | 35.2231 | -119.02 | No | Clear;32-90 F | Fuse | Broken | 24-0039138 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1923189 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | OCB | 1102/2/NORM | 20240307 | 322 | 20240308 | 5 | 2398913 | 1243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2566 | 353218 | 35.4222 | -118.9007 | No | Overcast-Fog;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0039032 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1923069 | 0 | EPSS Ckt | N | 2024 | CB TRIP TARGET
KERN | KERN | CHARCA-1103 | 254501103 | TRANSFORMER | 516258577124 | 20240307 | 826 | 20240307 | 1339 | 2399041 | 313 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 313 | 35.6121 | -119.2592 | No | Partly Cloudy;32-90 F |  |  | 24-0039128 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1923172 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 16245 | 20240307 | 1317 | 20240308 | 1014 | 2399426 | 1257 | Distribution Circuit | Animal | Other | 6 | 1832 | 35.3995 | -119.5095 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0039432 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1923306 | 1 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1106 | 254501106 | FUSE | 16909 | 20240307 | 1832 | 20240307 | 2254 | 2399561 | 262 | Distribution Circuit | 3rd Party | Vehicle | 133 | 8404 | 35.5832 | -119.3404 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0039518 | UG | Sus | 31685908 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923324 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | RECLOSER | 4107 | 20240307 | 1943 | 20240308 | 358 | 2399667 | 495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2310 | 35.3327 | -119.3061 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0039545 | OH | Sus | 31685779 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923335 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | LAMONT-1105 | 253911105 | SWITCH | 80580 | 20240307 | 2327 | 20240308 | 132 | 2399734 | 125 | Distribution Circuit | 3rd Party | Vehicle | 28 | 3416 | 35.2951 | -118.8072 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0039537 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923379 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516678968454 | 20240308 | 554 | 20240308 | 647 | 2399778 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 530 | 35.3753 | -119.1148 | No | Fog;32-90 F | Fuse | Broken | 24-0039618 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1923402 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | 517443967206 | 20240308 | 1615 | 20240308 | 1729 | 2400273 | 74 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 148 | 35.3435 | -118.8582 | No | Clear;32-90 F |  |  | 24-0039973 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1923615 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | OCB | 1101/2 | 20240309 | 633 | 20240309 | 1825 | 2400579 | 712 | Distribution Circuit | 3rd Party | Vehicle | 215 | 17612 | 35.4006 | -119.449 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0040055 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1923677 | 0 | Non-EPSS | N | 2024 | ABCG TIME
KERN | KERN | WEEDPATCH-1103 | 252971103 | OCB | 1103/2 | 20240309 | 843 | 20240309 | 1008 | 2400669 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2140 | 181900 | 35.2238 | -118.88 | No | Clear;32-90 F |  |  | 24-0040072 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923723 | 0 | Non-EPSS | N | 2024 | PRI PH TIME TGT
KERN | KERN | KERN OIL-1110 | 252721110 | OTHER | J1137 TWD T9878 | 20240309 | 1006 | 20240309 | 1140 | 2400719 | 94 | Distribution Circuit | Equipment Failure/Involved | Underground | 32 | 3008 | 35.4321 | -119.0266 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0040074 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923745 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 17922 | 20240309 | 1217 | 20240309 | 1303 | 2400777 | 46 | Distribution Circuit | Equipment Failure/Involved | Underground | 83 | 3818 | 35.4085 | -119.0622 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0040104 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923767 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517164461011 | 20240309 | 1416 | 20240309 | 1845 | 2400870 | 269 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 269 | 35.1728 | -118.9496 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0040129 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1923790 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1114 | 253491114 | TRANSFORMER | 516576873106 | 20240311 | 916 | 20240311 | 1324 | 2401422 | 248 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 248 | 35.5026 | -119.1509 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0040355 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924053 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 100000091338 | 20240311 | 1512 | 20240311 | 1548 | 2401856 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 36 | 35.3475 | -119.4271 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0040606 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924151 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | FUSE | 53061 | 20240311 | 1611 | 20240312 | 405 | 2402088 | 714 | Distribution Circuit | 3rd Party | Vehicle | 6 | 4284 | 35.3186 | -119.3754 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0040663 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1924169 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | OTHER | J1255 TWD T10158 | 20240311 | 2106 | 20240311 | 2205 | 2402187 | 59 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 1121 | 35.3818 | -119.1796 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0040688 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1924188 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 8486 | 20240312 | 754 | 20240313 | 210 | 2402381 | 1096 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 50928 | 35.3212 | -119.0095 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0040809 | UG | Sus | 46210921 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924293 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515496370504 | 20240312 | 1156 | 20240312 | 1821 | 2402719 | 385 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 385 | 35.4282 | -119.5129 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0041027 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924410 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517000567306 | 20240312 | 1413 | 20240312 | 1458 | 2402823 | 45 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 45 | 35.3451 | -119.0063 | No | Partly Cloudy;32-90 F |  |  | 24-0041134 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1924433 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516669163711 | 20240313 | 1610 | 20240313 | 2114 | 2403734 | 304 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 304 | 35.2457 | -119.1164 | No | Clear;32-90 F | Service conductor | Broken | 24-0041694 | OH | Sus | 31686547 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924758 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | RECLOSER | 1400 | 20240313 | 1822 | 20240314 | 228 | 2403872 | 486 | Distribution Circuit | 3rd Party | Vehicle | 238 | 7122 | 35.2666 | -119.0254 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0041718 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1924774 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | CHARCA-1103 | 254501103 | FUSE | 7089 | 20240314 | 937 | 20240314 | 1940 | 2404565 | 603 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1158 | 35.6306 | -119.2978 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0042086 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925101 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | FUSE | 19119 | 20240314 | 1054 | 20240314 | 1121 | 2404819 | 7 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 14 | 35.3178 | -119.3235 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0041971 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925075 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 16294 | 20240314 | 1150 | 20240314 | 2155 | 2404975 | 605 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 605 | 35.2997 | -119.2165 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0042121 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925120 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | JUMPER | WIRE DOWN HOT 1 SPAN N/O CGC 515608068133 | 20240314 | 1531 | 20240314 | 2359 | 2405476 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 4941 | 35.3639 | -119.4743 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0042428 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | Yes | Yes | 1925246 | 1 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1102 | 252461102 | TRANSFORMER | 516476278101 | 20240314 | 1617 | 20240315 | 551 | 2405387 | 814 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 814 | 35.64 | -119.1867 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0042468 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925261 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2105 | 254072105 | FUSE | 9764 | 20240315 | 826 | 20240315 | 1149 | 2405891 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 5887 | 35.3175 | -119.0698 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0042691 | OH | Sus | 46212421 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925515 | 1 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1103 | 253871103 | TRANSFORMER | 516260058097 | 20240315 | 1005 | 20240315 | 1604 | 2406099 | 359 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 359 | 35.091 | -119.2516 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0042956 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925626 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2105 | 254072105 | SWITCH | 5455 | 20240315 | 1556 | 20240315 | 1630 | 2406812 | 34 | Distribution Circuit | Company Initiated | Return Circuit Normal | 12 | 408 | 35.3164 | -119.0708 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0042691 | OH | Sus | 46212421 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925636 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 9868 | 20240316 | 539 | 20240316 | 1350 | 2407035 | 491 | Distribution Circuit | 3rd Party | Vehicle | 7 | 3437 | 35.2377 | -118.995 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0043073 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1925717 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1106 | 254071106 | TRANSFORMER | T0192 | 20240316 | 554 | 20240316 | 1359 | 2407037 | 485 | Distribution Circuit | Equipment Failure/Involved | Underground | 102 | 48570 | 35.3193 | -119.0571 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0043065 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925711 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1102 | 254501102 | FUSE | 7519 | 20240316 | 2228 | 20240317 | 1534 | 2407576 | 1026 | Distribution Circuit | 3rd Party | Vehicle | 8 | 8208 | 35.6597 | -119.3832 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0043210 | OH | Sus | 31686840 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1925874 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1102 | 253871102 | RECLOSER | 2399 | 20240317 | 1243 | 20240317 | 2221 | 2407760 | 578 | Distribution Circuit | 3rd Party | Gun Shot | 31 | 8925 | 35.094 | -119.3131 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0043255 | OH | Sus | 31686900 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1925940 | 0 | Non-EPSS | N | 2024 | A & GRD
KERN | KERN | LAMONT-1102 | 253911102 | RECLOSER | 2862 | 20240317 | 2010 | 20240317 | 2018 | 2407875 | 8 | Distribution Circuit | 3rd Party | Vehicle | 226 | 1808 | 35.2817 | -118.8798 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0043286 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925962 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | LAMONT-1106 | 253911106 | JUMPER | FLYERS 1 POLE S/OF 19365 | 20240317 | 2145 | 20240318 | 25 | 2407883 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 160 | 35.2703 | -118.9144 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0043280 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925969 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 8501 | 20240317 | 2320 | 20240318 | 1750 | 2407901 | 1100 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 12100 | 35.2651 | -118.9188 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0043359 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1926039 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1105 | 253951105 | FUSE | 2860 | 20240318 | 503 | 20240319 | 258 | 2407930 | 1315 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 14896 | 35.4109 | -118.9587 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0043367 | UG | Sus | 31686847 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926047 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1101 | 252461101 | RECLOSER | 2686 | 20240318 | 1027 | 20240318 | 2258 | 2408273 | 751 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 24716 | 35.6313 | -119.1355 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0043496 | OH | Sus | 31686904 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1926244 | 0 | Non-EPSS | N | 2024 | B C GRD
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 100000019435 | 20240318 | 1308 | 20240318 | 1515 | 2408482 | 127 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 127 | 35.7753 | -119.5243 | No | Clear;32-90 F |  |  | 24-0043672 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1926328 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 16986 | 20240318 | 1502 | 20240319 | 304 | 2408581 | 722 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 18772 | 35.3337 | -119.0303 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043710 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1926340 | 0 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1104 | 254541104 | TRANSFORMER | 515878272972 | 20240318 | 1736 | 20240318 | 1907 | 2408704 | 91 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 91 | 35.4974 | -119.3858 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0043738 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926351 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | TRANSFORMER | T7793 | 20240319 | 755 | 20240319 | 1906 | 2408984 | 671 | Transformer only | Equipment Failure/Involved | Underground | 1 | 671 | 35.2997 | -119.2161 | No | Clear;32-90 F | Transformer | Normal | 24-0044026 | UG | Sus | 46213461 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926619 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 735209 | 20240319 | 1429 | 20240319 | 1605 | 2409500 | 96 | Distribution Circuit | Animal | Bird found | 1 | 96 | 35.7845 | -119.6722 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0044300 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926687 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | OTHER | T12986 TWD T12987 | 20240319 | 1603 | 20240319 | 1716 | 2409565 | 73 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 2409 | 35.3594 | -119.1403 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0044183 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1926686 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516763662925 | 20240319 | 1740 | 20240319 | 1847 | 2409649 | 67 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 134 | 35.2243 | -119.0844 | No | Clear;32-90 F |  |  | 24-0044344 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1926701 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | OTHER | T12982 TWD T12983 | 20240319 | 2048 | 20240319 | 2207 | 2409737 | 79 | Distribution Circuit | Equipment Failure/Involved | Underground | 25 | 1975 | 35.3605 | -119.1364 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0044157 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1926708 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 14625 | 20240320 | 215 | 20240320 | 443 | 2409787 | 148 | Distribution Circuit | Animal | Bird found | 6 | 888 | 35.378 | -119.0095 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0044411 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1926743 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2102 | 255322102 | FUSE | 16417 | 20240320 | 249 | 20240320 | 358 | 2409794 | 69 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 5589 | 35.3178 | -119.1241 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0044408 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926739 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 16444 | 20240320 | 932 | 20240320 | 1515 | 2410490 | 343 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1372 | 35.4561 | -118.9319 | No | Clear;32-90 F |  |  | 24-0044805 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927013 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515601479994 | 20240320 | 1239 | 20240320 | 1647 | 2410353 | 248 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 248 | 35.6886 | -119.4819 | No | Clear;32-90 F |  |  | 24-0044856 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1927024 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 517108058222 | 20240320 | 1540 | 20240321 | 215 | 2410492 | 635 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1270 | 35.096 | -118.9678 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044881 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927037 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 18928 | 20240320 | 1654 | 20240321 | 2214 | 2410099 | 1760 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1760 | 35.4958 | -119.2872 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0044863 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927026 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516938568027 | 20240320 | 1900 | 20240320 | 2145 | 2410577 | 165 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 825 | 35.3648 | -119.0276 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0044895 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1927041 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1104 | 253141104 | TRANSFORMER | 514934852371 | 20240320 | 1908 | 20240320 | 2259 | 2410584 | 231 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 231 | 34.9275 | -119.6908 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0044969 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927095 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | RECLOSER | 4889 | 20240320 | 2001 | 20240320 | 2019 | 2410603 | 18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 10 | 180 | 35.3459 | -119.172 | No | Clear;32-90 F |  |  | 24-0044906 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927046 | 0 | Non-EPSS | N | 2024 | A AND C
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516969366945 | 20240320 | 2320 | 20240321 | 1712 | 2410640 | 1072 | Distribution Circuit | 3rd Party | Other | 21 | 16096 | 35.3353 | -119.0163 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0044980 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927102 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | RECLOSER | 1556 | 20240321 | 216 | 20240321 | 1527 | 2410651 | 791 | Distribution Circuit | Equipment Failure/Involved | Underground | 1461 | 202767 | 35.1363 | -119.4657 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 24-0044979 | UG | Sus | 46214235 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927101 | 0 | Non-EPSS | N | 2024 | C- GRD
KERN | KERN | LERDO-1115 | 253491115 | FUSE | 18643 | 20240321 | 1034 | 20240321 | 1314 | 2411144 | 160 | Distribution Circuit | Animal | Bird found | 5 | 800 | 35.4705 | -119.1195 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0045194 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927215 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 9773 | 20240321 | 1305 | 20240321 | 1430 | 2411241 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 170 | 35.1933 | -118.806 | No | Clear;32-90 F |  |  | 24-0045241 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927226 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEVIS-2105 | 255322105 | OCB | 2105/2 | 20240321 | 1306 | 20240321 | 1727 | 2411236 | 261 | Distribution Circuit | Equipment Failure/Involved | Underground | 2980 | 390978 | 35.3194 | -119.1291 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0045186 | UG | Sus | 46214595 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927209 | 0 | Non-EPSS | N | 2024 | B GRD PH OC TIME
KERN | KERN | TEVIS-2105 | 255322105 | OCB | 2105/2 | 20240321 | 1840 | 20240321 | 1959 | 2411425 | 79 | Distribution Circuit | Equipment Failure/Involved | Underground | 1239 | 32019 | 35.3194 | -119.1291 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0045186 | UG | Sus | 46214595 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927250 | 0 | Non-EPSS | N | 2024 | B- GRD- PH OC TIME
KERN | KERN | TEJON-1105 | 252931105 | TRANSFORMER | 517258557170 | 20240322 | 950 | 20240322 | 1750 | 2411836 | 480 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 960 | 35.0672 | -118.9171 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 24-0045567 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927478 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1110 | 253371110 | FUSE | 15234 | 20240322 | 955 | 20240322 | 1103 | 2411849 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 998 | 35.3906 | -119.0153 | No | Clear;32-90 F |  |  | 24-0045585 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927481 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517094568077 | 20240322 | 1050 | 20240322 | 1153 | 2411900 | 63 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 504 | 35.3668 | -118.9755 | No | Clear;32-90 F |  |  | 24-0045645 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1927502 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 14861 | 20240322 | 1337 | 20240322 | 1529 | 2412058 | 112 | Distribution Circuit | 3rd Party | Metallic Balloon | 123 | 13776 | 35.4512 | -118.9044 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0045731 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927537 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20240322 | 1427 | 20240322 | 1702 | 2412136 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 4960 | 35.3618 | -119.1627 | No | Clear;32-90 F |  |  | 24-0045787 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927551 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516370863475 | 20240323 | 712 | 20240323 | 823 | 2412620 | 71 | Transformer only | Animal | Other | 1 | 71 | 35.2381 | -119.2165 | No | Clear;32-90 F | Transformer (OH) |  | 24-0045937 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927677 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1102 | 253871102 | TRANSFORMER | 516019258685 | 20240323 | 725 | 20240323 | 735 | 2412596 | 10 | Transformer only | Animal | Other | 1 | 10 | 35.1045 | -119.3316 | No | Clear;32-90 F | Transformer (OH) |  | 24-0045926 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927662 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 15723 | 20240323 | 758 | 20240323 | 935 | 2412645 | 97 | Distribution Circuit | Animal | Bird found | 5 | 485 | 35.0934 | -118.9648 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 24-0045952 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927705 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 13089 | 20240323 | 934 | 20240323 | 1447 | 2412714 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 14398 | 35.3249 | -118.9814 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Deteriorated | 24-0045959 | OH | Sus | 31687238 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1927711 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1107 | 253701107 | FUSE | 20303 | 20240323 | 1018 | 20240324 | 1206 | 2412793 | 1537 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 3074 | 35.3837 | -119.0522 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0045987 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1927727 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | TRANSFORMER | 517093077788 | 20240323 | 1103 | 20240323 | 1123 | 2412711 | 20 | Transformer only | Vegetation | Other ground vegetation | 1 | 20 | 35.6333 | -118.9801 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0046001 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927731 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517342966283 | 20240323 | 1137 | 20240323 | 2202 | 2412680 | 625 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 625 | 35.318 | -118.8916 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0046005 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927733 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | OCB | 1102/2/NORM | 20240324 | 53 | 20240324 | 1927 | 2413214 | 1114 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2565 | 674980 | 35.4222 | -118.9007 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0046129 | OH | Sus | 35539640 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1927832 | 0 | EPSS Ckt | N | 2024 | PHASE OC- GRD TGTS
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 7407 | 20240324 | 348 | 20240326 | 1315 | 2413401 | 3447 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 10341 | 35.7013 | -119.5261 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0046179 | OH | Sus | 46215803 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1927890 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1108 | 253701108 | FUSE | 9303 | 20240324 | 812 | 20240324 | 854 | 2413303 | 42 | Distribution Circuit | Animal | Bird found | 13 | 546 | 35.3413 | -119.0256 | No | Overcast-Drizzle;32-90 F | Cutout- fuse holder | Normal | 24-0046150 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927864 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2101 | 255322101 | RECLOSER | 1007 | 20240324 | 1644 | 20240324 | 1930 | 2413529 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2032 | 35.2962 | -119.1703 | No | Clear;32-90 F |  |  | 24-0046219 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927914 | 0 | Non-EPSS | N | 2024 | A- GRD
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16181 | 20240324 | 1738 | 20240325 | 50 | 2413546 | 432 | Distribution Circuit | Environmental/External | Lightning | 6 | 1548 | 35.0943 | -119.1542 | No | Clear-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 24-0046230 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927921 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1103 | 252461103 | OCB | 1103/2 | 20240324 | 2348 | 20240325 | 310 | 2413655 | 202 | Distribution Circuit | Animal | Other | 159 | 27914 | 35.6055 | -119.2033 | No | Partly Cloudy;32-90 F | Recloser | Burned/flashed | 24-0046277 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927969 | 0 | Non-EPSS | N | 2024 | A&B TIME OC
KERN | KERN | STOCKDALE-2105 | 254072105 | TRANSFORMER | T7492 | 20240325 | 542 | 20240326 | 124 | 2414573 | 1182 | Transformer only | Equipment Failure/Involved | Underground | 16 | 18912 | 35.3053 | -119.0734 | No | Overcast;32-90 F | Secondary | Deteriorated | 24-0046735 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928266 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1107 | 253701107 | TRANSFORMER | 516864768723 | 20240325 | 740 | 20240325 | 1233 | 2413785 | 293 | Transformer only | Equipment Failure/Involved | Fire- pole | 2 | 586 | 35.3837 | -119.0527 | No | Overcast;32-90 F | Transformer | Broken | 24-0046401 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928135 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1104 | 252901104 | TRANSFORMER | 515491878412 | 20240325 | 843 | 20240326 | 1128 | 2413891 | 1605 | Transformer only | Animal | Bird found | 1 | 1605 | 35.645 | -119.5177 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0046649 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928218 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 88231 | 20240325 | 919 | 20240325 | 2145 | 2414074 | 746 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 5092 | 35.6739 | -119.51 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0046481 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1928174 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | JUMPER | BURNED OPEN JUMPER 1 P W/OF 2096 | 20240325 | 943 | 20240325 | 1205 | 2414067 | 142 | Distribution Circuit | 3rd Party | Vehicle | 327 | 21324 | 35.0936 | -118.975 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0046417 | OH | Sus | 46215777 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1928153 | 1 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1103 | 254541103 | OCB | 1103/2 | 20240325 | 1024 | 20240326 | 602 | 2414113 | 1178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 37878 | 35.5013 | -119.4493 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0046445 | OH | Sus | 46216214 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1928169 | 0 | Non-EPSS | N | 2024 | ABG TIME
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515763568622 | 20240325 | 1040 | 20240326 | 1010 | 2414128 | 1410 | Transformer only | Animal | Bird found | 1 | 1410 | 35.3773 | -119.4217 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0046676 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928223 | 0 | Non-EPSS | N | 2024
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514294878873 | 20240325 | 1715 | 20240325 | 1725 | 2414338 | 10 | Transformer only | Animal | Other | 1 | 10 | 35.6521 | -119.9212 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0046677 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928224 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517342966283 | 20240326 | 750 | 20240326 | 805 | 2414610 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 15 | 35.318 | -118.8916 | No | Clear;32-90 F | Fuse | Broken | 24-0046781 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928312 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 9973 | 20240326 | 808 | 20240326 | 931 | 2415001 | 83 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 5536 | 35.4048 | -118.9927 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0046797 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928367 | 1 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1103 | 252081103 | TRANSFORMER | 515625260610 | 20240326 | 1446 | 20240326 | 1743 | 2415801 | 177 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 1947 | 35.1566 | -119.4646 | No | Clear;32-90 F |  |  | 24-0047131 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928549 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 517164260740 | 20240326 | 1718 | 20240326 | 2043 | 2415904 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 205 | 35.1651 | -118.95 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0047126 | OH | Sus | 46216693 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928548 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516898667733 | 20240326 | 1828 | 20240326 | 2315 | 2416112 | 287 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3444 | 35.3567 | -119.041 | No | Clear;32-90 F | Secondary | Broken | 24-0047226 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1928637 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 7294 | 20240327 | 759 | 20240327 | 1730 | 2416228 | 571 | Distribution Circuit | 3rd Party | Vehicle | 6 | 3426 | 35.7039 | -119.5085 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0047378 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1928804 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | JUMPER | 19133 | 20240327 | 1111 | 20240328 | 134 | 2416499 | 863 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 863 | 35.3055 | -119.2533 | No | Clear;32-90 F | Jumper | Broken | 24-0047448 | OH | Sus | 46216966 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1928825 | 1 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | TRANSFORMER | 516317266275 | 20240327 | 1113 | 20240328 | 503 | 2416503 | 1070 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1070 | 35.3151 | -119.2354 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0047485 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928838 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517055566736 | 20240327 | 1428 | 20240327 | 2005 | 2416652 | 337 | Transformer only | Animal | Other | 8 | 2696 | 35.3299 | -118.9875 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0047632 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928878 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 55512 | 20240327 | 1609 | 20240327 | 2215 | 2416900 | 366 | Distribution Circuit | Animal | Other | 2 | 732 | 34.9275 | -119.5442 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0047732 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1928939 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN POWER-2103 | 255262103 | TRANSFORMER | T10271 | 20240327 | 2008 | 20240328 | 427 | 2416860 | 499 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 499 | 35.4008 | -119.1166 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0047698 | UG | Sus | 35540434 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928907 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | FUSE | 14233 | 20240327 | 2232 | 20240328 | 104 | 2416898 | 152 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 1368 | 35.368 | -119.7352 | No | Partly Cloudy;32-90 F |  |  | 24-0047742 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1928947 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | TRANSFORMER | T3186 | 20240328 | 919 | 20240328 | 1749 | 2417232 | 510 | Transformer only | Equipment Failure/Involved | Underground | 14 | 7140 | 35.3079 | -119.0094 | No | Overcast;32-90 F | Secondary | Failed/Faulted | 24-0047894 | UG | Sus | 46217250 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929142 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | FUSE | 13972 | 20240328 | 1429 | 20240328 | 1607 | 2417514 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 294 | 35.6338 | -118.9581 | No | Clear;32-90 F |  |  | 24-0048133 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929203 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1106 | 253371106 | FUSE | 646045 | 20240328 | 1938 | 20240329 | 420 | 2417755 | 522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 522 | 35.3909 | -118.9855 | No | Partly Cloudy;32-90 F | Insulator | Burned/flashed | 24-0048208 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1929270 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1112 | 253491112 | OTHER | 4323 | 20240328 | 2255 | 20240329 | 432 | 2417757 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 125 | 17153 | 35.5151 | -119.0819 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048212 | OH | Sus | 46217548 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | Yes | 1929274 | 1 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1102 | 253181102 | TRANSFORMER | 515970280189 | 20240329 | 710 | 20240329 | 1021 | 2417799 | 191 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 191 | 35.6959 | -119.3577 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0048322 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1929382 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1110 | 252721110 | TRANSFORMER | 516961170158 | 20240329 | 939 | 20240329 | 1050 | 2417956 | 71 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 2490 | 35.4234 | -119.0203 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048324 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929383 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | RECLOSER | 4770 | 20240329 | 1651 | 20240329 | 2336 | 2418401 | 405 | Distribution Circuit | Animal | Other | 569 | 31755 | 35.344 | -119.0029 | No | Overcast;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0048543 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1929456 | 0 | Non-EPSS | N | 2024 | A/GRD
KERN | KERN | TAFT-1101 | 252081101 | RECLOSER | 36578 | 20240329 | 1931 | 20240330 | 1205 | 2418467 | 994 | Distribution Circuit | 3rd Party | Other | 1405 | 63750 | 35.1337 | -119.4557 | No | Clear-Strong Winds;32-90 F | Secondary | Broken- wire on object | 24-0048588 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1929473 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 14210 | 20240329 | 1940 | 20240329 | 2208 | 2418517 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 6364 | 35.1424 | -119.4656 | No | Clear-Strong Winds;32-90 F |  |  | 24-0048603 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929487 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2103 | 254242103 | TRANSFORMER | 515361462840 | 20240330 | 102 | 20240330 | 227 | 2418773 | 85 | Transformer only | Animal | Other | 2 | 170 | 35.2175 | -119.5541 | No | Overcast-Drizzle;32-90 F | Fuse | Normal | 24-0048648 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929526 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SHAFTER-1112 | 253651112 | FUSE | 7357 | 20240330 | 127 | 20240403 | 450 | 2418777 | 5963 | Distribution Circuit | Animal | Other | 18 | 7544 | 35.5292 | -119.4032 | No | Overcast-Rain;32-90 F | Transformer (OH) | Burned/flashed | 24-0048647 | OH | Sus | 35541222 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929525 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 16239 | 20240330 | 138 | 20240402 | 54 | 2418778 | 4276 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 16 | 23244 | 35.4269 | -119.5374 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0048821 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1929637 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 196480 | 20240330 | 152 | 20240330 | 413 | 2418779 | 141 | Distribution Circuit | Animal | Other | 1 | 141 | 34.9273 | -119.6041 | No | Overcast-Fog-Heavy Rain;32-90 F | Fuse | Burned Open | 24-0048651 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929529 | 1 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 17491 | 20240330 | 202 | 20240330 | 355 | 2418781 | 113 | Distribution Circuit | 3rd Party | Vehicle | 80 | 9040 | 35.3544 | -118.9452 | No | Overcast-Rain;32-90 F | Secondary | Broken | 24-0048650 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929528 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1102 | 253871102 | RECLOSER | 2399 | 20240330 | 421 | 20240401 | 1529 | 2418789 | 3548 | Distribution Circuit | Animal | Other | 32 | 13468 | 35.094 | -119.3131 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0048652 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1929530 | 0 | Non-EPSS | N | 2024 | ABC
KERN | KERN | TAFT-1101 | 252081101 | TRANSFORMER | 515669060161 | 20240330 | 740 | 20240330 | 1205 | 2418826 | 265 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 1060 | 35.1443 | -119.4497 | No | Clear;32-90 F |  |  | 24-0048669 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929560 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7509 | 20240330 | 910 | 20240401 | 1614 | 2418919 | 3304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 11250 | 35.7175 | -119.4906 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0048769 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1929608 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2104 | 253642104 | RECLOSER | 48268 | 20240330 | 931 | 20240330 | 1758 | 2418975 | 507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 4563 | 35.4994 | -118.9013 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0048820 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929636 | 0 | EPSS Ckt | N | 2024 | B & GRD
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | 517179264189 | 20240330 | 936 | 20240330 | 1939 | 2418952 | 603 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 603 | 35.2597 | -118.9456 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0048736 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929595 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEVIS-2104 | 255322104 | OCB | 2104/2 | 20240330 | 1143 | 20240409 | 2149 | 2418974 | 15006 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 15006 | 35.3194 | -119.1291 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0048753 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1929603 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 517063866808 | 20240330 | 1157 | 20240330 | 1540 | 2419023 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 3513 | 35.3317 | -118.9854 | No | Overcast;32-90 F | Secondary | Broken- wire on ground | 24-0048794 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929616 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1105 | 252461105 | FUSE | 7211 | 20240330 | 1203 | 20240330 | 1347 | 2419028 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 624 | 35.5731 | -119.1965 | No | Partly Cloudy;32-90 F |  |  | 24-0048805 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929625 | 1 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1103 | 255451103 | SWITCH | 888449 | 20240330 | 1243 | 20240330 | 1430 | 2419056 | 107 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 7704 | 35.3917 | -118.8906 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0048814 | UG | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1929631 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | RECLOSER | 3533 | 20240330 | 2038 | 20240401 | 226 | 2419294 | 1690 | Distribution Circuit | Animal | Other | 203 | 27489 | 34.9277 | -119.5952 | No | Overcast-Fog;32-90 F | Lightning Arrestor | Burned/flashed | 24-0048850 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929664 | 0 | EPSS Ckt | N | 2024 | C GRD
KERN | KERN | CHARCA-1102 | 254501102 | RECLOSER | 4769 | 20240331 | 539 | 20240331 | 614 | 2419393 | 35 | Distribution Circuit | 3rd Party | Vehicle | 12 | 420 | 35.6671 | -119.3307 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0048884 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1929697 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | 517702265471 | 20240331 | 746 | 20240331 | 1442 | 2419384 | 416 | Transformer only | 3rd Party | Customer Equipment | 3 | 1248 | 35.2967 | -118.7709 | No | Partly Cloudy;32-90 F | Customer Equipment | Broken | 24-0048896 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929706 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CHARCA-1102 | 254501102 | RECLOSER | 4769 | 20240331 | 1308 | 20240331 | 1325 | 2419538 | 17 | Distribution Circuit | 3rd Party | Vehicle | 12 | 204 | 35.6671 | -119.3307 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0048923 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1929733 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | RENFRO-2105 | 254572105 | FUSE | 17258 | 20240331 | 1440 | 20240331 | 1547 | 2419569 | 67 | Distribution Circuit | Equipment Failure/Involved | Underground | 73 | 4891 | 35.398 | -119.1557 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0048927 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929738 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | OTHER | T9478 TWD T10355 | 20240331 | 1622 | 20240331 | 2129 | 2419594 | 307 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 3070 | 35.3998 | -119.1577 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0048927 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1929743 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1101 | 252021101 | RECLOSER | 3609 | 20240331 | 1903 | 20240401 | 1241 | 2419709 | 1058 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 12489 | 35.6583 | -120.0132 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048938 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1929754 | 0 | EPSS Ckt | N | 2024 | GRD- SGF
KERN | KERN | ARVIN-1102 | 253801102 | RECLOSER | 35412 | 20240331 | 1936 | 20240401 | 1213 | 2419721 | 989 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 64126 | 35.1582 | -118.9054 | No | Lightning-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048943 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1929759 | 0 | Non-EPSS | N | 2024 | C GRD
KERN | KERN | LAKEVIEW-1106 | 253411106 | RECLOSER | 4796 | 20240331 | 1947 | 20240401 | 1604 | 2419728 | 1217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 26587 | 35.0754 | -119.0827 | No | Partly Cloudy-Lightning;32-90 F |  |  | 24-0048945 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929762 | 0 | EPSS Ckt | N | 2024 | C GRD
KERN | KERN | LERDO-1112 | 253491112 | RECLOSER | 4323 | 20240401 | 708 | 20240401 | 1530 | 2419839 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 125 | 38404 | 35.5151 | -119.0819 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048980 | OH | Sus | 31689367 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1929794 | 0 | Non-EPSS | N | 2024 | B- C & GRD
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515773068875 | 20240401 | 748 | 20240401 | 955 | 2419855 | 127 | Transformer only | Animal | Other | 1 | 127 | 35.3838 | -119.4195 | No | Clear;32-90 F | Fuse | Broken | 24-0049077 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1929942 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515793382456 | 20240401 | 754 | 20240401 | 1300 | 2419863 | 306 | Transformer only | Animal | Other | 1 | 306 | 35.757 | -119.419 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0049209 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1929988 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 515529783425 | 20240401 | 829 | 20240401 | 1534 | 2419914 | 425 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 425 | 35.7827 | -119.5077 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 24-0049269 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930002 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 14152 | 20240401 | 838 | 20240401 | 1255 | 2419922 | 257 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 514 | 35.3326 | -119.2528 | No | Clear;32-90 F |  |  | 24-0049193 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1929983 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1112 | 253491112 | TRANSFORMER | 516729273348 | 20240401 | 839 | 20240401 | 1115 | 2419936 | 156 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 156 | 35.5103 | -119.0998 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0049139 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1929968 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515300472730 | 20240401 | 849 | 20240401 | 1815 | 2419958 | 566 | Transformer only | Animal | Other | 1 | 566 | 35.4876 | -119.5791 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0049130 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1929965 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1103 | 252081103 | FUSE | 15491 | 20240401 | 924 | 20240401 | 1708 | 2420051 | 464 | Distribution Circuit | 3rd Party | Vehicle | 16 | 7424 | 35.1668 | -119.4651 | No | Clear;32-90 F | Insulator | Broken- wire on ground | 24-0049089 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1929950 | 1 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1103 | 254541103 | FUSE | 14712 | 20240401 | 936 | 20240402 | 159 | 2420068 | 983 | Transformer only | Animal | Bird found | 1 | 983 | 35.5433 | -119.4388 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0049203 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1929986 | 0 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1101 | 253191101 | TRANSFORMER | 517550157007 | 20240401 | 1024 | 20240401 | 1355 | 2420128 | 211 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 211 | 35.0639 | -118.8204 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0049252 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1929996 | 0 | EPSS Ckt | N | 2024
KERN | KERN | OLD RIVER-1105 | 252821105 | FUSE | 100000028197 | 20240401 | 1128 | 20240401 | 2131 | 2420214 | 603 | Distribution Circuit | Animal | Other | 1 | 603 | 35.238 | -119.1727 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0049238 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1929993 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1105 | 252821105 | FUSE | 427514 | 20240401 | 1135 | 20240412 | 734 | 2420272 | 15599 | Distribution Circuit | Animal | Other | 1 | 15599 | 35.2456 | -119.1677 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0049190 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1929982 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | TRANSFORMER | 516214467188 | 20240401 | 1216 | 20240401 | 1521 | 2419942 | 185 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 185 | 35.3397 | -119.2702 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0049168 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1929975 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20240401 | 1248 | 20240402 | 228 | 2420275 | 820 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 21 | 5200 | 35.5593 | -118.9575 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0049195 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1929984 | 0 | EPSS Ckt | N | 2024 | B- C & GRD
KERN | KERN | TEVIS-2104 | 255322104 | TRANSFORMER | T88115 | 20240401 | 1341 | 20240401 | 1532 | 2420307 | 111 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 111 | 35.3128 | -119.177 | No | Clear;32-90 F |  |  | 24-0049323 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1930010 | 0 | Non-EPSS | N | 2024
KERN | KERN | MARICOPA-1101 | 254211101 | SWITCH | 1667 | 20240401 | 1548 | 20240401 | 1600 | 2420400 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 24 | 35.1085 | -119.3634 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0048652 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930015 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | FUSE | 9040 | 20240402 | 738 | 20240402 | 1145 | 2420689 | 247 | Distribution Circuit | Animal | Bird found | 3 | 741 | 35.0449 | -119.8681 | No | Clear;32-90 F | Fuse | Burned Open | 24-0049671 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930303 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ARVIN-1102 | 253801102 | TRANSFORMER | 517260360868 | 20240402 | 856 | 20240402 | 1950 | 2420809 | 654 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 654 | 35.1695 | -118.9179 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0049767 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930328 | 0 | Non-EPSS | N | 2024
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515872857327 | 20240402 | 1001 | 20240402 | 1443 | 2420926 | 282 | Transformer only | Animal | Other | 1 | 282 | 35.0674 | -119.3795 | No | Clear;32-90 F | Fuse | Broken | 24-0049841 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930338 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 623843 | 20240402 | 1110 | 20240402 | 1620 | 2420984 | 310 | Distribution Circuit | Animal | Bird found | 1 | 310 | 35.3171 | -119.1723 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0049913 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930349 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517067168074 | 20240402 | 1126 | 20240402 | 1236 | 2420998 | 70 | Transformer only | Vegetation | Tree - branch fell on line | 29 | 2030 | 35.367 | -118.984 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0049746 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930325 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1110 | 253951110 | FUSE | 17553 | 20240402 | 1138 | 20240402 | 1249 | 2421011 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1207 | 35.4011 | -118.949 | No | Clear;32-90 F |  |  | 24-0049734 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1930320 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517151161256 | 20240402 | 1421 | 20240402 | 2220 | 2420983 | 479 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 479 | 35.1795 | -118.9543 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0049814 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930335 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517086762866 | 20240402 | 1500 | 20240403 | 135 | 2421017 | 635 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1270 | 35.2232 | -118.9761 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0049853 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930339 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1112 | 252901112 | FUSE | 18430 | 20240402 | 1724 | 20240403 | 115 | 2421252 | 471 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1275 | 35.6234 | -119.4377 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0049946 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1930368 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2101 | 255262101 | FUSE | 814779 | 20240402 | 2020 | 20240402 | 2145 | 2421314 | 85 | Distribution Circuit | 3rd Party | Metallic Balloon | 1 | 85 | 35.3891 | -119.0952 | No | Clear;32-90 F | Fuse | Burned Open | 24-0049956 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930381 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 8486 | 20240402 | 2141 | 20240403 | 912 | 2421357 | 691 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 39387 | 35.3212 | -119.0095 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0049981 | UG | Sus | 46219604 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930407 | 0 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1104 | 254541104 | TRANSFORMER | 100000107214 | 20240403 | 722 | 20240403 | 2141 | 2421481 | 859 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 859 | 35.5144 | -119.4399 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0050324 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930645 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517368866706 | 20240403 | 744 | 20240403 | 851 | 2421496 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 67 | 35.3298 | -118.8831 | No | Clear;32-90 F | Fuse | Broken | 24-0050064 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930506 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARNERAS-1103 | 252321103 | FUSE | 16010 | 20240403 | 825 | 20240403 | 1812 | 2421547 | 587 | Distribution Circuit | Animal | Other | 3 | 1761 | 35.5792 | -119.7546 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0050423 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930676 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 177119 | 20240403 | 853 | 20240403 | 1700 | 2421719 | 487 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 487 | 35.3546 | -119.3902 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0050109 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1930590 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 517108059950 | 20240403 | 950 | 20240403 | 2254 | 2421696 | 784 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1568 | 35.1433 | -118.9682 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0050224 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930623 | 0 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1104 | 254541104 | TRANSFORMER | 515849571927 | 20240403 | 1038 | 20240403 | 2142 | 2421739 | 664 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 664 | 35.4685 | -119.3947 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0050360 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930658 | 0 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2102 | 254582102 | TRANSFORMER | 516609470382 | 20240403 | 1254 | 20240404 | 436 | 2421870 | 942 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 942 | 35.4284 | -119.1387 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0050281 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930635 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516576260060 | 20240403 | 1357 | 20240403 | 2142 | 2421901 | 465 | Transformer only | Animal | Other | 1 | 465 | 35.1449 | -119.1458 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0050422 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930675 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517248065864 | 20240403 | 1359 | 20240403 | 1510 | 2421902 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 71 | 35.3063 | -118.9235 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0050337 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930652 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 54429 | 20240403 | 1400 | 20240403 | 1728 | 2421896 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 832 | 35.3979 | -119.0709 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0050271 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930633 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | TRANSFORMER | 516317266275 | 20240403 | 1411 | 20240403 | 1650 | 2421910 | 159 | Transformer only | 3rd Party | Other | 1 | 159 | 35.3151 | -119.2354 | No | Clear;32-90 F | Fuse | Normal | 24-0050407 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930664 | 0 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2102 | 254582102 | TRANSFORMER | 516609470382 | 20240404 | 642 | 20240404 | 2138 | 2422206 | 896 | Transformer only | Company Initiated | Improper Construction | 1 | 896 | 35.4284 | -119.1387 | No | Overcast;32-90 F | Transformer | Burned/flashed | 24-0050575 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930797 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 515538381736 | 20240404 | 1330 | 20240404 | 1615 | 2422452 | 165 | Transformer only | Animal | Other | 1 | 165 | 35.7387 | -119.5067 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0050872 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930890 | 0 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1104 | 253191104 | TRANSFORMER | 517336558633 | 20240404 | 1352 | 20240405 | 52 | 2422576 | 660 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 660 | 35.1078 | -118.8915 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0050958 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930909 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | RECLOSER | 4107 | 20240404 | 1452 | 20240405 | 229 | 2422768 | 697 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 11807 | 35.3327 | -119.3061 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0050913 | OH | Sus | 35541975 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1930895 | 0 | Non-EPSS | N | 2024 | A GRD
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 18146 | 20240404 | 1502 | 20240404 | 1553 | 2422787 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 85 | 35.3835 | -119.2032 | No | Overcast-Rain;32-90 F |  |  | 24-0050957 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930908 | 1 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2101 | 255322101 | TRANSFORMER | 100000013379 | 20240404 | 1503 | 20240405 | 53 | 2422784 | 590 | Transformer only | Animal | Other | 1 | 590 | 35.2602 | -119.1815 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0051053 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930972 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1103 | 252611103 | FUSE | 17090 | 20240404 | 1519 | 20240405 | 503 | 2423184 | 824 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1648 | 35.4423 | -119.3942 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0051049 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930969 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | RECLOSER | 3522 | 20240404 | 1542 | 20240404 | 1850 | 2422913 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 28012 | 35.2297 | -119.3762 | No | Partly Cloudy;32-90 F |  |  | 24-0050954 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930905 | 0 | Non-EPSS | N | 2024 | B C
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 18146 | 20240404 | 1616 | 20240405 | 438 | s1931005 | 742 | Distribution Circuit | 3rd Party | Other | 5 | 3662 | 35.3835 | -119.2032 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051082 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931005 | 1 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1101 | 252971101 | FUSE | 16550 | 20240404 | 1620 | 20240404 | 1816 | 2422996 | 116 | Distribution Circuit | Animal | Other | 3 | 309 | 35.1941 | -118.9148 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0051019 | OH | Sus | 0 | CENTRAL VALLEY | APR |  | 0 | No | No | No | 1930945 | 1 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 16559 | 20240404 | 1658 | 20240404 | 1920 | 2423035 | 142 | Distribution Circuit | Animal | Other | 7 | 994 | 35.1945 | -118.797 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0051034 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930955 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16169 | 20240404 | 1659 | 20240404 | 1915 | 2423047 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 408 | 35.0946 | -119.1072 | No | Clear;32-90 F |  |  | 24-0051030 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930951 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515625269465 | 20240404 | 1731 | 20240404 | 1941 | 2423069 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 2210 | 35.4 | -119.4692 | No | Clear;32-90 F | Fuse | Broken | 24-0051038 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930959 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515627669498 | 20240404 | 1832 | 20240404 | 1927 | 2423118 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 385 | 35.4009 | -119.4684 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0051036 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930957 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | FUSE | 17872 | 20240404 | 1951 | 20240404 | 2258 | 2423166 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1309 | 35.3975 | -119.7532 | No | Clear-Strong Winds;32-90 F |  |  | 24-0051089 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931015 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | FUSE | 14233 | 20240404 | 2016 | 20240405 | 950 | 2423176 | 814 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 7326 | 35.368 | -119.7352 | No | Clear-Strong Winds;32-90 F |  |  | 24-0051196 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931121 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SHAFTER-1103 | 253651103 | FUSE | 79677 | 20240405 | 616 | 20240405 | 842 | 2423548 | 146 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 27 | 3942 | 35.5216 | -119.3137 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0051228 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931180 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | RECLOSER | 3533 | 20240405 | 1159 | 20240405 | 1350 | 2424092 | 111 | Distribution Circuit | Animal | Other | 204 | 22644 | 34.9277 | -119.5952 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0051400 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931256 | 0 | EPSS Ckt | N | 2024 | C GRD
KERN | KERN | MCKITTRICK-1101 | 252781101 | TRANSFORMER | 514783365248 | 20240405 | 1234 | 20240405 | 2217 | 2424898 | 583 | Transformer only | 3rd Party | Customer Equipment | 1 | 583 | 35.2811 | -119.7486 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0051638 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931402 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-1105 | 252771105 | FUSE | 15261 | 20240405 | 1427 | 20240406 | 343 | 2424270 | 796 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 15124 | 35.3687 | -118.9391 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 24-0051500 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931303 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 18061 | 20240405 | 1609 | 20240406 | 45 | 2424998 | 516 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 516 | 35.663 | -119.5089 | No | Partly Cloudy;32-90 F |  |  | 24-0051674 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931441 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1104 | 252901104 | FUSE | 18449 | 20240405 | 1611 | 20240405 | 1933 | 2424620 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1010 | 35.6302 | -119.5101 | No | Overcast-Lightning;32-90 F | Fuse | Burned Open | 24-0051626 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931390 | 0 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1102 | 253801102 | OCB | 1102/2 | 20240405 | 1626 | 20240405 | 1639 | 2424643 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 516 | 6708 | 35.1499 | -118.8789 | No | Clear-Lightning;32-90 F |  |  | 24-0051562 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931341 | 0 | Non-EPSS | N | 2024 | BU OC INST TIME
KERN | KERN | GANSO-1104 | 254541104 | FUSE | 17080 | 20240405 | 1631 | 20240405 | 2123 | 2424642 | 292 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2336 | 35.5007 | -119.4392 | No | Overcast;32-90 F |  |  | 24-0051647 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931412 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 7505 | 20240405 | 1636 | 20240405 | 1830 | 2424671 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 3802 | 35.5072 | -119.2733 | No | Overcast;32-90 F |  |  | 24-0051604 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931371 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2101 | 255262101 | OTHER | J1328 TWD T10581 | 20240405 | 1654 | 20240405 | 1727 | 2424759 | 33 | Distribution Circuit | Company Initiated | Improper Construction | 67 | 2211 | 35.3997 | -119.0991 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Underground | Normal | 24-0051452 | UG | Sus | 35542181 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931361 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2101 | 255262101 | OTHER | J1328 TWD T10580 | 20240405 | 1727 | 20240405 | 1822 | s1931860 | 55 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 605 | 35.3997 | -119.0991 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 24-0051452 | UG | Sus | 35542181 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931860 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1104 | 252901104 | TRANSFORMER | 515517977869 | 20240405 | 1738 | 20240405 | 1920 | 2424755 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 102 | 35.6304 | -119.509 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0051595 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931365 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1112 | 253491112 | FUSE | 16367 | 20240405 | 1759 | 20240406 | 710 | 2424796 | 791 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1582 | 35.4851 | -119.0831 | No | Partly Cloudy-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0051612 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931376 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | SWITCH | 1214 | 20240405 | 1853 | 20240405 | 1913 | 2424726 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 560 | 35.6612 | -119.5088 | No | Overcast-Lightning;32-90 F | Jumper | Burned Open | 24-0051615 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931379 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517390262835 | 20240405 | 1921 | 20240405 | 2015 | 2424848 | 54 | Transformer only | Vegetation | Tree - grew into line | 2 | 108 | 35.2235 | -118.8746 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0051636 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931399 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 15558 | 20240405 | 1933 | 20240405 | 2016 | 2424860 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 430 | 35.373 | -118.9839 | No | Overcast-Drizzle;32-90 F |  |  | 24-0051632 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931395 | 1 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515519178906 | 20240405 | 2008 | 20240405 | 2150 | 2424880 | 102 | Transformer only | Environmental/External | Lightning | 1 | 102 | 35.6586 | -119.5088 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051642 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931406 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | RECLOSER | 4164 | 20240405 | 2012 | 20240406 | 1004 | 2424885 | 832 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 33754 | 35.0595 | -118.978 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0051634 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931397 | 0 | EPSS Ckt | N | 2024 | A & C
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515520179181 | 20240406 | 734 | 20240406 | 909 | 2425073 | 95 | Transformer only | Environmental/External | Lightning | 1 | 95 | 35.6661 | -119.5088 | No | Partly Cloudy-Fog;32-90 F | Fuse | Failed/Faulted | 24-0051707 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931482 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517064167467 | 20240406 | 805 | 20240406 | 918 | 2425095 | 73 | Transformer only | Company Initiated | Coordination failure | 5 | 365 | 35.3503 | -118.9849 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0045528 | OH | Sus | 47040063 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1931456 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1112 | 252901112 | FUSE | 87100 | 20240406 | 1244 | 20240406 | 1419 | 2425285 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 665 | 35.6304 | -119.4561 | No | Clear;32-90 F |  |  | 24-0051787 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1931546 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517172667947 | 20240406 | 1257 | 20240406 | 1803 | 2425263 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 306 | 35.3638 | -118.9487 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 24-0051773 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931539 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 55512 | 20240406 | 1624 | 20240408 | 125 | 2425388 | 1981 | Distribution Circuit | Environmental/External | Lightning | 2 | 3962 | 34.9275 | -119.5442 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0051820 | OH | Sus | 31689839 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1931565 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | FUSE | 762669 | 20240406 | 2007 | 20240407 | 1025 | 2425466 | 858 | Distribution Circuit | Animal | Other | 2 | 1016 | 35.4281 | -118.8443 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051843 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1931586 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 13346 | 20240407 | 1235 | 20240407 | 1335 | 2425688 | 60 | Distribution Circuit | 3rd Party | Vehicle | 177 | 10605 | 35.4198 | -119.0134 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0051887 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931641 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1106 | 254071106 | FUSE | 17597 | 20240407 | 1432 | 20240407 | 1447 | 2425699 | 15 | Distribution Circuit | 3rd Party | Other | 20 | 300 | 35.3338 | -119.0456 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0051896 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931649 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1103 | 252861103 | FUSE | 15677 | 20240408 | 213 | 20240408 | 345 | 2425893 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 184 | 35.4413 | -119.2362 | No | Clear;32-90 F |  |  | 24-0051957 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931710 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | FUSE | 16099 | 20240408 | 853 | 20240408 | 1202 | 2426043 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 755 | 35.6014 | -119.6175 | No | Clear;32-90 F |  |  | 24-0052106 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931878 | 1 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1113 | 253491113 | TRANSFORMER | 516511574872 | 20240408 | 907 | 20240409 | 410 | 2426075 | 1143 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1143 | 35.5513 | -119.1733 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0052298 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931931 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | 516416368686 | 20240408 | 1225 | 20240408 | 1608 | 2426304 | 223 | Transformer only | 3rd Party | Customer Equipment | 1 | 223 | 35.3811 | -119.2033 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 24-0052202 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931905 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515520179181 | 20240408 | 1241 | 20240409 | 20 | 2425989 | 699 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 699 | 35.6661 | -119.5088 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0052135 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931891 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1112 | 252901112 | FUSE | 95912 | 20240408 | 1247 | 20240408 | 1618 | 2426324 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 281 | 35.6387 | -119.4556 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0052265 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931921 | 1 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | FUSE | 13145 | 20240408 | 1343 | 20240408 | 1829 | 2426571 | 286 | Distribution Circuit | Animal | Other | 1 | 286 | 35.3452 | -119.2891 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0052304 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931933 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1106 | 254071106 | INTERRUPTER | 318706 | 20240408 | 1718 | 20240409 | 1332 | 2426538 | 1214 | Distribution Circuit | Equipment Failure/Involved | Underground | 109 | 93521 | 35.3239 | -119.0564 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0052317 | UG | Sus | 35542718 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931941 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 8788 | 20240408 | 1949 | 20240408 | 2246 | 2426606 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 126 | 21186 | 35.344 | -119.063 | No | Clear;32-90 F |  |  | 24-0052398 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932026 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1110 | 252721110 | TRIP-SAVER | 8628 | 20240408 | 2120 | 20240408 | 2337 | 2426628 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 250 | 32500 | 35.416 | -119.0235 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0052327 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931951 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516867778200 | 20240409 | 842 | 20240409 | 1145 | 2426809 | 183 | Transformer only | Animal | Other | 1 | 183 | 35.644 | -119.0553 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0052530 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932200 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | FUSE | 7267 | 20240409 | 1009 | 20240409 | 1721 | 2427321 | 432 | Distribution Circuit | 3rd Party | Vandalism | 2 | 864 | 35.6446 | -119.7142 | No | Clear;32-90 F | Secondary | On Ground | 24-0052790 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932276 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | TRANSFORMER | 517510555284 | 20240409 | 1115 | 20240409 | 1124 | 2426719 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 9 | 35.0162 | -118.8335 | No | Clear;32-90 F | Secondary | Normal | 24-0052582 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932223 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 16869 | 20240409 | 1245 | 20240409 | 1355 | 2427106 | 70 | Distribution Circuit | 3rd Party | Metallic Balloon | 71 | 4996 | 35.3718 | -118.9586 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0052695 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932258 | 1 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 100000016531 | 20240409 | 1256 | 20240409 | 1536 | 2427117 | 160 | Transformer only | Animal | Bird found | 1 | 160 | 35.5645 | -119.5722 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0052636 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932248 | 0 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1103 | 254541103 | FUSE | 64111 | 20240409 | 1439 | 20240409 | 1817 | 2427393 | 218 | Distribution Circuit | Animal | Other | 1 | 218 | 35.5033 | -119.5619 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0052838 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932289 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516639077370 | 20240410 | 831 | 20240410 | 1140 | 2427598 | 189 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 378 | 35.6206 | -119.1318 | No | Clear;32-90 F |  |  | 24-0053067 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1932518 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516766763818 | 20240410 | 947 | 20240410 | 1102 | 2427749 | 75 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 75 | 35.2488 | -119.0832 | No | Clear;32-90 F |  |  | 24-0053050 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1932506 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1101 | 252971101 | JUMPER | BURNT OJ S/OF CGC 517296061800 | 20240410 | 1527 | 20240410 | 1814 | 2428000 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 422 | 35.1946 | -118.9051 | No | Clear;32-90 F | Jumper | Burned Open | 24-0053301 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1932565 | 1 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-2102 | 254762102 | FUSE | 11459 | 20240410 | 1611 | 20240411 | 751 | 2428031 | 940 | Distribution Circuit | Equipment Failure/Involved | Underground | 93 | 34723 | 35.3603 | -119.0647 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0053287 | UG | Sus | 46227327 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932562 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516766763818 | 20240410 | 1625 | 20240410 | 2215 | 2427939 | 350 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 350 | 35.2488 | -119.0832 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0053269 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932553 | 0 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1104 | 254541104 | TRANSFORMER | 515849571927 | 20240410 | 1635 | 20240410 | 2300 | 2428048 | 385 | Transformer only | Animal | Other | 1 | 385 | 35.4685 | -119.3947 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0053275 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932556 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 16072 | 20240410 | 1647 | 20240411 | 158 | 2428054 | 551 | Distribution Circuit | Animal | Other | 8 | 4408 | 35.72 | -119.8587 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0053351 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932607 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 517061264810 | 20240411 | 57 | 20240411 | 504 | 2428188 | 232 | Distribution Circuit | 3rd Party | Vehicle | 5 | 1139 | 35.2767 | -118.9854 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0053347 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932603 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 8501 | 20240411 | 644 | 20240411 | 939 | 2428227 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1925 | 35.2651 | -118.9188 | No | Clear;32-90 F |  |  | 24-0053434 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932746 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 9464 | 20240411 | 859 | 20240411 | 1920 | 2428235 | 621 | Distribution Circuit | Equipment Failure/Involved | Underground | 41 | 12481 | 35.3798 | -119.0755 | No | Clear;32-90 F | Secondary | Burned Open | 24-0053405 | UG | Sus | 31690305 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932661 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | FUSE | 15373 | 20240411 | 1037 | 20240411 | 1725 | 2428463 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 10320 | 35.3615 | -119.0277 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0053456 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932760 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | TRANSFORMER | 515433061222 | 20240411 | 1257 | 20240411 | 1357 | 2428629 | 60 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 60 | 35.1729 | -119.5291 | No | Clear;32-90 F |  |  | 24-0053625 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1932820 | 0 | EPSS Ckt | N | 2024
KERN | KERN | COPUS-1104 | 253871104 | RECLOSER | 3551 | 20240411 | 1701 | 20240411 | 1719 | 2428838 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 1404 | 35.0814 | -119.2782 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0053760 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932845 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | STOCKDALE-2114 | 254072114 | TRANSFORMER | 516797867407 | 20240411 | 1924 | 20240412 | 145 | 2428942 | 381 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2286 | 35.3475 | -119.0747 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0053847 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932929 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15048 | 20240412 | 749 | 20240412 | 939 | 2429145 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 5610 | 35.338 | -118.9147 | No | Clear;32-90 F |  |  | 24-0053965 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933077 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | FUSE | 18326 | 20240412 | 1327 | 20240413 | 645 | 2429552 | 1038 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1209 | 35.2821 | -118.7708 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0054200 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933163 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | RECLOSER | 2862 | 20240412 | 1356 | 20240412 | 1437 | 2429569 | 41 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 226 | 9266 | 35.2817 | -118.8798 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0054147 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1933139 | 0 | EPSS Ckt | N | 2024 | A B C INSTANTANEOUS
KERN | KERN | WESTPARK-1102 | 253701102 | TRANSFORMER | 516956368317 | 20240412 | 1402 | 20240412 | 1511 | 2429570 | 69 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 69 | 35.3728 | -119.0217 | No | Clear;32-90 F | Fuse | Broken | 24-0054194 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933156 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | FUSE | 15374 | 20240412 | 1439 | 20240412 | 1607 | 2429612 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 5752 | 35.3612 | -119.0249 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0054218 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933170 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 13346 | 20240412 | 1529 | 20240412 | 1635 | 2429802 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 177 | 11666 | 35.4198 | -119.0134 | No | Clear;32-90 F |  |  | 24-0054211 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933167 | 1 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | OCB | 2102/2 | 20240412 | 1649 | 20240413 | 2332 | 2429869 | 1816 | Distribution Circuit | 3rd Party | Other | 5436 | 462284 | 35.2955 | -119.0219 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0054231 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1933177 | 0 | Non-EPSS | N | 2024 | A B GRD TIME
KERN | KERN | STOCKDALE-2106 | 254072106 | TRANSFORMER | T3839 | 20240412 | 2044 | 20240413 | 545 | 2429944 | 541 | Transformer only | Equipment Failure/Involved | Underground | 10 | 5410 | 35.3023 | -119.0306 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0054282 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933207 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 144603 | 20240413 | 808 | 20240413 | 1443 | 2430184 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2898 | 35.471 | -119.3338 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0054386 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933291 | 1 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 684566 | 20240413 | 1213 | 20240414 | 935 | 2430304 | 1282 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 7692 | 35.0707 | -119.9955 | No | Overcast-Rain;32-90 F |  |  | 24-0054421 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933312 | 0 | EPSS Ckt | N | 2024 | B- C
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 13346 | 20240413 | 1226 | 20240413 | 1524 | 2430315 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 264 | 42768 | 35.4198 | -119.0134 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0054436 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933324 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRIP-SAVER | 9871 | 20240413 | 1234 | 20240413 | 1422 | 2430323 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2737 | 35.3253 | -118.9134 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0054465 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933349 | 1 | Non-EPSS | N | 2024 | A
KERN | KERN | GANSO-1104 | 254541104 | FUSE | 17080 | 20240413 | 1329 | 20240413 | 1659 | 2430397 | 206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1648 | 35.5007 | -119.4392 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0054474 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933354 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | SWITCH | 4149 | 20240413 | 1338 | 20240413 | 1421 | 2430517 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 566 | 24338 | 35.3546 | -119.0744 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0054468 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933352 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15062 | 20240413 | 1339 | 20240413 | 2145 | 2430427 | 486 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 26257 | 35.3325 | -118.9142 | No | Clear;32-90 F |  |  | 24-0054582 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933447 | 1 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 7505 | 20240413 | 1347 | 20240413 | 1500 | 2430433 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 2435 | 35.5072 | -119.2733 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0054511 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933375 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8640 | 20240413 | 1354 | 20240413 | 1740 | 2430850 | 226 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 12360 | 35.354 | -119.0744 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0054543 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933410 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517228565756 | 20240413 | 1401 | 20240413 | 2228 | 2430612 | 507 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 507 | 35.3033 | -118.9299 | No | Clear;32-90 F |  |  | 24-0054598 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1933463 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 15636 | 20240413 | 1407 | 20240413 | 1522 | 2430491 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 3750 | 35.3388 | -119.0281 | No | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Deteriorated | 24-0054489 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933364 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 8927 | 20240413 | 1411 | 20240413 | 1528 | 2430502 | 77 | Distribution Circuit | Vegetation | Tree - branch fell on line | 385 | 29645 | 35.3473 | -119.048 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0054507 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933372 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20240413 | 1430 | 20240414 | 1541 | 2430542 | 1511 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 31731 | 35.5593 | -118.9575 | No | Overcast-Rain;32-90 F |  |  | 24-0054479 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1933357 | 0 | EPSS Ckt | N | 2024 | A B C
KERN | KERN | MCKITTRICK-1101 | 252781101 | OCB | 1101/2 | 20240413 | 1431 | 20240414 | 9 | 2430547 | 578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 149 | 36528 | 35.297 | -119.6266 | No | Overcast-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0054481 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1933359 | 0 | EPSS Ckt | N | 2024 | A- B- PH OC TIME
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | T468900 | 20240413 | 1438 | 20240413 | 1708 | 2430552 | 150 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 150 | 35.6221 | -119.0785 | No | Overcast-Fog;32-90 F |  |  | 24-0054531 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1933394 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2103 | 254242103 | OCB | 2103/2 | 20240413 | 1438 | 20240413 | 2010 | 2430568 | 332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 189 | 62748 | 35.1948 | -119.5861 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0054485 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1933361 | 0 | EPSS Ckt | N | 2024 | A-B- C
KERN | KERN | KERN OIL-1104 | 252721104 | FUSE | 13348 | 20240413 | 1441 | 20240414 | 1900 | s1933494 | 1699 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 61164 | 35.4993 | -119.0111 | No | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0054503 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1933494 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 9636 | 20240413 | 1444 | 20240414 | 1048 | 2430581 | 1204 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 15652 | 35.3486 | -119.0735 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0054524 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933387 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 17613 | 20240413 | 1445 | 20240413 | 1533 | 2430586 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 1248 | 35.4196 | -119.0666 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0054508 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933373 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516946969706 | 20240413 | 1449 | 20240413 | 1809 | 2430589 | 200 | Transformer only | Unknown Cause | Patrol - found nothing | 19 | 3800 | 35.4109 | -119.0254 | No | Overcast-Strong Winds;32-90 F |  |  | 24-0054545 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1933411 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 18170 | 20240413 | 1455 | 20240414 | 1849 | 2430590 | 1674 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 105462 | 35.4068 | -119.019 | No | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0054525 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1933388 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | OCB | 1104/2 | 20240413 | 1455 | 20240414 | 1300 | 2431090 | 1325 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 88780 | 35.3831 | -119.6964 | No | Clear-Strong Winds;32-90 F |  |  | 24-0054636 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1933501 | 0 | EPSS Ckt | N | 2024 | A- B- C
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 14859 | 20240413 | 1459 | 20240414 | 1742 | 2430601 | 1603 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 54502 | 35.4558 | -118.9206 | No | Overcast-Strong Winds;32-90 F |  |  | 24-0054713 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933576 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | RECLOSER | 3459 | 20240413 | 1504 | 20240413 | 1607 | 2430626 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2823 | 177849 | 35.3755 | -118.9941 | No | Overcast-Drizzle;32-90 F |  |  | 24-0054494 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933366 | 0 | Non-EPSS | N | 2024 | A & B TIME
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20240413 | 1508 | 20240413 | 1731 | 2430634 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1677 | 239811 | 35.3885 | -119.0046 | No | Overcast-Strong Winds;32-90 F |  |  | 24-0054523 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933386 | 0 | Non-EPSS | N | 2024 | A & C
KERN | KERN | KERN OIL-1104 | 252721104 | OCB | 1104/2 | 20240413 | 1525 | 20240413 | 1613 | 2430651 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 7536 | 35.4407 | -119.0204 | No | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0054503 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933371 | 0 | EPSS Ckt | N | 2024 | NONE
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 7406 | 20240413 | 1526 | 20240413 | 2140 | 2430775 | 374 | Distribution Circuit | Animal | Other | 6 | 2245 | 35.7018 | -119.5797 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Normal | 24-0054580 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933445 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | FUSE | 9791 | 20240413 | 1530 | 20240413 | 2147 | 2430658 | 377 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2262 | 35.3257 | -118.7986 | No | Overcast-Drizzle;32-90 F |  |  | 24-0054583 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933448 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 7371 | 20240413 | 1541 | 20240413 | 2116 | 2430671 | 319 | Distribution Circuit | Animal | Other | 10 | 3190 | 35.3841 | -119.4482 | No | Clear;32-90 F | Crossarm- Wood | Normal | 24-0054578 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933443 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 97055 | 20240413 | 1602 | 20240414 | 1743 | 2430631 | 1541 | Distribution Circuit | 3rd Party | Other | 13 | 20033 | 35.133 | -119.4737 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0054522 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933385 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 8915 | 20240413 | 1611 | 20240414 | 1809 | 2430712 | 1558 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 32718 | 35.0244 | -118.7702 | No | Overcast-Fog;32-90 F |  |  | 24-0054730 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933590 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN OIL-1110 | 252721110 | FUSE | 15282 | 20240413 | 1612 | 20240413 | 1720 | 2430796 | 68 | Distribution Circuit | Company Initiated | Return Circuit Normal | 200 | 13600 | 35.4232 | -119.0196 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0054436 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1933397 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1110 | 252721110 | OCB | 1110/2 | 20240413 | 1614 | 20240414 | 633 | 2430728 | 859 | Distribution Circuit | Equipment Failure/Involved | Underground | 3155 | 393690 | 35.4407 | -119.0205 | No | Clear;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0054534 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933398 | 0 | Non-EPSS | N | 2024 | C & GRD
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 629353 | 20240413 | 1618 | 20240416 | 123 | 2430730 | 3425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 10275 | 35.7756 | -119.6896 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0054708 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933571 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | RECLOSER | 4164 | 20240413 | 1651 | 20240413 | 2202 | 2430779 | 311 | Distribution Circuit | Animal | Other | 80 | 24880 | 35.0595 | -118.978 | No | Overcast-Fog;32-90 F | Sectionalizer | Burned/flashed | 24-0054575 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933438 | 0 | EPSS Ckt | N | 2024 | B C GRD
KERN | KERN | MIDWAY-1103 | 252611103 | FUSE | 17092 | 20240413 | 1657 | 20240413 | 1900 | 2430770 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 492 | 35.4421 | -119.3498 | No | Overcast-Drizzle;32-90 F |  |  | 24-0054554 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933418 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13442 | 20240413 | 1658 | 20240414 | 207 | 2430622 | 549 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 13176 | 35.3576 | -118.9677 | No | Overcast-Rain;32-90 F |  |  | 24-0054610 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933477 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 15558 | 20240413 | 1702 | 20240414 | 46 | 2430777 | 464 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 4635 | 35.373 | -118.9839 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0054608 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933475 | 1 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1105 | 253551105 | FUSE | 7415 | 20240413 | 1706 | 20240414 | 1015 | 2430793 | 1029 | Distribution Circuit | Animal | Bird found | 4 | 4116 | 35.761 | -119.4369 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0054668 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933537 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 17654 | 20240413 | 1706 | 20240416 | 1102 | 2430791 | 3956 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 27596 | 35.151 | -118.9657 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0054561 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933423 | 1 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1101 | 252081101 | TRANSFORMER | 515648460062 | 20240413 | 1748 | 20240414 | 2215 | 2430836 | 1707 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 3414 | 35.1417 | -119.4566 | No | Overcast;32-90 F | Jumper | Broken | 24-0054701 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933566 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 16913 | 20240413 | 1909 | 20240414 | 1824 | 2430907 | 1395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 8374 | 35.4818 | -119.2962 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0054687 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933559 | 1 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | RECLOSER | 1052 | 20240413 | 2025 | 20240414 | 1917 | 2430872 | 1372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 52563 | 35.189 | -119.5722 | No | Overcast-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0054570 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1933433 | 0 | EPSS Ckt | N | 2024 | A B C
KERN | KERN | COPUS-1103 | 253871103 | FUSE | 8524 | 20240413 | 2056 | 20240415 | 1319 | 2431331 | 2423 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 57 | 26319 | 35.1228 | -119.2343 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0054702 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1933567 | 1 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1102 | 252461102 | JUMPER | WIRE DOWN 8 E/ OF 3660 | 20240413 | 2305 | 20240414 | 2035 | 2431203 | 1290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 32540 | 35.6166 | -119.1972 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0054664 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | Yes | 1933532 | 1 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 17513 | 20240414 | 701 | 20240414 | 1134 | 2431083 | 273 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 819 | 35.2095 | -119.1864 | No | Clear;32-90 F |  |  | 24-0054675 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933548 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1103 | 252611103 | TRANSFORMER | 515805970613 | 20240414 | 728 | 20240414 | 1304 | 2431100 | 336 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 336 | 35.432 | -119.4086 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0054685 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933557 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517023468480 | 20240414 | 730 | 20240414 | 840 | 2431168 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 140 | 35.3778 | -118.999 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0054653 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933522 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 514084178605 | 20240414 | 809 | 20240416 | 1952 | 2431124 | 3583 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 7166 | 35.6434 | -119.9925 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0054725 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933585 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2105 | 254072105 | JUMPER | FB'S E/OF CGC# 516875365868 | 20240414 | 919 | 20240414 | 1835 | 2431326 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8896 | 35.3054 | -119.0479 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0054699 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933564 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARNERAS-1102 | 252321102 | RECLOSER | 372456 | 20240414 | 922 | 20240414 | 1355 | 2431186 | 231 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 73 | 18980 | 35.543 | -119.7245 | No | Overcast;32-90 F |  |  | 24-0054660 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933528 | 0 | Non-EPSS | N | 2024 | C & GRD
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7285 | 20240414 | 930 | 20240415 | 1138 | 2431188 | 1568 | Distribution Circuit | Animal | Other | 12 | 8086 | 35.4569 | -119.4382 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 24-0054710 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933572 | 1 | Non-EPSS | N | 2024
KERN | KERN | CARNERAS-1102 | 252321102 | RECLOSER | 3266 | 20240414 | 952 | 20240415 | 1645 | s1933538 | 1853 | Distribution Circuit | Animal | Other | 1 | 1853 | 35.5372 | -119.803 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0054665 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933538 | 0 | Non-EPSS | N | 2024 | SGF
KERN | KERN | LAMONT-1102 | 253911102 | SWITCH | 2023 | 20240414 | 1058 | 20240414 | 1540 | 2431231 | 282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 8178 | 35.2525 | -118.8764 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0054658 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933541 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CHARCA-1102 | 254501102 | OCB | 1102/2 | 20240414 | 1114 | 20240414 | 1332 | 2431261 | 138 | Distribution Circuit | 3rd Party | Vehicle | 284 | 38012 | 35.6081 | -119.3255 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0054674 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1933547 | 0 | Non-EPSS | N | 2024 | A- C INST
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 18663 | 20240414 | 1126 | 20240414 | 1851 | 2431271 | 445 | Distribution Circuit | Animal | Bird found | 33 | 14685 | 34.9114 | -119.5953 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0054731 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933591 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SMYRNA-1105 | 253551105 | TRANSFORMER | 515743881275 | 20240414 | 1452 | 20240414 | 1924 | 2431339 | 272 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 272 | 35.7248 | -119.4355 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 24-0054736 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933598 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515934367910 | 20240414 | 1832 | 20240415 | 1353 | 2431416 | 1161 | Transformer only | Animal | Other | 1 | 1161 | 35.3582 | -119.3658 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0054733 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933594 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1102 | 252081102 | SWITCH | 99503 | 20240414 | 1934 | 20240414 | 1940 | 2431440 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 22 | 132 | 35.1368 | -119.482 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Normal | 24-0054570 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1933599 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | SWITCH | 2368 | 20240414 | 2028 | 20240414 | 2047 | 2431476 | 19 | Distribution Circuit | Company Initiated | Return Circuit Normal | 5 | 95 | 35.2079 | -119.5009 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Normal | 24-0054570 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933602 | 0 | EPSS Ckt | N | 2024
KERN | KERN | FAMOSO-1102 | 252461102 | JUMPER | OPEN CENTER PHASE JMPR | 20240414 | 2044 | 20240415 | 1148 | 2431483 | 904 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 26648 | 35.6166 | -119.201 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0054762 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1933626 | 1 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1102 | 253651102 | RECLOSER | 3621 | 20240415 | 634 | 20240415 | 643 | 2431561 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 468 | 35.5153 | -119.2604 | No | Partly Cloudy-Fog;32-90 F | Capacitor | Burned/flashed | 24-0054777 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933640 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 55321 | 20240415 | 706 | 20240415 | 915 | 2431572 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 129 | 35.3493 | -119.0478 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0054845 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933744 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1106 | 252081106 | FUSE | 58901 | 20240415 | 743 | 20240415 | 1110 | 2431590 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 207 | 35.1512 | -119.4715 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 24-0054907 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933790 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1102 | 252021102 | FUSE | 7167 | 20240415 | 935 | 20240416 | 355 | 2431771 | 1100 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 2200 | 35.6596 | -119.9924 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0054970 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933818 | 0 | EPSS Ckt | N | 2024
KERN | KERN | FAMOSO-1101 | 252461101 | FUSE | 16085 | 20240415 | 1010 | 20240415 | 1633 | 2431726 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 766 | 35.631 | -119.1157 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0054876 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933776 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517354765953 | 20240415 | 1016 | 20240415 | 2323 | 2431699 | 787 | Transformer only | Animal | Other | 1 | 787 | 35.3094 | -118.8877 | No | Clear;32-90 F | Transformer | Normal | 24-0054909 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933792 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | TRANSFORMER | 100000022815 | 20240415 | 1024 | 20240415 | 1727 | 2431828 | 423 | Transformer only | Animal | Other | 1 | 423 | 35.6523 | -119.6898 | No | Partly Cloudy;32-90 F | Jumper | Contaminated | 24-0055155 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933866 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | FUSE | 9072 | 20240415 | 1025 | 20240415 | 1220 | 2431830 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 115 | 35.1729 | -119.5214 | No | Clear;32-90 F |  |  | 24-0054966 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933815 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 15070 | 20240415 | 1025 | 20240416 | 444 | 2431832 | 1099 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 2198 | 35.1945 | -118.788 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0054935 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933804 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 770303 | 20240415 | 1027 | 20240415 | 1915 | 2432073 | 528 | Distribution Circuit | Animal | Other | 1 | 528 | 35.4279 | -119.4648 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0055080 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933849 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1103 | 252861103 | TRANSFORMER | 516509970592 | 20240415 | 1253 | 20240416 | 805 | 2431966 | 1152 | Transformer only | Environmental/External | Water | 1 | 1152 | 35.4341 | -119.1722 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 24-0055160 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933869 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | OCB | 1104/2 | 20240415 | 1342 | 20240416 | 148 | 2431837 | 726 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 761 | 120261 | 35.4006 | -119.449 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0055047 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1933840 | 0 | Non-EPSS | N | 2024 | A- B- C- TIME OC
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 1703 | 20240415 | 1429 | 20240416 | 1949 | s1934207 | 1760 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 1760 | 35.559 | -118.9797 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 24-0055595 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | No | No | 1934207 | 0 | EPSS Ckt | N | 2024 | A- B- C- TIME OC
KERN | KERN | MARICOPA-1102 | 254211102 | JUMPER | BURNT OPEN JMPR | 20240415 | 1655 | 20240416 | 1122 | 2432141 | 1107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1107 | 35.0743 | -119.4018 | No | Clear;32-90 F | Jumper | Burned Open | 24-0055182 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1933887 | 1 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517142367853 | 20240415 | 1704 | 20240415 | 1805 | 2432146 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 671 | 35.3607 | -118.9595 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0055146 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933865 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 17372 | 20240415 | 1754 | 20240415 | 1945 | 2432168 | 111 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 2109 | 35.2741 | -119.0094 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0055162 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933871 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1112 | 253701112 | TRANSFORMER | 516860067518 | 20240415 | 1815 | 20240415 | 1830 | 2432191 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 90 | 35.3507 | -119.0538 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0055167 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933874 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516976167095 | 20240415 | 2229 | 20240416 | 1115 | 2432227 | 766 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 766 | 35.3394 | -119.0141 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0055221 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933929 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 513781379404 | 20240416 | 753 | 20240417 | 222 | 2432401 | 1109 | Transformer only | Animal | Other | 2 | 2218 | 35.6651 | -120.0939 | No | Fog;32-90 F | Conductor- Overhead | Broken | 24-0055499 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934172 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 18170 | 20240416 | 845 | 20240416 | 1307 | 2432448 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 16506 | 35.4068 | -119.019 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0055297 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933998 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | TRANSFORMER | 515005576598 | 20240416 | 950 | 20240416 | 1513 | 2432608 | 323 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 323 | 35.5936 | -119.6819 | No | Clear;32-90 F |  |  | 24-0055545 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1934191 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20240416 | 955 | 20240416 | 1137 | 2432613 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 748 | 35.4767 | -119.5887 | No | Clear;32-90 F |  |  | 24-0055410 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934140 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 13547 | 20240416 | 957 | 20240416 | 1741 | 2432619 | 464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 13456 | 35.41 | -119.0427 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0055359 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934111 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | TRANSFORMER | 515498261217 | 20240416 | 1318 | 20240416 | 1622 | 2432770 | 184 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 184 | 35.1729 | -119.5068 | No | Clear;32-90 F |  |  | 24-0055582 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1934200 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516754064480 | 20240416 | 1604 | 20240417 | 222 | 2433094 | 618 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1854 | 35.2671 | -119.0878 | No | Clear;32-90 F | Secondary | Broken | 24-0055729 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934319 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRANSFORMER | 516034671473 | 20240416 | 1618 | 20240417 | 305 | 2432904 | 647 | Transformer only | Animal | Other | 2 | 1294 | 35.4562 | -119.3326 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0055581 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934199 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 14095 | 20240416 | 1739 | 20240416 | 2011 | 2432943 | 152 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 1724 | 35.267 | -118.933 | No | Clear;32-90 F |  |  | 24-0055622 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934229 | 1 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | RECLOSER | 1482 | 20240416 | 2026 | 20240416 | 2247 | 2433033 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 14523 | 35.3665 | -119.4477 | No | Clear;32-90 F | Capacitor | Burned/flashed | 24-0055630 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934232 | 0 | Non-EPSS | N | 2024 | SGF
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 17251 | 20240417 | 12 | 20240417 | 854 | 2433085 | 522 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 5 | 2610 | 35.2689 | -119.0214 | No | Clear;32-90 F | Other | Burned/flashed | 24-0055725 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934316 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20240417 | 608 | 20240417 | 844 | 2433118 | 156 | Distribution Circuit | 3rd Party | Customer Equipment | 32 | 4961 | 35.6271 | -118.9849 | No | Clear;32-90 F | Customer Equipment | Normal | 24-0055735 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934328 | 0 | EPSS Ckt | N | 2024 | C GRD
KERN | KERN | CUYAMA-1103 | 253141103 | FUSE | 9040 | 20240417 | 904 | 20240419 | 1507 | 2434935 | 3243 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 6486 | 35.0449 | -119.8681 | No | Clear;32-90 F |  |  | 24-0056896 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935023 | 0 | EPSS Ckt | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | FUSE | 13974 | 20240417 | 924 | 20240417 | 1620 | 2433337 | 416 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1664 | 35.6071 | -118.9585 | No | Clear;32-90 F |  |  | 24-0056089 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1934570 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | TRANSFORMER | 515195052193 | 20240417 | 1445 | 20240417 | 1457 | 2433354 | 12 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 12 | 34.9232 | -119.6039 | No | Partly Cloudy;32-90 F |  |  | 24-0056051 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1934556 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | FUSE | 53061 | 20240417 | 1544 | 20240417 | 2131 | 2433660 | 347 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1389 | 35.3186 | -119.3754 | No | Clear;32-90 F |  |  | 24-0056160 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1934622 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 9977 | 20240418 | 357 | 20240418 | 531 | 2433898 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 3666 | 35.4044 | -118.9943 | No | Clear;32-90 F |  |  | 24-0056185 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1934647 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | FUSE | 17005 | 20240418 | 540 | 20240418 | 754 | 2433953 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 670 | 34.9417 | -118.9316 | No | Overcast;32-90 F |  |  | 24-0056217 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1934672 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SEMITROPIC-1110 | 252901110 | TRANSFORMER | 515887077044 | 20240418 | 854 | 20240418 | 1026 | 2434010 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 980 | 35.6094 | -119.3847 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Arcing | 24-0056272 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934723 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | TRANSFORMER | 517144578007 | 20240418 | 1121 | 20240418 | 1529 | 2434127 | 248 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 248 | 35.6395 | -118.9628 | No | Clear;32-90 F |  |  | 24-0056529 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1934781 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | 517246464911 | 20240418 | 1337 | 20240418 | 1552 | 2434225 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 270 | 35.28 | -118.9238 | No | Clear;32-90 F | Fuse | Broken | 24-0056580 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934789 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LERDO-1116 | 253491116 | TRANSFORMER | 516684975116 | 20240418 | 1348 | 20240418 | 1819 | 2434229 | 271 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 271 | 35.5585 | -119.1156 | No | Clear;32-90 F |  |  | 24-0056615 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1934800 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 20264 | 20240418 | 1815 | 20240418 | 2120 | 2434372 | 185 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 185 | 35.3427 | -119.0493 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0056603 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934795 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-2102 | 254762102 | SWITCH | 11449SW | 20240418 | 2300 | 20240419 | 419 | 2434515 | 319 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 1276 | 35.359 | -119.0613 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0056589 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934849 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1104 | 253871104 | TRANSFORMER | 516152256544 | 20240419 | 819 | 20240419 | 1030 | 2434683 | 131 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 131 | 35.0471 | -119.2863 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0056832 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935000 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | RECLOSER | 4306 | 20240419 | 1315 | 20240419 | 2150 | 2435067 | 491 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 35846 | 35.2282 | -119.3774 | No | Clear;32-90 F | Jumper | Burned Open | 24-0056975 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935041 | 0 | Non-EPSS | N | 2024 | B/C
KERN | KERN | MIDWAY-1103 | 252611103 | TRANSFORMER | 515929870690 | 20240419 | 1423 | 20240419 | 2306 | 2435171 | 523 | Transformer only | Animal | Other | 1 | 523 | 35.4348 | -119.3666 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0057048 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935060 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | TRANSFORMER | 517144578007 | 20240419 | 1427 | 20240421 | 557 | 2434949 | 2370 | Transformer only | Animal | Bird found | 1 | 2370 | 35.6395 | -118.9628 | No | Clear;32-90 F | Transformer | Leaking | 24-0056998 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935047 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1103 | 252611103 | TRANSFORMER | 515954470688 | 20240419 | 1557 | 20240420 | 308 | 2435172 | 671 | Transformer only | Animal | Other | 1 | 671 | 35.4348 | -119.3587 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0057042 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935058 | 0 | Non-EPSS | N | 2024
KERN | KERN | DEVILS DEN-1102 | 253451102 | TRANSFORMER | 514087581622 | 20240419 | 2229 | 20240420 | 158 | 2435306 | 209 | Transformer only | Animal | Other | 1 | 209 | 35.7271 | -119.9923 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0057109 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935116 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | TRANSFORMER | T1175 | 20240419 | 2338 | 20240420 | 955 | 2435332 | 617 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 12238 | 35.3467 | -119.058 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0057105 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935112 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516965970233 | 20240420 | 214 | 20240420 | 1346 | 2435335 | 692 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 11072 | 35.4256 | -119.0192 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0057107 | OH | Sus | 31691176 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935114 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | TRANSFORMER | 516964470249 | 20240420 | 214 | 20240420 | 1817 | 2435334 | 963 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3852 | 35.4259 | -119.0193 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0057108 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935115 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 13007 | 20240420 | 1203 | 20240420 | 1304 | 2435513 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 2318 | 35.3363 | -119.012 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0057168 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935208 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | OCB | 1106/2 | 20240421 | 1014 | 20240421 | 1247 | 2435825 | 153 | Distribution Circuit | 3rd Party | Vehicle | 32 | 4896 | 35.3531 | -119.2709 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0057296 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935308 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | KERN OIL-1108 | 252721108 | FUSE | 12079 | 20240421 | 2001 | 20240422 | 546 | 2435965 | 585 | Distribution Circuit | Equipment Failure/Involved | Underground | 155 | 33560 | 35.4314 | -119.0367 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0057337 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935340 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRANSFORMER | 515999071365 | 20240422 | 820 | 20240422 | 1135 | 2436217 | 195 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 585 | 35.4534 | -119.3445 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0057551 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935539 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | T9947 | 20240422 | 1048 | 20240422 | 1210 | 2436529 | 82 | Transformer only | Animal | Other | 1 | 82 | 35.4918 | -119.3735 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0057573 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935550 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | TRANSFORMER | 514972677321 | 20240422 | 1111 | 20240422 | 1149 | 2436537 | 38 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 760 | 35.613 | -119.6921 | No | Clear;32-90 F | Secondary | Broken | 24-0057525 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935528 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T8910 TWD T8911 | 20240422 | 1135 | 20240422 | 2038 | 2436590 | 543 | Distribution Circuit | 3rd Party | Vehicle | 42 | 22806 | 35.4113 | -119.1231 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0057529 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935535 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 17688 | 20240422 | 1250 | 20240422 | 1400 | 2436647 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 822 | 35.3137 | -119.0027 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0057588 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935560 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516497360064 | 20240422 | 1655 | 20240423 | 1045 | 2436780 | 1070 | Transformer only | Animal | Other | 1 | 1070 | 35.1449 | -119.1727 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057747 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935609 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1102 | 253651102 | FUSE | 18065 | 20240422 | 1719 | 20240422 | 2009 | 2436867 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 754 | 35.5292 | -119.269 | No | Clear;32-90 F |  |  | 24-0057763 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935617 | 1 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-1102 | 254401102 | JUMPER | 7282 | 20240422 | 2031 | 20240423 | 831 | 2436980 | 720 | Distribution Circuit | 3rd Party | Other | 27 | 19440 | 35.7745 | -119.866 | No | Clear;32-90 F | Jumper | Broken | 24-0057798 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1935653 | 1 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1104 | 253701104 | OCB | 1104/2 | 20240422 | 2324 | 20240422 | 2330 | 2437024 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1732 | 10392 | 35.374 | -119.0405 | No | Clear;32-90 F | Insulator | Broken | 24-0057793 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935651 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517164061640 | 20240423 | 603 | 20240423 | 748 | 2437089 | 105 | Transformer only | Animal | Other | 1 | 105 | 35.1898 | -118.95 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0057861 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935677 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-2103 | 252552103 | TRANSFORMER | 516161970780 | 20240423 | 754 | 20240423 | 1452 | 2437160 | 418 | Distribution Circuit | Animal | Other | 2 | 836 | 35.4344 | -119.6249 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0057925 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935796 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 17358 | 20240423 | 802 | 20240423 | 1228 | 2437166 | 266 | Distribution Circuit | Equipment Failure/Involved | Underground | 53 | 14098 | 35.3501 | -119.1457 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0058012 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935829 | 0 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1103 | 253801103 | TRANSFORMER | 517236358637 | 20240423 | 817 | 20240424 | 728 | 2437189 | 1391 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1391 | 35.1075 | -118.9251 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057953 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935805 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 515497083028 | 20240423 | 959 | 20240423 | 1745 | 2437349 | 466 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 466 | 35.7715 | -119.519 | No | Clear;32-90 F | Jumper | Broken | 24-0058229 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935887 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | 516861063875 | 20240423 | 1218 | 20240423 | 1550 | 2437471 | 212 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 212 | 35.2505 | -119.0511 | No | Clear;32-90 F | Fuse | Broken | 24-0058186 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935877 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1118 | 253371118 | FUSE | 12103 | 20240423 | 1306 | 20240425 | 158 | 2437524 | 2212 | Distribution Circuit | Equipment Failure/Involved | Underground | 184 | 22213 | 35.3979 | -119.0184 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 24-0058078 | UG | Sus | 35547981 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1935846 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517064066509 | 20240423 | 1503 | 20240423 | 1948 | 2437604 | 285 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 4275 | 35.3236 | -118.9847 | No | Clear;32-90 F | Secondary | Broken | 24-0058153 | OH | Sus | 46232757 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935871 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 17730 | 20240423 | 1549 | 20240423 | 1734 | 2437632 | 105 | Distribution Circuit | 3rd Party | Metallic Balloon | 25 | 2625 | 35.3317 | -119.0207 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0058238 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935890 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | JUMPER | FB 1 POLE E/OF CGC # 517014968966 | 20240423 | 2242 | 20240424 | 317 | 2437777 | 275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1925 | 35.3907 | -119.0013 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0057968 | OH | Sus | 35547571 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935906 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 14613 | 20240424 | 721 | 20240424 | 950 | 2437852 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2533 | 35.2961 | -118.9375 | No | Clear;32-90 F |  |  | 24-0058413 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936109 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517063569073 | 20240424 | 806 | 20240424 | 832 | 2437879 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 156 | 35.3939 | -118.9856 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0058347 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935967 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 9224 | 20240424 | 851 | 20240424 | 1230 | 2437957 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 219 | 35.1236 | -119.1089 | No | Clear;32-90 F |  |  | 24-0058510 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936140 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | J2557 TWD T14556 | 20240425 | 836 | 20240425 | 945 | 2438679 | 69 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 1449 | 35.3961 | -119.1676 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0058689 | UG | Sus | 35548376 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936281 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARNERAS-1103 | 252321103 | FUSE | 58327 | 20240425 | 921 | 20240425 | 934 | 2438765 | 13 | Distribution Circuit | Animal | Other | 1 | 13 | 35.5753 | -119.8946 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0058801 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936341 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13476 | 20240425 | 955 | 20240425 | 1034 | 2438846 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 94 | 3666 | 35.3649 | -118.9745 | No | Overcast;32-90 F |  |  | 24-0058843 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936414 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | OTHER | T10724 TWD T10725 | 20240425 | 1336 | 20240425 | 1447 | 2439040 | 71 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 426 | 35.4026 | -119.1171 | No | Overcast;32-90 F | Transformer (UG) | Deteriorated | 24-0058858 | UG | Sus | 35548470 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936455 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 11539 | 20240425 | 1614 | 20240425 | 1952 | 2439137 | 218 | Distribution Circuit | Equipment Failure/Involved | Underground | 86 | 17897 | 35.3486 | -119.0924 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0059090 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936484 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517144368277 | 20240425 | 1723 | 20240425 | 1837 | 2439175 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 518 | 35.3727 | -118.9583 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0059092 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936485 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 16229 | 20240425 | 1844 | 20240425 | 1940 | 2439247 | 56 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 1680 | 35.3616 | -119.1814 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0059104 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936500 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | T551698 | 20240426 | 26 | 20240426 | 638 | 2439430 | 372 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2976 | 35.2657 | -119.0679 | No | Clear;32-90 F | Metering Equipment | Burned/flashed | 24-0059159 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936558 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 13324 | 20240426 | 1115 | 20240426 | 1302 | 2439769 | 107 | Distribution Circuit | Equipment Failure/Involved | Underground | 43 | 4601 | 35.3965 | -119.128 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0059290 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936719 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1112 | 252901112 | TRANSFORMER | 515596277321 | 20240426 | 1427 | 20240426 | 1650 | 2439860 | 143 | Transformer only | Equipment Failure/Involved | Fire- pole | 1 | 143 | 35.6158 | -119.4817 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0059408 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936759 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2102 | 254572102 | FUSE | 11417 | 20240426 | 1447 | 20240426 | 1808 | 2439931 | 201 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 4825 | 35.3725 | -119.156 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Leaking | 24-0059319 | UG | Sus | 35548630 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936761 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 1635 | 20240426 | 1700 | 20240426 | 2310 | 2440072 | 370 | Distribution Circuit | Animal | Other | 120 | 43729 | 34.9498 | -119.6935 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0059481 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936800 | 0 | EPSS Ckt | N | 2024 | SGF
KERN | KERN | LAMONT-1104 | 253911104 | FUSE | 9791 | 20240426 | 1909 | 20240427 | 457 | 2440186 | 588 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3528 | 35.3257 | -118.7986 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 24-0059528 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936839 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515612770889 | 20240427 | 715 | 20240427 | 920 | 2440386 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 250 | 35.4388 | -119.4737 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059593 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936925 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | OCB | 2104/2 | 20240427 | 1053 | 20240427 | 1517 | s1936960 | 264 | Distribution Circuit | Animal | Other | 2785 | 235692 | 35.3785 | -119.0985 | No | Overcast;32-90 F | Metering Equipment | Burned/flashed | 24-0059613 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1936960 | 0 | Non-EPSS | N | 2024 | ABC
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 1635 | 20240427 | 1150 | 20240427 | 1547 | 2440557 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 28223 | 34.9498 | -119.6935 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059619 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936963 | 0 | EPSS Ckt | N | 2024 | SGF
KERN | KERN | STOCKDALE-2113 | 254072113 | OCB | 530574 | 20240427 | 1458 | 20240427 | 1541 | 2440692 | 43 | Distribution Circuit | 3rd Party | Other | 3745 | 155451 | 35.3283 | -119.0213 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 24-0059664 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936989 | 0 | Non-EPSS | N | 2024 | A B & C
KERN | KERN | BAKERSFIELD-1114 | 253371114 | RECLOSER | 4420 | 20240428 | 122 | 20240428 | 1211 | 2440881 | 649 | Distribution Circuit | 3rd Party | Vehicle | 2405 | 257924 | 35.3787 | -118.9798 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0059732 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1937054 | 0 | Non-EPSS | N | 2024 | C- GRD
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 8710 | 20240428 | 1305 | 20240428 | 1319 | 2441076 | 14 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1 | 14 | 35.3681 | -118.9742 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0059778 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1937103 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | OTHER | T11088 TWD T11089 | 20240428 | 1305 | 20240428 | 1414 | 2441072 | 69 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 1449 | 35.3708 | -119.18 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0059766 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1937099 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1101 | 252971101 | RECLOSER | 4574 | 20240428 | 1424 | 20240429 | 110 | 2441088 | 646 | Distribution Circuit | 3rd Party | Vehicle | 56 | 13416 | 35.2087 | -118.8811 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0059781 | OH | Sus | 31692500 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1937106 | 0 | Non-EPSS | N | 2024 | A- GRD
KERN | KERN | KERN OIL-1104 | 252721104 | FUSE | 19353 | 20240428 | 2005 | 20240429 | 922 | 2441167 | 797 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1062 | 35.5407 | -118.9769 | No | Clear;32-90 F |  |  | 24-0059812 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937136 | 1 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | T2519 | 20240428 | 2156 | 20240428 | 2240 | 2441205 | 44 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 308 | 35.3209 | -119.0483 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0059814 | UG | Sus | 46235865 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1937137 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 19031 | 20240429 | 832 | 20240429 | 1111 | 2441400 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 11766 | 35.4133 | -119.0801 | No | Clear;32-90 F |  |  | 24-0059969 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937323 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 14274 | 20240429 | 1140 | 20240429 | 1228 | 2441706 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 48 | 34.8121 | -119.4569 | No | Clear;32-90 F | Jumper | Deteriorated | 24-0059994 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1937335 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515708368650 | 20240429 | 1314 | 20240429 | 1515 | 2441777 | 121 | Transformer only | Animal | Other | 5 | 605 | 35.3777 | -119.4406 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0060109 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937380 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 15274 | 20240429 | 1324 | 20240429 | 1450 | 2441783 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 122 | 10492 | 35.4141 | -119.0241 | No | Clear;32-90 F |  |  | 24-0060065 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937367 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-1104 | 254401104 | OCB | 1101/2 | 20240430 | 341 | 20240430 | 400 | 2442138 | 19 | Distribution Circuit | Company Initiated | Other Circuits | 2 | 37 | 35.7305 | -119.8581 | No | Clear;32-90 F | Circuit Breaker | Normal | 24-0060221 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1937471 | 0 | Non-EPSS | N | 2024 | SET A
KERN | KERN | ARVIN-1103 | 253801103 | FUSE | 18549 | 20240430 | 706 | 20240430 | 1330 | 2442203 | 384 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 384 | 35.1292 | -118.914 | No | Clear;32-90 F |  |  | 24-0060341 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937677 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1102 | 253181102 | TRANSFORMER | 515944979698 | 20240430 | 747 | 20240430 | 852 | 2442242 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 65 | 35.6829 | -119.3662 | No | Clear;32-90 F | Fuse | Broken | 24-0060306 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937589 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | OCB | 1106/2 | 20240430 | 928 | 20240430 | 1041 | 2442491 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1744 | 49444 | 35.2971 | -118.8618 | No | Clear;32-90 F |  |  | 24-0060328 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937652 | 0 | Non-EPSS | N | 2024 | B & GRD
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 513983280219 | 20240430 | 1141 | 20240430 | 1633 | 2442442 | 292 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 292 | 35.6873 | -120.028 | No | Clear;32-90 F | Jumper | Broken | 24-0060453 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937714 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | 516151372771 | 20240430 | 1300 | 20240501 | 803 | 2442736 | 1143 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1143 | 35.4926 | -119.293 | No | Clear;32-90 F |  |  | 24-0060548 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1937759 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 100000034243 | 20240430 | 1319 | 20240430 | 1915 | 2442759 | 356 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 712 | 35.7758 | -119.6631 | No | Clear;32-90 F | Insulator | Failed/Faulted | 24-0060620 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937774 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | RECLOSER | 4088 | 20240430 | 1711 | 20240430 | 1905 | 2442931 | 114 | Distribution Circuit | 3rd Party | Vehicle | 950 | 108300 | 35.256 | -118.9136 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0060622 | OH | Sus | 31692681 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937775 | 0 | Non-EPSS | N | 2024 | A & B
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 14572 | 20240430 | 2010 | 20240501 | 2 | 2443004 | 232 | Distribution Circuit | Animal | Other | 5 | 1238 | 35.3475 | -119.4291 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0060672 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937811 | 1 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1105 | 253951105 | RECLOSER | 4055 | 20240501 | 200 | 20240501 | 859 | 2443045 | 419 | Distribution Circuit | Animal | Bird found | 178 | 22094 | 35.4205 | -118.9498 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0060684 | OH | Sus | 31692682 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1937821 | 0 | Non-EPSS | N | 2024 | A- GRD
KERN | KERN | MAGUNDEN-1108 | 252771108 | TRANSFORMER | 517345567639 | 20240501 | 519 | 20240501 | 644 | 2443058 | 85 | Transformer only | 3rd Party | Customer Equipment | 1 | 85 | 35.3555 | -118.892 | No | Clear;32-90 F | Fuse | Broken | 24-0060693 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1937830 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SHAFTER-1103 | 253651103 | FUSE | 16094 | 20240501 | 703 | 20240501 | 920 | 2443082 | 137 | Distribution Circuit | 3rd Party | Vehicle | 7 | 959 | 35.5583 | -119.2945 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0060697 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1937831 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 513739679973 | 20240501 | 957 | 20240501 | 1318 | 2443309 | 201 | Transformer only | Animal | Other | 1 | 201 | 35.6806 | -120.108 | No | Clear;32-90 F | Fuse | Broken | 24-0060940 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938046 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515563369649 | 20240501 | 1930 | 20240501 | 1937 | 2443304 | 7 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 7 | 35.4046 | -119.4896 | No | Clear;32-90 F |  |  | 24-0061094 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1938113 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 15349 | 20240501 | 1945 | 20240501 | 2347 | 2443788 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 17182 | 35.4168 | -119.0495 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0061091 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1938111 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | RECLOSER | 2635 | 20240502 | 355 | 20240502 | 1028 | 2443847 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 570 | 73662 | 35.4418 | -119.2902 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0061127 | OH | Sus | 31692773 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1938145 | 0 | Non-EPSS | N | 2024 | SGF
KERN | KERN | ARVIN-1102 | 253801102 | FUSE | 587695 | 20240502 | 549 | 20240502 | 905 | 2443853 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 9800 | 35.171 | -118.9146 | No | Clear;32-90 F |  |  | 24-0061218 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938287 | 0 | Non-EPSS | N | 2024
KERN | KERN | BLACKWELL-2101 | 254682101 | TRANSFORMER | 514728776916 | 20240502 | 752 | 20240502 | 1909 | 2443911 | 677 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 677 | 35.601 | -119.7736 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0061252 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938342 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | 517620366390 | 20240502 | 756 | 20240502 | 1116 | 2443915 | 200 | Transformer only | Company Initiated | Operating error | 1 | 200 | 35.3208 | -118.7986 | No | Clear;32-90 F | Transformer (OH) |  | 24-0061272 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938348 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1111 | 253701111 | TRANSFORMER | 516898967802 | 20240502 | 855 | 20240502 | 1238 | 2444008 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 4410 | 35.3585 | -119.0409 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0061198 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1938234 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2101 | 255322101 | TRANSFORMER | 100000013379 | 20240502 | 1007 | 20240503 | 58 | 2444155 | 891 | Transformer only | Animal | Other | 1 | 891 | 35.2602 | -119.1815 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0061407 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938403 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | TRANSFORMER | 517224074840 | 20240502 | 1053 | 20240502 | 2204 | 2444207 | 671 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 671 | 35.5533 | -118.9337 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0061312 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938369 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8657 | 20240502 | 1324 | 20240502 | 2040 | 2444359 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 10114 | 35.3531 | -119.0839 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0061406 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938402 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 15087 | 20240502 | 1438 | 20240502 | 1950 | 2444396 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3038 | 35.4122 | -119.0076 | No | Clear;32-90 F | Switch (OH) | Failed/Faulted | 24-0061302 | OH | Sus | 35549671 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1938398 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | TRANSFORMER | 517740767282 | 20240502 | 2308 | 20240503 | 545 | 2444627 | 397 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 794 | 35.3461 | -118.758 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0061544 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938485 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN OIL-1110 | 252721110 | TRANSFORMER | 516954770033 | 20240503 | 18 | 20240503 | 154 | 2444641 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 2208 | 35.42 | -119.0228 | No | Clear;32-90 F | Secondary | Broken | 24-0061543 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1938484 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 8926 | 20240503 | 549 | 20240503 | 730 | 2444676 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 4444 | 35.3456 | -119.0483 | No | Clear;32-90 F |  |  | 24-0061576 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938515 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | TRIP-SAVER | 9126 | 20240503 | 611 | 20240503 | 1013 | 2444685 | 242 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 5327 | 35.3913 | -119.703 | No | Clear;32-90 F |  |  | 24-0061678 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938665 | 1 | EPSS Ckt | N | 2024
KERN | KERN | GANSO-1104 | 254541104 | TRANSFORMER | 100000009404 | 20240503 | 739 | 20240503 | 1338 | 2444716 | 359 | Distribution Circuit | Animal | Other | 1 | 359 | 35.4785 | -119.4657 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0061686 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938666 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514842779572 | 20240503 | 952 | 20240504 | 1437 | 2444926 | 1725 | Transformer only | Animal | Bird found | 1 | 1725 | 35.6737 | -119.7368 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0061845 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938723 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13399 | 20240503 | 1224 | 20240503 | 1819 | 2445082 | 355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2485 | 35.223 | -118.9075 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0061794 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1938710 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1105 | 252821105 | FUSE | 427514 | 20240503 | 1529 | 20240503 | 1700 | 2445189 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 91 | 35.2456 | -119.1677 | No | Clear;32-90 F |  |  | 24-0061867 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938726 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 8079 | 20240503 | 1803 | 20240503 | 2149 | 2445258 | 226 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 4972 | 35.3105 | -119.0208 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0061905 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938758 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1103 | 252611103 | OTHER | T6875 TWD J1396 | 20240503 | 2233 | 20240504 | 107 | 2445416 | 154 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 616 | 35.4023 | -119.4 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0061866 | UG | Sus | 31002441 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1938805 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 517104454062 | 20240504 | 1054 | 20240504 | 1305 | 2445709 | 131 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 131 | 34.9817 | -118.9684 | No | Partly Cloudy;32-90 F |  |  | 24-0062084 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1938901 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SEMITROPIC-1112 | 252901112 | TRANSFORMER | 515734677989 | 20240504 | 1545 | 20240505 | 1315 | 2445925 | 1290 | Transformer only | 3rd Party | Vehicle | 5 | 6450 | 35.6347 | -119.4377 | No | Overcast;32-90 F | Transformer | Broken | 24-0062175 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938954 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20240504 | 1748 | 20240505 | 1337 | 2446064 | 1189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 39205 | 35.6271 | -118.9849 | No | Overcast;32-90 F |  |  | 24-0062181 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938959 | 0 | EPSS Ckt | N | 2024 | B- GRD- INST 50
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 88231 | 20240504 | 1920 | 20240504 | 2127 | 2446158 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2667 | 35.6739 | -119.51 | No | Overcast-Drizzle;32-90 F |  |  | 24-0062238 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939012 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15063 | 20240504 | 2040 | 20240505 | 1241 | 2446185 | 961 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 17703 | 35.3507 | -118.9133 | No | Partly Cloudy-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0062267 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1939040 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1102 | 252461102 | FUSE | 7327 | 20240504 | 2043 | 20240505 | 57 | 2446188 | 254 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 4574 | 35.6312 | -119.1958 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062269 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939042 | 1 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | JUMPER | 79491 | 20240504 | 2127 | 20240506 | 308 | 2446199 | 1781 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3562 | 34.9237 | -119.5429 | No | Overcast-Strong Winds;Below 32 F | Jumper | Broken | 24-0062442 | OH | Sus | 31693141 | CENTRAL VALLEY | MAY | Open Circuit | 0 | No | No | No | 1939194 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | OCB | 1104/2 | 20240504 | 2145 | 20240504 | 2226 | 2446204 | 41 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 759 | 31119 | 35.4006 | -119.449 | No | Overcast;32-90 F | Capacitor | Burned/flashed | 24-0062244 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939019 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | FUSE | 9820 | 20240504 | 2159 | 20240505 | 120 | 2446212 | 201 | Distribution Circuit | Animal | Other | 3 | 536 | 35.1291 | -118.9912 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062288 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939057 | 1 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1101 | 252461101 | FUSE | 16110 | 20240504 | 2315 | 20240506 | 110 | 2446227 | 1555 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7775 | 35.6313 | -119.1777 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0062274 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939047 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1106 | 253411106 | FUSE | 16325 | 20240504 | 2315 | 20240507 | 240 | 2446229 | 3085 | Distribution Circuit | Animal | Other | 12 | 5670 | 35.0409 | -119.0914 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062301 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939066 | 1 | EPSS Ckt | N | 2024
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515887259556 | 20240505 | 106 | 20240505 | 2003 | 2446241 | 1137 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1137 | 35.1287 | -119.3766 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0062306 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939071 | 0 | EPSS Ckt | N | 2024
KERN | KERN | COPUS-1104 | 253871104 | FUSE | 9037 | 20240505 | 420 | 20240505 | 2209 | 2446268 | 1069 | Distribution Circuit | Animal | Other | 8 | 3729 | 35.0471 | -119.2797 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0062335 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939100 | 1 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1103 | 252081103 | OTHER | WIRE DOWN S/OF 515655760654 | 20240505 | 622 | 20240505 | 1645 | 2446323 | 623 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 8099 | 35.1577 | -119.4544 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0062322 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Open Circuit | 0 | No | Yes | Yes | 1939087 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | SWITCH | 1196 | 20240505 | 830 | 20240505 | 1240 | 2446331 | 250 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 250 | 35.3265 | -118.9649 | No | Partly Cloudy;32-90 F | Customer Equipment | Normal | 24-0062323 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939088 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | 514888053823 | 20240505 | 917 | 20240505 | 1900 | 2446381 | 583 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 583 | 34.9638 | -119.7095 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062362 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939125 | 0 | EPSS Ckt | N | 2024
KERN | KERN | DEVILS DEN-1102 | 253451102 | FUSE | 7378 | 20240505 | 1207 | 20240506 | 1401 | 2446511 | 1554 | Distribution Circuit | Animal | Other | 4 | 6216 | 35.7306 | -119.9211 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0062386 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1939145 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | 517025959444 | 20240505 | 1325 | 20240506 | 326 | 2446311 | 841 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 841 | 35.1291 | -118.9958 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0062373 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939138 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1102 | 252461102 | FUSE | 7327 | 20240505 | 1543 | 20240505 | 1622 | 2446527 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 1053 | 35.6312 | -119.1958 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0062391 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939150 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 14503 | 20240505 | 1706 | 20240505 | 1805 | 2446564 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 2242 | 35.3253 | -118.9155 | No | Clear;32-90 F |  |  | 24-0062405 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939161 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1112 | 252901112 | TRANSFORMER | 515734677989 | 20240505 | 1805 | 20240506 | 1039 | 2446578 | 994 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 4970 | 35.6347 | -119.4377 | No | Clear;32-90 F | Transformer | Broken | 24-0062410 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939167 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1107 | 253411107 | OCB | 1107/2 | 20240506 | 55 | 20240506 | 1234 | 2446632 | 699 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 53 | 2207 | 35.0935 | -119.1012 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0062440 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939191 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515638072600 | 20240506 | 741 | 20240507 | 927 | 2446712 | 1546 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1546 | 35.4859 | -119.466 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0062788 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939435 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515480269994 | 20240506 | 846 | 20240506 | 1621 | 2446807 | 455 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 910 | 35.4142 | -119.518 | No | Clear;32-90 F |  |  | 24-0062723 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939419 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1106 | 254201106 | TRANSFORMER | 515491878412 | 20240506 | 858 | 20240506 | 2310 | 2446826 | 852 | Transformer only | Animal | Other | 1 | 852 | 35.645 | -119.5177 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0062571 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939367 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7343 | 20240506 | 915 | 20240506 | 1940 | 2447482 | 625 | Distribution Circuit | Animal | Other | 2 | 1250 | 35.5865 | -119.5086 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0062812 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939451 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1104 | 253871104 | FUSE | 9037 | 20240506 | 942 | 20240506 | 1331 | 2447022 | 229 | Distribution Circuit | 3rd Party | Metallic Balloon | 5 | 1222 | 35.0471 | -119.2797 | No | Clear;32-90 F | Fuse | Burned Open | 24-0062657 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939406 | 1 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1104 | 253551104 | TRANSFORMER | 515711881557 | 20240506 | 1023 | 20240506 | 2130 | 2447056 | 667 | Transformer only | Animal | Other | 2 | 1334 | 35.7323 | -119.446 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062611 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939389 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARNERAS-1103 | 252321103 | TRANSFORMER | 514510472632 | 20240506 | 1147 | 20240506 | 1421 | 2447169 | 154 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 154 | 35.4819 | -119.8449 | No | Clear;32-90 F |  |  | 24-0062703 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939414 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ARVIN-1103 | 253801103 | TRANSFORMER | 517202559948 | 20240506 | 1148 | 20240506 | 1206 | 2446818 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 18 | 35.1437 | -118.937 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0062609 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939388 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517154768090 | 20240506 | 1224 | 20240506 | 2056 | 2447120 | 512 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2048 | 35.3676 | -118.9548 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0062617 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939392 | 0 | Non-EPSS | N | 2024
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 514291078520 | 20240506 | 1228 | 20240506 | 1837 | 2447196 | 369 | Transformer only | Animal | Other | 1 | 369 | 35.6428 | -119.9213 | No | Clear;32-90 F | Jumper | Contaminated | 24-0062800 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939443 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517033869434 | 20240506 | 1358 | 20240506 | 1955 | 2447245 | 357 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 1071 | 35.4038 | -118.9958 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0062685 | OH | Sus | 46239148 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939412 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | TRANSFORMER | 516169467193 | 20240506 | 1420 | 20240506 | 2252 | 2447303 | 512 | Transformer only | Animal | Other | 1 | 512 | 35.3398 | -119.2854 | No | Clear;32-90 F | Jumper | Contaminated | 24-0062835 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939476 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 100000029816 | 20240506 | 1507 | 20240506 | 2025 | 2447332 | 318 | Transformer only | Animal | Other | 1 | 318 | 35.7029 | -119.4742 | No | Clear;32-90 F | Jumper | Contaminated | 24-0062817 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939456 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516952762208 | 20240506 | 1610 | 20240506 | 1943 | 2447377 | 213 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 213 | 35.205 | -119.0204 | No | Clear;32-90 F |  |  | 24-0062811 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939450 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 10708SW | 20240506 | 1617 | 20240507 | 134 | 2447380 | 557 | Distribution Circuit | Equipment Failure/Involved | Underground | 73 | 13741 | 35.3299 | -119.0763 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0062789 | UG | Sus | 35551231 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939436 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515432871440 | 20240506 | 1654 | 20240506 | 1704 | 2446753 | 10 | Transformer only | Animal | Other | 1 | 10 | 35.453 | -119.5349 | No | Clear;32-90 F | Jumper | Contaminated | 24-0062780 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939431 | 0 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1101 | 253191101 | FUSE | 15404 | 20240507 | 734 | 20240507 | 1534 | 2447906 | 480 | Distribution Circuit | Animal | Other | 1 | 480 | 35.0926 | -118.8518 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0063220 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939730 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | FUSE | 9040 | 20240507 | 804 | 20240507 | 1503 | 2447655 | 419 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1257 | 35.0449 | -119.8681 | No | Clear;32-90 F |  |  | 24-0063169 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939710 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1112 | 253701112 | FUSE | 8094 | 20240507 | 1015 | 20240507 | 1108 | 2447858 | 53 | Distribution Circuit | Animal | Other | 61 | 3252 | 35.3477 | -119.0567 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0063025 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939655 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1110 | 252721110 | FUSE | 15281 | 20240507 | 1108 | 20240507 | 2012 | 2447839 | 544 | Distribution Circuit | Vegetation | Other ground vegetation | 97 | 52768 | 35.4232 | -119.0203 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0063026 | OH | Sus | 46239487 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939656 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | FUSE | 17344 | 20240507 | 1110 | 20240507 | 1425 | 2447897 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 195 | 35.3188 | -119.3238 | No | Clear;32-90 F |  |  | 24-0063148 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939703 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1116 | 253491116 | TRANSFORMER | 516682574984 | 20240507 | 1153 | 20240507 | 1712 | 2447935 | 319 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 319 | 35.5555 | -119.1158 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0063217 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939728 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1105 | 252821105 | TRANSFORMER | 100000028197 | 20240507 | 1419 | 20240507 | 1646 | 2448046 | 147 | Transformer only | Animal | Other | 1 | 147 | 35.238 | -119.1727 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0063267 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939741 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16172 | 20240507 | 1443 | 20240508 | 336 | 2448068 | 773 | Distribution Circuit | 3rd Party | Vehicle | 8 | 4706 | 35.1513 | -119.071 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 24-0063190 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1939717 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | RECLOSER | 4306 | 20240507 | 1452 | 20240508 | 108 | 2448079 | 616 | Distribution Circuit | 3rd Party | Other | 473 | 64109 | 35.2282 | -119.3774 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0063188 | OH | Sus | 31693419 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1939716 | 0 | Non-EPSS | N | 2024 | C- GRD
KERN | KERN | TUPMAN-1105 | 254561105 | TRANSFORMER | 516174566565 | 20240507 | 1510 | 20240507 | 1707 | 2447828 | 117 | Transformer only | Animal | Other | 1 | 117 | 35.3222 | -119.2833 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0063196 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939719 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 7294 | 20240507 | 1639 | 20240507 | 2200 | 2448147 | 321 | Distribution Circuit | Animal | Other | 6 | 1926 | 35.7039 | -119.5085 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0063299 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939777 | 0 | Non-EPSS | N | 2024
KERN | KERN | MCKITTRICK-1101 | 252781101 | JUMPER | 17035 | 20240507 | 1704 | 20240508 | 1010 | 2448163 | 1026 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1026 | 35.2857 | -119.626 | No | Clear;32-90 F | Jumper | Burned Open | 24-0063283 | OH | Sus | 46239646 | CENTRAL VALLEY | MAY | Open Circuit | 0 | No | No | No | 1939758 | 1 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517027568087 | 20240508 | 33 | 20240508 | 426 | 2448306 | 233 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1165 | 35.367 | -118.9974 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0063372 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939850 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | RECLOSER | 4889 | 20240508 | 343 | 20240508 | 449 | 2448340 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 660 | 35.3459 | -119.172 | No | Clear;32-90 F |  |  | 24-0063380 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939858 | 0 | Non-EPSS | N | 2024 | A- C
KERN | KERN | TEJON-1106 | 252931106 | TRANSFORMER | 100000113491 | 20240508 | 745 | 20240508 | 1335 | 2448406 | 350 | Transformer only | Animal | Other | 1 | 350 | 34.9584 | -118.8733 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0063737 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940087 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 8289 | 20240508 | 747 | 20240508 | 838 | 2448407 | 51 | Distribution Circuit | Animal | Squirrel | 127 | 6477 | 35.3415 | -119.0628 | No | Clear;32-90 F | Fuse | Normal | 24-0063447 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939921 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515495780788 | 20240508 | 841 | 20240508 | 1238 | 2448492 | 237 | Transformer only | Animal | Other | 1 | 237 | 35.7103 | -119.5171 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0063678 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940069 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515732569065 | 20240508 | 1010 | 20240509 | 600 | 2448665 | 1190 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1190 | 35.3895 | -119.4328 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0063564 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940032 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | RECLOSER | 90940 | 20240508 | 1040 | 20240508 | 1130 | 2448773 | 50 | Distribution Circuit | 3rd Party | Vehicle | 1114 | 55700 | 35.2671 | -118.9006 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0063492 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940025 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 8570 | 20240508 | 1058 | 20240508 | 1508 | 2448791 | 250 | Distribution Circuit | Equipment Failure/Involved | Underground | 69 | 5546 | 35.4123 | -119.0154 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0046680 | UG | Sus | 35539923 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940035 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516678968454 | 20240508 | 1512 | 20240508 | 1529 | 2449060 | 17 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 170 | 35.3753 | -119.1148 | No | Clear;32-90 F |  |  | 24-0063823 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1940112 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1106 | 252901106 | FUSE | 561735 | 20240508 | 1630 | 20240508 | 2300 | 2449189 | 390 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1170 | 35.5583 | -119.4117 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0063899 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1940133 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2103 | 255322103 | FUSE | 16160 | 20240508 | 2018 | 20240509 | 617 | 2449243 | 599 | Distribution Circuit | Equipment Failure/Involved | Underground | 71 | 12034 | 35.3432 | -119.1281 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0063928 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940152 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | T0480 | 20240508 | 2140 | 20240508 | 2200 | 2449242 | 20 | Transformer only | Equipment Failure/Involved | Underground | 9 | 180 | 35.3746 | -119.1188 | No | Clear;32-90 F | Secondary | Broken | 24-0063957 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940175 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2108 | 254072108 | JUMPER | 9808 FUCO #1 | 20240509 | 430 | 20240509 | 652 | 2449372 | 142 | Distribution Circuit | Equipment Failure/Involved | Underground | 77 | 10784 | 35.3182 | -119.0866 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0063986 | UG | Sus | 31693490 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940205 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 2181 | 20240509 | 905 | 20240509 | 914 | 2449557 | 9 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 17 | 153 | 35.5944 | -118.9585 | No | Clear;32-90 F |  |  | 24-0064074 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940290 | 0 | EPSS Ckt | N | 2024 | SGF
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 9773 | 20240509 | 1001 | 20240510 | 256 | 2449730 | 1015 | Distribution Circuit | Environmental/External | Lightning | 2 | 1168 | 35.1933 | -118.806 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0064220 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1940412 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WASCO-1104 | 252961104 | FUSE | 7607 | 20240509 | 1014 | 20240510 | 249 | 2449747 | 995 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 7 | 2327 | 35.589 | -119.3448 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0064262 | UG | Sus | 31693592 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940425 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | JUMPER | OPEN CENTER PHASE JUMPER @ 14522 | 20240509 | 1128 | 20240509 | 1758 | 2449826 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3510 | 35.3447 | -119.173 | No | Clear;32-90 F | Jumper | Burned Open | 24-0064378 | OH | Sus | 46240555 | CENTRAL VALLEY | MAY | Open Circuit | 0 | No | No | No | 1940455 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | T7008 | 20240509 | 1244 | 20240509 | 2243 | 2449884 | 599 | Distribution Circuit | Equipment Failure/Involved | Underground | 53 | 6772 | 35.2586 | -118.9189 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0064350 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940451 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516932566736 | 20240509 | 1719 | 20240510 | 148 | 2450081 | 509 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 5789 | 35.3293 | -119.0293 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0064462 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940486 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | T7008 | 20240510 | 1013 | 20240510 | 1211 | 2450741 | 118 | Transformer only | Equipment Failure/Involved | Underground | 8 | 944 | 35.2586 | -118.9189 | No | Clear;32-90 F | Transformer | Broken | 24-0064622 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940688 | 0 | Non-EPSS | N | 2024
KERN | KERN | BLACKWELL-1102 | 254681102 | TRANSFORMER | 100000007449 | 20240510 | 1214 | 20240510 | 1830 | 2450875 | 376 | Transformer only | Animal | Other | 1 | 376 | 35.6792 | -119.8579 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0064707 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940719 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2103 | 255262103 | OTHER | J1158 TWD T9968 | 20240511 | 1120 | 20240511 | 1250 | 2451455 | 90 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 900 | 35.4006 | -119.1164 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0064535 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940899 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20240511 | 1148 | 20240511 | 1307 | 2451466 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2528 | 35.3618 | -119.1627 | No | Clear;32-90 F |  |  | 24-0065011 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940906 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 515927269905 | 20240511 | 1421 | 20240511 | 1604 | 2451416 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 103 | 35.4134 | -119.3678 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0065044 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940917 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1103 | 255451103 | OCB | 1103/2/NORM | 20240511 | 1616 | 20240512 | 250 | 2451631 | 634 | Distribution Circuit | 3rd Party | Vehicle | 2288 | 115689 | 35.4222 | -118.9006 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 24-0065061 | OH | Sus | 31693862 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1940930 | 0 | Non-EPSS | N | 2024 | PH OC TIME GRD
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516974567071 | 20240511 | 1911 | 20240511 | 2037 | 2451698 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 430 | 35.3388 | -119.0146 | No | Clear;32-90 F |  |  | 24-0065088 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1940957 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1106 | 254501106 | OCB | 1106/2 | 20240511 | 1917 | 20240512 | 447 | 2451680 | 570 | Distribution Circuit | 3rd Party | Vehicle | 1738 | 148508 | 35.6081 | -119.3254 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0065081 | OH | Sus | 31693842 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940950 | 0 | Non-EPSS | N | 2024 | NA
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 517122463663 | 20240512 | 521 | 20240512 | 824 | 2451851 | 183 | Transformer only | Animal | Bird found | 2 | 366 | 35.245 | -118.9646 | No | Clear;32-90 F | Jumper | Contaminated | 24-0065140 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941009 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 8157 | 20240512 | 907 | 20240512 | 948 | 2451993 | 41 | Distribution Circuit | Animal | Squirrel | 36 | 1476 | 35.3496 | -119.0601 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0065149 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941020 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1102 | 253871102 | OTHER | WIRE DOWN 6 POLES W/OF 30304 | 20240512 | 1258 | 20240512 | 2035 | 2452055 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2742 | 35.0762 | -119.302 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0065179 | OH | Sus | 46246185 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | Yes | 1941042 | 1 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1106 | 252901106 | TRANSFORMER | 515832175721 | 20240512 | 1812 | 20240512 | 1951 | 2452134 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 99 | 35.573 | -119.4027 | No | Clear;32-90 F | Fuse | Broken | 24-0065211 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941062 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517021368088 | 20240512 | 1928 | 20240512 | 2005 | 2452188 | 37 | Transformer only | Animal | Bird found | 12 | 444 | 35.367 | -118.9995 | No | Clear;32-90 F | Fuse | Burned Open | 24-0065214 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941065 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1102 | 253871102 | RECLOSER | 205562 | 20240512 | 2056 | 20240512 | 2236 | 2452221 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 100 | 35.0765 | -119.3139 | No | Clear;32-90 F |  |  | 24-0065241 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941096 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 7469 | 20240513 | 32 | 20240513 | 1220 | 2452273 | 708 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 5196 | 35.7188 | -119.3302 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0065247 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941101 | 1 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | RECLOSER | 59326 | 20240513 | 555 | 20240513 | 1244 | 2452324 | 409 | Distribution Circuit | Animal | Other | 18 | 7310 | 35.4381 | -119.7368 | No | Clear;32-90 F | Recloser | Burned/flashed | 24-0065280 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941127 | 0 | EPSS Ckt | N | 2024 | GRD-SGF
KERN | KERN | STOCKDALE-1106 | 254071106 | INTERRUPTER | 318706 | 20240513 | 1026 | 20240514 | 1224 | 2452588 | 1558 | Distribution Circuit | Equipment Failure/Involved | Underground | 109 | 76266 | 35.3239 | -119.0564 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0065419 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941316 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | OCB | 2109/2 | 20240513 | 1033 | 20240513 | 1644 | 2452601 | 371 | Distribution Circuit | 3rd Party | Metallic Balloon | 4609 | 410119 | 35.3885 | -119.0044 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0065365 | OH | Sus | 46246580 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1941279 | 0 | Non-EPSS | N | 2024 | ABC TIME OC
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | T2375 | 20240513 | 1100 | 20240513 | 1127 | 2452636 | 27 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 297 | 35.3217 | -119.0271 | No | Clear;32-90 F |  |  | 24-0065394 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1941299 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 55553 | 20240513 | 1126 | 20240513 | 1225 | 2452659 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 3658 | 35.325 | -119.0175 | No | Clear;32-90 F |  |  | 24-0065411 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941311 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | TRANSFORMER | 517070968487 | 20240513 | 1149 | 20240513 | 1403 | 2452680 | 134 | Transformer only | Equipment Failure/Involved | Underground | 16 | 2144 | 35.3784 | -118.983 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0065478 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941339 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 16293 | 20240513 | 1354 | 20240513 | 1553 | 2452950 | 119 | Distribution Circuit | Animal | Bird found | 1 | 119 | 35.3366 | -119.048 | No | Clear;32-90 F | Crossarm- Wood | Normal | 24-0065544 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941363 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 20151 | 20240513 | 1423 | 20240513 | 1740 | 2452836 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1708 | 35.4475 | -118.9044 | No | Clear;32-90 F |  |  | 24-0065569 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941374 | 1 | EPSS Ckt | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | OTHER | 1105/2 | 20240513 | 1844 | 20240514 | 930 | 2453042 | 886 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 13916 | 35.3531 | -119.271 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0065586 | OH | Sus | 46246533 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | Yes | 1941385 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1105 | 254071105 | FUSE | 17946 | 20240513 | 1933 | 20240514 | 520 | 2453078 | 587 | Distribution Circuit | Equipment Failure/Involved | Underground | 70 | 13594 | 35.2893 | -119.0477 | No | Partly Cloudy;32-90 F | Transformer (UG) | Burned/flashed | 24-0065595 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941390 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | FUSE | 18011 | 20240513 | 2201 | 20240514 | 1142 | 2453134 | 821 | Distribution Circuit | Equipment Failure/Involved | Underground | 63 | 31031 | 35.3999 | -119.1631 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0065623 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941416 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | TRANSFORMER | 515189575135 | 20240514 | 1005 | 20240514 | 1211 | 2453472 | 126 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 126 | 35.554 | -119.618 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0065762 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941592 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1107 | 253701107 | OCB | 1107/2 | 20240514 | 1337 | 20240514 | 1428 | 2453656 | 51 | Distribution Circuit | 3rd Party | Other | 418 | 21318 | 35.374 | -119.0403 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0065903 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941637 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | TUPMAN-1105 | 254561105 | TRANSFORMER | 516136066949 | 20240514 | 1437 | 20240514 | 1838 | 2453640 | 241 | Transformer only | Animal | Other | 1 | 241 | 35.3326 | -119.2964 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0065958 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941643 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517089569217 | 20240514 | 1907 | 20240514 | 2331 | 2453892 | 264 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2640 | 35.3982 | -118.9769 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0066045 | OH | Sus | 46247024 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941679 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 390125 | 20240514 | 1919 | 20240514 | 2317 | 2453897 | 238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 476 | 35.3077 | -119.9804 | No | Clear;32-90 F |  |  | 24-0066070 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941707 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | TRANSFORMER | 515909867279 | 20240515 | 1119 | 20240515 | 1229 | 2454342 | 70 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 70 | 35.3403 | -119.3724 | No | Clear;32-90 F |  |  | 24-0066349 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1941935 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 80635 | 20240515 | 1153 | 20240515 | 1924 | 2454403 | 451 | Distribution Circuit | 3rd Party | Vehicle | 740 | 42698 | 35.3299 | -118.9143 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0066347 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941934 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 7330 | 20240515 | 1703 | 20240516 | 107 | 2454614 | 484 | Distribution Circuit | 3rd Party | Vehicle | 8 | 3872 | 35.6455 | -119.2058 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0066568 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941973 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1103 | 252721103 | SWITCH | 3882 | 20240516 | 922 | 20240516 | 945 | 2460560 | 23 | Distribution Circuit | 3rd Party | Vehicle | 38 | 874 | 35.4126 | -119.0486 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0066735 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942064 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T14554 TWD T14555 | 20240516 | 1619 | 20240516 | 1712 | 2460846 | 53 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 583 | 35.3964 | -119.167 | No | Clear;Above 90 | Transformer (UG) | Deteriorated | 24-0066875 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942141 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | RECLOSER | 993374 | 20240516 | 1650 | 20240516 | 2355 | 2460860 | 342 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 693 | 188352 | 35.6016 | -119.6899 | No | Clear;Above 90 |  |  | 24-0066966 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942144 | 0 | Non-EPSS | N | 2024 | SGF
KERN | KERN | WEEDPATCH-1102 | 252971102 | FUSE | 9696 | 20240516 | 2331 | 20240517 | 301 | 2461148 | 210 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 210 | 35.1996 | -118.8231 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0067041 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942213 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1108 | 252081108 | TRANSFORMER | 515640259693 | 20240516 | 2333 | 20240517 | 123 | 2461163 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1100 | 35.1313 | -119.4592 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0067046 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942217 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1103 | 252461103 | TRANSFORMER | 516786176835 | 20240517 | 611 | 20240517 | 809 | 2461219 | 118 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 118 | 35.6065 | -119.0817 | No | Clear;32-90 F |  |  | 24-0067115 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1942276 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 15644 | 20240517 | 705 | 20240517 | 755 | 2461241 | 50 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 15 | 750 | 35.3747 | -119.0044 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0067081 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942237 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516908567933 | 20240517 | 1048 | 20240517 | 1840 | 2461485 | 472 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 944 | 35.3622 | -119.0377 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0067229 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942402 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515592479716 | 20240517 | 1310 | 20240517 | 1320 | 2461643 | 10 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 10 | 35.6811 | -119.485 | No | Clear;32-90 F |  |  | 24-0067302 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1942422 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1106 | 253411106 | TRANSFORMER | 516856856161 | 20240517 | 1351 | 20240518 | 1210 | 2461723 | 1339 | Transformer only | Animal | Bird found | 1 | 1339 | 35.0396 | -119.0509 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0067375 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942444 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | RECLOSER | 4151 | 20240518 | 757 | 20240518 | 1039 | 2462074 | 162 | Distribution Circuit | Equipment Failure/Involved | Underground | 1368 | 104313 | 35.346 | -119.0737 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0067468 | UG | Sus | 46248920 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942522 | 0 | Non-EPSS | N | 2024 | C & GRD
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 13041 | 20240518 | 917 | 20240518 | 1532 | 2462292 | 375 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 3000 | 35.3322 | -118.9852 | No | Clear;32-90 F |  |  | 24-0067536 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942581 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 3855 | 20240518 | 1201 | 20240518 | 1855 | 2462198 | 414 | Distribution Circuit | 3rd Party | Metallic Balloon | 108 | 15417 | 35.3116 | -118.8251 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0067495 | OH | Sus | 31694332 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | No | No | 1942565 | 0 | EPSS Ckt | Y | 2024 | B C INST
KERN | KERN | LAMONT-1103 | 253911103 | RECLOSER | 90940 | 20240518 | 1825 | 20240519 | 520 | 2462372 | 655 | Distribution Circuit | 3rd Party | Vehicle | 2069 | 291711 | 35.2671 | -118.9006 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0067560 | OH | Sus | 31694334 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1942597 | 0 | Non-EPSS | N | 2024 | A B & C
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 15392 | 20240519 | 905 | 20240519 | 1039 | 2462472 | 94 | Distribution Circuit | Vegetation | Tree - grew into line | 24 | 2256 | 35.4151 | -119.0742 | No | Clear;32-90 F | Secondary | Broken | 24-0067613 | OH | Sus | 46249020 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942647 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | SWITCH | 2017 | 20240519 | 928 | 20240519 | 935 | 2462530 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 322 | 2254 | 35.239 | -118.9145 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0067560 | OH | Sus | 31694334 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942653 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516958067829 | 20240519 | 1051 | 20240519 | 1641 | 2462544 | 350 | Transformer only | Unknown Cause | Patrol - not conducted | 26 | 9100 | 35.3596 | -119.0207 | No | Clear;32-90 F |  |  | 24-0067626 | OH | Sus | 31694603 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1942661 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OTHER | T12967 TWD T12968 | 20240519 | 2348 | 20240520 | 33 | 2462802 | 45 | Distribution Circuit | Equipment Failure/Involved | Underground | 84 | 3780 | 35.3663 | -118.9782 | No | Clear;32-90 F | Elbow | Deteriorated | 24-0067270 | UG | Sus | 46247674 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942723 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 18310 | 20240520 | 646 | 20240520 | 759 | 2462884 | 73 | Distribution Circuit | Animal | Bird found | 127 | 9271 | 35.3175 | -119.0063 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0067730 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942747 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 9417 | 20240520 | 658 | 20240520 | 948 | 2462887 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 170 | 35.3708 | -119.0044 | No | Clear;32-90 F |  |  | 24-0067813 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942875 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | TRANSFORMER | 517017368660 | 20240520 | 939 | 20240520 | 1045 | 2463125 | 66 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 132 | 35.3827 | -119.0011 | No | Clear;32-90 F |  |  | 24-0067852 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1942899 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 20176 | 20240520 | 1518 | 20240520 | 2255 | 2463438 | 457 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 914 | 35.3961 | -118.9761 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0068048 | UG | Sus | 31694597 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942958 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 16986 | 20240520 | 1739 | 20240520 | 1839 | 2463588 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 1560 | 35.3337 | -119.0303 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0068061 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942965 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | RECLOSER | 2635 | 20240520 | 1833 | 20240521 | 403 | 2463615 | 570 | Distribution Circuit | 3rd Party | Vehicle | 570 | 42032 | 35.4418 | -119.2902 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0068074 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942975 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | ARVIN-1102 | 253801102 | FUSE | 17624 | 20240521 | 627 | 20240521 | 804 | 2463946 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 776 | 35.1657 | -118.9148 | No | Clear;32-90 F |  |  | 24-0068152 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1943044 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2105 | 255322105 | FUSE | 16257 | 20240521 | 1026 | 20240521 | 1125 | 2464243 | 59 | Distribution Circuit | Animal | Squirrel | 12 | 708 | 35.3251 | -119.1232 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0068293 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943203 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1108 | 252771108 | FUSE | 13938 | 20240521 | 1305 | 20240521 | 1403 | 2464367 | 58 | Distribution Circuit | Animal | Bird found | 50 | 2900 | 35.3618 | -118.9031 | No | Clear;32-90 F | Fuse | Burned Open | 24-0068406 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943236 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 13565 | 20240521 | 1332 | 20240521 | 1427 | 2464399 | 55 | Distribution Circuit | Animal | Bird found | 1 | 55 | 35.3324 | -119.2333 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0068436 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943243 | 1 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1102 | 253651102 | RECLOSER | 3621 | 20240521 | 2022 | 20240522 | 244 | 2464639 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 11644 | 35.5153 | -119.2604 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0068526 | OH | Sus | 31694924 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1943280 | 0 | Non-EPSS | N | 2024 | A & C
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 1703 | 20240522 | 138 | 20240522 | 439 | 2464742 | 181 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 181 | 35.559 | -118.9797 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0068561 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1943309 | 0 | EPSS Ckt | Y | 2024 | A & C
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 4456 | 20240522 | 525 | 20240522 | 1129 | 2464771 | 364 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 24103 | 35.5876 | -118.9581 | No | Clear;32-90 F |  |  | 24-0068569 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943318 | 0 | EPSS Ckt | Y | 2024 | B-GRD
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 8939 | 20240522 | 1744 | 20240524 | 48 | 2465366 | 1856 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 27840 | 35.3636 | -118.9653 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0068973 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943564 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1101 | 252861101 | FUSE | 7570 | 20240522 | 2040 | 20240522 | 2238 | 2465470 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 7824 | 35.4708 | -119.2624 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0068999 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943587 | 1 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1102 | 252021102 | TRANSFORMER | 514242578973 | 20240523 | 639 | 20240524 | 945 | 2465622 | 1626 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1626 | 35.6549 | -119.9389 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0069349 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943846 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | 516344879721 | 20240523 | 1154 | 20240523 | 1206 | 2465899 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 60 | 35.6847 | -119.2314 | No | Clear;32-90 F | Secondary | Normal | 24-0069221 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1943810 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2105 | 255322105 | TRANSFORMER | T5532 | 20240523 | 1447 | 20240523 | 1528 | 2466076 | 41 | Transformer only | Equipment Failure/Involved | Underground | 13 | 533 | 35.3214 | -119.1144 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0069326 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1943840 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1101 | 252021101 | RECLOSER | 2656 | 20240524 | 1044 | 20240524 | 1253 | 2466586 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 3225 | 35.6603 | -120.0102 | No | Clear;32-90 F | Insulator | Broken | 24-0069671 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944043 | 0 | EPSS Ckt | N | 2024 | A- C
KERN | KERN | COLUMBUS-1110 | 253951110 | TRANSFORMER | 517165668645 | 20240524 | 1337 | 20240524 | 2029 | 2466700 | 412 | Transformer only | Vegetation | Tree - grew into line | 6 | 2472 | 35.3829 | -118.9511 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0069845 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944081 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1102 | 252461102 | TRANSFORMER | 516489478215 | 20240524 | 1508 | 20240525 | 331 | 2466767 | 743 | Transformer only | Animal | Other | 1 | 743 | 35.6435 | -119.1823 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0069943 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944153 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1106 | 253411106 | TRANSFORMER | 516736557320 | 20240525 | 932 | 20240525 | 1201 | 2467359 | 149 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 149 | 35.0701 | -119.0915 | No | Clear;32-90 F |  |  | 24-0069996 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1944205 | 0 | EPSS Ckt | N | 2024
KERN | KERN | COLUMBUS-1106 | 253951106 | FUSE | 1104/2 | 20240525 | 1251 | 20240526 | 1830 | 2467502 | 1779 | Distribution Circuit | 3rd Party | Vehicle | 122 | 96878 | 35.3985 | -118.9399 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0070004 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944214 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1108 | 252721108 | OCB | 1108/2 | 20240525 | 1313 | 20240525 | 2122 | 2467506 | 489 | Distribution Circuit | 3rd Party | Other | 2359 | 240565 | 35.4407 | -119.0204 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0070009 | OH | Sus | 31695301 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1944211 | 0 | Non-EPSS | N | 2024 | ABC 51 SET A RLY
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 720132 | 20240525 | 1457 | 20240525 | 2130 | 2467539 | 393 | Distribution Circuit | Animal | Other | 131 | 47998 | 35.5604 | -118.9588 | No | Clear;32-90 F | Capacitor | Broken | 24-0070016 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944217 | 0 | EPSS Ckt | Y | 2024 | A SGF DCD
KERN | KERN | TAFT-1101 | 252081101 | TRANSFORMER | 515672060246 | 20240525 | 1549 | 20240525 | 1859 | 2467558 | 190 | Transformer only | 3rd Party | Other | 11 | 2090 | 35.1467 | -119.4488 | No | Clear;32-90 F | Transformer (OH) |  | 24-0070034 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944233 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | RECLOSER | 1913 | 20240525 | 2354 | 20240526 | 1445 | 2467675 | 246 | Distribution Circuit | 3rd Party | Vehicle | 742 | 24230 | 35.3127 | -118.9144 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0070050 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944250 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | COLUMBUS-1106 | 253951106 | TRANSFORMER | 517149069515 | 20240526 | 1458 | 20240526 | 1919 | 2467910 | 261 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1566 | 35.4063 | -118.9573 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0070126 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944302 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517029368337 | 20240526 | 1725 | 20240527 | 358 | 2467955 | 633 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4431 | 35.3738 | -118.9969 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070130 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944307 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | SWITCH | 1084 | 20240527 | 640 | 20240527 | 759 | 2468082 | 79 | Distribution Circuit | Equipment Failure/Involved | Underground | 457 | 36103 | 35.4124 | -119.1549 | No | Clear;32-90 F | Other | Broken | 24-0070143 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944347 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517130267926 | 20240527 | 1040 | 20240528 | 201 | 2468246 | 921 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 11052 | 35.3631 | -118.9631 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070207 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944374 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517130067889 | 20240527 | 1249 | 20240528 | 201 | 2468261 | 792 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 7128 | 35.3621 | -118.9631 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070212 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944379 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2102 | 253142102 | FUSE | 18660 | 20240527 | 1346 | 20240528 | 948 | 2468346 | 1202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 4296 | 34.9398 | -119.5933 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0070239 | OH | Sus | 46251855 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1944400 | 0 | EPSS Ckt | N | 2024
KERN | KERN | OLD RIVER-1101 | 252821101 | FUSE | 15705 | 20240527 | 1347 | 20240528 | 144 | 2468275 | 717 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3585 | 35.1808 | -119.146 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0070219 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944385 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 8608 | 20240527 | 1506 | 20240527 | 1601 | 2468299 | 55 | Distribution Circuit | 3rd Party | Metallic Balloon | 138 | 7590 | 35.2379 | -118.9605 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070231 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944394 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517184065235 | 20240527 | 1736 | 20240528 | 14 | 2468296 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 398 | 35.2888 | -118.9444 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070244 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944406 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 516979562574 | 20240527 | 1748 | 20240528 | 517 | 2468368 | 689 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 689 | 35.2154 | -119.012 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0070250 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944414 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13989 | 20240527 | 1927 | 20240528 | 201 | 2468381 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 10495 | 35.365 | -118.959 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0070251 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944415 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | SWITCH | 575767 | 20240527 | 2155 | 20240528 | 232 | 2468353 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 6648 | 35.616 | -119.6902 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0070263 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944424 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | TRANSFORMER | 515437261449 | 20240528 | 832 | 20240528 | 1027 | 2468598 | 115 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 115 | 35.1792 | -119.5285 | No | Clear;32-90 F | Metering Equipment | Failed/Faulted | 24-0070453 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944604 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1109 | 253701109 | FUSE | 15249 | 20240528 | 938 | 20240528 | 1406 | 2468726 | 268 | Distribution Circuit | Animal | Bird found | 82 | 21976 | 35.3939 | -119.0427 | No | Clear;32-90 F | Fuse | Burned Open | 24-0070577 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944663 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1102 | 252971102 | FUSE | 13131 | 20240528 | 1358 | 20240528 | 1556 | 2469093 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 866 | 35.1943 | -118.8793 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070657 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944685 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1110 | 253371110 | TRANSFORMER | 516973769050 | 20240528 | 1546 | 20240528 | 1748 | 2469202 | 122 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 1586 | 35.3928 | -119.0158 | No | Clear;32-90 F |  |  | 24-0070705 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1944704 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | RECLOSER | 1689 | 20240528 | 1937 | 20240528 | 1949 | 2469223 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 905 | 10860 | 35.3028 | -119.0029 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0070722 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944716 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | OLD RIVER-1101 | 252821101 | OTHER | WIRE DOWN 3 POLES W/OF 3850 | 20240528 | 2113 | 20240529 | 256 | 2469392 | 343 | Distribution Circuit | 3rd Party | Vehicle | 52 | 13357 | 35.1801 | -119.1604 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0070732 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1944724 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | FUSE | 12311 | 20240529 | 2211 | 20240530 | 30 | 2470473 | 139 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 10008 | 35.4195 | -119.1431 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0070983 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945057 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T11860 TWD T11903 | 20240530 | 111 | 20240530 | 151 | 2470500 | 40 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 1880 | 35.4205 | -119.1397 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0071185 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945079 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | OCB | 2104/2 | 20240530 | 136 | 20240531 | 1212 | 2470506 | 2076 | Distribution Circuit | Animal | Other | 129 | 20169 | 35.1948 | -119.5861 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0071187 | OH | Sus | 35556962 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1945081 | 0 | EPSS Ckt | N | 2024 | A- B
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13909 | 20240530 | 903 | 20240530 | 2209 | 2470692 | 786 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 13 | 10218 | 35.361 | -118.9763 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0071278 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945190 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | RECLOSER | 3264 | 20240530 | 1008 | 20240531 | 824 | 2470786 | 1336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 6715 | 35.6883 | -119.7604 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0071325 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1945248 | 0 | Non-EPSS | N | 2024 | A/B/C
KERN | KERN | CUYAMA-1103 | 253141103 | OCB | 1103/2 | 20240530 | 1406 | 20240530 | 1423 | 2470943 | 17 | Distribution Circuit | Animal | Bird found | 388 | 6596 | 34.9276 | -119.6204 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071489 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945309 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | LAMONT-1102 | 253911102 | FUSE | 18112 | 20240530 | 1635 | 20240530 | 2237 | 2471138 | 362 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1440 | 35.2581 | -118.8786 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0071584 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945330 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAMONT-1105 | 253911105 | RECLOSER | 801102 | 20240530 | 2345 | 20240531 | 54 | 2471371 | 69 | Distribution Circuit | Animal | Bird found | 231 | 15939 | 35.2694 | -118.8249 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071680 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1945397 | 0 | Non-EPSS | N | 2024 | A- B- C- TIME
KERN | KERN | TWISSELMAN-2105 | 254402105 | RECLOSER | 3264 | 20240531 | 1037 | 20240531 | 1356 | 2471928 | 199 | Distribution Circuit | Animal | Other | 22 | 4378 | 35.6883 | -119.7604 | No | Clear;32-90 F | Recloser | Burned/flashed | 24-0071967 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945610 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRANSFORMER | 516089271316 | 20240531 | 1126 | 20240531 | 1313 | 2471785 | 107 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 107 | 35.4525 | -119.3143 | No | Clear;32-90 F |  |  | 24-0071942 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1945603 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T11903 TWD T12078 | 20240531 | 1452 | 20240531 | 1523 | 2471963 | 31 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 1023 | 35.4212 | -119.1398 | No | Clear;Above 90 | Transformer (UG) | Deteriorated | 24-0071751 | UG | Sus | 35557258 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945624 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 1635 | 20240531 | 2047 | 20240601 | 909 | 2472158 | 742 | Distribution Circuit | 3rd Party | Vandalism | 9 | 6678 | 34.9498 | -119.6935 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0072092 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945658 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | OLD RIVER-1105 | 252821105 | FUSE | 9634 | 20240531 | 2132 | 20240601 | 230 | 2472236 | 298 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 298 | 35.2453 | -119.1547 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0072095 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945666 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1102 | 252961102 | TRANSFORMER | 516029276547 | 20240601 | 157 | 20240601 | 919 | 2472291 | 442 | Transformer only | 3rd Party | Fire- house or bldg. | 14 | 6188 | 35.5961 | -119.3371 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0072131 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945697 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 517165557813 | 20240601 | 745 | 20240601 | 936 | 2472358 | 111 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 111 | 35.0834 | -118.9481 | No | Clear;32-90 F |  |  | 24-0072156 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1945739 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1103 | 253651103 | TRANSFORMER | 516092074944 | 20240601 | 1330 | 20240601 | 1523 | 2472564 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 113 | 35.552 | -119.3139 | No | Clear;Above 90 | Fuse | Broken | 24-0072209 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945771 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | TRANSFORMER | T5505 | 20240601 | 1457 | 20240601 | 1713 | 2472605 | 136 | Transformer only | Equipment Failure/Involved | Underground | 12 | 1632 | 35.3552 | -119.0844 | No | Clear;Above 90 | Connector or Splice (UG) | Failed/Faulted | 24-0072224 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945783 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2108 | 254072108 | FUSE | 10941 | 20240601 | 1820 | 20240602 | 1330 | 2472743 | 1150 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 23150 | 35.3153 | -119.1033 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0072233 | UG | Sus | 35557492 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945792 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | TRANSFORMER | T8188 | 20240602 | 815 | 20240602 | 1636 | 2473281 | 501 | Transformer only | Equipment Failure/Involved | Underground | 13 | 6513 | 35.401 | -119.1267 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0072346 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945906 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-1102 | 254401102 | TRANSFORMER | 514421582788 | 20240602 | 837 | 20240602 | 1053 | 2473106 | 136 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 408 | 35.7601 | -119.8805 | No | Clear;32-90 F |  |  | 24-0072316 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1945882 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2109 | 254072109 | RECLOSER | 4718 | 20240602 | 1948 | 20240603 | 446 | 2473366 | 538 | Distribution Circuit | Equipment Failure/Involved | Underground | 2627 | 361594 | 35.2863 | -119.0389 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0072357 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945919 | 0 | Non-EPSS | N | 2024 | B-GRD
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 315849 | 20240602 | 2203 | 20240602 | 2302 | 2473414 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 413 | 35.3617 | -119.2121 | No | Clear;32-90 F |  |  | 24-0072373 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1945929 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 54677 | 20240603 | 1008 | 20240603 | 1158 | 2474127 | 110 | Distribution Circuit | Animal | Bird found | 1 | 110 | 35.3151 | -119.0675 | No | Clear;32-90 F | Fuse | Normal | 24-0072583 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946157 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | FUSE | 11812 | 20240603 | 1320 | 20240603 | 1531 | 2474200 | 131 | Distribution Circuit | Equipment Failure/Involved | Underground | 59 | 3319 | 35.4095 | -119.1235 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0072529 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946177 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1107 | 253371107 | OCB | 1107/2 | 20240604 | 4 | 20240604 | 1408 | 2474541 | 844 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 4542 | 514254 | 35.3886 | -119.0044 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0072793 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946250 | 0 | Non-EPSS | N | 2024 | A & GRD
KERN | KERN | TEVIS-2101 | 255322101 | OTHER | T13227 TWD T13228 | 20240604 | 851 | 20240604 | 1113 | 2474764 | 142 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 4118 | 35.2977 | -119.138 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0071892 | UG | Sus | 46253908 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946369 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1115 | 253371115 | SWITCH | 2296 | 20240604 | 1430 | 20240604 | 1449 | s1946644 | 19 | Distribution Circuit | Company Initiated | Return Circuit Normal | 125 | 2375 | 35.3763 | -119.013 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0072793 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946644 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1107 | 253371107 | TRANSFORMER | 516993368411 | 20240604 | 1519 | 20240604 | 1826 | 2475267 | 187 | Transformer only | Company Initiated | Coordination failure | 14 | 2618 | 35.3757 | -119.0091 | No | Clear;Above 90 | Other | Contaminated | 24-0073213 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946518 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2112 | 254072112 | RECLOSER | 1466 | 20240604 | 1815 | 20240605 | 342 | 2475437 | 567 | Distribution Circuit | Equipment Failure/Involved | Underground | 3192 | 246642 | 35.2878 | -119.0745 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0073282 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1946554 | 0 | Non-EPSS | N | 2024 | BC-GRD
KERN | KERN | RIO BRAVO-1103 | 252861103 | OCB | 1103/2 | 20240605 | 129 | 20240605 | 1657 | 2475735 | 928 | Distribution Circuit | 3rd Party | Vehicle | 151 | 29432 | 35.442 | -119.2606 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0073358 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | Yes | No | 1946629 | 0 | Non-EPSS | N | 2024 | B- C & GRD
KERN | KERN | SHAFTER-1104 | 253651104 | OTHER | T9366 TWD T9367 | 20240605 | 916 | 20240605 | 1414 | 2476025 | 298 | Distribution Circuit | Equipment Failure/Involved | Underground | 70 | 20860 | 35.5078 | -119.2835 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0073059 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946768 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | T3248 | 20240605 | 1036 | 20240606 | 1232 | 2476127 | 1556 | Transformer only | Equipment Failure/Involved | Underground | 12 | 18672 | 35.3331 | -119.0891 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 24-0073566 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946815 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517129767991 | 20240605 | 1411 | 20240605 | 2304 | 2476347 | 533 | Distribution Circuit | Equipment Failure/Involved | Overhead | 894 | 29351 | 35.3648 | -118.9631 | No | Clear;Above 90 | Secondary | Broken- wire on ground | 24-0073702 | OH | Sus | 46255825 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | Yes | 1946880 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | RECLOSER | 993374 | 20240605 | 1539 | 20240605 | 1935 | 2476416 | 236 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 693 | 142908 | 35.6016 | -119.6899 | No | Clear;Above 90 |  |  | 24-0073728 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946888 | 0 | Non-EPSS | N | 2024 | SGF
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | T747586 | 20240605 | 1749 | 20240606 | 137 | 2476799 | 468 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 12312 | 35.2971 | -118.9937 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0073808 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946934 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1102 | 252971102 | OTHER | T97020 TWD T24914 | 20240605 | 1753 | 20240605 | 1952 | 2476617 | 119 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 3332 | 35.1949 | -118.8323 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0073715 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946917 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517032369471 | 20240605 | 1806 | 20240606 | 505 | 2476633 | 659 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 8745 | 35.4048 | -118.9964 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0073814 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946939 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1105 | 253951105 | TRANSFORMER | 517210370931 | 20240605 | 1909 | 20240606 | 307 | 2476802 | 478 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 956 | 35.4448 | -118.9363 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0073832 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946954 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 12180 | 20240605 | 1950 | 20240606 | 436 | 2476885 | 526 | Distribution Circuit | Equipment Failure/Involved | Underground | 209 | 58778 | 35.3669 | -119.113 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0073839 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946961 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | TRANSFORMER | 516876166674 | 20240605 | 2052 | 20240606 | 1936 | 2477043 | 1364 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4092 | 35.3275 | -119.0482 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0073918 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947028 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2102 | 254572102 | FUSE | 11417 | 20240605 | 2129 | 20240606 | 642 | 2477100 | 553 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 17006 | 35.3725 | -119.156 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0073910 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947019 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1103 | 252861103 | FUSE | 14013 | 20240605 | 2135 | 20240606 | 52 | 2477103 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 657 | 35.4196 | -119.1988 | No | Clear;Above 90 |  |  | 24-0073917 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947027 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 10781 | 20240605 | 2236 | 20240606 | 2347 | 2477165 | 1511 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 25094 | 35.3388 | -119.0864 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0073924 | UG | Sus | 35558681 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947034 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 16120 | 20240605 | 2255 | 20240606 | 0 | 2477185 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 563 | 35.3621 | -119.0907 | No | Clear;32-90 F |  |  | 24-0073915 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947025 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OTHER | WIRE DOWN S/OF CGC# 517129767991 | 20240606 | 20 | 20240606 | 544 | 2477245 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 12377 | 35.3641 | -118.9631 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0073922 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | Yes | 1947032 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 713123 | 20240606 | 31 | 20240606 | 152 | 2477220 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 405 | 35.3541 | -119.1987 | No | Clear;32-90 F |  |  | 24-0073925 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947035 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1102 | 252961102 | FUSE | 14599 | 20240606 | 158 | 20240606 | 809 | 2477295 | 371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 175 | 30079 | 35.6013 | -119.3381 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0073934 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | Yes | 1947045 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15063 | 20240606 | 942 | 20240606 | 1053 | 2477652 | 71 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 106 | 7530 | 35.3507 | -118.9133 | No | Clear;32-90 F | Fuse | Burned Open | 24-0074071 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947204 | 1 | Non-EPSS | N | 2024
KERN | KERN | MARICOPA-1102 | 254211102 | OCB | 1102/2 | 20240606 | 947 | 20240606 | 1202 | 2477660 | 135 | Distribution Circuit | Animal | Bird found | 573 | 51828 | 35.1077 | -119.3972 | No | Clear;Above 90 | Conductor- Overhead | Contaminated | 24-0074049 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947188 | 0 | EPSS Ckt | Y | 2024 | G & INST OC
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 934590 | 20240606 | 1335 | 20240606 | 1423 | 2477979 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 1488 | 34.9832 | -119.786 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0074219 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1947255 | 0 | EPSS Ckt | N | 2024 | NA
KERN | KERN | 7TH STANDARD-2101 | 254582101 | TRANSFORMER | T9606 | 20240606 | 1447 | 20240606 | 2252 | 2478068 | 485 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 9104 | 35.4121 | -119.0953 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0074304 | UG | Sus | 35558681 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947280 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | RECLOSER | 1139 | 20240606 | 1643 | 20240607 | 1853 | 2478218 | 1570 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 60 | 44472 | 35.7317 | -119.7633 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 24-0074352 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | Yes | No | 1947289 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | KERN POWER-2104 | 255262104 | OCB | 2700/2 | 20240606 | 1738 | 20240607 | 2212 | 2478338 | 1649 | Distribution Circuit | Equipment Failure/Involved | Underground | 2785 | 605680 | 35.3785 | -119.0984 | No | Clear;Above 90 | Switch (UG) | Failed/Faulted | 24-0074369 | UG | Sus | 35558681 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947304 | 0 | Non-EPSS | N | 2024 | C- TIME OC
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517203466551 | 20240606 | 1858 | 20240607 | 241 | 2478575 | 463 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 463 | 35.3252 | -118.9387 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0074426 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947344 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1110 | 254071110 | OCB | 1110/2 | 20240606 | 1938 | 20240607 | 1656 | 2478584 | 497 | Distribution Circuit | Equipment Failure/Involved | Underground | 1511 | 602867 | 35.3164 | -119.0683 | No | Clear;Above 90 | Connector or Splice (UG) | Failed/Faulted | 24-0074395 | UG | Sus | 35558681 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947322 | 0 | Non-EPSS | N | 2024 | C GRD TIME
KERN | KERN | FRUITVALE-1104 | 253391104 | FUSE | 12083 | 20240606 | 2033 | 20240607 | 1554 | 2478629 | 1161 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 14679 | 35.4196 | -119.0823 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0074432 | UG | Sus | 35558681 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947349 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | FUSE | 13599 | 20240606 | 2136 | 20240608 | 346 | 2478670 | 1810 | Distribution Circuit | Equipment Failure/Involved | Underground | 92 | 56628 | 35.3752 | -119.1099 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0074483 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947391 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517171368219 | 20240606 | 2230 | 20240607 | 313 | 2478728 | 283 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 2264 | 35.3712 | -118.9491 | No | Clear;32-90 F |  |  | 24-0074484 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1947392 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-2103 | 252552103 | TRANSFORMER | 515174671320 | 20240607 | 802 | 20240607 | 1722 | 2479183 | 560 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 560 | 35.4487 | -119.6249 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0074702 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947555 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13528 | 20240607 | 1033 | 20240607 | 1129 | 2479158 | 56 | Distribution Circuit | 3rd Party | Metallic Balloon | 89 | 4984 | 35.3733 | -118.9873 | No | Clear;Above 90 | Transformer (OH) | Normal | 24-0074660 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947544 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | FUSE | 9817 | 20240607 | 1159 | 20240607 | 2048 | 2479269 | 529 | Distribution Circuit | Animal | Bird found | 21 | 4469 | 35.1113 | -118.9866 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074800 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947575 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 100000003629 | 20240607 | 1243 | 20240607 | 1735 | 2478985 | 292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 292 | 35.1869 | -119.1243 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074711 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947559 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1103 | 252861103 | FUSE | 16634 | 20240607 | 1442 | 20240608 | 630 | 2479425 | 948 | Distribution Circuit | 3rd Party | Vehicle | 26 | 8226 | 35.4421 | -119.1998 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 24-0074832 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | Yes | No | 1947594 | 0 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1103 | 254541103 | OCB | 1103/2 | 20240607 | 1738 | 20240607 | 2115 | 2479638 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 2463 | 35.5013 | -119.4493 | No | Clear;Above 90 | Anchor or Guy | Broken | 24-0074845 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1947599 | 0 | Non-EPSS | N | 2024 | NA
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13527 | 20240607 | 1939 | 20240607 | 2111 | 2479738 | 92 | Distribution Circuit | 3rd Party | Vandalism | 2870 | 25816 | 35.3743 | -118.9889 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0074861 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947613 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | TRANSFORMER | T2126 | 20240607 | 2250 | 20240608 | 2358 | 2480349 | 1508 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 17682 | 35.3519 | -119.0906 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0074905 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947797 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2101 | 255322101 | SWITCH | 37768 | 20240608 | 118 | 20240608 | 318 | 2479839 | 120 | Distribution Circuit | 3rd Party | Vehicle | 3615 | 433800 | 35.3112 | -119.1283 | No | Clear;32-90 F | Insulator | Broken | 24-0074909 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1947662 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1103 | 252861103 | TRANSFORMER | 516443269951 | 20240608 | 701 | 20240608 | 1811 | 2479886 | 670 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 670 | 35.416 | -119.1939 | No | Clear;32-90 F |  |  | 24-0074931 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947691 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 17500 | 20240608 | 854 | 20240608 | 1045 | 2479978 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 4072 | 35.438 | -118.8808 | No | Clear;32-90 F |  |  | 24-0074957 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947724 | 1 | EPSS Ckt | N | 2024
KERN | KERN | SHAFTER-1112 | 253651112 | TRANSFORMER | 516037573497 | 20240608 | 1325 | 20240608 | 1337 | 2480171 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 24 | 35.5123 | -119.3328 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 24-0074977 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947737 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1103 | 252081103 | RECLOSER | 3068 | 20240608 | 1341 | 20240609 | 113 | 2480187 | 692 | Distribution Circuit | 3rd Party | Gun Shot | 33 | 5028 | 35.1658 | -119.4547 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0074981 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1947739 | 0 | Non-EPSS | N | 2024 | SFG
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 9304 | 20240608 | 2133 | 20240608 | 2229 | 2480317 | 56 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 3976 | 35.299 | -119.0213 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Arcing | 24-0075014 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1947760 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517208167862 | 20240609 | 413 | 20240609 | 1455 | 2480391 | 642 | Distribution Circuit | 3rd Party | Vehicle | 2170 | 116380 | 35.3615 | -118.9368 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0075054 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1947808 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1112 | 253491112 | OCB | 1112/2 | 20240609 | 1308 | 20240609 | 1429 | 2480597 | 81 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 18549 | 35.5004 | -119.1519 | No | Partly Cloudy;32-90 F | Woodpin | Broken | 24-0075112 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1947860 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | 516154673582 | 20240609 | 1530 | 20240609 | 1634 | 2480628 | 64 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 256 | 35.5149 | -119.2931 | No | Clear;Above 90 |  |  | 24-0075127 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1947871 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 7270 | 20240609 | 2039 | 20240610 | 940 | 2480698 | 781 | Distribution Circuit | 3rd Party | Vandalism | 2 | 902 | 35.6594 | -119.7273 | No | Clear;32-90 F | Secondary | Broken | 24-0075140 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947883 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 11276 | 20240610 | 900 | 20240611 | 2156 | 2481113 | 2216 | Distribution Circuit | Equipment Failure/Involved | Underground | 305 | 22269 | 35.3316 | -119.0833 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0075269 | UG | Sus | 46262071 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948073 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 14757 | 20240610 | 904 | 20240610 | 1118 | 2481366 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 447 | 35.0018 | -118.8479 | No | Clear;32-90 F |  |  | 24-0075299 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948095 | 1 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2101 | 255322101 | OTHER | T13134 TWD T13135 | 20240610 | 917 | 20240610 | 1016 | 2481170 | 59 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 2301 | 35.2993 | -119.1314 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0075193 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948044 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | FUSE | 19171 | 20240610 | 1320 | 20240610 | 1805 | 2481503 | 285 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2565 | 35.413 | -118.8986 | No | Clear;32-90 F |  |  | 24-0075471 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1948160 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | JUMPER | FB 1 E/ OF 18257 | 20240610 | 1638 | 20240610 | 1931 | 2481647 | 173 | Distribution Circuit | 3rd Party | Vehicle | 47 | 8131 | 35.3507 | -118.9116 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0075454 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948156 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1106 | 254071106 | JUMPER | FB 3 E/OF CGC# 516881166923 | 20240610 | 2150 | 20240611 | 133 | 2481825 | 223 | Distribution Circuit | Vegetation | Tree - grew into line | 20 | 4460 | 35.3344 | -119.0457 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0075509 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948181 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 315849 | 20240611 | 514 | 20240611 | 613 | 2481920 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 98 | 35.3617 | -119.2121 | No | Clear;32-90 F |  |  | 24-0075578 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948235 | 1 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1102 | 254501102 | OCB | 1102/2 | 20240611 | 636 | 20240611 | 1508 | 2481925 | 512 | Distribution Circuit | 3rd Party | Vehicle | 284 | 83110 | 35.6081 | -119.3255 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0075589 | OH | Sus | 35559634 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1948242 | 0 | Non-EPSS | N | 2024 | A & C INST
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 55553 | 20240611 | 735 | 20240611 | 828 | 2481948 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 3286 | 35.325 | -119.0175 | No | Clear;32-90 F |  |  | 24-0075637 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1948288 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1109 | 253701109 | FUSE | 96550 | 20240611 | 1636 | 20240611 | 1742 | 2482592 | 66 | Distribution Circuit | Vegetation | Tree - branch fell on line | 180 | 11880 | 35.4124 | -119.0344 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0075961 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1948507 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516896163120 | 20240611 | 1642 | 20240611 | 2232 | 2482546 | 350 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 350 | 35.2301 | -119.0403 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 24-0075963 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948509 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 84243 | 20240612 | 611 | 20240612 | 804 | 2483027 | 113 | Distribution Circuit | Animal | Squirrel | 68 | 7684 | 35.5088 | -119.2714 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0076105 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948604 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1106 | 252771106 | TRANSFORMER | 517139568603 | 20240612 | 1046 | 20240612 | 1215 | 2483690 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 1424 | 35.3816 | -118.9599 | No | Clear;Above 90 | Service conductor | Broken | 24-0076275 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948784 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRIP-SAVER | 567861 | 20240612 | 1339 | 20240613 | 1936 | 2483731 | 1797 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 332 | 80045 | 35.2934 | -119.9703 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0076336 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1948800 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | ROSEDALE-2102 | 254762102 | FUSE | 11450 | 20240612 | 1450 | 20240612 | 1711 | 2483794 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 6627 | 35.3589 | -119.0613 | No | Clear;Above 90 |  |  | 24-0076415 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948817 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517171368219 | 20240612 | 1711 | 20240612 | 1806 | 2483905 | 55 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 440 | 35.3712 | -118.9491 | No | Clear;Above 90 |  |  | 24-0076436 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1948829 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-2102 | 254762102 | TRANSFORMER | T1836 | 20240612 | 1726 | 20240613 | 722 | 2483911 | 836 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 17949 | 35.3577 | -119.0622 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0076425 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948822 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | T8274 | 20240612 | 1956 | 20240613 | 225 | 2484020 | 389 | Transformer only | Equipment Failure/Involved | Underground | 9 | 3501 | 35.3603 | -119.1779 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0076502 | UG | Sus | 46262922 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948892 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 515553870469 | 20240612 | 2148 | 20240614 | 150 | 2484667 | 1682 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1682 | 35.4274 | -119.4934 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0076958 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949209 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | T331682 | 20240612 | 2323 | 20240613 | 420 | 2484097 | 297 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 7260 | 35.2849 | -119.1173 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0076497 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948887 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | RECLOSER | 1073 | 20240613 | 719 | 20240614 | 242 | 2484193 | 1163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 13033 | 35.2242 | -119.5984 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0076527 | OH | Sus | 31696873 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948918 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | MAGUNDEN-1106 | 252771106 | JUMPER | OJ'S 3 NE OF CGC# 517141568614 | 20240613 | 943 | 20240613 | 1645 | 2484410 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 8018 | 35.3821 | -118.9591 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0076584 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949025 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | TRANSFORMER | 516188266880 | 20240613 | 1016 | 20240613 | 1146 | 2484488 | 90 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 90 | 35.3309 | -119.2789 | No | Clear;32-90 F |  |  | 24-0076702 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1949102 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 13298 | 20240613 | 1130 | 20240613 | 1511 | 2484594 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2520 | 35.4345 | -119.2519 | No | Clear;32-90 F | Secondary | Broken | 24-0076729 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949112 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 15556 | 20240613 | 1809 | 20240613 | 1900 | 2484957 | 51 | Distribution Circuit | 3rd Party | Other | 927 | 4977 | 35.3649 | -119.0023 | No | Clear;Above 90 | Cutout- fuse holder | Normal | 24-0076903 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949155 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 17671 | 20240613 | 2210 | 20240614 | 432 | 2485050 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 5084 | 35.3159 | -119.0133 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0076953 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949204 | 0 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1102 | 253801102 | TRANSFORMER | 517296660586 | 20240614 | 1553 | 20240615 | 401 | 2485779 | 728 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1456 | 35.1608 | -118.9052 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0077274 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949441 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 7077 | 20240614 | 2215 | 20240615 | 107 | 2486153 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 516 | 35.7319 | -119.7786 | No | Clear;32-90 F |  |  | 24-0077319 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949486 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1103 | 254561103 | FUSE | 16221 | 20240615 | 1039 | 20240615 | 1126 | 2486412 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 282 | 35.3616 | -119.2522 | No | Clear;32-90 F |  |  | 24-0077364 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949534 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2109 | 254072109 | TRANSFORMER | 516906665524 | 20240615 | 1610 | 20240615 | 1620 | 2486597 | 10 | Transformer only | Animal | Bird found | 2 | 20 | 35.296 | -119.0376 | No | Clear;Above 90 | Fuse | Broken | 24-0077397 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949561 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1109 | 254071109 | FUSE | 13501 | 20240615 | 1743 | 20240615 | 1823 | 2486642 | 40 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 2440 | 35.3022 | -119.0565 | No | Clear;Above 90 | Cutout- fuse holder | Failed/Faulted | 24-0077414 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949576 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | OCB | 1107/2 | 20240616 | 1715 | 20240617 | 707 | 2487124 | 832 | Distribution Circuit | 3rd Party | Vehicle | 1143 | 135084 | 35.2971 | -118.8618 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0077507 | OH | Sus | 31697441 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1949660 | 0 | Non-EPSS | N | 2024 | ABC TIME
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | FUSE | 967375 | 20240616 | 2122 | 20240616 | 2343 | 2487269 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1656 | 35.1018 | -119.0391 | No | Clear;32-90 F |  |  | 24-0077549 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949695 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1103 | 255451103 | TRANSFORMER | T13152 | 20240617 | 827 | 20240617 | 1315 | 2487414 | 288 | Transformer only | Equipment Failure/Involved | Underground | 16 | 4608 | 35.392 | -118.8862 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0077606 | UG | Sus | 46264238 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949773 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1103 | 253871103 | FUSE | 14237 | 20240617 | 915 | 20240617 | 1600 | 2487610 | 405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 405 | 35.1516 | -119.2359 | No | Clear;32-90 F | Jumper | Burned Open | 24-0077674 | OH | Sus | 46264313 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949865 | 1 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | JUMPER | BROKEN #2 HS JUMPER | 20240617 | 1150 | 20240617 | 1736 | 2487802 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 7958 | 35.4052 | -119.0835 | No | Clear;32-90 F | Jumper | Broken | 24-0077699 | OH | Sus | 46264495 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1949889 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1103 | 255451103 | OCB | 1103/2/NORM | 20240617 | 1551 | 20240618 | 411 | 2488099 | 740 | Distribution Circuit | 3rd Party | Vehicle | 2328 | 153894 | 35.4222 | -118.9006 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0077800 | OH | Sus | 35561333 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1949927 | 0 | Non-EPSS | N | 2024 | PH OC TIME- PU PH/GRD INSTANT
KERN | KERN | STOCKDALE-1109 | 254071109 | TRANSFORMER | T14835 | 20240617 | 2332 | 20240618 | 42 | 2488846 | 70 | Distribution Circuit | 3rd Party | Vandalism | 22 | 1228 | 35.2966 | -119.0553 | No | Clear;32-90 F | Metering Equipment | Normal | 24-0077930 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1950039 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8841 | 20240618 | 943 | 20240618 | 1112 | 2489279 | 89 | Distribution Circuit | Animal | Bird found | 2 | 178 | 35.3436 | -119.087 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078122 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1950230 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | TRANSFORMER | 516798169871 | 20240618 | 2012 | 20240619 | 158 | 2489622 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3958 | 35.415 | -119.0752 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0078315 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950303 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 11109 | 20240619 | 6 | 20240619 | 1617 | 2489726 | 971 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 30022 | 35.3345 | -119.0856 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0078362 | UG | Sus | 46265685 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950343 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | OCB | 48518 | 20240619 | 623 | 20240619 | 1616 | 2489762 | 593 | Distribution Circuit | Animal | Bird found | 3599 | 173646 | 35.3632 | -118.9314 | No | Clear;32-90 F | Switch (OH) | Burned/flashed | 24-0078373 | OH | Sus | 31697534 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1950350 | 0 | Non-EPSS | N | 2024 | A C PH OC
KERN | KERN | MIDWAY-1101 | 252611101 | JUMPER | BURNT OPEN POS B JUMPER 2 POLES W/OF 16241 | 20240620 | 522 | 20240620 | 700 | 2490381 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 588 | 35.4269 | -119.5181 | No | Clear;32-90 F | Jumper | Burned Open | 24-0078573 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1950546 | 1 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1103 | 254561103 | TRANSFORMER | 516430569170 | 20240620 | 633 | 20240620 | 1528 | 2490564 | 535 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 535 | 35.3943 | -119.1978 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0078614 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950575 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1111 | 253491111 | SWITCH | 1606 | 20240620 | 1506 | 20240620 | 1521 | 2490974 | 15 | Distribution Circuit | Equipment Failure/Involved | Overhead | 254 | 3810 | 35.4998 | -119.1623 | No | Clear;Above 90 | Secondary | Broken- wire on ground | 24-0078783 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950644 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | OCB | 2109/2 | 20240620 | 1612 | 20240621 | 112 | 2491015 | 540 | Distribution Circuit | 3rd Party | Vehicle | 3841 | 442720 | 35.3885 | -119.0044 | No | Clear;Above 90 | Conductor- Overhead | Together | 24-0078809 | OH | Sus | 35561892 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1950650 | 0 | Non-EPSS | N | 2024 | A & B TIME
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 228405 | 20240621 | 938 | 20240621 | 1314 | 2491596 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 432 | 35.5582 | -119.6365 | No | Clear;32-90 F |  |  | 24-0079162 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950933 | 1 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 16241 | 20240621 | 1000 | 20240621 | 1140 | 2491639 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 400 | 35.4269 | -119.5169 | No | Clear;32-90 F |  |  | 24-0079111 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950909 | 1 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 17232 | 20240622 | 804 | 20240623 | 119 | 2492352 | 1035 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 15109 | 35.2932 | -119.974 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079395 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951046 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 16245 | 20240622 | 807 | 20240622 | 1015 | 2492356 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 768 | 35.3995 | -119.5095 | No | Clear;32-90 F |  |  | 24-0079392 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951043 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1110 | 252901110 | TRANSFORMER | 515995876652 | 20240622 | 1354 | 20240622 | 1520 | 2492554 | 86 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 32 | 2531 | 35.5984 | -119.3481 | No | Clear;Above 90 | Connector or Splice (OH) | Broken- wire on ground | 24-0079435 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1951067 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2103 | 255262103 | TRANSFORMER | 516781968977 | 20240622 | 1536 | 20240622 | 1910 | 2492611 | 214 | Transformer only | Equipment Failure/Involved | Underground | 6 | 1284 | 35.3907 | -119.0802 | No | Clear;Above 90 | Secondary | Deteriorated | 24-0079440 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951072 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516993066944 | 20240622 | 1811 | 20240622 | 1853 | 2492693 | 42 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 252 | 35.3353 | -119.0083 | No | Clear;Above 90 |  |  | 24-0079458 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1951080 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516974966863 | 20240622 | 1819 | 20240622 | 1906 | 2492699 | 47 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 188 | 35.3331 | -119.0145 | No | Clear;Above 90 |  |  | 24-0079461 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1951082 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | TRANSFORMER | 516792969905 | 20240623 | 347 | 20240623 | 458 | 2492840 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 284 | 35.416 | -119.077 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079497 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951113 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15060 | 20240623 | 703 | 20240623 | 854 | 2492871 | 111 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 27 | 2997 | 35.3398 | -118.9066 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079508 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951127 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARNERAS-1102 | 252321102 | RECLOSER | 3266 | 20240623 | 1215 | 20240623 | 1704 | 2492973 | 289 | Distribution Circuit | Animal | Other | 1 | 289 | 35.5372 | -119.803 | No | Clear;Above 90 | Regulator | Burned/flashed | 24-0079530 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951152 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15060 | 20240623 | 1438 | 20240623 | 1725 | 2493015 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 1317 | 35.3398 | -118.9066 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0079540 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951162 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRANSFORMER | 516993066944 | 20240623 | 1634 | 20240623 | 2259 | 2493122 | 385 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2310 | 35.3353 | -119.0083 | No | Clear;Above 90 | Transformer (OH) |  | 24-0079560 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951180 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | TRANSFORMER | 514977277320 | 20240623 | 1717 | 20240623 | 2230 | 2493070 | 313 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 2817 | 35.613 | -119.6906 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079565 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951185 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1109 | 253951109 | FUSE | 9465 | 20240623 | 1729 | 20240624 | 104 | 2493113 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 6548 | 35.3871 | -118.9357 | No | Clear;Above 90 | Conductor- Overhead | Together | 24-0079568 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951189 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1115 | 253491115 | FUSE | 18639 | 20240623 | 1808 | 20240623 | 2054 | 2493133 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 221 | 35.5009 | -119.117 | No | Clear;Above 90 |  |  | 24-0079580 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951197 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 69452 | 20240623 | 2020 | 20240624 | 205 | 2493195 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 11730 | 35.3647 | -119.0923 | No | Clear;Above 90 | Crossarm- Wood | Burned/flashed | 24-0079596 | OH | Sus | 31698202 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1951212 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 9991 | 20240623 | 2147 | 20240623 | 2156 | 2493202 | 9 | Distribution Circuit | 3rd Party | Metallic Balloon | 36 | 324 | 35.3234 | -119.0247 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0079583 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951199 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517144568310 | 20240623 | 2218 | 20240624 | 1410 | 2493674 | 952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 9072 | 35.3736 | -118.9581 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079712 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951375 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1108 | 252771108 | OTHER | T11725 TWD T11726 | 20240624 | 220 | 20240624 | 305 | 2493265 | 45 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 1035 | 35.3608 | -118.8976 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0079604 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951219 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | OCB | 1101/2 | 20240624 | 647 | 20240624 | 749 | 2493346 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2028 | 125736 | 35.374 | -119.0404 | No | Clear;32-90 F |  |  | 24-0079620 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951236 | 0 | Non-EPSS | N | 2024 | C B PH OC TIME MAINT ALARM
KERN | KERN | WEEDPATCH-1103 | 252971103 | RECLOSER | 1668 | 20240624 | 718 | 20240624 | 1517 | 2493342 | 479 | Distribution Circuit | 3rd Party | Vehicle | 357 | 86691 | 35.2233 | -118.8423 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0079618 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951240 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516932768079 | 20240624 | 809 | 20240625 | 130 | 2493414 | 1041 | Distribution Circuit | Equipment Failure/Involved | Overhead | 513 | 33746 | 35.3662 | -119.0297 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079725 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951388 | 0 | Non-EPSS | N | 2024
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515695159262 | 20240624 | 1020 | 20240624 | 1333 | 2493662 | 193 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 193 | 35.12 | -119.4393 | No | Clear;Above 90 |  |  | 24-0079821 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1951444 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TAFT SUB | 25208 | OCB | 1100/2 | 20240624 | 1207 | 20240624 | 1224 | 2493794 | 17 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 476 | 8092 | 35.1363 | -119.4822 | No | Clear;Above 90 | Secondary | Burned/flashed | 24-0079761 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951415 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | LAKEVIEW-1107 | 253411107 | TRANSFORMER | 516510057620 | 20240624 | 1328 | 20240624 | 1949 | 2493925 | 381 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 381 | 35.0771 | -119.1684 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0079853 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951464 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | FUSE | 2175 | 20240624 | 1438 | 20240624 | 2034 | 2494158 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 712 | 35.4098 | -118.9675 | No | Clear;Above 90 | Customer Equipment | Malfunctioning | 24-0080005 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951577 | 1 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-1101 | 254761101 | TRANSFORMER | 516860768936 | 20240624 | 1502 | 20240624 | 2146 | 2494374 | 404 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 404 | 35.3897 | -119.054 | No | Clear;Above 90 | Fuse | Broken | 24-0080031 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951595 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 12056 | 20240624 | 1506 | 20240625 | 426 | 2494332 | 800 | Distribution Circuit | Equipment Failure/Involved | Underground | 128 | 35120 | 35.3258 | -119.057 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0079918 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951505 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517144568310 | 20240624 | 1520 | 20240624 | 1910 | 2494371 | 230 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 1380 | 35.3736 | -118.9581 | No | Clear;32-90 F |  |  | 24-0079979 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1951548 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1110 | 253701110 | TRANSFORMER | 516961768172 | 20240624 | 1610 | 20240625 | 432 | 2494469 | 742 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 17474 | 35.369 | -119.0195 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0079986 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951553 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2105 | 255322105 | FUSE | 14473 | 20240624 | 1920 | 20240625 | 1119 | 2494718 | 959 | Distribution Circuit | Equipment Failure/Involved | Underground | 248 | 54810 | 35.325 | -119.1133 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0080006 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951578 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | T646167 | 20240625 | 58 | 20240625 | 852 | 2494934 | 474 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 474 | 35.2524 | -118.857 | No | Clear;32-90 F |  |  | 24-0080194 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1951767 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 14351 | 20240625 | 745 | 20240625 | 950 | 2494584 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2400 | 35.4018 | -118.9909 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0080149 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951696 | 0 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1104 | 253191104 | SWITCH | 18547 | 20240625 | 936 | 20240625 | 1500 | 2495225 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1229 | 35.0934 | -118.8869 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0080252 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1951843 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 20262 | 20240625 | 944 | 20240625 | 1146 | 2495420 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 122 | 35.3427 | -119.0638 | No | Clear;Above 90 |  |  | 24-0080310 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951879 | 1 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 513945478901 | 20240625 | 1344 | 20240626 | 353 | 2495522 | 849 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 6935 | 35.6508 | -120.0387 | No | Clear;Above 90 | Secondary | Burned/flashed | 24-0080429 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951924 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2105 | 254072105 | OCB | 2105/2 | 20240625 | 1825 | 20240626 | 147 | 2495913 | 442 | Distribution Circuit | Equipment Failure/Involved | Underground | 1953 | 712071 | 35.3165 | -119.068 | No | Clear;Above 90 | Elbow | Failed/Faulted | 24-0080548 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951973 | 0 | Non-EPSS | N | 2024 | SET A RLY TRIP
KERN | KERN | STOCKDALE-2111 | 254072111 | TRANSFORMER | T0580 | 20240625 | 1913 | 20240625 | 2207 | 2495900 | 174 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 1218 | 35.3312 | -119.06 | No | Clear;Above 90 |  |  | 24-0080580 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1952008 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2105 | 254072105 | FUSE | 11101 | 20240626 | 201 | 20240626 | 1225 | 2496051 | 609 | Distribution Circuit | Equipment Failure/Involved | Underground | 115 | 13827 | 35.307 | -119.0885 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0080637 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952023 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | OCB | 1102/2 | 20240626 | 557 | 20240626 | 1450 | s1967808 | 533 | Distribution Circuit | 3rd Party | Vehicle | 173 | 39961 | 35.2249 | -118.7784 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0080657 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1967808 | 0 | EPSS Ckt | N | 2024 | B- C- TIME OC
KERN | KERN | WELLFIELD-1104 | 254291104 | OCB | 1104/2 | 20240626 | 557 | 20240626 | 1523 | 2496101 | 566 | Distribution Circuit | 3rd Party | Vehicle | 19 | 3803 | 35.2249 | -118.7783 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0080657 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | Yes | No | 1952037 | 0 | Non-EPSS | N | 2024 | B- C- TIME OC
KERN | KERN | STOCKDALE-2105 | 254072105 | FUSE | 12116 | 20240626 | 907 | 20240626 | 1018 | 2496476 | 71 | Distribution Circuit | 3rd Party | Other | 85 | 6035 | 35.3074 | -119.0796 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0080773 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952183 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 16363 | 20240626 | 914 | 20240626 | 1411 | 2496494 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 792 | 35.6452 | -119.2592 | No | Clear;32-90 F | Jumper | Burned Open | 24-0080921 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1952230 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2109 | 254072109 | OCB | 2109/2 | 20240626 | 957 | 20240627 | 126 | 2496584 | 929 | Distribution Circuit | Equipment Failure/Involved | Underground | 3786 | 1346345 | 35.3165 | -119.0679 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0080782 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952190 | 0 | Non-EPSS | N | 2024 | PH OC TIME
KERN | KERN | ANTELOPE-1101 | 252021101 | TRANSFORMER | 514031578510 | 20240626 | 1720 | 20240626 | 2212 | 2497076 | 292 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 584 | 35.6408 | -120.0096 | No | Clear;Above 90 | Transformer (OH) |  | 24-0081034 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952266 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | TRANSFORMER | T0580 | 20240626 | 1816 | 20240626 | 1848 | 2497104 | 32 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 224 | 35.3312 | -119.06 | No | Clear;Above 90 |  |  | 24-0081051 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1952275 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 69452 | 20240627 | 228 | 20240627 | 455 | 2497314 | 147 | Distribution Circuit | Animal | Bird found | 34 | 4998 | 35.3647 | -119.0923 | No | Clear;32-90 F | Fuse | Normal | 24-0081126 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952335 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17784 | 20240627 | 2316 | 20240628 | 137 | 2498134 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 9485 | 35.3447 | -119.0708 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0081614 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952664 | 1 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13341 | 20240628 | 1741 | 20240628 | 2345 | 2499043 | 364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1092 | 35.0473 | -119.0115 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0081992 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952929 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | JUMPER | FB'S 2 W/OF CGC 516818367543 | 20240628 | 1823 | 20240628 | 1951 | 2498964 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 2552 | 35.3512 | -119.0684 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0081962 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1952899 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1103 | 252611103 | OCB | 1103/2 | 20240629 | 0 | 20240629 | 1556 | 2499067 | 956 | Distribution Circuit | 3rd Party | Vehicle | 172 | 66683 | 35.4006 | -119.449 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0081995 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1952932 | 0 | Non-EPSS | N | 2024 | ABC TIME
KERN | KERN | CAL WATER-1103 | 255451103 | FUSE | 13859 | 20240629 | 1250 | 20240629 | 2010 | 2499352 | 440 | Distribution Circuit | 3rd Party | Other | 6 | 2641 | 35.4127 | -118.9141 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0082071 | OH | Sus | 31698746 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1953002 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517257366596 | 20240629 | 1432 | 20240630 | 1021 | 2499388 | 1189 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 3567 | 35.3265 | -118.9203 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0082098 | OH | Sus | 31698747 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1953020 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517532562010 | 20240629 | 1943 | 20240629 | 2118 | 2499517 | 95 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 2090 | 35.2012 | -118.8268 | No | Clear;32-90 F | Connector or Splice (OH) | Normal | 24-0082123 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1953043 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | TRANSFORMER | 516264170912 | 20240629 | 2214 | 20240630 | 1400 | 2499562 | 946 | Transformer only | 3rd Party | Vehicle | 1 | 946 | 35.4417 | -119.2552 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 24-0082145 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1953065 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517194365416 | 20240630 | 732 | 20240630 | 1037 | 2499646 | 185 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 185 | 35.2939 | -118.9409 | No | Clear;32-90 F | Fuse | Broken | 24-0082189 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1953103 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | TRANSFORMER | T0154 | 20240630 | 812 | 20240630 | 1718 | 2499592 | 546 | Transformer only | Equipment Failure/Involved | Underground | 10 | 5460 | 35.1412 | -119.4664 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0082166 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1953084 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 9702 | 20240630 | 1206 | 20240630 | 1321 | 2499752 | 75 | Distribution Circuit | Animal | Bird found | 66 | 4950 | 35.303 | -119.0152 | No | Clear;Above 90 | Fuse | Normal | 24-0082204 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1953116 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 15003 | 20240630 | 1635 | 20240630 | 1742 | 2499903 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 2680 | 35.4194 | -119.0321 | No | Clear;Above 90 | Anchor or Guy | Broken | 24-0082230 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1953143 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1110 | 252901110 | FUSE | 14041 | 20240701 | 509 | 20240701 | 935 | 2500344 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1866 | 35.5869 | -119.3693 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0082315 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953217 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 17464 | 20240701 | 955 | 20240701 | 1130 | 2500574 | 95 | Distribution Circuit | Vegetation | Tree - grew into line | 72 | 6840 | 35.3672 | -118.9908 | No | Clear;32-90 F | Secondary | Contaminated | 24-0082382 | OH | Sus | 46270716 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953308 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1108 | 252721108 | FUSE | 15243 | 20240701 | 1300 | 20240701 | 1511 | 2500830 | 131 | Distribution Circuit | Vegetation | Tree - grew into line | 49 | 6419 | 35.4418 | -119.0238 | No | Clear;Above 90 | Conductor- Overhead | Together | 24-0082518 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953345 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517060868956 | 20240701 | 1447 | 20240701 | 1559 | 2500963 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 1296 | 35.3908 | -118.9869 | No | Clear;Above 90 | Connector or Splice (OH) | Burned Open | 24-0082639 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953371 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | 516896069422 | 20240701 | 1514 | 20240701 | 1659 | 2500989 | 105 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 210 | 35.4029 | -119.0423 | No | Clear;Above 90 |  |  | 24-0082634 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1953369 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-1102 | 254401102 | JUMPER | JMPRS S/O 18719 | 20240701 | 1637 | 20240701 | 1920 | 2501051 | 163 | Distribution Circuit | 3rd Party | Vehicle | 2 | 326 | 35.7312 | -119.8687 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0082655 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953375 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1101 | 253371101 | FUSE | 14304 | 20240701 | 2045 | 20240702 | 445 | 2501345 | 480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 10698 | 35.3974 | -118.9986 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0082724 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953409 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 16338 | 20240702 | 839 | 20240702 | 1442 | 2501666 | 363 | Distribution Circuit | Animal | Bird found | 9 | 1171 | 35.3821 | -119.1279 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0082911 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953571 | 1 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515345870324 | 20240702 | 846 | 20240702 | 1520 | 2501674 | 394 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 394 | 35.422 | -119.5628 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0082889 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953555 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1106 | 254071106 | FUSE | 14067 | 20240702 | 2002 | 20240703 | 402 | 2503048 | 480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 14400 | 35.3282 | -119.0457 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0083284 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953722 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1110 | 252901110 | OTHER | WIRE DOWN 2 S/OF CGC 515926076780 | 20240703 | 815 | 20240703 | 1150 | 2503571 | 215 | Distribution Circuit | 3rd Party | Vehicle | 5 | 1029 | 35.6014 | -119.3715 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0083432 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | Yes | 1953893 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2102 | 254572102 | TRANSFORMER | T5544 | 20240703 | 1300 | 20240704 | 24 | 2503804 | 684 | Transformer only | Equipment Failure/Involved | Underground | 12 | 8208 | 35.377 | -119.1583 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Deteriorated | 24-0083657 | UG | Sus | 46272117 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953932 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 2162 | 20240703 | 1522 | 20240703 | 1557 | 2503941 | 33 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 990 | 35.4092 | -119.0427 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083718 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953948 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1111 | 254071111 | SWITCH | 6105 | 20240703 | 1920 | 20240704 | 2 | 2504310 | 282 | Distribution Circuit | Equipment Failure/Involved | Underground | 41 | 3266 | 35.3294 | -119.0587 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Deteriorated | 24-0083438 | UG | Sus | 35564394 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953999 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | TRANSFORMER | T8914 | 20240703 | 1921 | 20240704 | 350 | 2504329 | 509 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 4581 | 35.4113 | -119.1197 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0083831 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954037 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 14507 | 20240704 | 548 | 20240704 | 1620 | 2505044 | 632 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 843 | 35.4538 | -118.9495 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084055 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954160 | 1 | EPSS Ckt | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | JUMPER | VERT JMPRS @ CGC# 517077663917 | 20240704 | 1201 | 20240704 | 1350 | 2505006 | 109 | Distribution Circuit | 3rd Party | Vandalism | 34 | 2254 | 35.2522 | -118.9798 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083995 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954135 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2108 | 254072108 | TRANSFORMER | T5243 | 20240704 | 1709 | 20240705 | 53 | 2505254 | 464 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 7888 | 35.314 | -119.1066 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084098 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954183 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517226568158 | 20240704 | 1740 | 20240705 | 40 | 2505388 | 420 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 43 | 10020 | 35.3693 | -118.9313 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Broken | 24-0084097 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954182 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-2102 | 254762102 | SWITCH | 595790 | 20240704 | 1857 | 20240705 | 329 | 2505415 | 512 | Distribution Circuit | Equipment Failure/Involved | Underground | 213 | 7912 | 35.3609 | -119.0592 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Broken | 24-0084093 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954187 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | FUSE | 19382 | 20240704 | 1946 | 20240704 | 2037 | 2505449 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 115 | 5865 | 35.4053 | -119.1656 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084114 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954197 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | TRANSFORMER | T13829 | 20240704 | 2127 | 20240705 | 533 | 2505503 | 486 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 4864 | 35.4068 | -119.1658 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084161 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954246 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | FUSE | 10779 | 20240704 | 2200 | 20240705 | 1445 | 2505537 | 1005 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 28464 | 35.3392 | -119.0914 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084222 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954282 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | TRIP-SAVER | 17747 | 20240704 | 2242 | 20240705 | 840 | 2505575 | 598 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 119002 | 35.3321 | -119.0133 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0084165 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1954250 | 0 | Non-EPSS | N | 2024 | NA
KERN | KERN | STOCKDALE-2111 | 254072111 | RECLOSER | 4035 | 20240704 | 2311 | 20240705 | 351 | 2505586 | 280 | Distribution Circuit | Equipment Failure/Involved | Underground | 1740 | 309977 | 35.3401 | -119.0609 | No | Clear;32-90 F | Elbow | Burned/flashed | 24-0084162 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954247 | 0 | Non-EPSS | N | 2024 | C & GRD
KERN | KERN | MARICOPA-1101 | 254211101 | TRANSFORMER | 515878559043 | 20240705 | 1008 | 20240705 | 1234 | 2505896 | 146 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 146 | 35.1144 | -119.379 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084313 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1954343 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 9630 | 20240705 | 1125 | 20240705 | 1418 | 2505964 | 173 | Distribution Circuit | Animal | Bird found | 1 | 173 | 35.3106 | -119.0072 | No | Clear-Heat Wave;Above 90 | Fuse | Burned Open | 24-0084345 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954359 | 1 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-2102 | 254762102 | SWITCH | 595790 | 20240705 | 1127 | 20240705 | 1750 | 2505963 | 383 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 1894 | 35.3609 | -119.0592 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Burned/flashed | 24-0084093 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954330 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1116 | 253491116 | FUSE | 921823 | 20240705 | 1200 | 20240705 | 1242 | 2505998 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 42 | 35.5443 | -119.148 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084317 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954346 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | JUMPER | FB 1 N/OF CGC# 517221565503 | 20240705 | 1328 | 20240705 | 1831 | 2506046 | 303 | Distribution Circuit | 3rd Party | Vehicle | 3 | 859 | 35.2967 | -118.9321 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0084214 | OH | Sus | 35564659 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954348 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2108 | 254072108 | TRANSFORMER | T5245 | 20240705 | 2007 | 20240706 | 358 | 2507007 | 471 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 5094 | 35.3147 | -119.105 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084447 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954423 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | RECLOSER | 2635 | 20240705 | 2026 | 20240706 | 243 | 2506615 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 570 | 105690 | 35.4418 | -119.2902 | No | Clear;Above 90 | Connector or Splice (OH) | Broken- wire on object | 24-0084442 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1954416 | 0 | Non-EPSS | N | 2024 | C & GRD
KERN | KERN | STOCKDALE-1109 | 254071109 | FUSE | 8699 | 20240706 | 247 | 20240706 | 1525 | 2507263 | 758 | Distribution Circuit | Equipment Failure/Involved | Underground | 193 | 54120 | 35.3067 | -119.0566 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0084507 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954482 | 1 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | SWITCH | 441075 | 20240706 | 257 | 20240706 | 304 | s1954745 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 280 | 1960 | 35.4067 | -119.3119 | No | Clear;Above 90 | Connector or Splice (OH) | Normal | 24-0084442 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954745 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517068868287 | 20240706 | 1540 | 20240706 | 1707 | 2507873 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 870 | 35.373 | -118.9836 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Normal | 24-0084661 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954559 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517049466435 | 20240706 | 1654 | 20240706 | 2343 | 2507782 | 409 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2454 | 35.3214 | -118.9893 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084669 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954565 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1110 | 253951110 | TRANSFORMER | T2663 | 20240706 | 1702 | 20240707 | 132 | 2507790 | 510 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 9112 | 35.3945 | -118.946 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084664 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954561 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517148667861 | 20240706 | 1741 | 20240707 | 153 | 2507884 | 492 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3444 | 35.3614 | -118.9569 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084674 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954570 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1103 | 252081103 | TRANSFORMER | 515636760438 | 20240706 | 1752 | 20240707 | 149 | 2508199 | 477 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 9540 | 35.1519 | -119.4607 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084693 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954591 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516895567667 | 20240706 | 1815 | 20240706 | 2001 | 2507990 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1272 | 35.3548 | -119.042 | No | Clear-Heat Wave;Above 90 | Connector or Splice (OH) | Broken | 24-0084712 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954612 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516895667696 | 20240706 | 1815 | 20240706 | 2002 | 2507993 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1177 | 35.3556 | -119.042 | No | Clear-Heat Wave;Above 90 | PGs- Kearneys | Deteriorated | 24-0084714 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954614 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1108 | 254071108 | TRANSFORMER | T666495 | 20240706 | 1846 | 20240706 | 2049 | 2508189 | 123 | Transformer only | Equipment Failure/Involved | Underground | 5 | 615 | 35.3383 | -119.0377 | No | Clear-Heat Wave;Above 90 | Fuse | Broken | 24-0084727 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954629 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | TRANSFORMER | 516879669958 | 20240706 | 1910 | 20240706 | 2004 | 2508375 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 540 | 35.4177 | -119.048 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Normal | 24-0084721 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954621 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 645327 | 20240706 | 1950 | 20240707 | 1110 | 2508544 | 920 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 14295 | 35.3151 | -119.0062 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084775 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954678 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | TRANSFORMER | 516181372895 | 20240706 | 2014 | 20240707 | 1402 | 2508356 | 1066 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 18122 | 35.4966 | -119.2835 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084732 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954634 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2103 | 255262103 | TRANSFORMER | T9969 | 20240706 | 2034 | 20240707 | 127 | 2508392 | 293 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 2344 | 35.4016 | -119.116 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084739 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954642 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1106 | 254501106 | TRANSFORMER | T6887 | 20240706 | 2104 | 20240707 | 1129 | 2508428 | 865 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 22322 | 35.5858 | -119.3487 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084743 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954646 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | TRANSFORMER | 516879669958 | 20240706 | 2126 | 20240707 | 1100 | 2508497 | 814 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 11495 | 35.4177 | -119.048 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084826 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954721 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517098968424 | 20240706 | 2230 | 20240707 | 14 | 2508543 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1040 | 35.3762 | -118.9741 | No | Clear;Above 90 | Fuse | Burned Open | 24-0084790 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954688 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 14363 | 20240707 | 1345 | 20240707 | 1844 | 2508934 | 299 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 598 | 35.3688 | -119.1153 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Burned/flashed | 24-0084874 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954750 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1104 | 253141104 | OCB | 1104/2 | 20240707 | 1412 | 20240707 | 1754 | s1954755 | 222 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 7434 | 34.9276 | -119.6203 | No | Clear;32-90 F |  |  | 24-0084879 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954755 | 0 | EPSS Ckt | Y | 2024 | B- GRD- INST OC- MAINT ALARM
KERN | KERN | WESTPARK-1104 | 253701104 | TRANSFORMER | 516928368993 | 20240707 | 1454 | 20240707 | 1545 | 2509032 | 51 | Transformer only | Vegetation | Tree - grew into line | 2 | 102 | 35.3912 | -119.0314 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Contaminated | 24-0084900 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954766 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2102 | 254572102 | OCB | 2102/2 | 20240707 | 1619 | 20240707 | 2303 | 2509118 | 404 | Distribution Circuit | Equipment Failure/Involved | Underground | 2404 | 590233 | 35.3871 | -119.1644 | No | Clear-Heat Wave;Above 90 | Elbow | Failed/Faulted | 24-0084908 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954772 | 0 | Non-EPSS | N | 2024 | A-GRD TIME OC
KERN | KERN | STOCKDALE-1108 | 254071108 | TRANSFORMER | T666495 | 20240707 | 1638 | 20240707 | 2253 | 2509149 | 375 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 1875 | 35.3383 | -119.0377 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084918 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954780 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | TRANSFORMER | 516820367492 | 20240707 | 1654 | 20240708 | 412 | 2509204 | 678 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 8136 | 35.3498 | -119.0673 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084934 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954791 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | TRANSFORMER | 516816667480 | 20240707 | 1658 | 20240708 | 357 | 2509201 | 659 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 9808 | 35.3494 | -119.0685 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084936 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954792 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1106 | 252771106 | TRANSFORMER | 517131468591 | 20240707 | 1703 | 20240708 | 2049 | 2510677 | 1666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 26446 | 35.3813 | -118.9625 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0085345 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955097 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1104 | 252771104 | FUSE | 13677 | 20240707 | 1712 | 20240708 | 948 | 2509213 | 996 | Distribution Circuit | Equipment Failure/Involved | Underground | 63 | 19738 | 35.378 | -118.9073 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084947 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954804 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516895567667 | 20240707 | 1715 | 20240708 | 945 | 2509220 | 990 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 21736 | 35.3548 | -119.042 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084937 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954793 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | FUSE | 11033 | 20240707 | 1803 | 20240708 | 417 | 2509322 | 614 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 30274 | 35.3297 | -119.0936 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084954 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954810 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2115 | 254072115 | TRANSFORMER | T6333 | 20240707 | 1834 | 20240708 | 439 | 2509340 | 605 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 9075 | 35.3282 | -119.0941 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0084977 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954835 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1105 | 252771105 | TRANSFORMER | 517191268259 | 20240707 | 1900 | 20240707 | 1959 | 2508995 | 59 | Transformer only | Equipment Failure/Involved | Electrical Overload | 13 | 767 | 35.3723 | -118.9425 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0084894 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954763 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2102 | 255262102 | TRANSFORMER | T9187 | 20240707 | 1914 | 20240708 | 959 | 2509374 | 885 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 13374 | 35.3624 | -119.1023 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084988 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954846 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 516963265747 | 20240707 | 1921 | 20240708 | 1545 | 2509435 | 1224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 11000 | 35.3023 | -119.0182 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084957 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954814 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516666468686 | 20240707 | 1951 | 20240708 | 209 | 2509422 | 378 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 4158 | 35.382 | -119.1191 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0084974 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954829 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRANSFORMER | 516066969866 | 20240707 | 1951 | 20240708 | 120 | 2509423 | 329 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 987 | 35.4126 | -119.3207 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084971 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954827 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2105 | 254072105 | TRANSFORMER | T8988 | 20240707 | 1951 | 20240708 | 1058 | 2509420 | 907 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 15820 | 35.2984 | -119.0704 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084982 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954840 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2104 | 255322104 | TRANSFORMER | J1265 TWD T10334 | 20240707 | 1958 | 20240708 | 416 | 2509428 | 498 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 8964 | 35.3492 | -119.1314 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0084998 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954857 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517054267174 | 20240707 | 2003 | 20240708 | 1457 | 2509615 | 1132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 30450 | 35.3421 | -118.9882 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0085026 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954876 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2102 | 253142102 | RECLOSER | 3542 | 20240707 | 2004 | 20240708 | 41 | 2509444 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 27900 | 34.8716 | -119.4938 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0084961 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954818 | 0 | EPSS Ckt | Y | 2024 | GRD (C-GRD)
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517078969150 | 20240707 | 2008 | 20240707 | 2102 | 2509449 | 54 | Transformer only | Unknown Cause | Patrol - not conducted | 11 | 594 | 35.3962 | -118.9805 | No | Clear;Above 90 |  |  | 24-0084975 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1954831 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | T1434 | 20240707 | 2008 | 20240708 | 1504 | 2509450 | 1125 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 15876 | 35.3958 | -119.1214 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084976 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954832 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | 516175272978 | 20240707 | 2048 | 20240707 | 2135 | 2509519 | 47 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 470 | 35.4985 | -119.2858 | No | Clear;Above 90 |  |  | 24-0084983 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954841 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | TRANSFORMER | 516875267768 | 20240707 | 2123 | 20240708 | 1053 | 2509583 | 810 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 11980 | 35.3575 | -119.0488 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0085014 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954870 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | TRANSFORMER | 517073469375 | 20240707 | 2149 | 20240707 | 2232 | 2509537 | 43 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 258 | 35.4024 | -118.9825 | No | Clear;Above 90 |  |  | 24-0085013 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954869 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2101 | 255262101 | TRANSFORMER | T11407 | 20240707 | 2217 | 20240707 | 2320 | 2509573 | 63 | Transformer only | Equipment Failure/Involved | Underground | 8 | 504 | 35.3956 | -119.0683 | No | Clear;Above 90 | Fuse | Failed/Faulted | 24-0085025 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954875 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2103 | 255322103 | OCB | 2103/2 | 20240708 | 22 | 20240708 | 1724 | 2509645 | 1022 | Distribution Circuit | Equipment Failure/Involved | Underground | 2808 | 820625 | 35.3194 | -119.1292 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0085035 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954882 | 0 | Non-EPSS | N | 2024 | A-B / RCL LO
KERN | KERN | KERN OIL-1106 | 252721106 | JUMPER | FLYERS @ 516990170419 | 20240708 | 422 | 20240708 | 616 | 2509734 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1368 | 35.4308 | -119.0108 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0085050 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954899 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-1104 | 252771104 | FUSE | 13678 | 20240708 | 955 | 20240708 | 1001 | 2510143 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 25 | 150 | 35.3783 | -118.9069 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Normal | 24-0084947 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955020 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2102 | 253142102 | RECLOSER | 3542 | 20240708 | 959 | 20240708 | 1026 | 2509862 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 124 | 3348 | 34.8716 | -119.4938 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0085147 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955012 | 0 | EPSS Ckt | Y | 2024 | C
KERN | KERN | CUYAMA-2102 | 253142102 | TRANSFORMER | 515590248581 | 20240708 | 1331 | 20240709 | 130 | 2510434 | 719 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 719 | 34.8266 | -119.4711 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0085239 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955072 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1104 | 253701104 | TRANSFORMER | 516935968528 | 20240708 | 1536 | 20240708 | 1614 | 2510561 | 38 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 342 | 35.3787 | -119.0288 | No | Clear-Heat Wave;Above 90 |  |  | 24-0085321 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1955088 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1111 | 253701111 | TRANSFORMER | 516884067863 | 20240708 | 1818 | 20240708 | 1906 | 2510726 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 144 | 35.3602 | -119.0459 | No | Clear-Heat Wave;Above 90 | Fuse | Burned Open | 24-0085363 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955107 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | FUSE | 2175 | 20240708 | 1823 | 20240708 | 2145 | 2510725 | 62 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 2 | 132 | 35.4098 | -118.9675 | No | Clear-Heat Wave;Above 90 | Fuse | Failed/Faulted | 24-0085374 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1955115 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 52609 | 20240708 | 1856 | 20240708 | 1910 | 2510687 | 14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 336 | 35.3204 | -118.9144 | No | Clear;32-90 F | Secondary | Burned Open | 24-0085369 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955111 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1103 | 252721103 | TRANSFORMER | 516966370602 | 20240708 | 1955 | 20240709 | 358 | 2510832 | 483 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4830 | 35.4356 | -119.0187 | No | Clear;Above 90 | Transformer | Leaking | 24-0085387 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955122 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T13418 TWD T13419 | 20240708 | 2054 | 20240708 | 2256 | 2510900 | 122 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 732 | 35.3964 | -119.1793 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0085355 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955120 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1104 | 252771104 | TRANSFORMER | T6419 | 20240708 | 2349 | 20240709 | 458 | 2511027 | 309 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 3261 | 35.3811 | -118.915 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0085440 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955167 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | RECLOSER | 4035 | 20240709 | 344 | 20240709 | 431 | 2511109 | 47 | Distribution Circuit | Equipment Failure/Involved | Underground | 463 | 21712 | 35.3401 | -119.0609 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0085448 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955175 | 0 | Non-EPSS | N | 2024 | B GRD
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 55553 | 20240709 | 1053 | 20240709 | 1116 | 2511474 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 475 | 35.325 | -119.0175 | No | Clear-Heat Wave;Above 90 | Capacitor | Failed/Faulted | 24-0085663 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955332 | 1 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 16922 | 20240709 | 1300 | 20240709 | 2139 | 2511588 | 519 | Distribution Circuit | 3rd Party | Vehicle | 6 | 3114 | 35.4419 | -119.3104 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Broken- wire on ground | 24-0085752 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | Yes | No | 1955359 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517070965421 | 20240709 | 1929 | 20240709 | 2050 | 2511865 | 81 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 81 | 35.2937 | -118.9825 | No | Clear;32-90 F |  |  | 24-0085843 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1955397 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1108 | 252721108 | TRANSFORMER | 516908171154 | 20240709 | 1957 | 20240710 | 205 | 2511917 | 368 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1840 | 35.4508 | -119.0384 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0085844 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955398 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7457 | 20240709 | 2104 | 20240709 | 2243 | 2511946 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 594 | 35.4799 | -119.5648 | No | Clear;Above 90 |  |  | 24-0085888 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955444 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1106 | 252931106 | SWITCH | 78399 | 20240709 | 2325 | 20240710 | 350 | 2512004 | 265 | Distribution Circuit | 3rd Party | Vehicle | 13 | 3445 | 35.0192 | -118.9541 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0085833 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955445 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | OCB | 1103/2 | 20240709 | 2328 | 20240710 | 345 | s1979521 | 257 | Distribution Circuit | 3rd Party | Vehicle | 36 | 9252 | 35.0198 | -118.9548 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0085833 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1979521 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | STOCKDALE-2110 | 254072110 | SWITCH | 6561 | 20240710 | 201 | 20240710 | 210 | 2512030 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 234 | 2106 | 35.3468 | -119.0594 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0085448 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955451 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1105 | 253551105 | JUMPER | POS 1 JMPR OPEN 1 N OF 7415 | 20240710 | 447 | 20240710 | 831 | 2512064 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 672 | 35.7617 | -119.4369 | No | Clear;32-90 F | Jumper | Burned Open | 24-0085904 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1955473 | 1 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7285 | 20240710 | 1111 | 20240710 | 1836 | 2512424 | 445 | Distribution Circuit | 3rd Party | Vehicle | 12 | 5340 | 35.4569 | -119.4382 | No | Clear;Above 90 | Anchor or Guy | Broken | 24-0086386 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955676 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | JUMPER | WIRE DOWN HOT @366725 | 20240710 | 1111 | 20240710 | 2138 | 2512446 | 627 | Distribution Circuit | 3rd Party | Vehicle | 9 | 4919 | 35.3258 | -119.349 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 24-0086168 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | Yes | 1955631 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1105 | 252771105 | TRANSFORMER | 517191268259 | 20240710 | 1323 | 20240710 | 1952 | 2512583 | 389 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 5057 | 35.3723 | -118.9425 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0086236 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955641 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 14824 | 20240710 | 1521 | 20240710 | 1622 | 2512693 | 61 | Distribution Circuit | Animal | Bird found | 88 | 5368 | 35.3853 | -118.999 | No | Clear;Above 90 | Transformer (OH) | Normal | 24-0086354 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955668 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1104 | 253701104 | TRANSFORMER | 516934568765 | 20240710 | 1532 | 20240710 | 2122 | 2512663 | 350 | Transformer only | Vegetation | Tree - branch fell on line | 9 | 3150 | 35.3849 | -119.0293 | No | Clear;Above 90 | Secondary | Broken | 24-0086320 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955658 | 0 | Non-EPSS | N | 2024
KERN | KERN | SISQUOC-1102 | 182811102 | TRANSFORMER | 514209561370 | 20240710 | 1547 | 20240711 | 308 | 2512710 | 681 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 681 | 35.1706 | -119.9384 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 24-0086431 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955704 | 0 | EPSS Ckt | N | 2024
KERN | KERN | OLD RIVER-1101 | 252821101 | TRANSFORMER | 516685462359 | 20240710 | 1913 | 20240710 | 2222 | 2512858 | 189 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 378 | 35.2087 | -119.11 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0086396 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955682 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1105 | 253371105 | TRANSFORMER | T32155 | 20240711 | 858 | 20240711 | 1139 | 2513172 | 161 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 161 | 35.3853 | -119.014 | No | Heat Wave-Clear;Above 90 | Other | Broken- wire on ground | 24-0086582 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1955850 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1104 | 253141104 | OCB | 1104/2 | 20240711 | 1241 | 20240711 | 1536 | 2513780 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 7700 | 34.9276 | -119.6203 | No | Clear-Heat Wave;Above 90 |  |  | 24-0086744 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955960 | 0 | EPSS Ckt | N | 2024 | -GRD INST OC
KERN | KERN | STOCKDALE-2111 | 254072111 | OCB | 2200/2 | 20240711 | 1403 | 20240711 | 1713 | 2513887 | 190 | Distribution Circuit | Equipment Failure/Involved | Underground | 4245 | 436311 | 35.3165 | -119.0679 | No | Clear-Heat Wave;Above 90 | Connector or Splice (UG) | Failed/Faulted | 24-0086799 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955972 | 0 | Non-EPSS | N | 2024 | B-GRD TIME OC
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13494 | 20240711 | 1629 | 20240712 | 20 | 2514096 | 471 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 44 | 6001 | 35.3686 | -118.9805 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0086898 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956004 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1108 | 252771108 | TRANSFORMER | 517321268189 | 20240711 | 1732 | 20240711 | 1929 | 2514176 | 117 | Transformer only | Environmental/External | Fire- Forest/Grass | 2 | 234 | 35.3705 | -118.8986 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Burned/flashed | 24-0086942 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956029 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | TRANSFORMER | 516928767217 | 20240711 | 1927 | 20240712 | 212 | s1979563 | 405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3240 | 35.3426 | -119.0305 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0086944 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1979563 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 69452 | 20240711 | 1935 | 20240711 | 2116 | 2514335 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3434 | 35.3647 | -119.0923 | No | Clear-Heat Wave;Above 90 |  |  | 24-0086981 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956057 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1108 | 253701108 | FUSE | 14123 | 20240711 | 2012 | 20240712 | 650 | 2514428 | 638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 76273 | 35.3466 | -119.0182 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0086997 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956070 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1103 | 252081103 | OCB | 1103/2 | 20240711 | 2021 | 20240712 | 11 | 2514378 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2300 | 35.1363 | -119.4822 | No | Clear;Above 90 | Transformer (OH) | Leaking | 24-0086969 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956046 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | STOCKDALE-2111 | 254072111 | SWITCH | 6108 | 20240711 | 2049 | 20240711 | 2102 | 2514375 | 13 | Distribution Circuit | Equipment Failure/Involved | Underground | 148 | 1924 | 35.3317 | -119.06 | No | Clear-Heat Wave;Above 90 | Connector or Splice (UG) | Failed/Faulted | 24-0086799 | UG | Sus | 35563091 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956054 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRIP-SAVER | 3527 | 20240711 | 2200 | 20240712 | 310 | 2514494 | 310 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 212 | 56108 | 35.3482 | -120.0054 | No | Clear;32-90 F |  |  | 24-0087045 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956114 | 1 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 15370 | 20240711 | 2209 | 20240712 | 212 | 2514218 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 3093 | 35.3436 | -119.0344 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0086944 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956031 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1103 | 252611103 | SWITCH | 1129 | 20240712 | 358 | 20240712 | 1121 | 2514669 | 443 | Distribution Circuit | 3rd Party | Vehicle | 46 | 10673 | 35.4409 | -119.4292 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0087059 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956128 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | 516236373113 | 20240712 | 705 | 20240712 | 1803 | 2514721 | 658 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3948 | 35.5022 | -119.2655 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 24-0087117 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1956204 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | 516236373088 | 20240712 | 757 | 20240712 | 1803 | 2514709 | 606 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 6060 | 35.5015 | -119.2655 | No | Partly Cloudy;32-90 F | Other | Broken- wire on ground | 24-0087116 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1956201 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | FUSE | 18395 | 20240712 | 817 | 20240712 | 1255 | 2514774 | 278 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 742 | 35.4134 | -119.3765 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0087148 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956235 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 8575 | 20240712 | 830 | 20240712 | 918 | 2514787 | 48 | Distribution Circuit | Company Initiated | Return Circuit Normal | 148 | 5696 | 35.3329 | -119.0567 | No | Partly Cloudy-Heat Wave;Above 90 | Conductor- Underground | Normal | 24-0086799 | UG | Sus | 35563091 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956180 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | SWITCH | 1430 | 20240712 | 1138 | 20240712 | 1149 | 2515040 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 15 | 165 | 35.4409 | -119.3845 | No | Partly Cloudy-Heat Wave;Above 90 | Pole-Wood | Normal | 24-0087059 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956271 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2101 | 255322101 | TRANSFORMER | 516508564288 | 20240712 | 1500 | 20240712 | 1634 | 2515266 | 94 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 94 | 35.2602 | -119.1707 | No | Clear;32-90 F |  |  | 24-0087382 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956326 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | OTHER | T8500 TWD T8501 | 20240712 | 1935 | 20240712 | 2058 | 2515600 | 83 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 6142 | 35.3993 | -119.1312 | No | Partly Cloudy;Above 90 | Transformer (UG) | Leaking | 24-0087281 | UG | Sus | 35564805 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956351 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | 516550269065 | 20240713 | 748 | 20240713 | 842 | 2515820 | 54 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 108 | 35.3927 | -119.1576 | No | Partly Cloudy;32-90 F |  |  | 24-0087493 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956439 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 8939 | 20240713 | 1045 | 20240713 | 1230 | 2515935 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1575 | 35.3636 | -118.9653 | No | Clear;Above 90 |  |  | 24-0087549 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956477 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | JUMPER | OPEN JUMPERS 2 N/OF 516908467622 | 20240713 | 1300 | 20240713 | 1545 | 2515846 | 165 | Distribution Circuit | 3rd Party | Vehicle | 9 | 1485 | 35.354 | -119.0373 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0087553 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956479 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | FUSE | 372119 | 20240713 | 1324 | 20240719 | 1422 | 2516043 | 8698 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20007 | 35.2282 | -119.6721 | No | Partly Cloudy;Above 90 | Pole-Wood | Burned/flashed | 24-0087561 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956483 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 57521 | 20240713 | 1509 | 20240713 | 1542 | 2516165 | 33 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 99 | 35.4424 | -119.4839 | No | Partly Cloudy;Above 90 |  |  | 24-0087593 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956502 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1110 | 252901110 | SWITCH | 11596 | 20240713 | 1608 | 20240713 | 2130 | 2516155 | 322 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 379 | 35.5943 | -119.3516 | No | Partly Cloudy;Above 90 | Transformer (UG) | Leaking | 24-0087540 | UG | Sus | 35564805 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956498 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRANSFORMER | 514442265515 | 20240713 | 1648 | 20240713 | 2320 | 2516168 | 392 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 392 | 35.2847 | -119.8673 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 24-0087608 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956515 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | 516550269065 | 20240713 | 1918 | 20240713 | 1958 | 2516254 | 40 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 80 | 35.3927 | -119.1576 | No | Clear;Above 90 |  |  | 24-0087613 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956520 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | T11741 | 20240713 | 1926 | 20240713 | 2206 | 2516259 | 160 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 1120 | 35.3784 | -119.1709 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0087614 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956521 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1108 | 253701108 | TRANSFORMER | 516925867511 | 20240713 | 1946 | 20240714 | 122 | 2516271 | 336 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 2016 | 35.3508 | -119.0317 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0087621 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956534 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517093068579 | 20240714 | 153 | 20240714 | 328 | 2516414 | 95 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 100 | 2860 | 35.3812 | -118.9757 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0087658 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956569 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1105 | 252931105 | RECLOSER | 95130 | 20240714 | 720 | 20240714 | 1719 | 2516533 | 599 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 4650 | 35.0307 | -118.934 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0087688 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956597 | 0 | Non-EPSS | N | 2024 | BC TIME OC
KERN | KERN | ELK HILLS-1104 | 252441104 | RECLOSER | 4306 | 20240714 | 1405 | 20240714 | 1531 | 2516705 | 86 | Distribution Circuit | 3rd Party | Vehicle | 241 | 20246 | 35.2282 | -119.3774 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0087718 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956639 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | MAGUNDEN-2108 | 252772108 | RECLOSER | 1267 | 20240714 | 1702 | 20240717 | 2154 | 2516755 | 4612 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 16 | 4732 | 35.3539 | -118.9586 | No | Clear;Above 90 | Pole-Wood | Burned/flashed | 24-0087741 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956652 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | LERDO-1115 | 253491115 | OCB | 1115/2 | 20240714 | 1916 | 20240714 | 2016 | 2516801 | 60 | Distribution Circuit | 3rd Party | Vehicle | 16 | 960 | 35.5004 | -119.1519 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0087747 | OH | Sus | 35564804 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956667 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | MARICOPA-1101 | 254211101 | FUSE | 18477 | 20240714 | 1923 | 20240714 | 2129 | 2516804 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 840 | 35.0616 | -119.3491 | No | Clear;Above 90 |  |  | 24-0087764 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956674 | 1 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | INTERRUPTER | 4022 | 20240714 | 1953 | 20240715 | 145 | 2516814 | 352 | Distribution Circuit | Equipment Failure/Involved | Underground | 259 | 44076 | 35.3213 | -119.0682 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0087763 | UG | Sus | 35564805 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1956671 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | FUSE | 7267 | 20240715 | 102 | 20240715 | 1043 | 2516878 | 581 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 1162 | 35.6446 | -119.7142 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0087803 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956711 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1108 | 252721108 | FUSE | 15242 | 20240715 | 307 | 20240715 | 918 | 2516888 | 371 | Distribution Circuit | Equipment Failure/Involved | Underground | 185 | 60449 | 35.4436 | -119.0236 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0087820 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956725 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1106 | 252901106 | OCB | 1106/2 | 20240715 | 829 | 20240715 | 900 | 2517036 | 31 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 113 | 3503 | 35.6006 | -119.4374 | No | Clear;32-90 F |  |  | 24-0087871 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956794 | 0 | Non-EPSS | N | 2024 | A- B- 50RLY- SET-A RLY
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 69452 | 20240715 | 831 | 20240715 | 1010 | 2517023 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3366 | 35.3647 | -119.0923 | No | Clear;32-90 F |  |  | 24-0087903 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956851 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1106 | 252901106 | FUSE | 15172 | 20240715 | 919 | 20240715 | 1040 | 2517140 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 162 | 35.5613 | -119.4229 | No | Clear;32-90 F |  |  | 24-0087947 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956874 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1106 | 252901106 | TRANSFORMER | 515695474337 | 20240715 | 1118 | 20240715 | 1240 | 2517139 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 82 | 35.5342 | -119.4479 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0088003 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956898 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517241865617 | 20240715 | 1406 | 20240715 | 1500 | 2517503 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 54 | 35.2996 | -118.9255 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0088112 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956933 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1110 | 253701110 | RECLOSER | 4871 | 20240715 | 1442 | 20240715 | 2253 | 2517533 | 491 | Distribution Circuit | 3rd Party | Vehicle | 1033 | 29653 | 35.3635 | -119.0182 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0088072 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956935 | 0 | Non-EPSS | N | 2024 | NA
KERN | KERN | FRUITVALE-1104 | 253391104 | FUSE | 9690 | 20240715 | 1944 | 20240715 | 2049 | 2517725 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 303 | 35.4271 | -119.0794 | No | Clear;Above 90 |  |  | 24-0088221 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956972 | 1 | Non-EPSS | N | 2024
KERN | KERN | MARICOPA-1101 | 254211101 | FUSE | 18477 | 20240715 | 1944 | 20240715 | 2300 | 2517726 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1307 | 35.0616 | -119.3491 | No | Partly Cloudy;Above 90 |  |  | 24-0088248 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956997 | 1 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | OTHER | T12315 TWD T12316 | 20240716 | 46 | 20240716 | 202 | 2517790 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 2128 | 35.3454 | -118.9281 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0088144 | UG | Sus | 35566392 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957003 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1102 | 252021102 | FUSE | 7059 | 20240716 | 205 | 20240716 | 518 | 2517817 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 772 | 35.6609 | -119.9389 | No | Clear;32-90 F |  |  | 24-0088257 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957015 | 1 | EPSS Ckt | N | 2024
KERN | KERN | FRUITVALE-1104 | 253391104 | FUSE | 9690 | 20240716 | 534 | 20240716 | 836 | 2517873 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 850 | 35.4271 | -119.0794 | No | Clear;32-90 F |  |  | 24-0088334 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957111 | 1 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 8694 | 20240716 | 1039 | 20240716 | 1047 | 2518165 | 8 | Distribution Circuit | Animal | Bird found | 6 | 48 | 35.2236 | -119.2072 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088407 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957188 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | OCB | 1109/2 | 20240716 | 1501 | 20240717 | 505 | 2518431 | 844 | Distribution Circuit | Equipment Failure/Involved | Underground | 1939 | 276721 | 35.4407 | -119.0203 | No | Clear;Above 90 | Elbow | Burned/flashed | 24-0088576 | UG | Sus | 46280574 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957246 | 0 | Non-EPSS | N | 2024 | BG
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517207268013 | 20240716 | 1713 | 20240717 | 424 | 2518471 | 671 | Transformer only | Company Initiated | Improper Construction | 15 | 10065 | 35.3656 | -118.9371 | No | Clear;Above 90 | Connector or Splice (OH) | Burned/flashed | 24-0088634 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957260 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 16239 | 20240717 | 603 | 20240717 | 800 | 2519041 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1872 | 35.4269 | -119.5374 | No | Clear;32-90 F |  |  | 24-0088754 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1957377 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517027168386 | 20240717 | 1441 | 20240717 | 1923 | 2519659 | 282 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 5640 | 35.3752 | -118.9977 | No | Clear;Above 90 | Secondary | Broken- wire on ground | 24-0089041 | OH | Sus | 31701364 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957540 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1105 | 253371105 | FUSE | 460087 | 20240718 | 657 | 20240718 | 850 | 2520008 | 113 | Distribution Circuit | Animal | Bird found | 19 | 2147 | 35.3821 | -119.0217 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0089196 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1957639 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1108 | 254071108 | FUSE | 8098 | 20240718 | 713 | 20240718 | 806 | 2520015 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 901 | 35.3353 | -119.0511 | No | Clear;32-90 F |  |  | 24-0089174 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957623 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517200266375 | 20240718 | 1141 | 20240718 | 1651 | 2520224 | 310 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 620 | 35.3202 | -118.9388 | No | Clear;32-90 F |  |  | 24-0089334 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1957699 | 0 | Non-EPSS | N | 2024
KERN | KERN | MARICOPA-1101 | 254211101 | FUSE | 18477 | 20240718 | 2021 | 20240718 | 2204 | 2520545 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 687 | 35.0616 | -119.3491 | No | Clear;Above 90 |  |  | 24-0089542 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957775 | 1 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-1105 | 254071105 | OTHER | T8293 TWD T8294 | 20240718 | 2042 | 20240718 | 2155 | 2520547 | 73 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 1460 | 35.2954 | -119.0447 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0089514 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957754 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2112 | 254072112 | SWITCH | 4650 | 20240719 | 144 | 20240719 | 1128 | 2520720 | 584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 623 | 99746 | 35.3051 | -119.0746 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0089484 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957787 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1108 | 253391108 | OCB | 1108/2 | 20240719 | 255 | 20240719 | 321 | 2520734 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 283 | 7358 | 35.3777 | -119.0926 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 24-0089559 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957790 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | MARICOPA-1101 | 254211101 | FUSE | 18477 | 20240719 | 1953 | 20240719 | 2105 | 2521439 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 480 | 35.0616 | -119.3491 | No | Clear;Above 90 |  |  | 24-0089931 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958028 | 1 | EPSS Ckt | N | 2024
KERN | KERN | 7TH STANDARD-2103 | 254582103 | FUSE | 884021 | 20240720 | 38 | 20240720 | 210 | 2521539 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1471 | 35.4294 | -119.1099 | No | Clear;32-90 F |  |  | 24-0089958 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958046 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | RECLOSER | 4409 | 20240720 | 324 | 20240720 | 1545 | 2521555 | 741 | Distribution Circuit | 3rd Party | Vehicle | 114 | 15030 | 35.2807 | -118.8786 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0089962 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1958052 | 0 | EPSS Ckt | N | 2024 | C GRD
KERN | KERN | COLUMBUS-1105 | 253951105 | FUSE | 3134 | 20240720 | 431 | 20240720 | 1747 | 2521559 | 796 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 23635 | 35.4119 | -118.9588 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0089977 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958066 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1108 | 252771108 | JUMPER | FLYERS 3 SPAN S/OF CGC# 517321268189 | 20240720 | 808 | 20240720 | 1004 | 2521615 | 116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 232 | 35.3694 | -118.8986 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0089985 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958077 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1101 | 253371101 | FUSE | 14345 | 20240720 | 811 | 20240720 | 1400 | 2521617 | 349 | Distribution Circuit | 3rd Party | Vehicle | 31 | 10819 | 35.3974 | -118.9971 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0090013 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958105 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1113 | 253491113 | RECLOSER | 3661 | 20240720 | 811 | 20240721 | 416 | 2521619 | 1205 | Distribution Circuit | 3rd Party | Vehicle | 161 | 22377 | 35.5134 | -119.1796 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0089987 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1958080 | 0 | Non-EPSS | N | 2024 | B & GRD
KERN | KERN | STOCKDALE-2112 | 254072112 | RECLOSER | 1466 | 20240720 | 1704 | 20240721 | 1408 | 2521943 | 1264 | Distribution Circuit | 3rd Party | Vehicle | 4487 | 932683 | 35.2878 | -119.0745 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0090074 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1958152 | 0 | Non-EPSS | N | 2024 | A B & GRD
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 11616 | 20240720 | 2020 | 20240721 | 811 | 2522103 | 711 | Distribution Circuit | Equipment Failure/Involved | Underground | 64 | 20318 | 35.3485 | -119.0924 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0090092 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958168 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1109 | 253951109 | RECLOSER | 3953 | 20240721 | 108 | 20240721 | 149 | 2522233 | 41 | Distribution Circuit | Equipment Failure/Involved | Underground | 1017 | 41697 | 35.3979 | -118.9295 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0090124 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1958200 | 0 | Non-EPSS | N | 2024 | B C GRD
KERN | KERN | COLUMBUS-1109 | 253951109 | TRANSFORMER | T3118 | 20240721 | 526 | 20240721 | 1635 | 2522307 | 669 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 6772 | 35.404 | -118.9236 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0090139 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958217 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 8079 | 20240721 | 1006 | 20240721 | 1206 | 2522375 | 120 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 2368 | 35.3105 | -119.0208 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0090163 | UG | Sus | 31701553 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958235 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1105 | 253911105 | FUSE | 16992 | 20240721 | 1302 | 20240721 | 1343 | 2522466 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 123 | 35.2892 | -118.8246 | No | Clear;Above 90 | Crossarm- Wood | Deteriorated | 24-0090179 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958248 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15063 | 20240721 | 1541 | 20240721 | 1639 | 2522512 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 1934 | 35.3507 | -118.9133 | No | Clear;Above 90 |  |  | 24-0090205 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958273 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 17182 | 20240721 | 1933 | 20240722 | 305 | 2522661 | 452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1808 | 35.316 | -119.0215 | No | Clear;Above 90 | Lightning Arrestor | Burned/flashed | 24-0090226 | OH | Sus | 31701528 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958287 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1106 | 253701106 | TRANSFORMER | 516932368424 | 20240721 | 2158 | 20240722 | 500 | 2522703 | 422 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 7596 | 35.3758 | -119.0299 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0090234 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958297 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 13787 | 20240722 | 804 | 20240722 | 1029 | 2522866 | 145 | Distribution Circuit | Animal | Bird found | 2 | 290 | 35.0926 | -118.9439 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0090383 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1958472 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | JUMPER | OJ 1 W/OF CGC 516947167830 | 20240722 | 822 | 20240722 | 1054 | 2522888 | 152 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1520 | 35.3594 | -119.0248 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0090296 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958365 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1104 | 253951104 | FUSE | 18997 | 20240722 | 952 | 20240722 | 1440 | 2522725 | 288 | Distribution Circuit | 3rd Party | Vehicle | 97 | 27666 | 35.3832 | -118.9586 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0090302 | OH | Sus | 35567571 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958448 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | T12225 | 20240722 | 1840 | 20240722 | 2252 | 2523635 | 252 | Distribution Circuit | Equipment Failure/Involved | Underground | 78 | 4872 | 35.2801 | -119.0169 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0090657 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958549 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | OTHER | T10558 TWD T10559 | 20240722 | 1845 | 20240722 | 1934 | 2523637 | 49 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 833 | 35.4046 | -119.1125 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0090448 | UG | Sus | 35567783 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958541 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1105 | 252771105 | TRANSFORMER | 517244068414 | 20240722 | 1917 | 20240722 | 1943 | 2523655 | 26 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 156 | 35.3767 | -118.9247 | No | Clear;Above 90 |  |  | 24-0090653 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1958546 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | JUMPER | 16229 | 20240723 | 512 | 20240723 | 1200 | 2523861 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 9859 | 35.3616 | -119.1814 | No | Clear;32-90 F | Jumper | Burned Open | 24-0090734 | OH | Sus | 46283052 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1958622 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 8069 | 20240723 | 1820 | 20240724 | 332 | 2524722 | 552 | Distribution Circuit | Equipment Failure/Involved | Underground | 130 | 24534 | 35.4159 | -119.0468 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0091138 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1958868 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | RECLOSER | 815842 | 20240723 | 1826 | 20240723 | 1933 | 2524717 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 896 | 60032 | 35.3786 | -119.1274 | No | Clear-Heat Wave;Above 90 | Regulator | Failed/Faulted | 24-0091135 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1958865 | 0 | Non-EPSS | N | 2024 | A C
KERN | KERN | BAKERSFIELD-1102 | 253371102 | TRANSFORMER | 517047169350 | 20240723 | 1830 | 20240723 | 2258 | 2524720 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 3731 | 35.4016 | -118.9913 | No | Clear-Heat Wave;Above 90 | Connector or Splice (OH) | Burned Open | 24-0091155 | OH | Sus | 46283336 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958876 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2103 | 255262103 | OCB | 2103/2 | 20240723 | 1901 | 20240724 | 551 | 2524749 | 126 | Distribution Circuit | Equipment Failure/Involved | Underground | 4197 | 283952 | 35.3785 | -119.0985 | No | Clear;Above 90 | Connector or Splice (UG) | Failed/Faulted | 24-0091148 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958871 | 0 | Non-EPSS | N | 2024 | A- GROUND
KERN | KERN | CUYAMA-1104 | 253141104 | OCB | 1104/2 | 20240723 | 2008 | 20240723 | 2208 | 2524931 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 5280 | 34.9276 | -119.6203 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 24-0091171 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958884 | 0 | EPSS Ckt | N | 2024 | PH OC GRD
KERN | KERN | FRUITVALE-1105 | 253391105 | OCB | 1105/2 | 20240724 | 200 | 20240724 | 525 | s1982634 | 205 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 205 | 35.3777 | -119.0928 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0091148 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1982634 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | FRUITVALE-1106 | 253391106 | OCB | 1106/2 | 20240724 | 202 | 20240724 | 524 | 2525116 | 202 | Distribution Circuit | Equipment Failure/Involved | Underground | 2246 | 453692 | 35.3777 | -119.0926 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0091148 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958943 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | KERN POWER-2101 | 255262101 | SWITCH | 4794 | 20240724 | 650 | 20240724 | 659 | 2525216 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 147 | 1323 | 35.3933 | -119.0921 | No | Clear;32-90 F | Connector or Splice (UG) | Normal | 24-0091148 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958958 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 13881 | 20240724 | 942 | 20240724 | 1355 | 2525500 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 190 | 48070 | 35.2672 | -118.9099 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0091414 | OH | Sus | 46283887 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | Yes | No | 1959144 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 14906 | 20240724 | 1407 | 20240724 | 2045 | 2525830 | 398 | Distribution Circuit | Vegetation | Tree - grew into line | 49 | 19502 | 35.3432 | -119.0432 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Arcing | 24-0091537 | OH | Sus | 46283970 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959181 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | FUSE | 16537 | 20240724 | 1443 | 20240724 | 1557 | 2525881 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 444 | 35.343 | -118.8508 | No | Clear-Drizzle-Heat Wave;Above 90 |  |  | 24-0091602 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959199 | 1 | EPSS Ckt | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 13389 | 20240724 | 2114 | 20240725 | 315 | 2526147 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2527 | 35.1793 | -118.9679 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0091746 | OH | Sus | 46284026 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | Yes | No | 1959290 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 15368 | 20240724 | 2156 | 20240725 | 117 | 2526092 | 201 | Distribution Circuit | 3rd Party | Vehicle | 66 | 8514 | 35.3461 | -119.0345 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0091694 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959232 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | SWITCH | 1600 | 20240725 | 409 | 20240725 | 418 | 2526290 | 9 | Distribution Circuit | 3rd Party | Vandalism | 573 | 5157 | 35.3291 | -119.0029 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0091763 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959311 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | T8125 | 20240725 | 616 | 20240725 | 813 | 2526304 | 117 | Transformer only | Equipment Failure/Involved | Underground | 4 | 468 | 35.3563 | -119.1897 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0091805 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959361 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | T8125 | 20240725 | 921 | 20240725 | 2201 | 2526516 | 760 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 4359 | 35.3563 | -119.1897 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0091939 | UG | Sus | 35568737 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959492 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | 516550269065 | 20240725 | 1018 | 20240725 | 1324 | 2526601 | 186 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 372 | 35.3927 | -119.1576 | No | Clear-Heat Wave;Above 90 |  |  | 24-0092009 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1959515 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1102 | 252021102 | TRANSFORMER | 514349478610 | 20240725 | 1447 | 20240726 | 115 | 2526811 | 628 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 628 | 35.6444 | -119.9035 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0092186 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959560 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 9640 | 20240726 | 229 | 20240726 | 424 | 2527117 | 115 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 230 | 35.3843 | -119.0744 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0092229 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959618 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | 516550269065 | 20240726 | 1013 | 20240726 | 1233 | 2527445 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 280 | 35.3927 | -119.1576 | No | Clear;Above 90 | Fuse | Failed/Faulted | 24-0092456 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959792 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | RECLOSER | 384116 | 20240726 | 1453 | 20240726 | 2040 | 2527713 | 347 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 332 | 115204 | 35.3805 | -120.0405 | No | Clear;Above 90 |  |  | 24-0092555 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959820 | 0 | EPSS Ckt | Y | 2024 | AB
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 17498 | 20240726 | 1614 | 20240726 | 1731 | 2527776 | 77 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 1771 | 35.4557 | -118.9067 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0092614 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959835 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 713123 | 20240726 | 1923 | 20240727 | 1520 | 2527923 | 1197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 5985 | 35.3541 | -119.1987 | No | Clear;Above 90 | Cutout- fuse holder | Broken | 24-0092680 | OH | Sus | 46285321 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959900 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | RECLOSER | 4265 | 20240726 | 1930 | 20240726 | 2300 | 2527931 | 210 | Distribution Circuit | Equipment Failure/Involved | Underground | 1023 | 130334 | 35.3181 | -119.0826 | No | Clear;Above 90 | Switch (UG) | Failed/Faulted | 24-0092634 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959855 | 0 | Non-EPSS | N | 2024 | C & GRD
KERN | KERN | COPUS-1104 | 253871104 | TRANSFORMER | 516337557864 | 20240727 | 1222 | 20240728 | 847 | 2528316 | 1225 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1225 | 35.0838 | -119.2251 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0092762 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959992 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20240728 | 820 | 20240728 | 1129 | 2528604 | 189 | Distribution Circuit | Animal | Bird found | 33 | 6237 | 35.6271 | -118.9849 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092855 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1960079 | 0 | EPSS Ckt | Y | 2024 | A B C TIME
KERN | KERN | LAKEVIEW-1106 | 253411106 | OCB | 1106/2 | 20240728 | 1151 | 20240728 | 2244 | 2528693 | 653 | Distribution Circuit | 3rd Party | Other | 108 | 11214 | 35.0935 | -119.1012 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0092871 | OH | Sus | 31702660 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1960099 | 0 | EPSS Ckt | N | 2024 | B GRD TIME
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | 122 TWD T60962 | 20240728 | 1342 | 20240728 | 1422 | 2528708 | 40 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 680 | 35.3964 | -119.1746 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0092876 | UG | Sus | 35569261 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960102 | 0 | Non-EPSS | N | 2024
KERN | KERN | MARICOPA-1101 | 254211101 | FUSE | 18477 | 20240728 | 1948 | 20240729 | 200 | 2528790 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1777 | 35.0616 | -119.3491 | No | Clear;32-90 F | Jumper | Burned Open | 24-0092930 | OH | Sus | 46285626 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960130 | 1 | EPSS Ckt | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 17298 | 20240729 | 1928 | 20240729 | 1938 | 2529810 | 10 | Distribution Circuit | Company Initiated | Other Circuits | 103 | 1030 | 35.4153 | -119.0613 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0093429 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960417 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | FUSE | 13008 | 20240729 | 2246 | 20240730 | 324 | 2529875 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 6116 | 35.3353 | -119.0119 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0093466 | OH | Sus | 31702667 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960447 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | JUMPER | TSB @ 9815 TWD THE EAST | 20240729 | 2323 | 20240730 | 215 | 2529860 | 172 | Distribution Circuit | Company Initiated | Other Circuits | 109 | 18748 | 35.4052 | -119.0876 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093429 | OH | Sus | 41875744 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960442 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 822793 | 20240730 | 235 | 20240730 | 445 | 2529923 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1169 | 35.2413 | -119.0214 | No | Clear;32-90 F |  |  | 24-0093482 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1960465 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 8491 | 20240730 | 702 | 20240730 | 815 | 2530004 | 73 | Distribution Circuit | Animal | Squirrel | 30 | 2190 | 35.3251 | -119.0451 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0093543 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960535 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | TRANSFORMER | T2357 | 20240730 | 1202 | 20240730 | 2156 | 2530331 | 594 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 3964 | 35.3398 | -119.0767 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0093744 | UG | Sus | 35569751 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960711 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | TRANSFORMER | 516812463370 | 20240730 | 2007 | 20240731 | 632 | 2530659 | 625 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1875 | 35.2367 | -119.0686 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0093960 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960782 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | OTHER | T13840 TWD T13841 | 20240731 | 841 | 20240731 | 1024 | 2530951 | 103 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 309 | 35.4957 | -119.2707 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0093827 | UG | Sus | 35569717 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960926 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | OTHER | T14675 TWD T14676 | 20240731 | 1235 | 20240731 | 1404 | 2531267 | 89 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 1958 | 35.4912 | -119.2743 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0094151 | UG | Sus | 35569875 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1961039 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-2103 | 252552103 | TRANSFORMER | 516161970780 | 20240731 | 1455 | 20240731 | 1654 | 2531346 | 119 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 238 | 35.4344 | -119.6249 | No | Clear;32-90 F | Transformer | Broken | 24-0094400 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1961080 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | 516335280445 | 20240801 | 1040 | 20240801 | 1340 | 2531931 | 180 | Transformer only | Animal | Bird found | 2 | 360 | 35.7043 | -119.2349 | No | Clear;Above 90 | Fuse | Broken | 24-0094759 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961327 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | JUMPER | WIRE DOWN 1 N/O CGC# 517594265750 | 20240801 | 1141 | 20240801 | 1334 | 2532024 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 411 | 35.3048 | -118.8073 | No | Clear;Above 90 | Insulator | Broken | 24-0094720 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961312 | 1 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517106768338 | 20240801 | 1427 | 20240801 | 1932 | 2532106 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 7672 | 35.3743 | -118.9708 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0094787 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961336 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1102 | 253871102 | SWITCH | 3006 | 20240801 | 2025 | 20240802 | 107 | 2532432 | 282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 564 | 35.1081 | -119.341 | No | Partly Cloudy;Above 90 | Conductor- Overhead | Normal | 24-0094815 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961385 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | 517104168349 | 20240801 | 2038 | 20240802 | 136 | 2532439 | 298 | Transformer only | Equipment Failure/Involved | Underground | 29 | 8642 | 35.3747 | -118.9716 | No | Clear;Above 90 | Service conductor | Deteriorated | 24-0094937 | UG | Sus | 46288281 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961413 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8657 | 20240802 | 43 | 20240802 | 309 | 2532530 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 121 | 17666 | 35.3531 | -119.0839 | No | Clear;32-90 F |  |  | 24-0094954 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1961441 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | OTHER | J1850 TWD T12413 | 20240802 | 219 | 20240802 | 309 | 2532541 | 50 | Distribution Circuit | Equipment Failure/Involved | Underground | 84 | 4200 | 35.3461 | -118.949 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0094621 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961438 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | OTHER | T11981 TWD T11982 | 20240802 | 332 | 20240802 | 411 | 2532549 | 39 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 702 | 35.3487 | -118.9414 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0094676 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961443 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | RECLOSER | 952122 | 20240802 | 709 | 20240802 | 1412 | 2532659 | 423 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 23595 | 34.9145 | -119.5954 | No | Clear;32-90 F |  |  | 24-0094974 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961455 | 0 | EPSS Ckt | Y | 2024 | C & GRD
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | T7242 | 20240803 | 1256 | 20240803 | 1413 | 2533696 | 77 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 308 | 35.5089 | -119.2755 | No | Clear;Above 90 |  |  | 24-0095429 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1961754 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 14024 | 20240803 | 1510 | 20240803 | 1702 | 2533779 | 112 | Distribution Circuit | Equipment Failure/Involved | Underground | 123 | 8829 | 35.2601 | -118.9176 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0095400 | UG | Sus | 35570515 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961761 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | 516266980192 | 20240804 | 749 | 20240804 | 815 | 2534106 | 26 | Transformer only | Company Initiated | Personnel- company | 4 | 104 | 35.6967 | -119.2581 | No | Clear;32-90 F |  |  | 24-0095520 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961843 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1118 | 253371118 | RECLOSER | 3338 | 20240804 | 1754 | 20240804 | 1843 | 2534315 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1134 | 55566 | 35.405 | -119.0199 | No | Partly Cloudy;Above 90 |  |  | 24-0095573 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961884 | 0 | Non-EPSS | N | 2024 | B
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 17784 | 20240804 | 1905 | 20240804 | 2007 | 2534335 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 4356 | 35.3447 | -119.0708 | No | Partly Cloudy;Above 90 |  |  | 24-0095582 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961887 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2102 | 254572102 | FUSE | 86130 | 20240804 | 2002 | 20240805 | 1200 | 2534358 | 958 | Distribution Circuit | Equipment Failure/Involved | Underground | 273 | 101121 | 35.3589 | -119.146 | No | Partly Cloudy;Above 90 | Transformer (UG) | Failed/Faulted | 24-0095598 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1961895 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 16120 | 20240804 | 2013 | 20240805 | 534 | 2534366 | 561 | Distribution Circuit | Animal | Bird found | 34 | 17218 | 35.3621 | -119.0907 | No | Clear;Above 90 | Lightning Arrestor | Burned/flashed | 24-0095627 | OH | Sus | 31703444 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1961919 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | SWITCH | 10690 | 20240805 | 118 | 20240805 | 734 | 2534386 | 376 | Distribution Circuit | Equipment Failure/Involved | Underground | 183 | 6248 | 35.3274 | -119.0658 | No | Clear;Above 90 | Secondary | Broken | 24-0095630 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961923 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1102 | 253651102 | RECLOSER | 3621 | 20240805 | 631 | 20240805 | 1154 | 2534604 | 323 | Distribution Circuit | 3rd Party | Vehicle | 100 | 8526 | 35.5153 | -119.2604 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0095645 | OH | Sus | 35570750 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | Yes | 1961938 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | SMYRNA-1106 | 253551106 | TRANSFORMER | 515971580985 | 20240805 | 735 | 20240805 | 1622 | 2534640 | 527 | Transformer only | Animal | Bird found | 1 | 527 | 35.7177 | -119.3574 | No | Clear;32-90 F | Fuse | Broken | 24-0096061 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962142 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1113 | 253491113 | FUSE | 15997 | 20240805 | 826 | 20240805 | 1131 | 2534859 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2035 | 35.5142 | -119.1802 | No | Clear;32-90 F |  |  | 24-0095845 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962079 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 19186 | 20240805 | 953 | 20240805 | 1553 | 2534832 | 360 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 360 | 35.3359 | -119.0043 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0095762 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962057 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1106 | 252901106 | OCB | 1106/2 | 20240805 | 1227 | 20240805 | 1234 | 2534996 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 116 | 812 | 35.6006 | -119.4374 | No | Clear;Above 90 |  |  | 24-0095891 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962095 | 0 | Non-EPSS | N | 2024 | B C TIME
KERN | KERN | BAKERSFIELD-2104 | 253372104 | RECLOSER | 1574 | 20240805 | 2248 | 20240806 | 32 | 2535403 | 104 | Distribution Circuit | 3rd Party | Metallic Balloon | 1202 | 94921 | 35.3444 | -119.0017 | No | Clear;32-90 F | Jumper | Burned Open | 24-0096138 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962204 | 0 | Non-EPSS | N | 2024 | B
KERN | KERN | POSO MOUNTAIN-2104 | 253642104 | RECLOSER | 48268 | 20240806 | 26 | 20240806 | 627 | 2535424 | 361 | Distribution Circuit | Animal | Other | 9 | 3249 | 35.4994 | -118.9013 | No | Clear;32-90 F | Fuse | Burned Open | 24-0096144 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962210 | 0 | EPSS Ckt | Y | 2024 | INST
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517391167327 | 20240806 | 1128 | 20240807 | 40 | 2535820 | 792 | Transformer only | Environmental/External | Fire- Forest/Grass | 10 | 7920 | 35.347 | -118.8756 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0096391 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962434 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T13913 TWD T13914 | 20240806 | 1211 | 20240806 | 1323 | 2535853 | 72 | Distribution Circuit | Equipment Failure/Involved | Underground | 51 | 3672 | 35.4132 | -119.1506 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0096301 | UG | Sus | 35571185 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962396 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | FUSE | 18559 | 20240806 | 1425 | 20240806 | 1919 | 2535958 | 294 | Distribution Circuit | 3rd Party | Vehicle | 2 | 309 | 35.2198 | -118.8423 | No | Clear;Above 90 | Bushing | Broken | 24-0096438 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962453 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517171368219 | 20240806 | 1729 | 20240806 | 1919 | 2536110 | 110 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 880 | 35.3712 | -118.9491 | No | Partly Cloudy;Above 90 |  |  | 24-0096557 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1962503 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516468058160 | 20240806 | 2110 | 20240807 | 456 | 2536290 | 466 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 466 | 35.0913 | -119.1808 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0096586 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962531 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13342 | 20240806 | 2243 | 20240806 | 2257 | 2536239 | 14 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 56 | 35.0476 | -119.0296 | No | Clear;32-90 F |  |  | 24-0096582 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962528 | 1 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | RECLOSER | 1594 | 20240807 | 35 | 20240807 | 1239 | 2536313 | 724 | Distribution Circuit | 3rd Party | Vehicle | 1248 | 385132 | 35.398 | -119.1442 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0096588 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962536 | 0 | Non-EPSS | N | 2024 | A & C
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 9616 | 20240807 | 132 | 20240807 | 702 | 2536322 | 330 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 4620 | 35.3333 | -119.0028 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0096595 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962545 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516994366289 | 20240807 | 433 | 20240807 | 1423 | 2536379 | 590 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2950 | 35.3172 | -119.0078 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0096601 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962552 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517034068418 | 20240807 | 634 | 20240807 | 1922 | 2536395 | 768 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 6912 | 35.3758 | -118.9956 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0096684 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962668 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | OTHER | T14678 TWD T14679 | 20240807 | 856 | 20240807 | 1006 | 2536540 | 70 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 1540 | 35.4903 | -119.2779 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0096556 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962645 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13387 | 20240807 | 956 | 20240807 | 1011 | 2536533 | 15 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 450 | 35.3703 | -118.9762 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0096668 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962641 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514697482234 | 20240807 | 1110 | 20240807 | 1212 | 2536698 | 62 | Transformer only | Animal | Bird found | 1 | 62 | 35.746 | -119.7876 | No | Clear;Above 90 | Fuse | Broken | 24-0096795 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962732 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | OTHER | J1507 TWD T11185 | 20240807 | 1540 | 20240807 | 1633 | 2536922 | 53 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 848 | 35.2873 | -119.0087 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0096754 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962767 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | SWITCH | 957534 | 20240807 | 1607 | 20240807 | 1709 | 2536949 | 62 | Distribution Circuit | Company Initiated | Return Circuit Normal | 711 | 43474 | 35.3981 | -119.1212 | No | Partly Cloudy;Above 90 | Pole-Wood | Normal | 24-0096588 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1962774 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20240807 | 1638 | 20240807 | 1821 | 2537000 | 103 | Distribution Circuit | 3rd Party | Customer Equipment | 33 | 1607 | 35.6271 | -118.9849 | No | Partly Cloudy;Above 90 | Customer Equipment | Broken | 24-0096948 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962782 | 0 | EPSS Ckt | Y | 2024 | A GRD INST
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | T10412 | 20240807 | 1729 | 20240808 | 19 | 2537025 | 410 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 4510 | 35.2895 | -119.0083 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0096978 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962793 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | SWITCH | 11411 | 20240807 | 1745 | 20240807 | 1800 | 2537031 | 15 | Distribution Circuit | Company Initiated | Return Circuit Normal | 67 | 1005 | 35.3941 | -119.139 | No | Partly Cloudy;Above 90 | Pole-Wood | Normal | 24-0096588 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1962788 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 16438 | 20240808 | 200 | 20240808 | 1109 | 2537261 | 549 | Distribution Circuit | Equipment Failure/Involved | Overhead | 89 | 29633 | 35.2957 | -119.0086 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0097051 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962848 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 10848 | 20240808 | 745 | 20240808 | 917 | 2537364 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1748 | 35.3332 | -119.0804 | No | Clear;32-90 F |  |  | 24-0097123 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962909 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | FUSE | 13203 | 20240808 | 844 | 20240808 | 945 | 2537458 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 3843 | 35.3786 | -119.1127 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0097126 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962919 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1106 | 253411106 | TRANSFORMER | 516726956544 | 20240808 | 1050 | 20240808 | 1205 | 2537639 | 75 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 75 | 35.0485 | -119.0941 | No | Clear;32-90 F |  |  | 24-0097248 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1963024 | 0 | EPSS Ckt | N | 2024
KERN | KERN | FAMOSO-1102 | 252461102 | OCB | 1102/2 | 20240808 | 1940 | 20240808 | 2056 | 2538296 | 76 | Distribution Circuit | 3rd Party | Vehicle | 101 | 7676 | 35.6055 | -119.2033 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0097460 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963093 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | WASCO-1102 | 252961102 | FUSE | 17388 | 20240808 | 2345 | 20240809 | 159 | 2538386 | 134 | Distribution Circuit | Equipment Failure/Involved | Underground | 67 | 8978 | 35.6055 | -119.336 | No | Clear;32-90 F | Elbow | Burned/flashed | 24-0097480 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963130 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1110 | 253701110 | FUSE | 15661 | 20240809 | 3 | 20240809 | 545 | 2538388 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 10808 | 35.3646 | -119.0148 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0097488 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963135 | 1 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1105 | 253181105 | FUSE | 18371 | 20240809 | 908 | 20240810 | 1027 | 2538614 | 47 | Distribution Circuit | 3rd Party | Vehicle | 5 | 383 | 35.7177 | -119.3208 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0097599 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | Yes | Yes | 1963258 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1108 | 254071108 | FUSE | 8251 | 20240809 | 934 | 20240809 | 1353 | 2538635 | 259 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 1414 | 35.339 | -119.0509 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0097683 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963296 | 1 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | 516337779605 | 20240809 | 1341 | 20240809 | 1654 | 2538827 | 193 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 579 | 35.6815 | -119.2338 | No | Clear;Above 90 |  |  | 24-0097874 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1963348 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 20151 | 20240809 | 1945 | 20240809 | 2134 | 2539044 | 109 | Distribution Circuit | Animal | Bird found | 9 | 945 | 35.4475 | -118.9044 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0097909 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963367 | 1 | EPSS Ckt | N | 2024
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 69452 | 20240809 | 2022 | 20240809 | 2202 | 2539061 | 100 | Distribution Circuit | Animal | Bird found | 34 | 3400 | 35.3647 | -119.0923 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0097912 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1963375 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1108 | 254071108 | SWITCH | 5936 | 20240809 | 2036 | 20240810 | 40 | 2539053 | 244 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 258 | 35.3397 | -119.0499 | No | Clear;Above 90 | Connector or Splice (UG) | Failed/Faulted | 24-0097683 | UG | Sus | 35572481 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963365 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7447 | 20240810 | 318 | 20240810 | 2245 | 2539241 | 1167 | Distribution Circuit | 3rd Party | Vandalism | 6 | 3027 | 35.6301 | -119.5817 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0097968 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1963425 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514724480770 | 20240810 | 835 | 20240810 | 2107 | 2539340 | 752 | Transformer only | Equipment Failure/Involved | Fire- pole | 1 | 752 | 35.706 | -119.7792 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0097980 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963439 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1104 | 253871104 | TRANSFORMER | 516311555749 | 20240810 | 941 | 20240810 | 1242 | 2539271 | 181 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 181 | 35.0257 | -119.2332 | No | Clear;Above 90 |  |  | 24-0097998 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1963454 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 15021 | 20240810 | 1925 | 20240811 | 803 | 2539586 | 758 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 43206 | 35.3914 | -118.9812 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0098051 | OH | Sus | 46297108 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963514 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRANSFORMER | 517078169028 | 20240811 | 1026 | 20240811 | 1041 | 2539756 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 180 | 35.3929 | -118.9812 | No | Clear;Above 90 | Secondary | Burned/flashed | 24-0098068 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963541 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | TRANSFORMER | 100000041314 | 20240812 | 738 | 20240812 | 1801 | 2540027 | 623 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 623 | 35.3762 | -119.4875 | No | Clear;32-90 F |  |  | 24-0098538 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1963824 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 1635 | 20240812 | 854 | 20240813 | 1222 | 2540218 | 1648 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 68430 | 34.9496 | -119.6931 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0098199 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1963686 | 0 | EPSS Ckt | Y | 2024 | AB
KERN | KERN | CUYAMA-1104 | 253141104 | FUSE | 2329 | 20240812 | 1224 | 20240812 | 1715 | 2540445 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1596 | 34.9274 | -119.6305 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0098513 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963817 | 1 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 10848 | 20240812 | 1242 | 20240812 | 2146 | 2540456 | 544 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 5320 | 35.3332 | -119.0804 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0098395 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963793 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517312064035 | 20240812 | 1624 | 20240813 | 413 | 2540611 | 709 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1367 | 35.256 | -118.9012 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0098518 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1963819 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1104 | 253141104 | TRANSFORMER | 515113152348 | 20240812 | 2030 | 20240812 | 2245 | 2540775 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 135 | 34.9282 | -119.6304 | No | Clear;32-90 F | Metering Equipment | Burned/flashed | 24-0098578 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963860 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-1110 | 254071110 | FUSE | 99370 | 20240813 | 533 | 20240814 | 1324 | 2540867 | 1911 | Distribution Circuit | Equipment Failure/Involved | Underground | 284 | 217137 | 35.3218 | -119.0391 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0098600 | UG | Sus | 31704485 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963880 | 1 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | FUSE | 7427 | 20240813 | 1548 | 20240814 | 403 | 2541541 | 735 | Distribution Circuit | 3rd Party | Vehicle | 10 | 7350 | 35.3838 | -119.3233 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 24-0099063 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1964140 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1109 | 253951109 | FUSE | 9466 | 20240813 | 1756 | 20240813 | 2251 | 2541526 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 5605 | 35.3872 | -118.9375 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0099059 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964139 | 0 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2104 | 254582104 | SWITCH | 41631 | 20240813 | 1900 | 20240814 | 947 | 2541569 | 887 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 887 | 35.4418 | -119.1307 | No | Clear;Above 90 | Circuit Breaker | Malfunctioning | 24-0099079 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964146 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-2102 | 254762102 | FUSE | 10884 | 20240814 | 749 | 20240814 | 1005 | 2541743 | 136 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 8100 | 35.3645 | -119.0525 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0099179 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964239 | 0 | Non-EPSS | N | 2024
KERN | KERN | ROSEDALE-2102 | 254762102 | FUSE | 10882 | 20240814 | 1016 | 20240815 | 117 | 2542000 | 901 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 15519 | 35.3632 | -119.0495 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0099179 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964358 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1104 | 253181104 | TRANSFORMER | 516192479646 | 20240814 | 1628 | 20240814 | 1744 | 2542308 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 76 | 35.6815 | -119.2832 | No | Clear;Above 90 | Connector or Splice (OH) | Broken | 24-0099494 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964440 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | JUMPER | OJS 1 S/OF CGC# 517154768090 | 20240814 | 2100 | 20240815 | 318 | 2542569 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1512 | 35.3674 | -118.9549 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0099509 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964452 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | TRANSFORMER | 15867 | 20240815 | 104 | 20240815 | 830 | 2542654 | 446 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3568 | 35.4046 | -118.9654 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0099537 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964474 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1103 | 254501103 | TRANSFORMER | 516195277795 | 20240815 | 818 | 20240815 | 1350 | 2542791 | 332 | Transformer only | 3rd Party | Vehicle | 1 | 332 | 35.6307 | -119.281 | No | Clear;32-90 F | Secondary | Broken | 24-0099589 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964513 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2103 | 255262103 | TRANSFORMER | 516775268978 | 20240815 | 1142 | 20240815 | 1152 | 2542774 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 50 | 35.3906 | -119.0826 | No | Clear;32-90 F | Jumper | Deteriorated | 24-0099608 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964535 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1106 | 253951106 | FUSE | 14390 | 20240815 | 1603 | 20240815 | 2310 | 2543120 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 27328 | 35.3978 | -118.971 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0099817 | OH | Sus | 31705225 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1964589 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | OCB | 1102/2/NORM | 20240815 | 1659 | 20240815 | 2121 | 2543162 | 262 | Distribution Circuit | Equipment Failure/Involved | Underground | 2486 | 427527 | 35.4222 | -118.9007 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0099816 | UG | Sus | 46300076 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964588 | 0 | EPSS Ckt | Y | 2024 | C GRD
KERN | KERN | CUYAMA-2101 | 253142101 | RECLOSER | 952122 | 20240815 | 1804 | 20240816 | 1108 | 2543193 | 1024 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 39712 | 34.9145 | -119.5954 | No | Clear;32-90 F |  |  | 24-0099823 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964590 | 0 | EPSS Ckt | Y | 2024 | C GRD
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 516998966897 | 20240815 | 2006 | 20240816 | 125 | 2543259 | 316 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 4108 | 35.334 | -119.0063 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0099851 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964615 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517217468004 | 20240816 | 641 | 20240816 | 1307 | 2543404 | 386 | Transformer only | 3rd Party | Fire- house or bldg. | 10 | 3860 | 35.3654 | -118.9337 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0099911 | OH | Sus | 46300286 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964705 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517220868004 | 20240816 | 641 | 20240816 | 1307 | 2543405 | 386 | Transformer only | 3rd Party | Fire- house or bldg. | 12 | 4632 | 35.3654 | -118.9326 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0099914 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964724 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | FUSE | 15962 | 20240816 | 808 | 20240816 | 1830 | 2543466 | 622 | Distribution Circuit | Animal | Other | 130 | 17000 | 35.2053 | -118.8309 | No | Clear;32-90 F | Bushing | Burned/flashed | 24-0099959 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1964783 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | TRANSFORMER | T4585 | 20240816 | 909 | 20240816 | 1531 | s1964797 | 382 | Transformer only | Equipment Failure/Involved | Underground | 1 | 382 | 35.4045 | -118.839 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0099978 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964797 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-1110 | 254071110 | SWITCH | 76374SW | 20240816 | 1038 | 20240816 | 1511 | 2543661 | 273 | Distribution Circuit | Equipment Failure/Involved | Underground | 169 | 14920 | 35.3225 | -119.0391 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0099875 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964798 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | OCB | 1102/2/NORM | 20240816 | 1716 | 20240816 | 1811 | 2543966 | 55 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2484 | 136620 | 35.4222 | -118.9007 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0100169 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964866 | 0 | EPSS Ckt | N | 2024 | NONE
KERN | KERN | KERN POWER-2102 | 255262102 | TRANSFORMER | 516751668381 | 20240816 | 2138 | 20240816 | 2220 | 2544059 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 42 | 35.369 | -119.0904 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0100199 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964887 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 20286 | 20240817 | 701 | 20240817 | 1704 | 2544158 | 603 | Distribution Circuit | Equipment Failure/Involved | Underground | 253 | 46413 | 35.4182 | -119.0615 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0100225 | UG | Sus | 46300643 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964921 | 1 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 7563 | 20240817 | 824 | 20240817 | 1227 | 2544197 | 243 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 486 | 35.3617 | -119.4744 | No | Clear;32-90 F |  |  | 24-0100276 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964983 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1111 | 254071111 | FUSE | 8491 | 20240817 | 826 | 20240817 | 1054 | 2544196 | 148 | Distribution Circuit | Animal | Squirrel | 30 | 4440 | 35.3251 | -119.0451 | No | Clear;32-90 F | Fuse | Burned Open | 24-0100253 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964965 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517070965421 | 20240817 | 1520 | 20240817 | 1624 | 2544432 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 64 | 35.2937 | -118.9825 | No | Clear;32-90 F | Fuse | Broken | 24-0100306 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965000 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | JUMPER | JMPRS 3 S/O CGC #516685768392 | 20240818 | 1331 | 20240818 | 1453 | 2544807 | 82 | Distribution Circuit | 3rd Party | Vehicle | 2 | 164 | 35.3727 | -119.1125 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0100396 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965087 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | TRANSFORMER | 516078969675 | 20240818 | 1805 | 20240818 | 1953 | 2544924 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 234 | 35.4068 | -119.3164 | No | Clear;32-90 F | Fuse | Broken | 24-0100429 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965119 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | JUMPER | WIRE DOWN 2 N/OF 15069 | 20240818 | 1842 | 20240819 | 113 | 2544909 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1564 | 35.21 | -118.8076 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0100423 | OH | Sus | 46300813 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1965115 | 1 | EPSS Ckt | N | 2024
KERN | KERN | ROSEDALE-1101 | 254761101 | TRANSFORMER | T10806 | 20240819 | 1214 | 20240819 | 1256 | 2545516 | 42 | Transformer only | Equipment Failure/Involved | Underground | 2 | 84 | 35.3952 | -119.0809 | No | Clear;32-90 F | Service conductor | Annealed | 24-0100611 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965317 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2101 | 255322101 | TRANSFORMER | 516538264641 | 20240819 | 1552 | 20240820 | 112 | 2545736 | 560 | Transformer only | Animal | Other | 1 | 560 | 35.2707 | -119.1606 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0100756 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965359 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 15690 | 20240819 | 2049 | 20240819 | 2240 | 2545946 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1443 | 35.2079 | -119.0746 | No | Clear;32-90 F |  |  | 24-0100820 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965401 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | RECLOSER | 122328 | 20240820 | 515 | 20240820 | 1253 | 2546019 | 458 | Distribution Circuit | 3rd Party | Vehicle | 114 | 35286 | 35.7029 | -119.4911 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0100840 | OH | Sus | 35575414 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965425 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 14550 | 20240820 | 1118 | 20240820 | 1258 | 2546391 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 289 | 35.1834 | -119.0746 | No | Clear;32-90 F |  |  | 24-0101056 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965633 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516675768560 | 20240820 | 2005 | 20240820 | 2103 | 2546791 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 464 | 35.3785 | -119.1163 | No | Clear;32-90 F | Secondary | Broken | 24-0101232 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965687 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | FUSE | 14550 | 20240821 | 8 | 20240821 | 200 | 2546832 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 336 | 35.1834 | -119.0746 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0101245 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965706 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8008 | 20240821 | 857 | 20240821 | 959 | 2547094 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 4960 | 35.3491 | -119.0845 | No | Clear;32-90 F |  |  | 24-0101361 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965887 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | JUMPER | OJ 4 W/OF 516854661135 | 20240821 | 1336 | 20240822 | 135 | 2547612 | 719 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 719 | 35.1723 | -119.0569 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0101689 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | Yes | No | 1965989 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13898 | 20240822 | 749 | 20240822 | 1200 | 2547827 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 251 | 35.6882 | -119.763 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0101978 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966232 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | 517295364402 | 20240822 | 822 | 20240822 | 1408 | 2547885 | 346 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 21 | 7266 | 35.2662 | -118.9068 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0101848 | OH | Sus | 31705991 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1966173 | 0 | Non-EPSS | N | 2024
KERN | KERN | MCKITTRICK-1101 | 252781101 | TRANSFORMER | 515261965863 | 20240822 | 1030 | 20240822 | 1455 | 2548052 | 265 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 265 | 35.2995 | -119.5893 | No | Clear;32-90 F |  |  | 24-0102060 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1966258 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WASCO-1102 | 252961102 | FUSE | 17403 | 20240822 | 1212 | 20240822 | 1220 | 2548135 | 8 | Distribution Circuit | Equipment Failure/Involved | Underground | 81 | 648 | 35.6069 | -119.3358 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0101933 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966209 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514845579190 | 20240823 | 608 | 20240823 | 1930 | 2548828 | 802 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 802 | 35.6636 | -119.736 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0102382 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966503 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | TRANSFORMER | T89473 | 20240823 | 736 | 20240823 | 1308 | 2548827 | 332 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 664 | 34.9113 | -119.5413 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0102278 | OH | Sus | 46303943 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966394 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | TRANSFORMER | T953 | 20240823 | 742 | 20240823 | 846 | 2548876 | 64 | Transformer only | Animal | Squirrel | 7 | 448 | 35.51 | -119.2733 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0102297 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966439 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | RECLOSER | 4169 | 20240823 | 941 | 20240823 | 1640 | 2549069 | 419 | Distribution Circuit | 3rd Party | Vehicle | 332 | 67998 | 35.2375 | -119.1008 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0102339 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1966494 | 0 | Non-EPSS | N | 2024 | A B & C
KERN | KERN | COPUS-1104 | 253871104 | TRANSFORMER | 516258556020 | 20240823 | 1006 | 20240823 | 1718 | 2549088 | 432 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 432 | 35.0327 | -119.2509 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0102481 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966551 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | JUMPER | 516815170035 | 20240823 | 1006 | 20240823 | 1025 | 2549089 | 19 | Distribution Circuit | Company Initiated | Personnel- company | 5 | 95 | 35.4196 | -119.0695 | No | Clear;32-90 F |  |  | 24-0102362 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1966498 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1106 | 252901106 | FUSE | 345149 | 20240823 | 1031 | 20240823 | 1450 | 2549114 | 259 | Distribution Circuit | 3rd Party | Vehicle | 8 | 2072 | 35.5223 | -119.43 | No | Clear;32-90 F | Insulator | Broken | 24-0102467 | OH | Sus | 31706328 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1966544 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 17224 | 20240823 | 1139 | 20240823 | 1205 | 2549172 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 138 | 3588 | 35.4175 | -119.0613 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102430 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966517 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1105 | 253181105 | TRIP-SAVER | 128091 | 20240824 | 224 | 20240824 | 415 | 2549593 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1333 | 35.7186 | -119.3118 | No | Clear;32-90 F |  |  | 24-0102680 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966613 | 1 | Non-EPSS | N | 2024 | N/A
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 951453 | 20240824 | 1042 | 20240824 | 1230 | 2550117 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 864 | 35.7402 | -119.3479 | No | Clear;32-90 F |  |  | 24-0102787 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966720 | 1 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | RECLOSER | 952122 | 20240824 | 1427 | 20240824 | 1719 | 2550257 | 172 | Distribution Circuit | Animal | Other | 74 | 12728 | 34.9145 | -119.5954 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102801 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1966735 | 0 | EPSS Ckt | Y | 2024 | A- C
KERN | KERN | SHAFTER-1103 | 253651103 | JUMPER | WIRE DOWN 2 W/OF CGC# 516095474635 | 20240824 | 1622 | 20240824 | 2230 | 2550481 | 368 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3458 | 35.5435 | -119.3128 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0102833 | OH | Sus | 31706155 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1966760 | 1 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | FUSE | 16838 | 20240826 | 30 | 20240826 | 125 | 2551056 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 1980 | 35.6946 | -119.2408 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0102963 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966913 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | 516442268265 | 20240826 | 1040 | 20240826 | 1115 | 2551451 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 35 | 35.3695 | -119.1944 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0103107 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967123 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 9600 | 20240826 | 1104 | 20240826 | 1120 | 2551478 | 16 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 96 | 1536 | 35.4197 | -119.0658 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103117 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967125 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1114 | 253371114 | FUSE | 20178 | 20240826 | 1134 | 20240826 | 1155 | 2551524 | 21 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 85 | 1785 | 35.3736 | -118.9632 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103137 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967138 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1104 | 253651104 | TRANSFORMER | 516205673075 | 20240826 | 1605 | 20240826 | 1723 | 2551829 | 78 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 936 | 35.501 | -119.2757 | No | Clear;Above 90 | Connector or Splice (OH) | Burned Open | 24-0103325 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967209 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | OCB | 1102/2 | 20240826 | 1658 | 20240827 | 1011 | 2551873 | 1033 | Distribution Circuit | 3rd Party | Vehicle | 789 | 165988 | 35.0198 | -118.9548 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0103321 | OH | Sus | 35577029 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1967205 | 0 | EPSS Ckt | N | 2024 | A- B- C 51T
KERN | KERN | TUPMAN-1103 | 254561103 | JUMPER | 13295 | 20240826 | 1746 | 20240826 | 2218 | 2551926 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 8298 | 35.4207 | -119.2341 | No | Clear;Above 90 | Jumper | Burned Open | 24-0103331 | OH | Sus | 31706613 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1967211 | 1 | Non-EPSS | N | 2024
KERN | KERN | BLACKWELL-1102 | 254681102 | JUMPER | JUMPERS 1 N/OF 7093 | 20240826 | 2008 | 20240827 | 156 | 2551997 | 348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 696 | 35.6828 | -119.8498 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0103349 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967221 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | T11459 | 20240827 | 1428 | 20240827 | 2018 | 2552807 | 350 | Distribution Circuit | Equipment Failure/Involved | Underground | 98 | 6228 | 35.2885 | -119.0061 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0103691 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967549 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1105 | 252771105 | TRANSFORMER | 517244068414 | 20240827 | 2023 | 20240827 | 2108 | 2553067 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 270 | 35.3767 | -118.9247 | No | Clear;32-90 F | Fuse | Broken | 24-0103807 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967596 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 11286 | 20240827 | 2038 | 20240828 | 1129 | 2553086 | 891 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 8052 | 35.3555 | -119.0722 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0103800 | UG | Sus | 35577380 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967589 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | JUMPER | CAR POLE @ 19349 | 20240828 | 357 | 20240829 | 130 | 2553315 | 1293 | Distribution Circuit | 3rd Party | Vehicle | 2028 | 84912 | 35.3618 | -119.0317 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0103834 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967627 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1103 | 252721103 | FUSE | 13884 | 20240828 | 806 | 20240829 | 415 | 2553608 | 1209 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 2485 | 35.4354 | -119.0155 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0103953 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967802 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | 516462769487 | 20240828 | 1532 | 20240828 | 1658 | 2554024 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 86 | 35.4035 | -119.1877 | No | Partly Cloudy;Above 90 |  |  | 24-0104372 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1967935 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1103 | 252861103 | FUSE | 20276 | 20240828 | 2054 | 20240829 | 256 | 2554357 | 362 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1810 | 35.4404 | -119.1987 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0104439 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967970 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1103 | 252721103 | TRANSFORMER | T2112 | 20240829 | 726 | 20240829 | 1049 | 2554490 | 203 | Transformer only | Company Initiated | Personnel- company | 1 | 203 | 35.4371 | -119.0141 | No | Clear;32-90 F | Transformer | On Ground | 24-0104519 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968013 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | JUMPER | OJS 1 W/OF CGC 514752080398 | 20240829 | 1904 | 20240830 | 51 | 2555368 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 347 | 35.6953 | -119.7709 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0105029 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1968296 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | RECLOSER | 1482 | 20240829 | 2316 | 20240830 | 1204 | s1968346 | 768 | Distribution Circuit | 3rd Party | Vehicle | 103 | 36215 | 35.3665 | -119.4477 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105069 | OH | Sus | 35577832 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1968346 | 1 | Non-EPSS | N | 2024 | A/GRD
KERN | KERN | SHAFTER-1103 | 253651103 | FUSE | 14567 | 20240830 | 1219 | 20240830 | 1400 | 2555960 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 202 | 35.5654 | -119.2953 | No | Clear;32-90 F |  |  | 24-0105407 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968557 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517330267520 | 20240830 | 1333 | 20240830 | 2156 | 2556005 | 503 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 503 | 35.3522 | -118.8969 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0105379 | OH | Sus | 46307343 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1968544 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1109 | 253701109 | FUSE | 12454 | 20240830 | 1629 | 20240831 | 514 | 2556129 | 765 | Distribution Circuit | 3rd Party | Vehicle | 1206 | 63839 | 35.3847 | -119.0477 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0105471 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1968572 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1112 | 252901112 | TRANSFORMER | 515565577336 | 20240831 | 856 | 20240831 | 1552 | 2556399 | 416 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 416 | 35.6165 | -119.4923 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0105577 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968645 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1105 | 253951105 | TRIP-SAVER | 4059 | 20240831 | 1226 | 20240831 | 1403 | 2556430 | 97 | Distribution Circuit | Vegetation | Tree - grew into line | 140 | 13580 | 35.4359 | -118.9498 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0105573 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1968652 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | WESTPARK-1104 | 253701104 | TRANSFORMER | 516941968388 | 20240831 | 1444 | 20240831 | 1547 | 2556561 | 63 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 441 | 35.3748 | -119.0267 | No | Clear;Above 90 | Transformer (OH) | Leaking | 24-0105599 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1968660 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 96317 | 20240901 | 659 | 20240901 | 1253 | 2557011 | 354 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1416 | 35.2983 | -118.9145 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105667 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1968710 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517000568302 | 20240901 | 1645 | 20240901 | 1733 | 2557235 | 48 | Transformer only | Animal | Other | 1 | 48 | 35.3728 | -119.0055 | No | Clear;Above 90 | Fuse | Broken | 24-0105726 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968756 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | 516335280445 | 20240901 | 1920 | 20240901 | 1954 | 2557273 | 34 | Transformer only | Animal | Bird found | 2 | 68 | 35.7043 | -119.2349 | No | Partly Cloudy;Above 90 | Fuse | Burned Open | 24-0105743 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968773 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | FUSE | 805071 | 20240902 | 450 | 20240902 | 620 | 2557446 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1440 | 35.3332 | -119.3718 | No | Clear;32-90 F |  |  | 24-0105770 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1968798 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | RECLOSER | 3776 | 20240902 | 639 | 20240903 | 202 | 2557459 | 1163 | Distribution Circuit | 3rd Party | Vehicle | 51 | 7473 | 35.1108 | -119.1095 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105771 | OH | Sus | 31707245 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1968799 | 0 | Non-EPSS | N | 2024 | A- B-C
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 17943 | 20240902 | 841 | 20240902 | 1524 | 2557514 | 403 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1209 | 35.3252 | -118.9667 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0105792 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1968811 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1115 | 253371115 | TRANSFORMER | 516980368448 | 20240902 | 1322 | 20240902 | 1540 | 2557683 | 138 | Transformer only | 3rd Party | Fire- house or bldg. | 8 | 1104 | 35.3767 | -119.0134 | No | Clear;32-90 F | Fuse | Broken | 24-0105846 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968843 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 14555 | 20240902 | 1931 | 20240902 | 2112 | 2557747 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3434 | 35.2664 | -119.0028 | No | Clear;32-90 F |  |  | 24-0105863 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1968856 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | RECLOSER | 1146 | 20240902 | 2059 | 20240903 | 803 | 2557788 | 664 | Distribution Circuit | 3rd Party | Vehicle | 878 | 82829 | 35.3676 | -119.1809 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105865 | OH | Sus | 31707270 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1968860 | 0 | Non-EPSS | N | 2024 | C- GRD
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 14978 | 20240903 | 208 | 20240903 | 339 | 2557812 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 206 | 18746 | 35.3213 | -119.0211 | No | Clear;32-90 F |  |  | 24-0105877 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1968872 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 13436 | 20240903 | 1608 | 20240903 | 1650 | 2558622 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 2520 | 35.3609 | -118.9846 | No | Clear;Above 90 |  |  | 24-0106401 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969168 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | OTHER | WIRE DOWN @ CGC 517003964419 | 20240904 | 218 | 20240904 | 825 | 2558865 | 367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3677 | 35.2652 | -119.0037 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0106451 | OH | Sus | 31707517 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | Yes | 1969205 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1104 | 252721104 | FUSE | 7347 | 20240904 | 809 | 20240904 | 935 | 2559013 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 86 | 35.4728 | -119.0471 | No | Clear;32-90 F |  |  | 24-0106518 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969268 | 1 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2107 | 254572107 | OTHER | T10250 TWD T10251 | 20240904 | 939 | 20240904 | 1056 | 2559291 | 77 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 4312 | 35.4192 | -119.1421 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0106530 | UG | Sus | 35556966 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1969414 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | TRANSFORMER | 514842779572 | 20240904 | 1101 | 20240904 | 1935 | 2559300 | 514 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 514 | 35.6737 | -119.7368 | No | Clear;Above 90 |  |  | 24-0106829 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969477 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2109 | 253372109 | RECLOSER | 4129 | 20240904 | 1245 | 20240904 | 1316 | 2559402 | 31 | Distribution Circuit | 3rd Party | Vehicle | 753 | 23343 | 35.351 | -119.0084 | No | Clear;Above 90 | Pole-Wood | Normal | 24-0106751 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969443 | 0 | Non-EPSS | N | 2024 | B GRD
KERN | KERN | LAMONT-1103 | 253911103 | JUMPER | OJS 2 S/OF CGC# 517281064198 | 20240904 | 1313 | 20240904 | 1413 | 2559411 | 60 | Distribution Circuit | 3rd Party | Gun Shot | 15 | 900 | 35.2597 | -118.9116 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0106761 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1969446 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | TRANSFORMER | 517115458016 | 20240905 | 1152 | 20240905 | 1830 | 2560268 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 398 | 35.0903 | -118.9654 | No | Clear;32-90 F | Transformer | Burned Open | 24-0107310 | OH | Sus | 46309215 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969763 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16172 | 20240905 | 1455 | 20240906 | 225 | 2560489 | 690 | Distribution Circuit | 3rd Party | Vehicle | 8 | 3110 | 35.1513 | -119.071 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0107539 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | Yes | No | 1969808 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | RECLOSER | 535428 | 20240905 | 1649 | 20240905 | 1744 | 2560563 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 220 | 35.1236 | -119.11 | No | Clear;32-90 F | Recloser | Normal | 24-0107547 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1969810 | 0 | Non-EPSS | N | 2024 | 3
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517171368219 | 20240905 | 1847 | 20240905 | 1926 | 2560633 | 39 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 312 | 35.3712 | -118.9491 | No | Clear;Above 90 |  |  | 24-0107601 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1969830 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1102 | 252961102 | FUSE | 14599 | 20240905 | 2029 | 20240905 | 2044 | 2560663 | 15 | Distribution Circuit | Company Initiated | Other Circuits | 175 | 2625 | 35.6013 | -119.3381 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0107604 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1969832 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 82045 | 20240906 | 220 | 20240906 | 631 | 2560736 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 251 | 35.349 | -119.2611 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0107647 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1969867 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 1703 | 20240906 | 707 | 20240906 | 1208 | 2560840 | 301 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 301 | 35.559 | -118.9797 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 24-0107871 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970054 | 0 | EPSS Ckt | Y | 2024 | A B
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 13450 | 20240906 | 815 | 20240906 | 1720 | 2560867 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 545 | 35.1364 | -118.9589 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0107768 | OH | Sus | 31707842 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970002 | 1 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 15067 | 20240906 | 1240 | 20240907 | 2111 | 2561240 | 1951 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 7804 | 35.2206 | -118.8062 | No | Clear;Above 90 | Pole-Wood | Burned/flashed | 24-0107942 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970080 | 0 | EPSS Ckt | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | JUMPER | OPEN CENTER PHASE JUMPER | 20240906 | 1757 | 20240906 | 2003 | 2561577 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 220 | 25880 | 35.3064 | -119.0013 | No | Clear;Above 90 | Jumper | Broken | 24-0108125 | OH | Sus | 46310311 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1970145 | 1 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 44701 | 20240906 | 1910 | 20240906 | 2237 | 2561583 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 10971 | 35.133 | -119.476 | No | Clear;Above 90 |  |  | 24-0108137 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970159 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 9049 | 20240906 | 1911 | 20240907 | 201 | 2561585 | 410 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 30184 | 35.1423 | -119.4662 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0108150 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970170 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1104 | 253951104 | TRANSFORMER | 517109468995 | 20240907 | 703 | 20240907 | 846 | 2561799 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1442 | 35.3921 | -118.9701 | No | Clear;32-90 F | Fuse | Broken | 24-0108194 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970239 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1106 | 252931106 | FUSE | 90523 | 20240907 | 847 | 20240907 | 1132 | 2561867 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 660 | 34.9945 | -118.9353 | No | Clear;32-90 F |  |  | 24-0108235 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970271 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 517014762340 | 20240907 | 959 | 20240907 | 1058 | 2561907 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 59 | 35.2086 | -118.9997 | No | Clear;32-90 F | Jumper | Broken | 24-0108229 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970267 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1108 | 253701108 | TRANSFORMER | 516934067523 | 20240907 | 1735 | 20240908 | 414 | 2562158 | 639 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 7668 | 35.3511 | -119.029 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0108302 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970315 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2105 | 254072105 | FUSE | 12029 | 20240908 | 549 | 20240908 | 657 | 2562352 | 68 | Distribution Circuit | Equipment Failure/Involved | Underground | 93 | 4410 | 35.303 | -119.061 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0108328 | UG | Sus | 35579681 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970342 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 17638 | 20240908 | 1330 | 20240908 | 1350 | 2562572 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 20 | 35.3971 | -119.1276 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0108379 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970388 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1101 | 252821101 | FUSE | 17919 | 20240909 | 153 | 20240909 | 333 | 2562922 | 100 | Distribution Circuit | 3rd Party | Vehicle | 6 | 600 | 35.1801 | -119.2182 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0108438 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1970449 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517381866260 | 20240909 | 511 | 20240909 | 1749 | 2562952 | 758 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 758 | 35.3177 | -118.8786 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0108553 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970620 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 19315 | 20240909 | 835 | 20240909 | 847 | 2563106 | 12 | Distribution Circuit | Company Initiated | Other Circuits | 93 | 1116 | 35.396 | -118.9894 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108497 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1970542 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 19314 | 20240909 | 900 | 20240909 | 912 | 2563126 | 12 | Distribution Circuit | Company Initiated | Other Circuits | 71 | 852 | 35.397 | -118.9894 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108505 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970551 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 735577 | 20240909 | 1019 | 20240909 | 1042 | 2563267 | 23 | Distribution Circuit | Company Initiated | Other Circuits | 32 | 736 | 35.3962 | -118.9837 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0108570 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970627 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14348 | 20240909 | 1100 | 20240909 | 1110 | 2563312 | 10 | Distribution Circuit | Company Initiated | Other Circuits | 84 | 840 | 35.4012 | -118.9942 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0108605 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970635 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1103 | 253871103 | SWITCH | 3564 | 20240909 | 1112 | 20240909 | 1203 | 2563405 | 51 | Distribution Circuit | Company Initiated | Return Circuit Normal | 6 | 306 | 35.1666 | -119.2358 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0108438 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970654 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | TRIP-SAVER | 76859 | 20240909 | 1153 | 20240909 | 1208 | 2563343 | 15 | Distribution Circuit | Company Initiated | Other Circuits | 46 | 690 | 35.3939 | -118.9774 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0108643 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970644 | 0 | Non-EPSS | N | 2024 | NA
KERN | KERN | BAKERSFIELD-2106 | 253372106 | RECLOSER | 3459 | 20240909 | 1229 | 20240909 | 1803 | 2563422 | 334 | Distribution Circuit | Animal | Bird found | 894 | 37230 | 35.3755 | -118.9941 | No | Clear;Above 90 | Cutout- fuse holder | Burned/flashed | 24-0108687 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970656 | 0 | Non-EPSS | N | 2024 | B & GRD
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 7119 | 20240909 | 1434 | 20240909 | 1618 | 2563592 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 416 | 35.5719 | -119.5985 | No | Clear;Above 90 |  |  | 24-0108884 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970703 | 1 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1104 | 253651104 | TRANSFORMER | 516205673075 | 20240909 | 1810 | 20240909 | 1917 | 2563799 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 804 | 35.501 | -119.2757 | No | Clear;Above 90 | Connector or Splice (OH) | Burned Open | 24-0108939 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970730 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | TRANSFORMER | 516335280445 | 20240909 | 1813 | 20240910 | 235 | 2563705 | 502 | Transformer only | Animal | Bird found | 2 | 1004 | 35.7043 | -119.2349 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0108923 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970722 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517171368219 | 20240909 | 1902 | 20240909 | 1956 | 2563840 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 432 | 35.3712 | -118.9491 | No | Clear;Above 90 | Transformer (OH) |  | 24-0108940 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970731 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 13093 | 20240909 | 2237 | 20240909 | 2359 | 2563986 | 82 | Distribution Circuit | Animal | Bird found | 7 | 574 | 35.152 | -118.9676 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108959 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970748 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2102 | 254572102 | FUSE | 17744 | 20240910 | 29 | 20240910 | 253 | 2564014 | 144 | Distribution Circuit | Equipment Failure/Involved | Underground | 51 | 6562 | 35.3799 | -119.1545 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0108963 | UG | Sus | 31708342 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970752 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2102 | 253142102 | RECLOSER | 3542 | 20240910 | 955 | 20240910 | 1148 | 2564411 | 113 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 124 | 14012 | 34.8716 | -119.4938 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109081 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970951 | 0 | EPSS Ckt | Y | 2024 | AC INST OC
KERN | KERN | KERN OIL-1104 | 252721104 | FUSE | 13348 | 20240911 | 955 | 20240911 | 1346 | 2565312 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 8547 | 35.4993 | -119.0111 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0109580 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971286 | 0 | EPSS Ckt | N | 2024
KERN | KERN | FELLOWS-2103 | 254242103 | FUSE | 16486 | 20240911 | 1402 | 20240911 | 2035 | 2565802 | 393 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1572 | 35.2189 | -119.5663 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0109897 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1971391 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-1111 | 254071111 | TRANSFORMER | 516921766945 | 20240911 | 2001 | 20240911 | 2201 | 2565966 | 120 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 1800 | 35.3351 | -119.0329 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0109954 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971423 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517290164296 | 20240912 | 800 | 20240912 | 1236 | 2566257 | 276 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 4416 | 35.2629 | -118.9087 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0110104 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971566 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517229267605 | 20240912 | 951 | 20240912 | 1325 | 2566486 | 214 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 214 | 35.3542 | -118.9297 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0106362 | OH | Sus | 35061357 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1971652 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARNERAS-1103 | 252321103 | SWITCH | 19056 | 20240912 | 1004 | 20240912 | 1147 | 2566467 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 103 | 35.4915 | -119.8591 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0110162 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971647 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | TRANSFORMER | 517121567928 | 20240912 | 1919 | 20240913 | 233 | 2566918 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2859 | 35.3627 | -118.9664 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0110512 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971730 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1105 | 253551105 | FUSE | 242715 | 20240913 | 619 | 20240913 | 1112 | 2567141 | 293 | Distribution Circuit | 3rd Party | Vehicle | 3 | 782 | 35.761 | -119.3833 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0110596 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971807 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 17485 | 20240913 | 930 | 20240913 | 1333 | 2567284 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3402 | 35.3736 | -118.9543 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0110654 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971893 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 17255 | 20240913 | 1433 | 20240913 | 2030 | 2567632 | 357 | Distribution Circuit | 3rd Party | Vehicle | 187 | 18893 | 35.2812 | -119.0027 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0110901 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972004 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | FUSE | 15063 | 20240913 | 1457 | 20240913 | 1641 | 2567650 | 104 | Distribution Circuit | 3rd Party | Other | 50 | 5200 | 35.3507 | -118.9133 | No | Clear;32-90 F | Fuse | Burned Open | 24-0110913 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972008 | 0 | Non-EPSS | N | 2024
KERN | KERN | BLACKWELL-1102 | 254681102 | FUSE | 7277 | 20240913 | 1904 | 20240913 | 2118 | 2567828 | 134 | Distribution Circuit | Animal | Bird found | 7 | 938 | 35.6729 | -119.8664 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0110952 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972027 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 8051 | 20240913 | 1954 | 20240914 | 1645 | 2567849 | 1251 | Distribution Circuit | Equipment Failure/Involved | Underground | 429 | 123210 | 35.3489 | -119.0591 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0110947 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972024 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1106 | 253911106 | TRANSFORMER | 517284464484 | 20240913 | 2153 | 20240913 | 2227 | 2567867 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 510 | 35.2684 | -118.9107 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0110954 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972029 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | J675 TWD T7956 | 20240913 | 2349 | 20240915 | 20 | 2567910 | 1471 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 16181 | 35.3554 | -119.1535 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0110962 | UG | Sus | 35581385 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972046 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | TRANSFORMER | 10057 | 20240914 | 211 | 20240914 | 1310 | 2567977 | 659 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 27670 | 35.3587 | -119.0891 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0110974 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972060 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 8902 | 20240914 | 1557 | 20240914 | 2004 | 2568363 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 3091 | 35.3252 | -118.933 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0111089 | OH | Sus | 31708871 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1972179 | 1 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1104 | 253951104 | OCB | 1104/2 | 20240915 | 153 | 20240916 | 311 | 2568484 | 1518 | Distribution Circuit | Equipment Failure/Involved | Underground | 399 | 94604 | 35.3985 | -118.9399 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0111131 | UG | Sus | 46321980 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972205 | 0 | Non-EPSS | N | 2024 | A- GRD
KERN | KERN | STOCKDALE-2115 | 254072115 | RECLOSER | 2858 | 20240915 | 201 | 20240915 | 1330 | 2568485 | 689 | Distribution Circuit | 3rd Party | Vehicle | 774 | 66053 | 35.2981 | -119.0919 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0111132 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1972206 | 0 | Non-EPSS | N | 2024 | A- B- C
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 17255 | 20240915 | 1017 | 20240915 | 1113 | 2568692 | 56 | Distribution Circuit | 3rd Party | Metallic Balloon | 187 | 10472 | 35.2812 | -119.0027 | No | Clear;32-90 F | Fuse | Burned Open | 24-0111168 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972250 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 7077 | 20240915 | 1449 | 20240915 | 1642 | 2568895 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 339 | 35.7319 | -119.7786 | No | Clear;32-90 F |  |  | 24-0111205 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972282 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | FUSE | 7509 | 20240915 | 1734 | 20240915 | 2056 | 2569121 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2222 | 35.7175 | -119.4906 | No | Clear;32-90 F |  |  | 24-0111241 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972320 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | FUSE | 815597 | 20240916 | 942 | 20240916 | 948 | 2569539 | 6 | Distribution Circuit | Animal | Other | 1 | 6 | 34.9611 | -119.667 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0111405 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972525 | 1 | EPSS Ckt | N | 2024
KERN | KERN | GOOSE LAKE-1106 | 254201106 | OCB | 1106/2 | 20240916 | 1133 | 20240916 | 1253 | 2569681 | 80 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 212 | 16960 | 35.6018 | -119.5799 | No | Clear;32-90 F | Pole-Wood | On Ground | 24-0111508 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972567 | 0 | Non-EPSS | N | 2024 | A & GRD
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 14684 | 20240916 | 2216 | 20240917 | 502 | 2570184 | 406 | Distribution Circuit | 3rd Party | Vehicle | 12 | 4872 | 35.2091 | -119.249 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0111791 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1972686 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1114 | 253371114 | FUSE | 98691 | 20240917 | 9 | 20240917 | 16 | 2570197 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 231 | 35.3743 | -118.9676 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0111794 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972690 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1110 | 253701110 | FUSE | 15098 | 20240917 | 803 | 20240917 | 1241 | 2570309 | 278 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 37530 | 35.3658 | -119.0214 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0111851 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972732 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516689778022 | 20240917 | 907 | 20240917 | 923 | 2570262 | 16 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 16 | 35.6385 | -119.1147 | No | Fog;32-90 F |  |  | 24-0111904 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1972866 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 516100269407 | 20240917 | 1528 | 20240917 | 1612 | 2570871 | 44 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 44 | 35.3998 | -119.3098 | No | Clear;32-90 F |  |  | 24-0112140 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1972974 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 14842 | 20240917 | 1538 | 20240917 | 2144 | 2570878 | 366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3294 | 35.4022 | -118.9854 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0112160 | OH | Sus | 31708898 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1972981 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2108 | 254072108 | FUSE | 11911 | 20240917 | 2016 | 20240918 | 201 | 2571061 | 345 | Distribution Circuit | Equipment Failure/Involved | Underground | 100 | 17080 | 35.3179 | -119.1082 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0112196 | UG | Sus | 35582145 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972996 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1112 | 253491112 | JUMPER | JUMPERS @ L&B POLE S/OF CGC 516846574050 | 20240918 | 1422 | 20240918 | 1645 | 2571797 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 286 | 35.5301 | -119.0606 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0112608 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1973332 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | OCB | 1103/2 | 20240918 | 2328 | 20240919 | 413 | 2572113 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1685 | 164869 | 35.3985 | -118.9399 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0112797 | OH | Sus | 46323558 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973388 | 0 | Non-EPSS | N | 2024 | A B TIME
KERN | KERN | COLUMBUS-1105 | 253951105 | SWITCH | 11127 | 20240919 | 833 | 20240919 | 902 | 2572303 | 29 | Distribution Circuit | Company Initiated | Return Circuit Normal | 60 | 1740 | 35.4061 | -118.9394 | No | Clear;32-90 F | Jumper | Normal | 24-0112797 | OH | Sus | 46323558 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1973467 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515361779093 | 20240919 | 929 | 20240919 | 936 | 2572310 | 7 | Transformer only | Animal | Bird found | 1 | 7 | 35.6633 | -119.5598 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0112921 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973511 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1109 | 253951109 | SWITCH | 11788 | 20240919 | 932 | 20240919 | 945 | 2572416 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 216 | 2808 | 35.4034 | -118.9412 | No | Clear;32-90 F | Jumper | Normal | 24-0112797 | OH | Sus | 46323558 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1973526 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1106 | 252771106 | TRANSFORMER | 517240568594 | 20240919 | 1527 | 20240920 | 15 | 2572625 | 528 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 10268 | 35.3818 | -118.926 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0113201 | OH | Sus | 31709423 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973603 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1102 | 252021102 | TRANSFORMER | 514177978962 | 20240919 | 1613 | 20240919 | 1641 | 2572656 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 35.6544 | -119.9605 | No | Partly Cloudy-Drizzle;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0113224 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973608 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 622728 | 20240919 | 1625 | 20240919 | 1852 | 2572775 | 147 | Distribution Circuit | Environmental/External | Lightning | 53 | 7791 | 35.0056 | -119.808 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0113237 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1973611 | 0 | EPSS Ckt | Y | 2024 | ABC INST
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | FUSE | 14157 | 20240919 | 1831 | 20240920 | 230 | 2572865 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 958 | 35.0949 | -119.0224 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0113293 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1973627 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | FUSE | 16838 | 20240919 | 1941 | 20240919 | 2108 | 2572907 | 87 | Distribution Circuit | Animal | Bird found | 36 | 3132 | 35.6946 | -119.2408 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0113320 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973642 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16172 | 20240919 | 2251 | 20240920 | 356 | 2572969 | 305 | Distribution Circuit | 3rd Party | Vehicle | 8 | 2440 | 35.1513 | -119.071 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0113371 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1973662 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | FUSE | 15292 | 20240920 | 914 | 20240920 | 1019 | 2573293 | 65 | Distribution Circuit | Animal | Bird found | 109 | 7085 | 35.3613 | -119.0367 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0113541 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973860 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1101 | 252461101 | TRANSFORMER | 516867778200 | 20240920 | 1205 | 20240920 | 1223 | 2573432 | 18 | Transformer only | Animal | Bird found | 1 | 18 | 35.644 | -119.0553 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0113666 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973902 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1102 | 253181102 | FUSE | 15984 | 20240921 | 955 | 20240921 | 1657 | 2574064 | 422 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 422 | 35.6884 | -119.3209 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0113998 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1974089 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-1102 | 254401102 | TRANSFORMER | 514434581965 | 20240922 | 1615 | 20240922 | 1757 | 2574629 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 204 | 35.7381 | -119.8765 | No | Clear;32-90 F | Fuse | Broken | 24-0114156 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974268 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-1106 | 252771106 | TRANSFORMER | 517181868777 | 20240922 | 1725 | 20240922 | 2238 | 2574640 | 313 | Distribution Circuit | Vegetation | Tree - grew into line | 10 | 3058 | 35.3862 | -118.9464 | No | Clear;Above 90 | Secondary | Normal | 24-0114149 | OH | Sus | 46325206 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1974260 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 8428 | 20240922 | 1930 | 20240922 | 2056 | 2574702 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 3956 | 35.3474 | -119.0738 | No | Clear;32-90 F |  |  | 24-0114164 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974277 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1110 | 252721110 | TRANSFORMER | 516914270142 | 20240923 | 930 | 20240923 | 1141 | 2575184 | 131 | Transformer only | Vegetation | Tree - grew into line | 10 | 1310 | 35.4228 | -119.0364 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0114303 | OH | Sus | 46325059 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974506 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | OCB | 2101/2 | 20240923 | 1255 | 20240923 | 1616 | 2575407 | 201 | Distribution Circuit | Animal | Bird found | 149 | 22889 | 35.5593 | -118.9574 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0114391 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974540 | 0 | EPSS Ckt | Y | 2024 | A GRD PH OC INST
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 18451 | 20240923 | 2034 | 20240923 | 2216 | 2575813 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 918 | 35.6884 | -119.5087 | No | Clear;32-90 F |  |  | 24-0114612 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974623 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | OTHER | J573 TWD T8233 | 20240923 | 2204 | 20240924 | 200 | 2575790 | 236 | Distribution Circuit | Equipment Failure/Involved | Underground | 91 | 21476 | 35.6852 | -119.2334 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0114466 | UG | Sus | 35583037 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1974618 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | RECLOSER | 90940 | 20240923 | 2231 | 20240923 | 2329 | 2575828 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2064 | 119712 | 35.2671 | -118.9006 | No | Clear;32-90 F | Regulator | Failed/Faulted | 24-0114623 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974627 | 0 | Non-EPSS | N | 2024 | A GRD SGF
KERN | KERN | RENFRO-2105 | 254572105 | OTHER | T8414 TWD J724 | 20240924 | 947 | 20240924 | 1012 | 2576272 | 25 | Distribution Circuit | 3rd Party | Vehicle | 68 | 1700 | 35.4057 | -119.1254 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0114754 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1974849 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1112 | 252901112 | FUSE | 95912 | 20240924 | 1143 | 20240924 | 1342 | 2576394 | 119 | Distribution Circuit | 3rd Party | Vehicle | 1 | 79 | 35.6387 | -119.4556 | No | Clear;Above 90 | Conductor- Overhead | Together | 24-0114943 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974927 | 1 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | FUSE | 10904 | 20240924 | 1542 | 20240925 | 527 | 2576608 | 825 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 12006 | 35.4077 | -118.9472 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0115122 | UG | Sus | 46326305 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974979 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | OTHER | T8846 TWD T8847 | 20240924 | 1937 | 20240924 | 2122 | 2576820 | 105 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 840 | 35.4896 | -119.2814 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0114942 | UG | Sus | 35583490 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1974998 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | OTHER | J895 TWD T8839 | 20240924 | 2209 | 20240925 | 43 | 2576881 | 154 | Distribution Circuit | Equipment Failure/Involved | Underground | 64 | 9856 | 35.4898 | -119.2843 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0114904 | UG | Sus | 35583486 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975013 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1101 | 252081101 | TRANSFORMER | 515661659858 | 20240925 | 504 | 20240925 | 630 | 2576952 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 172 | 35.136 | -119.4521 | No | Clear;32-90 F | Secondary | Normal | 24-0115191 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1975036 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1114 | 253371114 | FUSE | 14447 | 20240925 | 930 | 20240925 | 1000 | 2577228 | 30 | Distribution Circuit | Company Initiated | Personnel- company | 109 | 3270 | 35.385 | -118.9818 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115311 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975214 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517274365908 | 20240925 | 1314 | 20240925 | 1510 | 2577522 | 116 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 696 | 35.3076 | -118.9144 | No | Clear;32-90 F | Secondary | Normal | 24-0115617 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1975332 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1106 | 254501106 | FUSE | 129005 | 20240925 | 1922 | 20240925 | 1943 | 2577813 | 21 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 1071 | 35.5798 | -119.3377 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0115697 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975369 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 15363 | 20240926 | 3 | 20240926 | 310 | 2577874 | 187 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 6732 | 35.3584 | -119.0319 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0115735 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975386 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | TRANSFORMER | 515354762136 | 20240926 | 636 | 20240926 | 954 | 2577905 | 198 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 198 | 35.1977 | -119.5554 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0115875 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1975565 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ELK HILLS-1106 | 252441106 | SWITCH | 60836 | 20240926 | 916 | 20240926 | 2036 | 2578168 | 680 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 928 | 35.2337 | -119.2773 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0110855 | UG | Sus | 35581362 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975528 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | FUSE | 16134 | 20240926 | 1200 | 20240926 | 1432 | 2578356 | 152 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 10488 | 35.3905 | -119.1234 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0115969 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975601 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | RECLOSER | 3428 | 20240926 | 1220 | 20240927 | 510 | 2578383 | 1010 | Distribution Circuit | Equipment Failure/Involved | Underground | 228 | 33962 | 35.4212 | -118.8425 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0115995 | UG | Sus | 31710220 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1975612 | 0 | EPSS Ckt | N | 2024 | B & GRD
KERN | KERN | LAKEVIEW-1102 | 253411102 | TRANSFORMER | 516694457807 | 20240926 | 1653 | 20240926 | 1707 | 2578555 | 14 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 14 | 35.084 | -119.1058 | No | Clear;32-90 F |  |  | 24-0116224 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1975681 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | OCB | 1109/2 | 20240927 | 44 | 20240927 | 1755 | 2578925 | 1031 | Distribution Circuit | Equipment Failure/Involved | Underground | 1900 | 128729 | 35.4407 | -119.0203 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0116299 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1975736 | 0 | Non-EPSS | N | 2024 | C GRD OC
KERN | KERN | FRUITVALE-1103 | 253391103 | FUSE | 14999 | 20240927 | 928 | 20240927 | 1214 | 2579270 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 10292 | 35.3842 | -119.1358 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0116433 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975892 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRANSFORMER | 517285567349 | 20240927 | 1038 | 20240927 | 1150 | 2579427 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 72 | 35.3472 | -118.9112 | No | Clear;32-90 F | Fuse | Burned Open | 24-0116614 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1975949 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 516907064240 | 20240927 | 1516 | 20240927 | 1720 | 2579576 | 124 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 248 | 35.2606 | -119.0367 | No | Clear;32-90 F | Fuse | Burned Open | 24-0116792 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976009 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | JUMPER | FB 1 W/OF CGC 517090556977 | 20240927 | 1924 | 20240927 | 2326 | 2579685 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1424 | 35.0624 | -118.9739 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0116758 | OH | Sus | 35584210 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1976026 | 0 | EPSS Ckt | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | FUSE | 14336 | 20240928 | 214 | 20240928 | 1629 | 2579774 | 855 | Distribution Circuit | Equipment Failure/Involved | Underground | 37 | 15423 | 35.3789 | -119.1368 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0116850 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976057 | 1 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1105 | 252931105 | TRANSFORMER | 517308856639 | 20240928 | 1734 | 20240929 | 125 | 2580267 | 471 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 471 | 35.0528 | -118.8997 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0116950 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976234 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13912 | 20240929 | 947 | 20240929 | 1118 | 2580601 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 333 | 35.7015 | -119.69 | No | Clear;32-90 F |  |  | 24-0117055 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976335 | 1 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | RECLOSER | 3310 | 20240929 | 1007 | 20240929 | 1104 | 2580612 | 57 | Distribution Circuit | 3rd Party | Vehicle | 352 | 20064 | 35.2085 | -119.0417 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0117036 | OH | Sus | 46328799 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1976319 | 0 | Non-EPSS | N | 2024 | A-B-GRD
KERN | KERN | TEMBLOR-1104 | 252551104 | OCB | 1104/2 | 20240929 | 1225 | 20240929 | 1626 | 2580716 | 241 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 14016 | 35.3831 | -119.6964 | No | Clear;32-90 F |  |  | 24-0117065 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1976344 | 0 | EPSS Ckt | Y | 2024 | B-C-PH INST OC
KERN | KERN | WESTPARK-1103 | 253701103 | JUMPER | JUMPERS N/O 516924467625 | 20240929 | 1730 | 20240930 | 146 | 2580812 | 496 | Distribution Circuit | 3rd Party | Vehicle | 21 | 10416 | 35.354 | -119.0323 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0117120 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1976378 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 18561 | 20240929 | 1853 | 20240929 | 2035 | 2580840 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 510 | 35.2311 | -118.7886 | No | Clear;32-90 F |  |  | 24-0117135 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1976389 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | RECLOSER | 1668 | 20240930 | 134 | 20240930 | 1130 | 2580889 | 596 | Distribution Circuit | 3rd Party | Vehicle | 357 | 13262 | 35.2233 | -118.8423 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0117145 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1976403 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | SHAFTER-1102 | 253651102 | TRIP-SAVER | 7492 | 20240930 | 1357 | 20240930 | 1523 | 2581505 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 860 | 35.5215 | -119.2781 | No | Clear;32-90 F |  |  | 24-0117422 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976627 | 1 | Non-EPSS | N | 2024 | A
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 535138 | 20240930 | 1627 | 20241001 | 1348 | 2581632 | 1281 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 1281 | 35.6495 | -118.9809 | No | Clear;32-90 F | Customer Equipment | Burned Open | 24-0117480 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1976647 | 0 | EPSS Ckt | Y | 2024 | AC INST OC
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 9595 | 20240930 | 1709 | 20240930 | 1750 | 2581702 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 3567 | 35.3517 | -119.1544 | No | Clear;Above 90 | Connector or Splice (OH) | Deteriorated | 24-0117511 | OH | Sus | 31710452 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976659 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 14148 | 20240930 | 1741 | 20240930 | 1918 | 2581688 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 226 | 35.3706 | -119.003 | No | Clear;Above 90 | Lightning Arrestor | Burned/flashed | 24-0117529 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976667 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1104 | 252721104 | FUSE | 18443 | 20240930 | 2059 | 20241001 | 1107 | 2581767 | 848 | Distribution Circuit | Animal | Bird found | 7 | 5936 | 35.5427 | -119.0108 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117573 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976700 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRIP-SAVER | 3527 | 20240930 | 2320 | 20241001 | 423 | 2581825 | 303 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 212 | 64236 | 35.3482 | -120.0054 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0117557 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1976690 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | TEVIS-2104 | 255322104 | OTHER | T11828 TWD T11829 | 20240930 | 2337 | 20241001 | 29 | 2581828 | 52 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 2028 | 35.3407 | -119.141 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0117356 | UG | Sus | 35584446 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1976693 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 9595 | 20241001 | 158 | 20241001 | 210 | 2581867 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 1044 | 35.3517 | -119.1544 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0117575 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976702 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1103 | 254501103 | TRANSFORMER | 516337976759 | 20241001 | 946 | 20241001 | 1835 | 2582198 | 529 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 529 | 35.6023 | -119.2329 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0117874 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1976989 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1116 | 252721116 | FUSE | 12595 | 20241001 | 1302 | 20241001 | 1714 | 2582424 | 252 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 63 | 15876 | 35.4367 | -119.0688 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0117913 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977005 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1116 | 252721116 | OTHER | J1469 TWD J2294 | 20241001 | 2146 | 20241002 | 404 | 2582880 | 378 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 18 | 6804 | 35.4373 | -119.07 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0117913 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977069 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | OTHER | J1454 TWD T10981 | 20241001 | 2308 | 20241002 | 47 | 2582897 | 99 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 1881 | 35.4988 | -119.288 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0117732 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977077 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | OTHER | T11557 TWD T11558 | 20241002 | 221 | 20241002 | 322 | 2582939 | 61 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 2318 | 35.4965 | -119.289 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0117742 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977088 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1106 | 254201106 | RECLOSER | 3290 | 20241002 | 645 | 20241002 | 1153 | 2582997 | 308 | Distribution Circuit | 3rd Party | Customer Equipment | 32 | 9856 | 35.5999 | -119.545 | No | Clear;32-90 F | Customer Equipment | Broken | 24-0118124 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977103 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 16317 | 20241002 | 811 | 20241002 | 933 | 2583082 | 82 | Distribution Circuit | Animal | Bird found | 2 | 164 | 35.256 | -118.9141 | No | Clear;32-90 F | Fuse | Burned Open | 24-0118234 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977267 | 1 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | TRANSFORMER | 516408567155 | 20241002 | 932 | 20241002 | 1305 | 2583306 | 213 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 213 | 35.3396 | -119.205 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0118374 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977335 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1109 | 253951109 | FUSE | 8859 | 20241002 | 1153 | 20241002 | 1233 | 2583513 | 40 | Distribution Circuit | Animal | Bird found | 123 | 4920 | 35.3979 | -118.9277 | No | Clear;Above 90 | Fuse | Burned Open | 24-0118343 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1977319 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | OCB | 2106/2 | 20241002 | 1256 | 20241002 | 2255 | 2583574 | 599 | Distribution Circuit | 3rd Party | Vehicle | 2457 | 291774 | 35.3165 | -119.068 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0118375 | OH | Sus | 35585198 | CENTRAL VALLEY | OCT | Multi-Fault | 0 | No | No | No | 1977336 | 0 | Non-EPSS | N | 2024 | PH OC TIME
KERN | KERN | MARICOPA-1102 | 254211102 | TRANSFORMER | 515788057156 | 20241002 | 1720 | 20241002 | 1813 | 2583914 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 265 | 35.0624 | -119.4074 | No | Clear;Above 90 | Fuse | Burned Open | 24-0118612 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977391 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2109 | 254072109 | FUSE | 9305 | 20241003 | 1035 | 20241004 | 47 | 2584719 | 852 | Distribution Circuit | Equipment Failure/Involved | Underground | 51 | 33064 | 35.2961 | -119.0243 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0118910 | UG | Sus | 31710864 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977608 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | TRANSFORMER | 515684568092 | 20241003 | 1904 | 20241004 | 200 | 2585163 | 416 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1248 | 35.3621 | -119.4477 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0119237 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977698 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1112 | 253491112 | SWITCH | 1339 | 20241003 | 2130 | 20241004 | 551 | 2585100 | 501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 27054 | 35.5448 | -119.0815 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0119186 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977669 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 1858 | 20241003 | 2234 | 20241003 | 2323 | 2585305 | 49 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 1715 | 35.3785 | -118.9934 | No | Clear;32-90 F | Secondary | Broken | 24-0119267 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977727 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-1102 | 254401102 | FUSE | 7054 | 20241003 | 2355 | 20241004 | 250 | 2585308 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1200 | 35.7455 | -119.8665 | No | Clear;32-90 F |  |  | 24-0119280 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1977740 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CHARCA-1106 | 254501106 | TRANSFORMER | T91353 | 20241004 | 417 | 20241004 | 1313 | 2585618 | 536 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 536 | 35.5978 | -119.3307 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0119380 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977857 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1105 | 252771105 | TRANSFORMER | 517192868373 | 20241004 | 1644 | 20241004 | 2316 | 2586034 | 392 | Transformer only | Environmental/External | Fire- Forest/Grass | 5 | 1960 | 35.3755 | -118.942 | No | Clear;Above 90 | Service conductor | Broken- wire on ground | 24-0119691 | OH | Sus | 31711027 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977948 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | TRANSFORMER | T5288 | 20241004 | 1902 | 20241005 | 403 | 2586170 | 541 | Distribution Circuit | Equipment Failure/Involved | Underground | 86 | 10932 | 35.3591 | -119.0907 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0119708 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977973 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 1635 | 20241005 | 439 | 20241005 | 1214 | 2586531 | 455 | Distribution Circuit | 3rd Party | Vehicle | 120 | 54600 | 34.9496 | -119.6931 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0119731 | OH | Sus | 31710871 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | No | No | 1977987 | 0 | EPSS Ckt | Y | 2024 | A B & C
KERN | KERN | WASCO-1104 | 252961104 | TRANSFORMER | T27060 | 20241005 | 745 | 20241005 | 944 | 2586564 | 119 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 119 | 35.5974 | -119.3285 | No | Clear;32-90 F |  |  | 24-0119768 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1978049 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 10809 | 20241005 | 923 | 20241005 | 2124 | 2586670 | 721 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 9956 | 35.3443 | -119.0919 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0119813 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978082 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2103 | 254242103 | OCB | 2103/2 | 20241005 | 1053 | 20241005 | 1516 | 2586729 | 263 | Distribution Circuit | Equipment Failure/Involved | Overhead | 189 | 37105 | 35.1948 | -119.5861 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0119790 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978067 | 0 | EPSS Ckt | N | 2024 | GRD OC INST
KERN | KERN | FELLOWS-2104 | 254242104 | TRANSFORMER | 515346562088 | 20241005 | 1622 | 20241005 | 1821 | 2586920 | 119 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 119 | 35.1962 | -119.5585 | No | Clear;Above 90 |  |  | 24-0119875 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1978116 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ARVIN-1102 | 253801102 | FUSE | 17624 | 20241005 | 1720 | 20241005 | 2027 | 2586887 | 187 | Distribution Circuit | 3rd Party | Vehicle | 8 | 1496 | 35.1657 | -118.9148 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0119859 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1978104 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 44701 | 20241005 | 1842 | 20241005 | 2115 | 2587010 | 153 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 6092 | 35.133 | -119.476 | No | Clear;Above 90 | Connector or Splice (OH) | Deteriorated | 24-0119878 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1978119 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1101 | 252861101 | FUSE | 7153 | 20241006 | 948 | 20241006 | 1040 | 2587335 | 52 | Distribution Circuit | Animal | Squirrel | 43 | 2236 | 35.5021 | -119.2595 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0119933 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1978186 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 713123 | 20241006 | 1755 | 20241006 | 1906 | 2587645 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 355 | 35.3541 | -119.1987 | No | Clear;Above 90 |  |  | 24-0119993 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1978246 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 44701 | 20241006 | 1840 | 20241006 | 2147 | 2587783 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 7609 | 35.133 | -119.476 | No | Clear;Above 90 |  |  | 24-0120010 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1978261 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1106 | 252441106 | FUSE | 91681 | 20241006 | 1902 | 20241008 | 249 | 2587735 | 1863 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 16352 | 35.2352 | -119.2904 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0120037 | UG | Sus | 35586115 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | No | No | 1978288 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13899 | 20241006 | 1909 | 20241007 | 47 | 2587840 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2704 | 35.6697 | -119.7414 | No | Clear;32-90 F | Cutout- fuse holder | Arcing | 24-0120030 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978281 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRIP-SAVER | 3527 | 20241007 | 706 | 20241007 | 1033 | 2587964 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 141 | 29133 | 35.3482 | -120.0054 | No | Clear;32-90 F |  |  | 24-0120140 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978468 | 1 | EPSS Ckt | N | 2024 | LINE-GRD
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7097 | 20241007 | 1038 | 20241007 | 1837 | 2588385 | 479 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2395 | 35.5211 | -119.5463 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0120237 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1978526 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1106 | 254201106 | TRANSFORMER | 515193676334 | 20241007 | 1403 | 20241007 | 2255 | 2588489 | 532 | Transformer only | Animal | Other | 1 | 532 | 35.5871 | -119.6177 | No | Partly Cloudy;32-90 F | Transformer (OH) | Contaminated | 24-0120317 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978575 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 17492 | 20241007 | 1514 | 20241007 | 1615 | 2588544 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 427 | 35.3544 | -118.9361 | No | Clear;Above 90 |  |  | 24-0120381 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978601 | 0 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1103 | 253801103 | TRANSFORMER | 517298758886 | 20241007 | 1719 | 20241007 | 1738 | 2588579 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 19 | 35.1147 | -118.9048 | No | Clear;32-90 F | Metering Equipment | Broken | 24-0120409 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978617 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 713123 | 20241007 | 1733 | 20241007 | 1913 | 2588699 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 500 | 35.3541 | -119.1987 | No | Clear;Above 90 |  |  | 24-0120415 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1978621 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2102 | 255262102 | FUSE | 69452 | 20241008 | 652 | 20241008 | 803 | 2589094 | 71 | Distribution Circuit | Animal | Bird found | 11 | 804 | 35.3647 | -119.0923 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0120499 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978692 | 1 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 196480 | 20241008 | 1128 | 20241008 | 1656 | 2589538 | 328 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 624 | 34.9273 | -119.6041 | No | Clear;32-90 F |  |  | 24-0120792 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1978932 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 8923 | 20241008 | 1421 | 20241008 | 1545 | 2589721 | 84 | Distribution Circuit | Vegetation | Tree - grew into line | 22 | 1848 | 35.343 | -119.049 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0120898 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978958 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | JUMPER | OPEN JUMPERS 4 W/OF 517019567662 | 20241008 | 1440 | 20241008 | 1645 | 2589723 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 3375 | 35.3553 | -119.0014 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0120811 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1978938 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1116 | 253491116 | OCB | 1116/2 | 20241009 | 310 | 20241009 | 1332 | s1979011 | 622 | Distribution Circuit | 3rd Party | Vehicle | 150 | 23084 | 35.5004 | -119.1518 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0120966 | OH | Sus | 46333178 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1979011 | 0 | Non-EPSS | N | 2024 | A B & C
KERN | KERN | STOCKDALE-2114 | 254072114 | FUSE | 10799 | 20241009 | 1109 | 20241009 | 1401 | 2590586 | 172 | Distribution Circuit | Equipment Failure/Involved | Underground | 66 | 10018 | 35.3338 | -119.0918 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0121272 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979245 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 9071 | 20241009 | 1510 | 20241009 | 1719 | 2590823 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1677 | 35.3957 | -120.096 | No | Clear;Above 90 |  |  | 24-0121496 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1979303 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MC FARLAND-1101 | 253181101 | FUSE | 556403 | 20241009 | 1758 | 20241009 | 1913 | 2591012 | 75 | Distribution Circuit | 3rd Party | Vehicle | 15 | 1125 | 35.6889 | -119.2343 | No | Clear;32-90 F | Anchor or Guy | Normal | 24-0121540 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | No | No | 1979315 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 44701 | 20241009 | 1839 | 20241010 | 505 | 2591026 | 626 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 10466 | 35.133 | -119.476 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0121556 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1979323 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1106 | 254201106 | SWITCH | 4674 | 20241009 | 1943 | 20241010 | 738 | 2591073 | 715 | Distribution Circuit | Vegetation | Tree - grew into line | 28 | 20020 | 35.5747 | -119.5453 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0121534 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979322 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1106 | 252931106 | OTHER | WIRE DOWN @ 90523 | 20241010 | 602 | 20241010 | 1500 | 2591240 | 538 | Distribution Circuit | 3rd Party | Vehicle | 187 | 4165 | 34.9945 | -118.9354 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0121643 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | Yes | 1979368 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 17784 | 20241010 | 1007 | 20241010 | 1121 | 2591455 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 211 | 14981 | 35.3447 | -119.0708 | No | Clear;32-90 F |  |  | 24-0121739 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1979518 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14455 | 20241011 | 345 | 20241011 | 1120 | 2591965 | 455 | Distribution Circuit | Animal | Bird found | 176 | 20568 | 35.3938 | -118.9788 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 24-0122048 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979640 | 1 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | TRANSFORMER | 515423183430 | 20241011 | 1758 | 20241011 | 1831 | 2592463 | 33 | Transformer only | Animal | Bird found | 1 | 33 | 35.7828 | -119.5435 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0122459 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979881 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | SWITCH | 10647 | 20241012 | 15 | 20241012 | 415 | 2592680 | 240 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 480 | 35.3529 | -119.0575 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0121671 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979897 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1103 | 254561103 | RECLOSER | 1190 | 20241012 | 222 | 20241012 | 1319 | 2592690 | 657 | Distribution Circuit | 3rd Party | Vehicle | 47 | 28004 | 35.3835 | -119.2471 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0122489 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1979902 | 0 | Non-EPSS | N | 2024 | A B C
KERN | KERN | STOCKDALE-2111 | 254072111 | FUSE | 11178 | 20241012 | 616 | 20241013 | 51 | 2592704 | 1115 | Distribution Circuit | Equipment Failure/Involved | Underground | 66 | 38781 | 35.3253 | -119.0641 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0122503 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979918 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | JUMPER | 515585659668 | 20241012 | 849 | 20241012 | 1340 | 2592847 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2037 | 35.1307 | -119.4775 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0122525 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979968 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1111 | 253701111 | FUSE | 18006 | 20241012 | 929 | 20241012 | 1043 | 2592885 | 74 | Distribution Circuit | Animal | Bird found | 19 | 1406 | 35.3638 | -119.0443 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0122547 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1979991 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1106 | 252901106 | FUSE | 15178 | 20241012 | 1154 | 20241012 | 1330 | 2593007 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1152 | 35.5288 | -119.4471 | No | Clear;32-90 F |  |  | 24-0122588 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1980018 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1114 | 253371114 | TRANSFORMER | T2521 | 20241012 | 1427 | 20241012 | 1435 | 2593098 | 8 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 136 | 35.3853 | -118.9819 | No | Clear;32-90 F |  |  | 24-0122602 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1980033 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 17663 | 20241012 | 1802 | 20241012 | 1926 | 2593236 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 5712 | 35.3197 | -119.0141 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0122621 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980052 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1110 | 253701110 | FUSE | 15310 | 20241012 | 2109 | 20241012 | 2128 | 2593289 | 19 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 58 | 1102 | 35.3631 | -119.0215 | No | Clear;32-90 F | Service conductor | Normal | 24-0122638 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980071 | 0 | Non-EPSS | N | 2024
KERN | KERN | NORCO-1101 | 254691101 | RECLOSER | 3965 | 20241013 | 2306 | 20241014 | 1400 | 2593781 | 894 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 2094 | 35.2962 | -119.2534 | No | Clear;32-90 F | Customer Equipment | Broken | 24-0122736 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980166 | 0 | Non-EPSS | N | 2024 | B C GRD
KERN | KERN | MAGUNDEN-1108 | 252771108 | RECLOSER | 468940 | 20241014 | 100 | 20241014 | 359 | 2593792 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 7697 | 35.3692 | -118.8621 | No | Clear;32-90 F |  |  | 24-0122739 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980169 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 18561 | 20241014 | 609 | 20241014 | 724 | 2593863 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 355 | 35.2311 | -118.7886 | No | Clear;32-90 F |  |  | 24-0122769 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1980197 | 0 | EPSS Ckt | N | 2024
KERN | KERN | FRUITVALE-1104 | 253391104 | TRANSFORMER | 516698568751 | 20241014 | 1010 | 20241014 | 1240 | 2594253 | 150 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 150 | 35.3842 | -119.1085 | No | Clear;32-90 F | Jumper | Broken | 24-0122899 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980404 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1102 | 252021102 | FUSE | 7172 | 20241014 | 1457 | 20241014 | 1617 | 2594512 | 80 | Distribution Circuit | Animal | Bird found | 8 | 640 | 35.6568 | -119.9747 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123079 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1980476 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 8486 | 20241014 | 1714 | 20241014 | 1859 | 2594616 | 105 | Distribution Circuit | Animal | Bird found | 57 | 5985 | 35.3212 | -119.0095 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0123112 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980487 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | FUSE | 18439 | 20241014 | 1845 | 20241014 | 2100 | 2594631 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1620 | 35.3613 | -119.0344 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0123105 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980485 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20241015 | 1759 | 20241016 | 1423 | 2595630 | 1224 | Distribution Circuit | 3rd Party | Customer Equipment | 33 | 6184 | 35.6271 | -118.9849 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 24-0123574 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980832 | 0 | EPSS Ckt | Y | 2024 | C & GRD
KERN | KERN | TEVIS-2104 | 255322104 | FUSE | 12458 | 20241015 | 1814 | 20241015 | 1917 | 2595614 | 63 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 1962 | 35.3394 | -119.1399 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0123264 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980829 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1106 | 252441106 | FUSE | 54781 | 20241015 | 1845 | 20241015 | 2140 | 2595650 | 175 | Distribution Circuit | 3rd Party | Thrown Object | 1 | 175 | 35.2343 | -119.3296 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123617 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1980863 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 13615 | 20241015 | 2102 | 20241015 | 2300 | 2595676 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 118 | 35.3251 | -119.2343 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0123600 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980849 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 15068 | 20241015 | 2106 | 20241016 | 355 | 2595661 | 409 | Distribution Circuit | 3rd Party | Gun Shot | 5 | 2037 | 35.2164 | -118.8062 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 24-0123608 | OH | Sus | 31712671 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980855 | 1 | EPSS Ckt | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | OTHER | 6214 | 20241015 | 2309 | 20241016 | 144 | 2595716 | 155 | Distribution Circuit | Company Initiated | Return Circuit Normal | 28 | 4244 | 35.4085 | -118.942 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0123620 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980871 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1102 | 254501102 | FUSE | 7184 | 20241016 | 3 | 20241016 | 220 | 2595723 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1918 | 35.6669 | -119.3293 | No | Clear;32-90 F |  |  | 24-0123635 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1980877 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514885169624 | 20241016 | 734 | 20241016 | 1956 | 2595786 | 742 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 742 | 35.4007 | -119.7169 | No | Clear;32-90 F |  |  | 24-0124241 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1981174 | 0 | EPSS Ckt | N | 2024
KERN | KERN | LERDO-1115 | 253491115 | FUSE | 7361 | 20241016 | 1914 | 20241016 | 2155 | 2596592 | 161 | Distribution Circuit | 3rd Party | Metallic Balloon | 13 | 2093 | 35.5153 | -119.1087 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0124268 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981189 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2102 | 255262102 | SWITCH | 58270 | 20241016 | 2039 | 20241016 | 2231 | 2596646 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 3808 | 35.3659 | -119.0921 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0124240 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981183 | 0 | Non-EPSS | N | 2024
KERN | KERN | MCKITTRICK-1101 | 252781101 | JUMPER | JMPRS @ CGC# 515159066136 | 20241016 | 2205 | 20241017 | 132 | 2596651 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 207 | 35.3065 | -119.6227 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0124261 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981185 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRIP-SAVER | 13390 | 20241017 | 547 | 20241017 | 1745 | 2596791 | 718 | Distribution Circuit | 3rd Party | Vehicle | 35 | 6344 | 35.1795 | -118.9669 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0124329 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1981216 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 3751 | 20241017 | 711 | 20241017 | 930 | 2596827 | 139 | Distribution Circuit | 3rd Party | Vehicle | 617 | 80628 | 34.9321 | -118.9283 | Yes | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0124334 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981217 | 0 | EPSS Ckt | Y | 2024 | A- C- INST OC
KERN | KERN | BAKERSFIELD-1115 | 253371115 | SWITCH | 12316 | 20241017 | 928 | 20241017 | 1956 | 2597570 | 628 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 3140 | 35.3777 | -119.0175 | Yes | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0124690 | UG | Sus | 46340600 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981448 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2112 | 254072112 | TRANSFORMER | T600200 | 20241017 | 1143 | 20241017 | 1257 | 2597089 | 74 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 518 | 35.2882 | -119.0838 | Yes | Clear;32-90 F |  |  | 24-0124569 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1981328 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1106 | 252441106 | FUSE | 91681 | 20241017 | 1403 | 20241017 | 1630 | 2597339 | 147 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 1917 | 35.2352 | -119.2904 | Yes | Clear;32-90 F | Connector or Splice (UG) | Contaminated | 24-0124675 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981404 | 1 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2103 | 254582103 | FUSE | 66801 | 20241017 | 1429 | 20241017 | 1745 | 2597368 | 196 | Distribution Circuit | Animal | Other | 1 | 196 | 35.4562 | -119.1289 | Yes | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0124760 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981467 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1111 | 253491111 | TRANSFORMER | 516488972073 | 20241017 | 1431 | 20241017 | 2205 | 2597370 | 454 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 454 | 35.4745 | -119.1804 | Yes | Clear;32-90 F | Jumper | Deteriorated | 24-0124704 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981418 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 20241017 | 2119 | 20241017 | 2232 | 2598007 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 550 | 40150 | 34.8817 | -118.9019 | Yes | Partly Cloudy;32-90 F |  |  | 24-0124807 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981574 | 0 | EPSS Ckt | Y | 2024 | B- C
KERN | KERN | KERN OIL-1110 | 252721110 | FUSE | 13591 | 20241018 | 1516 | 20241018 | 1644 | 2598832 | 88 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 1584 | 35.424 | -119.0343 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0125213 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981835 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | FUSE | 13607 | 20241019 | 1048 | 20241019 | 1231 | 2599279 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 4017 | 35.3453 | -119.0729 | No | Clear;32-90 F | Secondary | Broken- wire on object | 24-0125361 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981979 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517160868452 | 20241020 | 1308 | 20241020 | 1410 | 2599827 | 62 | Transformer only | Animal | Other | 1 | 62 | 35.3776 | -118.9527 | No | Clear;32-90 F | Jumper | Contaminated | 24-0125549 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1982118 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2109 | 254072109 | FUSE | 14671 | 20241021 | 802 | 20241021 | 810 | 2600041 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 8 | 35.3074 | -119.0257 | No | Partly Cloudy;32-90 F |  |  | 24-0125628 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1982178 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | TRANSFORMER | 517213967703 | 20241021 | 1150 | 20241021 | 1755 | 2600426 | 365 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1825 | 35.357 | -118.9351 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0125865 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1982377 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1106 | 252771106 | TRANSFORMER | 517237268588 | 20241021 | 1415 | 20241021 | 1512 | 2600553 | 57 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 570 | 35.3815 | -118.927 | No | Clear;32-90 F |  |  | 24-0125953 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1982393 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1104 | 253391104 | FUSE | 9690 | 20241021 | 1659 | 20241021 | 1809 | 2600674 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 490 | 35.4271 | -119.0794 | No | Clear;32-90 F |  |  | 24-0126011 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1982406 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2109 | 254072109 | FUSE | 14671 | 20241021 | 2145 | 20241022 | 55 | 2600780 | 190 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 190 | 35.3074 | -119.0257 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0126040 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1982421 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517525762115 | 20241022 | 1749 | 20241022 | 1843 | 2601605 | 54 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 702 | 35.2041 | -118.8289 | No | Clear;32-90 F |  |  | 24-0126573 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1982734 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1105 | 252931105 | TRANSFORMER | 517215856375 | 20241023 | 13 | 20241023 | 338 | 2601715 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 205 | 35.0454 | -118.9312 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0126622 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1982763 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1106 | 252771106 | TRANSFORMER | 517202668674 | 20241023 | 556 | 20241023 | 1922 | 2601761 | 806 | Transformer only | Vegetation | Tree - grew into line | 3 | 2418 | 35.3835 | -118.939 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0126666 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1982786 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 535138 | 20241023 | 1349 | 20241023 | 1726 | 2602310 | 217 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 217 | 35.6495 | -118.9809 | No | Clear;32-90 F | Customer Equipment | Broken | 24-0126945 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983027 | 0 | EPSS Ckt | Y | 2024 | AB INST
KERN | KERN | COLUMBUS-1109 | 253951109 | FUSE | 14485 | 20241024 | 114 | 20241024 | 615 | 2602660 | 301 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1806 | 35.3978 | -118.9306 | No | Clear;32-90 F |  |  | 24-0127140 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983095 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8841 | 20241024 | 716 | 20241024 | 926 | 2602906 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 260 | 35.3436 | -119.087 | No | Clear;32-90 F |  |  | 24-0127217 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983227 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 58355 | 20241024 | 1022 | 20241024 | 1955 | 2603129 | 573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 573 | 35.0749 | -118.9218 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0127541 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983335 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1104 | 252961104 | JUMPER | 1 POLE N/OF CGC 516006276579 | 20241024 | 1026 | 20241024 | 1033 | 2602962 | 7 | Distribution Circuit | Company Initiated | Personnel- company | 124 | 868 | 35.5967 | -119.3448 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0127246 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983251 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1104 | 252961104 | FUSE | 15191 | 20241024 | 1220 | 20241024 | 1237 | 2603083 | 17 | Distribution Circuit | Company Initiated | Personnel- company | 54 | 918 | 35.5924 | -119.3447 | No | Partly Cloudy;32-90 F |  |  | 24-0127355 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983304 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | SWITCH | 1665 | 20241024 | 1245 | 20241024 | 2041 | 2603108 | 476 | Distribution Circuit | 3rd Party | Vehicle | 13 | 6188 | 35.1805 | -119.5275 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0127316 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983311 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WASCO-1104 | 252961104 | FUSE | 16002 | 20241024 | 1253 | 20241024 | 1300 | 2603109 | 7 | Distribution Circuit | Company Initiated | Personnel- company | 133 | 931 | 35.5907 | -119.3448 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0127373 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983312 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1106 | 252081106 | FUSE | 847825 | 20241024 | 1911 | 20241024 | 2034 | 2603349 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 83 | 35.1467 | -119.471 | No | Clear;32-90 F |  |  | 24-0127643 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983372 | 1 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1105 | 252931105 | FUSE | 18593 | 20241024 | 2045 | 20241024 | 2310 | 2603435 | 145 | Distribution Circuit | 3rd Party | Vehicle | 3 | 435 | 35.0454 | -118.8908 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0127644 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983374 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13895 | 20241025 | 528 | 20241025 | 953 | 2603531 | 265 | Distribution Circuit | Animal | Bird found | 3 | 882 | 35.7322 | -119.8033 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127819 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983552 | 1 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1104 | 254541104 | TRANSFORMER | 515746172582 | 20241025 | 1337 | 20241025 | 1506 | 2603931 | 89 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 89 | 35.4858 | -119.4295 | No | Clear;32-90 F | Transformer | Burned Open | 24-0127974 | OH | Sus | 46344077 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983590 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | OTHER | J2252 TWD T13621 | 20241025 | 1508 | 20241025 | 1711 | 2603996 | 123 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 3444 | 35.3537 | -119.1657 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0127863 | UG | Sus | 35592723 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983601 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | OCB | 2101/2 | 20241025 | 1536 | 20241025 | 1723 | 2604046 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4324 | 210012 | 35.3871 | -119.1644 | No | Clear;32-90 F |  |  | 24-0128037 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983607 | 0 | Non-EPSS | N | 2024 | C & 50 TIME
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | JUMPER | JMPRS @ CGC #516951358698 | 20241026 | 915 | 20241026 | 1226 | 2604639 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 573 | 35.1083 | -119.0207 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0128129 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983720 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 535138 | 20241026 | 1021 | 20241026 | 2022 | 2604766 | 601 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 601 | 35.6495 | -118.9809 | No | Partly Cloudy;32-90 F | Other | Malfunctioning | 24-0128158 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983764 | 0 | EPSS Ckt | Y | 2024 | B C
KERN | KERN | LAMONT-1105 | 253911105 | SWITCH | 49217 | 20241026 | 1219 | 20241026 | 1252 | 2604882 | 33 | Distribution Circuit | 3rd Party | Vehicle | 119 | 3927 | 35.2382 | -118.8405 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0128176 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983782 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241026 | 1434 | 20241026 | 1535 | 2604928 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 1952 | 35.3618 | -119.1627 | No | Clear;32-90 F |  |  | 24-0128208 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983815 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | FUSE | 18561 | 20241027 | 643 | 20241027 | 1131 | 2605322 | 288 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1440 | 35.2311 | -118.7886 | No | Overcast;32-90 F |  |  | 24-0128293 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983923 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SMYRNA-1106 | 253551106 | RECLOSER | 1200 | 20241027 | 1924 | 20241028 | 420 | 2605591 | 536 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 164 | 28435 | 35.7176 | -119.4204 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0128335 | OH | Sus | 46344991 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1983957 | 0 | Non-EPSS | N | 2024 | SGF
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 8172 | 20241028 | 38 | 20241029 | 329 | 2605633 | 1611 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 28164 | 35.288 | -118.9145 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0128454 | UG | Sus | 31713967 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984126 | 1 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2103 | 254242103 | TRANSFORMER | T6109 | 20241028 | 1121 | 20241028 | 2022 | 2606282 | 541 | Transformer only | Company Initiated | Coordination failure | 1 | 541 | 35.23 | -119.5713 | No | Clear;32-90 F | Connector or Splice (OH) | Normal | 24-0128744 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984246 | 0 | EPSS Ckt | N | 2024
KERN | KERN | FRUITVALE-1106 | 253391106 | FUSE | 9826 | 20241028 | 1305 | 20241028 | 1500 | 2606266 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 110 | 12650 | 35.413 | -119.0741 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0128583 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984191 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1103 | 253651103 | FUSE | 836135 | 20241028 | 1537 | 20241028 | 1804 | 2606468 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 196 | 35.558 | -119.328 | No | Partly Cloudy;32-90 F |  |  | 24-0128748 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984250 | 1 | Non-EPSS | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 286725 | 20241028 | 1543 | 20241028 | 1925 | 2606473 | 222 | Distribution Circuit | Animal | Other | 4 | 888 | 35.3409 | -120.0054 | No | Clear;32-90 F | Fuse | Burned Open | 24-0128764 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1984254 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516925268047 | 20241028 | 1740 | 20241028 | 1913 | 2606525 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 651 | 35.3653 | -119.0322 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0128731 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984242 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | RECLOSER | 4765 | 20241028 | 2356 | 20241029 | 58 | 2606705 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3921 | 215605 | 35.3175 | -119.034 | No | Overcast;32-90 F |  |  | 24-0128792 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984279 | 0 | Non-EPSS | N | 2024 | A
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | FUSE | 286725 | 20241029 | 10 | 20241029 | 18 | 2606715 | 8 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 32 | 35.3409 | -120.0054 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0128764 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984280 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 14861 | 20241029 | 345 | 20241029 | 535 | 2606740 | 110 | Distribution Circuit | Animal | Bird found | 123 | 13530 | 35.4512 | -118.9044 | No | Overcast;32-90 F | Fuse | Burned Open | 24-0128796 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1984286 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | RECLOSER | 286542 | 20241029 | 507 | 20241029 | 1827 | 2606748 | 800 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 15 | 12000 | 35.0245 | -118.7714 | No | Overcast-Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0128799 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1984287 | 0 | EPSS Ckt | Y | 2024 | AC
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | OCB | 1102/2 | 20241029 | 814 | 20241030 | 208 | 2606926 | 1074 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 125 | 24525 | 35.0891 | -118.9767 | No | Overcast-Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0128865 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984346 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13335 | 20241029 | 1326 | 20241029 | 1605 | 2607362 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 636 | 35.0769 | -118.9757 | No | Clear;32-90 F |  |  | 24-0129189 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984598 | 1 | EPSS Ckt | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13335 | 20241029 | 1326 | 20241029 | 2054 | 2607723 | 448 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2184 | 35.0769 | -118.9757 | No | Clear;32-90 F |  |  | 24-0129273 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984627 | 1 | EPSS Ckt | N | 2024
KERN | KERN | SAN BERNARD-1104 | 253191104 | TRANSFORMER | 517309557960 | 20241029 | 1352 | 20241029 | 1553 | 2607385 | 121 | Transformer only | Animal | Other | 1 | 121 | 35.0899 | -118.9002 | No | Clear;32-90 F | Fuse | Broken | 24-0129171 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984594 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1110 | 253371110 | FUSE | 15227 | 20241029 | 1445 | 20241029 | 1534 | 2607449 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 654 | 35.39 | -119.0147 | No | Partly Cloudy;32-90 F |  |  | 24-0129186 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984597 | 1 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1103 | 254561103 | TRANSFORMER | 516349369291 | 20241029 | 2345 | 20241030 | 230 | 2607854 | 165 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 165 | 35.3977 | -119.2259 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0129304 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984644 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 99477 | 20241030 | 221 | 20241030 | 428 | 2607876 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 508 | 35.4623 | -119.2786 | No | Clear;32-90 F |  |  | 24-0129316 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1984656 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1106 | 252441106 | SWITCH | 60836 | 20241030 | 855 | 20241030 | 1342 | 2608093 | 287 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 574 | 35.2343 | -119.2776 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0129351 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984773 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | OCB | 1101/2 | 20241030 | 1845 | 20241030 | 2036 | 2608761 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 290 | 32190 | 35.0891 | -118.9767 | No | Clear;32-90 F |  |  | 24-0129774 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984978 | 0 | EPSS Ckt | N | 2024 | GRD/SGF INST OC
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14394 | 20241030 | 1955 | 20241030 | 2006 | 2608780 | 11 | Distribution Circuit | 3rd Party | Metallic Balloon | 39 | 429 | 35.4044 | -118.9769 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0129782 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984984 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1103 | 254561103 | TRANSFORMER | 516401769171 | 20241030 | 2124 | 20241030 | 2350 | 2608870 | 146 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 146 | 35.3943 | -119.2078 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0129819 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1985016 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13341 | 20241030 | 2355 | 20241101 | 245 | 2608935 | 1610 | Distribution Circuit | 3rd Party | Vehicle | 3 | 4830 | 35.0473 | -119.0115 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0129827 | OH | Sus | 31714174 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1985023 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WASCO-1101 | 252961101 | FUSE | 14561 | 20241031 | 733 | 20241031 | 905 | 2609120 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 123 | 35.6019 | -119.3037 | No | Clear;32-90 F |  |  | 24-0129963 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1985176 | 1 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1108 | 252721108 | FUSE | 15244 | 20241031 | 833 | 20241031 | 1141 | 2609226 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 7896 | 35.4418 | -119.0247 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0129937 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1985121 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1106 | 252441106 | SWITCH | 60836 | 20241031 | 835 | 20241031 | 1506 | 2609243 | 391 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2 | 782 | 35.2343 | -119.2776 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0129624 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1985136 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 8888 | 20241031 | 953 | 20241031 | 1103 | 2609410 | 70 | Distribution Circuit | Animal | Bird found | 11 | 770 | 35.3655 | -118.9626 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0130060 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1985238 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | OTHER | J8655 TWD T0800 | 20241031 | 1337 | 20241031 | 1510 | 2609687 | 31 | Distribution Circuit | Company Initiated | Return Circuit Normal | 99 | 1895 | 35.3302 | -119.0616 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 24-0116903 | UG | Sus | 35462944 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1985289 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1104 | 253951104 | OCB | 1104/2 | 20241031 | 1556 | 20241031 | 2015 | 2609791 | 259 | Distribution Circuit | 3rd Party | Vehicle | 2 | 518 | 35.3985 | -118.9399 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0130275 | OH | Sus | 31713915 | CENTRAL VALLEY | OCT | Force Out | 0 | No | Yes | Yes | 1985319 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | FRUITVALE-1103 | 253391103 | JUMPER | OJ 1 W/OF CGC 516602068769 | 20241031 | 2135 | 20241031 | 2300 | 2609929 | 85 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 85 | 35.3842 | -119.1411 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0130334 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1985345 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 174980 | 20241101 | 814 | 20241101 | 1734 | 2610204 | 560 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1680 | 35.4994 | -119.6205 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0130464 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1985494 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1101 | 252861101 | TRANSFORMER | 516243772201 | 20241101 | 1453 | 20241101 | 2005 | 2610633 | 312 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 312 | 35.4774 | -119.2632 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0130706 | OH | Sus | 46362053 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985603 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1104 | 253701104 | TRANSFORMER | 516940468838 | 20241101 | 2213 | 20241102 | 130 | 2610921 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 3671 | 35.3869 | -119.0273 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0130774 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985648 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | FUSE | 15955 | 20241102 | 356 | 20241102 | 619 | 2611166 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 715 | 35.2236 | -118.8693 | No | Clear;32-90 F |  |  | 24-0130838 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985705 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1104 | 253141104 | OCB | 1104/2 | 20241102 | 737 | 20241102 | 1815 | 2611378 | 638 | Distribution Circuit | 3rd Party | Customer Equipment | 44 | 16255 | 34.9276 | -119.6203 | No | Partly Cloudy;32-90 F | Customer Equipment | Malfunctioning | 24-0130855 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985726 | 0 | EPSS Ckt | N | 2024 | TIME OC A & B
KERN | KERN | COPUS-1103 | 253871103 | RECLOSER | 535428 | 20241102 | 814 | 20241102 | 1026 | 2611436 | 132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 528 | 35.1236 | -119.11 | No | Clear;32-90 F | Regulator | Malfunctioning | 24-0130863 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1985756 | 0 | Non-EPSS | N | 2024 | 3
KERN | KERN | COPUS-1103 | 253871103 | RECLOSER | 4801 | 20241102 | 1004 | 20241102 | 1024 | 2611576 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 207 | 4140 | 35.0938 | -119.2522 | No | Partly Cloudy;32-90 F | Regulator | Malfunctioning | 24-0130918 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985822 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | TUPMAN-1106 | 254561106 | TRANSFORMER | 516360767582 | 20241102 | 1139 | 20241102 | 1621 | 2611658 | 282 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 282 | 35.3508 | -119.2213 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0130961 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985859 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1104 | 253701104 | JUMPER | JUMPERS 1 P S/OF CGC# 516933368851 | 20241102 | 1453 | 20241102 | 1536 | 2611810 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 1290 | 35.387 | -119.03 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0131000 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985886 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | JUMPER | DDE 2 P S/OF CGC# 517024068514 | 20241102 | 1634 | 20241103 | 713 | 2611823 | 879 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 6 | 5274 | 35.3781 | -118.9993 | No | Partly Cloudy;32-90 F | Secondary | Burned Open | 24-0131015 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985893 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1108 | 252081108 | FUSE | 9004 | 20241102 | 1952 | 20241105 | 1314 | 2611919 | 3922 | Distribution Circuit | 3rd Party | Vandalism | 1 | 3922 | 35.1373 | -119.4616 | No | Partly Cloudy;32-90 F | Metering Equipment | Broken | 24-0131040 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985907 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 20241103 | 305 | 20241103 | 1056 | 2612123 | 471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 566 | 238586 | 34.8817 | -118.9019 | No | Overcast-Fog;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0131073 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985931 | 0 | EPSS Ckt | Y | 2024 | BC
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13447 | 20241103 | 805 | 20241104 | 1050 | 2612189 | 1605 | Distribution Circuit | Equipment Failure/Involved | Overhead | 134 | 215070 | 35.365 | -118.9703 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 24-0131089 | OH | Sus | 31716380 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | Yes | 1985956 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | 100000024400 | 20241103 | 1312 | 20241103 | 1353 | 2612514 | 41 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 41 | 35.1515 | -119.0216 | No | Clear;32-90 F |  |  | 24-0131144 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1986011 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1105 | 253371105 | TRANSFORMER | 516943168642 | 20241103 | 2152 | 20241103 | 2229 | 2612742 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 148 | 35.3819 | -119.0263 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0131214 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986047 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 284661 | 20241104 | 859 | 20241104 | 1245 | 2613074 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2034 | 35.6744 | -119.24 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0131302 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986164 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1103 | 252971103 | TRANSFORMER | 517546362431 | 20241104 | 1531 | 20241104 | 1627 | 2613671 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 224 | 35.2127 | -118.8224 | No | Clear;32-90 F | Fuse | Burned Open | 24-0131657 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986374 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1116 | 252721116 | SWITCH | 4207 | 20241104 | 1952 | 20241104 | 2223 | 2613731 | 151 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 151 | 35.4269 | -119.0645 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131688 | OH | Sus | 46381148 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986386 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1105 | 253551105 | FUSE | 242715 | 20241105 | 1217 | 20241105 | 1455 | 2614333 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 422 | 35.761 | -119.3833 | Yes | Clear;32-90 F |  |  | 24-0132183 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986673 | 1 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1105 | 253371105 | TRANSFORMER | 516949768716 | 20241106 | 9 | 20241106 | 302 | 2615227 | 173 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 692 | 35.3835 | -119.0242 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0132315 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986875 | 0 | Non-EPSS | N | 2024
KERN | KERN | CUYAMA-1104 | 253141104 | OCB | 1104/2 | 20241106 | 513 | 20241106 | 1131 | 2615554 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 12217 | 34.9276 | -119.6203 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132371 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1986937 | 0 | EPSS Ckt | N | 2024 | B-GRD TIME OC
KERN | KERN | LAMONT-1104 | 253911104 | SWITCH | 809792 | 20241106 | 520 | 20241107 | 927 | 2615557 | 1687 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 8435 | 35.334 | -118.7348 | No | Partly Cloudy;32-90 F |  |  | 24-0131220 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986938 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | SWITCH | 4782 | 20241106 | 526 | 20241107 | 1016 | s1986947 | 1730 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 520 | 899600 | 34.8602 | -118.8819 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131199 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986947 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 20241106 | 530 | 20241107 | 946 | s1986948 | 1696 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 41 | 69536 | 34.8817 | -118.9019 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131199 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986948 | 0 | EPSS Ckt | N | 2024 | NA
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 3751 | 20241106 | 532 | 20241107 | 940 | s1986953 | 1688 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 51 | 86088 | 34.9321 | -118.9283 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131199 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986953 | 0 | EPSS Ckt | N | 2024 | NA
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 4525 | 20241106 | 732 | 20241106 | 1747 | 2615786 | 615 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 12915 | 34.9719 | -118.9397 | No | Clear-Strong Winds;32-90 F | Other | Broken- wire on object | 24-0132412 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1986994 | 0 | EPSS Ckt | Y | 2024 | C GRD
KERN | KERN | WASCO-1102 | 252961102 | TRANSFORMER | 516026176782 | 20241106 | 842 | 20241106 | 950 | 2616147 | 68 | Transformer only | Company Initiated | Personnel- company | 2 | 136 | 35.6022 | -119.338 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0132479 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987103 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2101 | 255262101 | OCB | 2101/2 | 20241106 | 1115 | 20241106 | 1653 | 2616658 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2168 | 278152 | 35.3785 | -119.0985 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132607 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1987226 | 0 | Non-EPSS | N | 2024 | AB TIME OC
KERN | KERN | CUYAMA-1103 | 253141103 | SWITCH | 1614 | 20241106 | 1149 | 20241106 | 1204 | 2616814 | 15 | Distribution Circuit | Company Initiated | Return Circuit Normal | 13 | 195 | 34.9286 | -119.6923 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132371 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1987258 | 0 | EPSS Ckt | N | 2024
KERN | KERN | KERN OIL-1108 | 252721108 | FUSE | 15241 | 20241106 | 1155 | 20241106 | 1313 | 2616734 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 2262 | 35.4466 | -119.0258 | No | Clear;32-90 F |  |  | 24-0132678 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1987270 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 17663 | 20241106 | 1302 | 20241106 | 2012 | 2616893 | 430 | Distribution Circuit | 3rd Party | Other | 68 | 29240 | 35.3197 | -119.0141 | No | Clear;32-90 F | Secondary | Broken | 24-0132698 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987278 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1105 | 253951105 | FUSE | 2508 | 20241106 | 1345 | 20241106 | 1531 | 2616905 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1484 | 35.4198 | -118.9499 | No | Clear;32-90 F |  |  | 24-0132795 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1987301 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | TRANSFORMER | 516836267306 | 20241106 | 1509 | 20241106 | 1711 | 2616934 | 122 | Transformer only | Vegetation | Tree - grew into line | 7 | 854 | 35.3447 | -119.0618 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0132807 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987302 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 13282 | 20241106 | 1603 | 20241106 | 1740 | 2617154 | 97 | Distribution Circuit | Animal | Bird found | 1 | 97 | 35.3463 | -119.0483 | No | Clear;32-90 F | Fuse | Burned Open | 24-0132875 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987322 | 1 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2104 | 255322104 | OTHER | T11745 TWD T11751 | 20241106 | 2106 | 20241106 | 2118 | 2617311 | 12 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 180 | 35.3424 | -119.13 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0131517 | UG | Sus | 35595847 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987338 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2104 | 255322104 | OTHER | T11199 TWD T11200 | 20241106 | 2136 | 20241107 | 20 | 2617320 | 164 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 2132 | 35.3415 | -119.1323 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0132907 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987344 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2103 | 255322103 | OTHER | J1317 TWD T10767 | 20241107 | 36 | 20241107 | 114 | 2617348 | 38 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 988 | 35.3447 | -119.1339 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0132765 | UG | Sus | 35596273 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987357 | 0 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1101 | 253801101 | OTHER | J2109 TWD T13219 | 20241107 | 230 | 20241107 | 319 | 2617357 | 49 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 931 | 35.1895 | -118.8262 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0131442 | UG | Sus | 45451364 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987361 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 196480 | 20241107 | 1306 | 20241107 | 1435 | 2617995 | 89 | Distribution Circuit | Animal | Bird found | 3 | 267 | 34.9273 | -119.6041 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0133208 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1987605 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1110 | 253371110 | FUSE | 528495 | 20241107 | 2325 | 20241108 | 445 | 2618286 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 9280 | 35.3845 | -119.0242 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0133337 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987645 | 0 | Non-EPSS | N | 2024
KERN | KERN | CAL WATER-1102 | 255451102 | RECLOSER | 329532 | 20241109 | 724 | 20241109 | 903 | 2619511 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1685 | 165375 | 35.4136 | -118.8567 | No | Clear;32-90 F |  |  | 24-0133767 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987999 | 0 | EPSS Ckt | N | 2024 | A-B
KERN | KERN | LAMONT-1106 | 253911106 | FUSE | 13881 | 20241109 | 821 | 20241109 | 1130 | 2619565 | 189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 191 | 36099 | 35.2672 | -118.9099 | No | Clear;32-90 F | Other | Normal | 24-0133817 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988081 | 0 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1106 | 252441106 | TRANSFORMER | 516155664046 | 20241109 | 1350 | 20241109 | 1358 | 2619704 | 8 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 8 | 35.2533 | -119.2896 | No | Clear;32-90 F |  |  | 24-0133833 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1988096 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT SUB | 25208 | OCB | 1100/2 | 20241110 | 650 | 20241110 | 1034 | 2620042 | 224 | Distribution Circuit | 3rd Party | Vehicle | 475 | 22558 | 35.1363 | -119.4822 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0133887 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988162 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | WESTPARK-1105 | 253701105 | OCB | 1105/2 | 20241110 | 1047 | 20241110 | 1709 | 2620174 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 355 | 8226 | 35.374 | -119.0404 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0133912 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988198 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 516002182021 | 20241110 | 1550 | 20241110 | 2341 | 2620290 | 471 | Transformer only | 3rd Party | Fire- house or bldg. | 1 | 471 | 35.7464 | -119.3478 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0133972 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988238 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1111 | 253701111 | SWITCH | 5066 | 20241110 | 1729 | 20241110 | 1735 | s1988242 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 4 | 24 | 35.3682 | -119.0529 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0133912 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988242 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | JUMPER | FB 1 S/O CGC #516002982054 | 20241110 | 2337 | 20241111 | 1022 | 2620385 | 645 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3870 | 35.7471 | -119.3478 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0133992 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988268 | 0 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13912 | 20241111 | 414 | 20241111 | 701 | 2620416 | 167 | Distribution Circuit | Animal | Other | 11 | 1837 | 35.7015 | -119.69 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0134016 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988295 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 13787 | 20241111 | 801 | 20241111 | 901 | 2620533 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 120 | 35.0926 | -118.9439 | No | Clear;32-90 F |  |  | 24-0134051 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988345 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1104 | 253951104 | FUSE | 20069 | 20241111 | 1051 | 20241111 | 1421 | 2620821 | 210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 5670 | 35.3929 | -118.9723 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0134086 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988396 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1106 | 253701106 | OCB | 1106/2 | 20241111 | 1431 | 20241111 | 1630 | 2621421 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 847 | 63533 | 35.374 | -119.0404 | No | Partly Cloudy;32-90 F |  |  | 24-0134187 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988501 | 0 | Non-EPSS | N | 2024 | B & C INST
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 16317 | 20241111 | 1500 | 20241111 | 1643 | 2621806 | 103 | Distribution Circuit | Animal | Bird found | 2 | 206 | 35.256 | -118.9141 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0134265 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988566 | 1 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1102 | 252961102 | SWITCH | 7604 | 20241111 | 1555 | 20241112 | 139 | 2622178 | 584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 394 | 218387 | 35.5871 | -119.3498 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0134350 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1988654 | 1 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 7505 | 20241111 | 1607 | 20241111 | 2335 | 2621741 | 448 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 22400 | 35.5072 | -119.2733 | No | Overcast-Drizzle;32-90 F |  |  | 24-0134409 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988716 | 0 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1104 | 254541104 | FUSE | 17082 | 20241111 | 1612 | 20241111 | 1740 | 2621747 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1056 | 35.4855 | -119.4394 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0134289 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988590 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1104 | 252721104 | RECLOSER | 76778 | 20241111 | 1617 | 20241112 | 1844 | 2621770 | 1587 | Distribution Circuit | 3rd Party | Customer Equipment | 11 | 17457 | 35.5152 | -119.011 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0134259 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1988561 | 0 | EPSS Ckt | N | 2024 | A B C
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20241111 | 1625 | 20241111 | 1759 | 2621823 | 94 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 33 | 3102 | 35.6271 | -118.9849 | No | Overcast;32-90 F |  |  | 24-0134269 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988570 | 0 | EPSS Ckt | Y | 2024 | B GRD INST
KERN | KERN | TUPMAN-1105 | 254561105 | FUSE | 49723 | 20241111 | 1625 | 20241112 | 600 | 2621760 | 815 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 1630 | 35.3105 | -119.3178 | No | Overcast;32-90 F |  |  | 24-0134443 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988767 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | 516934669713 | 20241111 | 1632 | 20241112 | 1543 | 2621764 | 1391 | Transformer only | Vegetation | Tree - bark fell into line | 20 | 27820 | 35.4111 | -119.0295 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0134422 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1988730 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241111 | 1633 | 20241112 | 129 | 2621789 | 536 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 17152 | 35.3618 | -119.1627 | No | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0134396 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988704 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1104 | 253701104 | RECLOSER | 1514 | 20241111 | 1633 | 20241111 | 1748 | 2621774 | 75 | Distribution Circuit | Vegetation | Tree - branch fell on line | 439 | 32925 | 35.3823 | -119.0351 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0134270 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988571 | 0 | Non-EPSS | N | 2024 | A C GRD
KERN | KERN | KERN OIL-1106 | 252721106 | FUSE | 17498 | 20241111 | 1634 | 20241112 | 19 | 2621769 | 465 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 10695 | 35.4557 | -118.9067 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0134383 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988691 | 0 | EPSS Ckt | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516667968746 | 20241111 | 1636 | 20241112 | 1740 | 2621804 | 1504 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 6016 | 35.3838 | -119.1186 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Transformer (OH) | Deteriorated | 24-0134412 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988722 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20241111 | 1637 | 20241111 | 1936 | 2621790 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4536 | 708383 | 35.3885 | -119.0046 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0134262 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1988564 | 0 | Non-EPSS | N | 2024 | A B C TIME INST
KERN | KERN | BAKERSFIELD-2109 | 253372109 | RECLOSER | 90726 | 20241111 | 1638 | 20241112 | 502 | 2621801 | 744 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3845 | 1404871 | 35.3783 | -119.0095 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0134273 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988574 | 0 | Non-EPSS | N | 2024 | B C GRD
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 8927 | 20241111 | 1641 | 20241111 | 2024 | 2621802 | 223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 385 | 85855 | 35.3473 | -119.048 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0134337 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988637 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517035065887 | 20241111 | 1646 | 20241111 | 2333 | 2621830 | 407 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 1221 | 35.3064 | -118.9941 | No | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0134374 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1988682 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 2427 | 20241111 | 1704 | 20241112 | 135 | 2621857 | 511 | Distribution Circuit | Equipment Failure/Involved | Overhead | 204 | 104244 | 35.3087 | -119.0026 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0134367 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1988671 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | RECLOSER | 1482 | 20241111 | 1707 | 20241111 | 2128 | 2621869 | 261 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 26622 | 35.3665 | -119.4477 | No | Clear;32-90 F | Jumper | Bent or Twisted | 24-0134288 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988588 | 0 | Non-EPSS | N | 2024 | A GRD
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 18173 | 20241111 | 1713 | 20241111 | 2303 | 2621890 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 13300 | 35.4091 | -119.0193 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0134356 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1988660 | 0 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1102 | 253801102 | FUSE | 587695 | 20241111 | 1719 | 20241112 | 202 | 2621900 | 523 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 17442 | 35.171 | -118.9146 | No | Clear;32-90 F |  |  | 24-0134403 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988710 | 1 | Non-EPSS | N | 2024
KERN | KERN | GANSO-1104 | 254541104 | RECLOSER | 312168 | 20241111 | 1720 | 20241112 | 1655 | 2621918 | 1415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 7229 | 35.4817 | -119.3859 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0134293 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988594 | 0 | Non-EPSS | N | 2024 | B & C
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | 516532367970 | 20241111 | 1739 | 20241112 | 150 | 2621948 | 491 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 491 | 35.3618 | -119.1637 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0134407 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1988714 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | OCB | 1102/2 | 20241111 | 1753 | 20241112 | 522 | 2621960 | 689 | Distribution Circuit | Equipment Failure/Involved | Overhead | 416 | 182934 | 35.2971 | -118.8619 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0134307 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1988608 | 0 | EPSS Ckt | N | 2024 | A B C TIME
KERN | KERN | BAKERSFIELD-2104 | 253372104 | OCB | 2104/2 | 20241111 | 1803 | 20241112 | 252 | 2621985 | 529 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4775 | 483705 | 35.3885 | -119.0046 | No | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0134324 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | No | No | 1988624 | 0 | Non-EPSS | N | 2024 | B- C & GRD
KERN | KERN | KERN OIL-1109 | 252721109 | FUSE | 15253 | 20241111 | 1803 | 20241111 | 2029 | 2621968 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2921 | 35.4172 | -119.0545 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0134317 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988618 | 1 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | FUSE | 13599 | 20241111 | 1804 | 20241112 | 709 | 2621971 | 785 | Distribution Circuit | Equipment Failure/Involved | Underground | 92 | 34372 | 35.3752 | -119.1099 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Burned/flashed | 24-0134343 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988647 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1104 | 252961104 | FUSE | 15187 | 20241111 | 1806 | 20241111 | 2120 | 2621989 | 194 | Distribution Circuit | Equipment Failure/Involved | Overhead | 143 | 27742 | 35.5916 | -119.3376 | No | Overcast;32-90 F | Insulator | Broken | 24-0134306 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988607 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 517003365134 | 20241111 | 1811 | 20241112 | 717 | 2621999 | 786 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 4716 | 35.2858 | -119.0047 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0134392 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988700 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1101 | 252821101 | RECLOSER | 3570 | 20241111 | 1812 | 20241112 | 606 | 2622000 | 714 | Distribution Circuit | Animal | Other | 15 | 10710 | 35.179 | -119.1461 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0134305 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988606 | 0 | Non-EPSS | N | 2024 | B
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 14848 | 20241111 | 1815 | 20241112 | 18 | 2621994 | 363 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1452 | 35.3031 | -119.0064 | No | Overcast-Drizzle;32-90 F |  |  | 24-0134385 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988693 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1104 | 253181104 | RECLOSER | 950506 | 20241111 | 1823 | 20241112 | 558 | 2622006 | 695 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 20155 | 35.6602 | -119.153 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0134311 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1988612 | 0 | Non-EPSS | N | 2024 | A B C
KERN | KERN | ARVIN-1101 | 253801101 | OCB | 1101/2 | 20241111 | 1826 | 20241112 | 1915 | 2622137 | 1489 | Distribution Circuit | 3rd Party | Vehicle | 416 | 199511 | 35.1499 | -118.8788 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0134338 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1988638 | 0 | EPSS Ckt | Y | 2024 | NONE
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 17654 | 20241111 | 1830 | 20241112 | 720 | 2622013 | 770 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 3595 | 35.151 | -118.9657 | No | Clear;32-90 F |  |  | 24-0134458 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988779 | 1 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | RECLOSER | 4164 | 20241111 | 1835 | 20241112 | 454 | 2622029 | 619 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 48901 | 35.0595 | -118.978 | No | Clear;32-90 F | Regulator | Failed/Faulted | 24-0134334 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988634 | 0 | EPSS Ckt | N | 2024 | A GRD
KERN | KERN | LAKEVIEW-1102 | 253411102 | OCB | 1102/2 | 20241111 | 1839 | 20241112 | 138 | 2622043 | 419 | Distribution Circuit | Animal | Other | 153 | 64107 | 35.0936 | -119.1012 | No | Overcast-Drizzle;32-90 F | Recloser | Burned/flashed | 24-0134331 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1988631 | 0 | Non-EPSS | N | 2024 | A B C TIME
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 535138 | 20241111 | 1844 | 20241112 | 1326 | 2622128 | 1122 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 1122 | 35.6495 | -118.9809 | No | Clear;32-90 F | Customer Equipment | Normal | 24-0134330 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988630 | 0 | EPSS Ckt | Y | 2024 | A- C- INST OC
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 14990 | 20241111 | 1848 | 20241112 | 142 | 2622047 | 414 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2898 | 35.3033 | -118.9321 | No | Clear;32-90 F |  |  | 24-0134408 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988715 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 13296 | 20241111 | 1851 | 20241112 | 1305 | 2622057 | 1094 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 33914 | 35.42 | -119.2516 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0134429 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1988738 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | OCB | 2104/2 | 20241111 | 1858 | 20241111 | 2313 | 2622067 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 31641 | 35.1948 | -119.5861 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0134329 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1988629 | 0 | EPSS Ckt | N | 2024 | A B C INST
KERN | KERN | BAKERSFIELD-1102 | 253371102 | FUSE | 878715 | 20241111 | 1917 | 20241112 | 1546 | 2622193 | 1229 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 63 | 64083 | 35.3972 | -118.9853 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0134391 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988699 | 1 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 17854 | 20241111 | 2015 | 20241112 | 1308 | 2622142 | 1013 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 9117 | 35.4423 | -119.3327 | No | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 24-0134432 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988741 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | FUSE | 17024 | 20241111 | 2107 | 20241112 | 328 | 2622173 | 381 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 5 | 1905 | 35.2085 | -118.9526 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0134345 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988649 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13442 | 20241111 | 2126 | 20241112 | 234 | 2622188 | 306 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 7344 | 35.3576 | -118.9677 | No | Overcast;32-90 F |  |  | 24-0134415 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988724 | 0 | Non-EPSS | N | 2024
KERN | KERN | FAMOSO-1102 | 252461102 | FUSE | 7328 | 20241111 | 2142 | 20241112 | 1500 | 2622213 | 1038 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 17646 | 35.6384 | -119.1677 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0134411 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988720 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | FUSE | 14582 | 20241111 | 2336 | 20241112 | 1138 | 2622249 | 722 | Distribution Circuit | Equipment Failure/Involved | Underground | 93 | 67146 | 35.4926 | -119.2821 | No | Partly Cloudy-Fog;32-90 F | Elbow | Broken | 24-0134420 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988728 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 16913 | 20241112 | 227 | 20241112 | 423 | 2622311 | 116 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 696 | 35.4818 | -119.2962 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0134431 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988740 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1107 | 253911107 | TRIP-SAVER | 15043 | 20241112 | 353 | 20241112 | 1117 | 2622331 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 15249 | 35.3034 | -118.9142 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0134427 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988736 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | SAN BERNARD-1104 | 253191104 | FUSE | 13316 | 20241112 | 644 | 20241112 | 857 | 2622407 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1729 | 35.0927 | -118.9002 | No | Clear;32-90 F |  |  | 24-0134493 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988850 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 16866 | 20241112 | 656 | 20241112 | 819 | 2622422 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 7304 | 35.3537 | -118.9942 | No | Overcast;32-90 F |  |  | 24-0134464 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988784 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 17513 | 20241112 | 707 | 20241112 | 1030 | 2622430 | 203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 609 | 35.2095 | -119.1864 | No | Clear;32-90 F |  |  | 24-0134553 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988969 | 0 | Non-EPSS | N | 2024
KERN | KERN | MARICOPA-1102 | 254211102 | TRANSFORMER | 515797256315 | 20241112 | 708 | 20241112 | 1025 | 2622431 | 197 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 197 | 35.0391 | -119.4039 | No | Clear;32-90 F |  |  | 24-0134555 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1988972 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WEEDPATCH-1101 | 252971101 | FUSE | 15712 | 20241112 | 710 | 20241113 | 410 | 2622433 | 1260 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3780 | 35.2162 | -118.8604 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0134452 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1988777 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2106 | 254072106 | FUSE | 2844 | 20241112 | 828 | 20241112 | 1105 | 2622573 | 157 | Distribution Circuit | Vegetation | Other ground vegetation | 48 | 7476 | 35.3141 | -119.0207 | No | Overcast;32-90 F | Transformer (UG) | Normal | 24-0134573 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988986 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1105 | 253911105 | FUSE | 13381 | 20241112 | 900 | 20241113 | 440 | 2622815 | 1180 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 3540 | 35.2688 | -118.7978 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0134543 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988954 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1110 | 253371110 | TRANSFORMER | 517001768832 | 20241112 | 1106 | 20241112 | 1200 | 2622895 | 54 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 108 | 35.3868 | -119.0062 | No | Partly Cloudy;32-90 F |  |  | 24-0134616 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1989009 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1102 | 253371102 | SWITCH | 194881 | 20241112 | 1137 | 20241112 | 2131 | 2622893 | 594 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 395 | 39140 | 35.3976 | -118.9931 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0134601 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988999 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | 517097365183 | 20241112 | 1328 | 20241112 | 1810 | 2623061 | 282 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 564 | 35.2698 | -118.9732 | No | Clear;32-90 F |  |  | 24-0134835 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1989098 | 0 | EPSS Ckt | N | 2024
KERN | KERN | STOCKDALE-2111 | 254072111 | TRANSFORMER | T2185 | 20241112 | 1333 | 20241113 | 331 | 2622800 | 838 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 10238 | 35.3488 | -119.0615 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0134691 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989038 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | TRANSFORMER | 517778363068 | 20241112 | 1353 | 20241113 | 1258 | 2623093 | 1385 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2770 | 35.2313 | -118.743 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0134831 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989096 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | OCB | 2104/2 | 20241112 | 1423 | 20241112 | 2144 | 2623131 | 441 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 882 | 35.3885 | -119.0046 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0134728 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | Yes | No | 1989057 | 0 | Non-EPSS | N | 2024 | NA
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | TRANSFORMER | 514422665809 | 20241112 | 1446 | 20241112 | 1749 | 2623150 | 183 | Transformer only | Animal | Bird found | 1 | 183 | 35.2929 | -119.8739 | No | Clear;32-90 F | Fuse | Broken | 24-0134837 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989100 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517161568481 | 20241112 | 1628 | 20241112 | 2107 | 2623315 | 279 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 9 | 2511 | 35.3784 | -118.9524 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0134805 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989082 | 0 | Non-EPSS | N | 2024
KERN | KERN | CARNERAS-1103 | 252321103 | OCB | 1103/2 | 20241112 | 1638 | 20241112 | 1946 | 2623332 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 7332 | 35.5408 | -119.8047 | No | Clear;32-90 F |  |  | 24-0134812 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1989086 | 0 | EPSS Ckt | N | 2024 | A- B- C
KERN | KERN | WASCO-1101 | 252961101 | JUMPER | OJ @ LINE & BUCK SS OF CGC 515991875607 | 20241112 | 1649 | 20241112 | 1850 | 2623342 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 242 | 35.5697 | -119.3496 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0134813 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989087 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1102 | 254501102 | JUMPER | FB'S 1 SOUTH OF CGC# 515929979294 | 20241112 | 1723 | 20241112 | 1950 | 2623365 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 294 | 35.6705 | -119.3706 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 24-0134826 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989092 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1105 | 253911105 | FUSE | 9895 | 20241113 | 644 | 20241113 | 923 | 2623573 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 742 | 35.2818 | -118.8407 | No | Clear;32-90 F |  |  | 24-0135017 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989338 | 1 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1104 | 253181104 | TRANSFORMER | 516695578530 | 20241113 | 812 | 20241113 | 1435 | 2624190 | 383 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 766 | 35.6523 | -119.1129 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0135197 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989429 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1106 | 253551106 | FUSE | 7242 | 20241113 | 834 | 20241113 | 1254 | 2623706 | 260 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2860 | 35.7181 | -119.4106 | No | Partly Cloudy;32-90 F |  |  | 24-0135084 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989377 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAKEVIEW-1103 | 253411103 | FUSE | 14226 | 20241113 | 1531 | 20241115 | 1555 | 2624316 | 2904 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 8712 | 35.0111 | -119.1355 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0135280 | OH | Sus | 31717516 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1989460 | 1 | EPSS Ckt | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | SWITCH | 3846 | 20241113 | 2123 | 20241113 | 2333 | 2624521 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 130 | 35.3462 | -119.2169 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0135313 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989491 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 13028 | 20241114 | 611 | 20241114 | 744 | 2624635 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2419 | 35.256 | -118.91 | No | Clear;32-90 F |  |  | 24-0135365 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989529 | 1 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | OTHER | T13694 TWD T13695 | 20241114 | 858 | 20241114 | 953 | 2624813 | 55 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 2420 | 35.2793 | -119.0005 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0132769 | UG | Sus | 35596255 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989617 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1106 | 252971106 | TRANSFORMER | 100000009866 | 20241114 | 903 | 20241114 | 1036 | 2624825 | 93 | Transformer only | Animal | Other | 1 | 93 | 35.2123 | -118.9121 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0135460 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989715 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 7405 | 20241114 | 953 | 20241114 | 1218 | 2625126 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 725 | 35.7029 | -119.5825 | No | Clear;32-90 F |  |  | 24-0135548 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989757 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | OTHER | J2270 TWD T13690 | 20241114 | 1009 | 20241114 | 1100 | s1989709 | 51 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 2550 | 35.2809 | -119.0012 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0132782 | UG | Sus | 35596255 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989709 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1102 | 253871102 | FUSE | 9060 | 20241114 | 1039 | 20241115 | 0 | 2625100 | 801 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4914 | 35.123 | -119.305 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0135527 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1989746 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | OCB | 1103/2 | 20241114 | 1719 | 20241114 | 2059 | 2625346 | 220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 618 | 43103 | 35.0891 | -118.9767 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0135705 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989814 | 0 | Non-EPSS | N | 2024 | AC
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 14148 | 20241115 | 212 | 20241115 | 733 | 2625533 | 321 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1126 | 35.3706 | -119.003 | No | Overcast-Rain;32-90 F | Lightning Arrestor | Burned/flashed | 24-0135758 | OH | Sus | 31717459 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989860 | 1 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1104 | 253951104 | OCB | 1104/2 | 20241115 | 229 | 20241115 | 1324 | 2625538 | 655 | Distribution Circuit | Equipment Failure/Involved | Underground | 399 | 83911 | 35.3985 | -118.9399 | No | Overcast-Rain;32-90 F | Conductor- Underground | Broken | 24-0135753 | UG | Sus | 46389781 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989853 | 0 | Non-EPSS | N | 2024 | AG TIME
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 16866 | 20241115 | 238 | 20241115 | 631 | 2625540 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 20504 | 35.3537 | -118.9942 | No | Overcast-Rain;32-90 F |  |  | 24-0135755 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989858 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 14809 | 20241115 | 507 | 20241115 | 747 | 2625604 | 160 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 110 | 16040 | 35.3325 | -119.0561 | No | Overcast-Drizzle;32-90 F | Fuse | Burned Open | 24-0135761 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989861 | 1 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1104 | 253951104 | JUMPER | WIRE DOWN W/OF 225593 | 20241115 | 611 | 20241115 | 909 | 2625701 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 18656 | 35.3921 | -118.9692 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0135800 | OH | Sus | 31717458 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | Yes | 1989878 | 0 | Non-EPSS | N | 2024
KERN | KERN | BLACKWELL-1102 | 254681102 | FUSE | 19261 | 20241115 | 643 | 20241115 | 1014 | 2625667 | 211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 9073 | 35.6155 | -119.8544 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0135900 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990062 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 516894956719 | 20241115 | 708 | 20241115 | 1637 | 2625673 | 569 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 1138 | 35.0549 | -119.0386 | No | Overcast;32-90 F |  |  | 24-0135844 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1989977 | 0 | EPSS Ckt | N | 2024
KERN | KERN | COLUMBUS-1106 | 253951106 | JUMPER | SEC WRP IN NEUT CGC# 517110369368 | 20241115 | 1053 | 20241115 | 2324 | 2626157 | 751 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 22043 | 35.4003 | -118.97 | No | Overcast;32-90 F | Secondary | Together | 24-0135964 | OH | Sus | 31717648 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990096 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1104 | 252961104 | SWITCH | 684627 | 20241115 | 1117 | 20241115 | 1142 | 2626053 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 4475 | 35.5865 | -119.3506 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0135907 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990064 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1104 | 253701104 | SWITCH | 2581 | 20241115 | 1230 | 20241115 | 1611 | 2626146 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 13481 | 35.3821 | -119.0303 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0135571 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990091 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | OCB | 1102/2 | 20241115 | 1407 | 20241115 | 1439 | 2626262 | 32 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 775 | 24800 | 35.0198 | -118.9548 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0136018 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990114 | 0 | EPSS Ckt | N | 2024 | NONE
KERN | KERN | MIDWAY-1101 | 252611101 | RECLOSER | 389356 | 20241115 | 1611 | 20241115 | 2121 | 2626259 | 310 | Distribution Circuit | 3rd Party | Vehicle | 44 | 13640 | 35.4427 | -119.4394 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0136056 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990128 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | TWISSELMAN-2105 | 254402105 | OCB | 2105/2 | 20241115 | 1937 | 20241115 | 2007 | 2626436 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 152 | 4560 | 35.7305 | -119.8581 | No | Clear;32-90 F | Recloser | Burned/flashed | 24-0136129 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990146 | 0 | Non-EPSS | N | 2024 | G TIME
KERN | KERN | STOCKDALE-2113 | 254072113 | JUMPER | OJ 1 S/OF CGC#516988966536 | 20241115 | 2313 | 20241116 | 200 | s1990162 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 835 | 35.3236 | -119.0097 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0136134 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990162 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 14100 | 20241116 | 837 | 20241116 | 1731 | 2626811 | 534 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 38448 | 35.3824 | -118.9524 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0136176 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990209 | 0 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1101 | 253191101 | OCB | 1101/2 | 20241117 | 1041 | 20241118 | 345 | 2627410 | 1024 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 24207 | 35.0921 | -118.878 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0136310 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | No | No | 1990374 | 0 | EPSS Ckt | N | 2024 | A- B- GRD SGF
KERN | KERN | BLACKWELL-1102 | 254681102 | OCB | 1102/2 | 20241117 | 1431 | 20241117 | 1635 | 2627547 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1488 | 35.6142 | -119.8539 | No | Clear;32-90 F | Crossarm- Wood | Normal | 24-0136340 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990401 | 0 | Non-EPSS | N | 2024 | B- C TIME OC
KERN | KERN | GOOSE LAKE-1106 | 254201106 | FUSE | 7094 | 20241118 | 736 | 20241118 | 1351 | 2627854 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 5408 | 35.5191 | -119.5464 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0136508 | OH | Sus | 31717880 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990640 | 0 | Non-EPSS | N | 2024
KERN | KERN | WEEDPATCH-1102 | 252971102 | OTHER | T12753 TWD T12754 | 20241118 | 904 | 20241118 | 1234 | 2628078 | 210 | Distribution Circuit | Equipment Failure/Involved | Underground | 70 | 6900 | 35.191 | -118.8412 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0129924 | UG | Sus | 35593788 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990586 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | FUSE | 8486 | 20241118 | 942 | 20241118 | 1020 | 2628121 | 38 | Distribution Circuit | Animal | Bird found | 57 | 2166 | 35.3212 | -119.0095 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0136496 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990630 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 46905 | 20241118 | 1559 | 20241118 | 1608 | 2628463 | 9 | Distribution Circuit | Animal | Other | 14 | 126 | 35.2597 | -119.0305 | No | Clear;32-90 F | Fuse | Normal | 24-0136763 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990728 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1118 | 253371118 | FUSE | 9891 | 20241118 | 1632 | 20241118 | 1823 | 2628556 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 14541 | 35.405 | -119.0301 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0136757 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990725 | 0 | Non-EPSS | N | 2024
KERN | KERN | CHARCA-1106 | 254501106 | FUSE | 13978 | 20241118 | 1910 | 20241119 | 15 | 2628687 | 305 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 6 | 1830 | 35.5921 | -119.331 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0136795 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990748 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1103 | 253911103 | FUSE | 13028 | 20241118 | 2155 | 20241118 | 2306 | 2628724 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 1847 | 35.256 | -118.91 | No | Clear;32-90 F |  |  | 24-0136815 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990763 | 1 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-2104 | 254202104 | JUMPER | OJ 1 S/OF 003374 @ LINE & BUCK | 20241119 | 317 | 20241119 | 443 | 2628770 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 725 | 61214 | 35.6014 | -119.69 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0136825 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1990773 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | 516592268811 | 20241119 | 806 | 20241119 | 1306 | 2628865 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 600 | 35.3853 | -119.1444 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0136896 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990798 | 0 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1106 | 253951106 | TRANSFORMER | T5928 | 20241119 | 857 | 20241120 | 158 | 2628996 | 1021 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 6126 | 35.3977 | -118.9525 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0137059 | OH | Sus | 46393907 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991008 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | TRANSFORMER | 517325763920 | 20241119 | 1029 | 20241120 | 0 | 2629201 | 811 | Transformer only | Animal | Bird found | 1 | 811 | 35.2529 | -118.8966 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0137037 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991004 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1104 | 253701104 | TRANSFORMER | 516929768689 | 20241119 | 1110 | 20241119 | 1732 | 2629311 | 381 | Transformer only | Vegetation | Tree - bark fell into line | 5 | 1845 | 35.3828 | -119.031 | No | Clear;32-90 F | Transformer | Broken | 24-0137125 | OH | Sus | 46391479 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991027 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | FUSE | 13107 | 20241119 | 1523 | 20241119 | 1715 | 2629545 | 112 | Distribution Circuit | Animal | Squirrel | 33 | 3176 | 35.6459 | -118.9796 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0137307 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1991079 | 0 | EPSS Ckt | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | OTHER | T13625 TWD T13627 | 20241119 | 1952 | 20241119 | 2050 | 2629828 | 58 | Distribution Circuit | Equipment Failure/Involved | Underground | 69 | 4002 | 35.295 | -119.0018 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0137225 | UG | Sus | 35598812 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991116 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 8805 | 20241119 | 2232 | 20241120 | 330 | 2629904 | 298 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 3444 | 35.3836 | -119.2021 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0137393 | UG | Sus | 35598856 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991133 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | FUSE | 8804 | 20241119 | 2305 | 20241119 | 2321 | 2629924 | 16 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 352 | 35.3836 | -119.2 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0137393 | UG | Sus | 35598856 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991142 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | 516925069561 | 20241120 | 1245 | 20241120 | 1603 | 2630964 | 195 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1950 | 35.4069 | -119.0326 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0137735 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991422 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1103 | 252721103 | TRANSFORMER | 516928169724 | 20241120 | 1945 | 20241120 | 2129 | 2631842 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 2080 | 35.4114 | -119.0316 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0138064 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991611 | 0 | Non-EPSS | N | 2024
KERN | KERN | MCKITTRICK-1101 | 252781101 | FUSE | 1686 | 20241121 | 823 | 20241121 | 955 | 2632388 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 614 | 35.3125 | -119.7135 | No | Clear;32-90 F |  |  | 24-0138323 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991799 | 1 | EPSS Ckt | N | 2024
KERN | KERN | WEEDPATCH-1101 | 252971101 | TRANSFORMER | 517409362571 | 20241121 | 910 | 20241122 | 147 | 2632466 | 997 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 997 | 35.2162 | -118.8676 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0138383 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991828 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1116 | 252721116 | OCB | 1116/2 | 20241121 | 942 | 20241122 | 525 | 2632517 | 1183 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1024 | 121904 | 35.4407 | -119.0206 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0138303 | UG | Sus | 31718092 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991783 | 0 | Non-EPSS | N | 2024 | C GRD TIME OC
KERN | KERN | SMYRNA-1104 | 253551104 | FUSE | 7290 | 20241121 | 1524 | 20241122 | 31 | 2632933 | 547 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 6 | 3282 | 35.7792 | -119.4634 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0138569 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1991906 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | JUMPER | OJ 3 E/ OF CGC 517097559045 | 20241121 | 1900 | 20241122 | 305 | 2633298 | 485 | Distribution Circuit | 3rd Party | Vehicle | 1 | 485 | 35.1187 | -118.9676 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0138675 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991943 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | SWITCH | 5449 | 20241121 | 2302 | 20241122 | 123 | 2633663 | 141 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 2679 | 35.1441 | -119.4685 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0138552 | UG | Sus | 35599282 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991979 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | JUMPER | CHANCE CLAMPS @ 16811 | 20241122 | 100 | 20241122 | 1115 | 2633697 | 615 | Distribution Circuit | 3rd Party | Vehicle | 1 | 615 | 35.3503 | -118.9823 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0138739 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991986 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | RECLOSER | 39520 | 20241122 | 226 | 20241122 | 233 | 2633772 | 7 | Distribution Circuit | Equipment Failure/Involved | Underground | 376 | 2632 | 35.1397 | -119.4626 | No | Clear;32-90 F | Elbow | Broken | 24-0138753 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992000 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 14527 | 20241122 | 825 | 20241122 | 912 | 2634042 | 47 | Distribution Circuit | Animal | Bird found | 74 | 3478 | 35.3577 | -118.9499 | No | Clear;32-90 F | Fuse | Burned Open | 24-0138848 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992078 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 14574 | 20241122 | 1157 | 20241122 | 1930 | 2634456 | 453 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2115 | 35.369 | -119.43 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0139030 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992166 | 1 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | FUSE | 443122 | 20241122 | 1432 | 20241122 | 1600 | 2634843 | 88 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 88 | 35.2949 | -119.0029 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0122768 | UG | Sus | 35545393 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992202 | 1 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1110 | 252901110 | TRANSFORMER | T5494 | 20241122 | 1533 | 20241122 | 1940 | 2635020 | 247 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 247 | 35.6012 | -119.3496 | No | Partly Cloudy;32-90 F |  |  | 24-0139286 | UG | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1992296 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2103 | 254242103 | FUSE | 1686 | 20241122 | 1605 | 20241122 | 1820 | 2634618 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 900 | 35.3125 | -119.7135 | No | Clear;32-90 F |  |  | 24-0139236 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992260 | 1 | EPSS Ckt | N | 2024
KERN | KERN | TEVIS-2101 | 255322101 | FUSE | 13115 | 20241122 | 1705 | 20241122 | 1959 | 2635069 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1740 | 35.2733 | -119.1639 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0139206 | OH | Sus | 46399164 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992238 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1118 | 253371118 | TRANSFORMER | 516955969640 | 20241122 | 2146 | 20241122 | 2351 | 2635521 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 500 | 35.4091 | -119.0223 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0139314 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992322 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1104 | 252771104 | TRANSFORMER | 517306768623 | 20241123 | 753 | 20241123 | 954 | 2635944 | 121 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 242 | 35.3827 | -118.9037 | No | Overcast-Rain;32-90 F |  |  | 24-0139479 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1992478 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20241123 | 801 | 20241123 | 940 | 2635959 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 3267 | 35.6271 | -118.9849 | No | Overcast;32-90 F |  |  | 24-0139431 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992435 | 0 | EPSS Ckt | Y | 2024 | B & GRD INST
KERN | KERN | RIO BRAVO-1102 | 252861102 | TRANSFORMER | 516105572497 | 20241123 | 836 | 20241123 | 1432 | 2635928 | 356 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 356 | 35.4849 | -119.3089 | No | Overcast;32-90 F | Transformer | Contaminated | 24-0139445 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992452 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | TRANSFORMER | 517009568338 | 20241123 | 905 | 20241123 | 1050 | 2636081 | 105 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 630 | 35.3738 | -119.0036 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0139507 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1992499 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2104 | 253642104 | OCB | 2104/2 | 20241123 | 937 | 20241123 | 1100 | 2636147 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1494 | 35.5593 | -118.9576 | No | Overcast;32-90 F | Jumper | Burned/flashed | 24-0139468 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992471 | 0 | EPSS Ckt | Y | 2024 | NONE
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 13335 | 20241123 | 1424 | 20241123 | 1534 | 2636471 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 420 | 35.0769 | -118.9757 | No | Overcast-Fog;32-90 F |  |  | 24-0139581 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992553 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ARVIN-1103 | 253801103 | FUSE | 13313 | 20241124 | 852 | 20241124 | 1010 | 2636925 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 702 | 35.1219 | -118.9145 | No | Clear;32-90 F |  |  | 24-0139681 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992634 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 18300 | 20241124 | 1403 | 20241124 | 1520 | 2637067 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 770 | 35.076 | -118.9578 | No | Partly Cloudy;32-90 F |  |  | 24-0139734 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992668 | 0 | EPSS Ckt | N | 2024
KERN | KERN | MCKITTRICK-1101 | 252781101 | FUSE | 1686 | 20241125 | 619 | 20241125 | 1428 | 2637415 | 489 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 3262 | 35.3125 | -119.7135 | No | Overcast-Rain;32-90 F |  |  | 24-0139966 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992765 | 1 | EPSS Ckt | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20241125 | 1154 | 20241125 | 1420 | 2637677 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1071 | 35.4767 | -119.5887 | No | Clear;32-90 F |  |  | 24-0140067 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992802 | 1 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 18300 | 20241125 | 1258 | 20241125 | 1434 | 2637759 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 960 | 35.076 | -118.9578 | No | Overcast-Fog;32-90 F |  |  | 24-0140078 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992803 | 0 | EPSS Ckt | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | TRANSFORMER | 516338861883 | 20241125 | 1430 | 20241126 | 202 | 2637775 | 692 | Transformer only | 3rd Party | Other | 1 | 692 | 35.1945 | -119.2265 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0140098 | OH | Sus | 31718605 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992814 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | FUSE | 15916 | 20241125 | 1543 | 20241125 | 1606 | 2637898 | 23 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 2116 | 35.3707 | -118.9322 | No | Overcast;32-90 F | Secondary | Normal | 24-0140104 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992817 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20241125 | 1605 | 20241126 | 1131 | 2637930 | 1166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 38478 | 35.6271 | -118.9849 | No | Overcast-Fog;32-90 F |  |  | 24-0140122 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992824 | 0 | EPSS Ckt | N | 2024 | B- GRD- INST
KERN | KERN | MC FARLAND-1104 | 253181104 | TRIP-SAVER | 956589 | 20241125 | 1740 | 20241126 | 1007 | 2638006 | 987 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 6909 | 35.66 | -119.1162 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0140193 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992849 | 1 | Non-EPSS | N | 2024 | #2
KERN | KERN | STOCKDALE-1106 | 254071106 | JUMPER | OPEN JUMPER 1/2 SPAN SE/ OF 14063 | 20241125 | 1843 | 20241125 | 1937 | 2638079 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 1350 | 35.3374 | -119.0433 | No | Overcast-Fog-Drizzle;32-90 F | Jumper | Burned Open | 24-0140189 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1992848 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1114 | 253371114 | FUSE | 20180 | 20241126 | 311 | 20241126 | 842 | 2638198 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 25818 | 35.3721 | -118.9631 | No | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Burned/flashed | 24-0140228 | OH | Sus | 31718631 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992881 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1116 | 253371116 | FUSE | 14320 | 20241126 | 327 | 20241126 | 1215 | 2638205 | 528 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 27456 | 35.4031 | -118.9664 | No | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Burned/flashed | 24-0140231 | OH | Sus | 31718632 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992885 | 0 | Non-EPSS | N | 2024
KERN | KERN | NORCO-1101 | 254691101 | RECLOSER | 3938 | 20241126 | 504 | 20241127 | 1818 | 2638223 | 2234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 36650 | 35.3096 | -119.2886 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0140230 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992884 | 0 | Non-EPSS | N | 2024 | C- GRD
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 9785 | 20241126 | 507 | 20241127 | 320 | 2638221 | 1333 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 15 | 19995 | 35.3261 | -118.8074 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Burned/flashed | 24-0140541 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993034 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | TUPMAN-1105 | 254561105 | TRANSFORMER | 516214466679 | 20241126 | 510 | 20241127 | 1059 | 2638224 | 1789 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1789 | 35.3255 | -119.2702 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0140568 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993039 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | TRANSFORMER | 517006064095 | 20241126 | 542 | 20241127 | 700 | 2638236 | 1518 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4554 | 35.2568 | -119.0036 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0140375 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992980 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1101 | 252821101 | RECLOSER | 3570 | 20241126 | 650 | 20241126 | 1517 | 2638281 | 507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 7605 | 35.179 | -119.1461 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0140250 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992895 | 0 | Non-EPSS | N | 2024 | A-B
KERN | KERN | STOCKDALE-1109 | 254071109 | FUSE | 8699 | 20241126 | 654 | 20241128 | 849 | 2638268 | 2995 | Distribution Circuit | Equipment Failure/Involved | Underground | 193 | 471102 | 35.3067 | -119.0566 | No | Overcast-Fog-Rain;32-90 F | Conductor- Underground | Broken | 24-0140306 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992927 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 955101 | 20241126 | 700 | 20241126 | 857 | 2638271 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 11856 | 35.3649 | -118.9667 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Burned/flashed | 24-0140316 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992933 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517113068123 | 20241126 | 722 | 20241126 | 1141 | 2638303 | 259 | Transformer only | Animal | Bird found | 9 | 2331 | 35.3687 | -118.9686 | No | Overcast-Fog-Rain;32-90 F | Fuse | Broken | 24-0140463 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993004 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | RECLOSER | 1689 | 20241126 | 745 | 20241126 | 1634 | 2638344 | 529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 903 | 42149 | 35.3028 | -119.0029 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Burned/flashed | 24-0140276 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992903 | 0 | Non-EPSS | N | 2024 | NA
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 516923056719 | 20241126 | 745 | 20241126 | 1227 | 2638343 | 282 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 282 | 35.055 | -119.0293 | No | Clear;32-90 F |  |  | 24-0140493 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1993018 | 0 | EPSS Ckt | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | TRANSFORMER | 517137369524 | 20241126 | 805 | 20241126 | 1201 | 2638366 | 236 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 3068 | 35.4066 | -118.9612 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0140483 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1993012 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1105 | 254561105 | TRANSFORMER | 516162367472 | 20241126 | 809 | 20241126 | 1753 | 2638225 | 584 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 584 | 35.3469 | -119.2881 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0140510 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993026 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | OCB | 1104/2 | 20241126 | 1028 | 20241126 | 1037 | 2638373 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 408 | 3672 | 35.3531 | -119.271 | No | Clear;32-90 F | Insulator | Arcing | 24-0140411 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992991 | 0 | Non-EPSS | N | 2024 | A-C- TIME
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 516149267899 | 20241126 | 1116 | 20241126 | 1759 | 2638638 | 403 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 403 | 35.3588 | -119.2925 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0140478 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993010 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | OCB | 1102/2 | 20241126 | 1328 | 20241126 | 1911 | 2638750 | 343 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 173 | 59339 | 35.2249 | -118.7784 | No | Overcast-Fog;32-90 F |  |  | 24-0140648 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993057 | 0 | EPSS Ckt | N | 2024 | B & C
KERN | KERN | COPUS-1104 | 253871104 | TRANSFORMER | 516313557055 | 20241126 | 1545 | 20241128 | 1110 | 2638844 | 2605 | Transformer only | Animal | Other | 2 | 5210 | 35.062 | -119.2338 | No | Overcast-Fog;32-90 F | Transformer (OH) | Burned/flashed | 24-0140628 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993052 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1102 | 252861102 | TRANSFORMER | 516182572558 | 20241126 | 1611 | 20241127 | 2349 | 2638867 | 1898 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1898 | 35.4868 | -119.2829 | No | Overcast-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0140731 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993088 | 0 | Non-EPSS | N | 2024
KERN | KERN | PANAMA-2102 | 253422102 | TRANSFORMER | 517211865446 | 20241126 | 1655 | 20241126 | 1705 | 2638828 | 10 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 10 | 35.2947 | -118.9352 | No | Clear;32-90 F |  |  | 24-0140660 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1993060 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | TRANSFORMER | 517053868387 | 20241126 | 1902 | 20241127 | 717 | 2638966 | 735 | Transformer only | Equipment Failure/Involved | Underground | 4 | 2940 | 35.3753 | -118.9887 | No | Rain-Overcast-Fog;32-90 F | Transformer | Broken | 24-0140682 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1993063 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | RECLOSER | 4113 | 20241126 | 2047 | 20241128 | 352 | 2638994 | 1865 | Distribution Circuit | 3rd Party | Vehicle | 108 | 42624 | 35.312 | -118.843 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0140700 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1993070 | 0 | EPSS Ckt | N | 2024 | SGF
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | FUSE | 967375 | 20241127 | 836 | 20241127 | 1842 | 2639189 | 606 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 4850 | 35.1018 | -119.0391 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0140892 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993155 | 1 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20241127 | 1253 | 20241127 | 1428 | 2639439 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1045 | 35.4767 | -119.5887 | No | Clear;32-90 F |  |  | 24-0141068 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993187 | 0 | Non-EPSS | N | 2024
KERN | KERN | WASCO-1104 | 252961104 | FUSE | 19937 | 20241127 | 1456 | 20241128 | 1115 | 2639520 | 1219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 42168 | 35.5939 | -119.3448 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141120 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993200 | 1 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20241127 | 1511 | 20241127 | 1812 | 2639525 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1328 | 35.4767 | -119.5887 | No | Partly Cloudy;32-90 F |  |  | 24-0141154 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993209 | 1 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | OCB | 1103/2 | 20241127 | 1512 | 20241128 | 1217 | 2639547 | 1265 | Distribution Circuit | 3rd Party | Vehicle | 1621 | 87265 | 35.3777 | -119.0927 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0141115 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | Yes | No | 1993198 | 0 | Non-EPSS | N | 2024 | A/B/C/GRD
KERN | KERN | WESTPARK-1102 | 253701102 | SWITCH | 5693 | 20241127 | 1525 | 20241127 | 1826 | 2638612 | 181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 588 | 35.3725 | -119.0254 | No | Overcast;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0140621 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1993197 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 516949757531 | 20241127 | 2125 | 20241128 | 1133 | 2639710 | 848 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 848 | 35.0765 | -119.0212 | No | Clear;32-90 F | Fuse | Broken | 24-0141204 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993247 | 0 | EPSS Ckt | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20241128 | 1406 | 20241128 | 1531 | 2639893 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 935 | 35.4767 | -119.5887 | No | Clear;32-90 F |  |  | 24-0141224 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993270 | 0 | Non-EPSS | N | 2024
KERN | KERN | RIO BRAVO-1101 | 252861101 | FUSE | 18127 | 20241128 | 1952 | 20241128 | 2055 | 2639971 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 315 | 35.4598 | -119.2612 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0141235 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993282 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514885169624 | 20241129 | 639 | 20241129 | 1304 | 2640032 | 385 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 385 | 35.4007 | -119.7169 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141255 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993300 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2104 | 253372104 | FUSE | 124213 | 20241129 | 814 | 20241129 | 927 | 2640074 | 73 | Distribution Circuit | Animal | Bird found | 1 | 73 | 35.3203 | -119.0028 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0141263 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993308 | 0 | Non-EPSS | N | 2024
KERN | KERN | GOOSE LAKE-1103 | 254201103 | FUSE | 229025 | 20241129 | 841 | 20241129 | 1138 | 2640088 | 177 | Distribution Circuit | Animal | Bird found | 7 | 1299 | 35.4767 | -119.5887 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0141281 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993323 | 1 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1107 | 253701107 | TRANSFORMER | 516865668599 | 20241129 | 1043 | 20241129 | 1115 | 2640161 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 32 | 35.3806 | -119.0524 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0141275 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1993317 | 0 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1105 | 253181105 | FUSE | 673501 | 20241129 | 1147 | 20241129 | 1536 | 2640196 | 229 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 4580 | 35.7178 | -119.2942 | No | Overcast;32-90 F |  |  | 24-0141302 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993335 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | TRANSFORMER | 515361779093 | 20241129 | 1654 | 20241129 | 1710 | 2640299 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 16 | 35.6633 | -119.5598 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0141313 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993344 | 0 | Non-EPSS | N | 2024
KERN | KERN | WESTPARK-1101 | 253701101 | TRANSFORMER | 516947167830 | 20241130 | 456 | 20241130 | 628 | 2640463 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 960 | 35.3594 | -119.0247 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Broken | 24-0141348 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1993370 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2108 | 254072108 | FUSE | 16710 | 20241201 | 610 | 20241201 | 1255 | 2640949 | 405 | Distribution Circuit | Equipment Failure/Involved | Underground | 94 | 38070 | 35.318 | -119.0946 | No | Partly Cloudy-Fog;32-90 F | Elbow | Failed/Faulted | 24-0141477 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1993454 | 0 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2103 | 254582103 | RECLOSER | 1381 | 20241201 | 1208 | 20241201 | 1718 | 2641099 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 2731 | 35.4429 | -119.1366 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0141514 | OH | Sus | 46402524 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1993481 | 0 | Non-EPSS | N | 2024 | A- GRD- SGF
KERN | KERN | MAGUNDEN-2109 | 252772109 | FUSE | 13948 | 20241201 | 1740 | 20241201 | 2252 | 2641182 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 11856 | 35.3649 | -118.9683 | No | Clear;32-90 F | Secondary | Broken- wire on object | 24-0141556 | OH | Sus | 46402564 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | Yes | 1993504 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | FUSE | 13599 | 20241202 | 603 | 20241202 | 2159 | 2641310 | 956 | Distribution Circuit | Equipment Failure/Involved | Underground | 92 | 27601 | 35.3752 | -119.1099 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0141625 | UG | Sus | 31718965 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1993550 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1102 | 253551102 | RECLOSER | 793576 | 20241202 | 716 | 20241202 | 1245 | 2641368 | 329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2313 | 35.7001 | -119.4907 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0141609 | OH | Sus | 31719046 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1993544 | 0 | Non-EPSS | N | 2024 | A C TIME
KERN | KERN | TUPMAN-1104 | 254561104 | FUSE | 18393 | 20241202 | 820 | 20241202 | 945 | 2641441 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 454 | 35.4234 | -119.3763 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0141692 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1993704 | 1 | Non-EPSS | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | SWITCH | 794945 | 20241202 | 1107 | 20241202 | 1739 | 2641453 | 392 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 12 | 4704 | 35.7309 | -119.8587 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0141718 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1993723 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1104 | 253551104 | FUSE | 7290 | 20241202 | 1526 | 20241203 | 400 | 2642213 | 754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 4524 | 35.7792 | -119.4634 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0141925 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1993812 | 0 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1103 | 253801103 | FUSE | 18536 | 20241202 | 1559 | 20241203 | 35 | 2642254 | 516 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 516 | 35.1439 | -118.9132 | No | Clear;32-90 F | Insulator | Broken | 24-0141908 | OH | Sus | 46402992 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1993804 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1113 | 253491113 | RECLOSER | 137668 | 20241203 | 926 | 20241203 | 958 | 2642785 | 32 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 96 | 35.5876 | -119.2034 | No | Partly Cloudy;32-90 F | Regulator | Malfunctioning | 24-0003562 | OH | Sus | 74002944 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1994037 | 0 | Non-EPSS | N | 2024 | 3
KERN | KERN | LERDO-1113 | 253491113 | RECLOSER | 137668 | 20241203 | 1009 | 20241203 | 1023 | s1994479 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 3 | 42 | 35.5876 | -119.2034 | No | Partly Cloudy;32-90 F | Regulator | Malfunctioning | 24-0003562 | OH | Sus | 74002944 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1994479 | 0 | Non-EPSS | N | 2024 | 3
KERN | KERN | LERDO-1113 | 253491113 | RECLOSER | 137668 | 20241203 | 1036 | 20241203 | 1216 | 2642847 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 300 | 35.5876 | -119.2034 | No | Partly Cloudy;32-90 F | Regulator | Malfunctioning | 24-0003562 | OH | Sus | 74002944 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1994056 | 0 | Non-EPSS | N | 2024 | 3
KERN | KERN | OLD RIVER-1105 | 252821105 | TRANSFORMER | 516582263709 | 20241203 | 1624 | 20241203 | 1646 | 2643144 | 22 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 22 | 35.2452 | -119.1455 | No | Clear;32-90 F |  |  | 24-0142281 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1994147 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1110 | 252901110 | TRANSFORMER | 515937575485 | 20241203 | 1948 | 20241203 | 2234 | 2643300 | 166 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 332 | 35.5665 | -119.3673 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0142327 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994164 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1109 | 252721109 | TRANSFORMER | 516881669958 | 20241203 | 2225 | 20241204 | 158 | 2643344 | 213 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2769 | 35.4177 | -119.0473 | No | Clear;32-90 F | Woodpin | Broken | 24-0142329 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1994190 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | OCB | 1106/2 | 20241203 | 2338 | 20241204 | 1051 | 2643362 | 673 | Distribution Circuit | 3rd Party | Vehicle | 150 | 28734 | 35.3531 | -119.2709 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0142338 | OH | Sus | 31719183 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1994178 | 0 | Non-EPSS | N | 2024 | B- C- TIME OC
KERN | KERN | SHAFTER-1112 | 253651112 | FUSE | 3677 | 20241204 | 617 | 20241204 | 840 | 2643420 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2003 | 35.5299 | -119.3943 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0142416 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994288 | 1 | Non-EPSS | N | 2024
KERN | KERN | COLUMBUS-1105 | 253951105 | TRANSFORMER | T0076 | 20241204 | 1434 | 20241204 | 1533 | 2644106 | 59 | Transformer only | Equipment Failure/Involved | Underground | 6 | 354 | 35.4106 | -118.9577 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0142659 | UG | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1994519 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2105 | 254572105 | TRANSFORMER | T8052 | 20241204 | 1647 | 20241204 | 1728 | 2644187 | 41 | Transformer only | 3rd Party | Dig in- 3rd party | 12 | 492 | 35.4073 | -119.124 | No | Clear;32-90 F | Metering Equipment | Broken | 24-0142704 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994531 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1105 | 254071105 | FUSE | 9301 | 20241204 | 2102 | 20241205 | 121 | 2644287 | 259 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 259 | 35.3129 | -119.0574 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0142743 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1994543 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-1106 | 253371106 | RECLOSER | 2723 | 20241205 | 46 | 20241205 | 1245 | 2644324 | 719 | Distribution Circuit | Equipment Failure/Involved | Underground | 386 | 45598 | 35.3903 | -118.9829 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0142757 | UG | Sus | 46404179 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994558 | 0 | Non-EPSS | N | 2024 | A/GRD
KERN | KERN | ARVIN-1102 | 253801102 | FUSE | 705869 | 20241205 | 1159 | 20241205 | 1425 | 2645224 | 146 | Distribution Circuit | 3rd Party | Vehicle | 1 | 146 | 35.1579 | -118.8952 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0143021 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1994862 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | FUSE | 2396 | 20241205 | 1236 | 20241205 | 1601 | 2645067 | 205 | Distribution Circuit | Equipment Failure/Involved | Underground | 37 | 7585 | 35.1401 | -119.4683 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0142776 | UG | Sus | 35603112 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1994831 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1104 | 252721104 | OCB | 1104/2 | 20241205 | 2339 | 20241206 | 556 | 2645493 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 192 | 38449 | 35.4407 | -119.0204 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 24-0143179 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994941 | 0 | EPSS Ckt | N | 2024 | GRD SGF INST
KERN | KERN | SEMITROPIC-1112 | 252901112 | FUSE | 87100 | 20241206 | 6 | 20241206 | 1350 | 2645498 | 824 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 5768 | 35.6304 | -119.4561 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken | 24-0143235 | OH | Sus | 31719192 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995051 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | TRANSFORMER | 517057861795 | 20241206 | 926 | 20241206 | 2353 | 2645772 | 867 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 867 | 35.1941 | -118.9859 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143307 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995149 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | OCB | 1102/2 | 20241206 | 940 | 20241206 | 1244 | 2645789 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 173 | 31832 | 35.2249 | -118.7784 | No | Clear;32-90 F |  |  | 24-0143306 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995146 | 0 | EPSS Ckt | N | 2024 | INST- B
KERN | KERN | ROSEDALE-1101 | 254761101 | FUSE | 8232 | 20241206 | 952 | 20241206 | 2155 | 2645801 | 723 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 723 | 35.4121 | -119.0623 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0143299 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995145 | 1 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1103 | 253801103 | TRANSFORMER | 517255059154 | 20241206 | 1059 | 20241206 | 1320 | 2645897 | 141 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 141 | 35.1219 | -118.9192 | No | Clear;32-90 F |  |  | 24-0143375 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1995181 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1103 | 254561103 | TRANSFORMER | 516218469190 | 20241206 | 1119 | 20241206 | 1622 | 2645749 | 303 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 303 | 35.3941 | -119.2697 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 24-0143333 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995158 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1104 | 252611104 | FUSE | 7370 | 20241206 | 1210 | 20241206 | 1332 | 2645980 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 984 | 35.3691 | -119.4688 | No | Clear;32-90 F |  |  | 24-0143378 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995183 | 0 | Non-EPSS | N | 2024
KERN | KERN | ARVIN-1102 | 253801102 | FUSE | 849153 | 20241206 | 1800 | 20241206 | 1908 | 2646201 | 68 | Distribution Circuit | Animal | Other | 1 | 68 | 35.1757 | -118.9054 | No | Clear;32-90 F | Pothead(Riser Termination) | Contaminated | 24-0143481 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995215 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | JUMPER | OJ @ 14988 | 20241207 | 101 | 20241207 | 1247 | 2646282 | 706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 11296 | 35.3106 | -118.9326 | No | Clear;32-90 F | Jumper | Burned Open | 24-0143515 | OH | Sus | 46405497 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1995239 | 1 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | MTR#1010147949 | 20241207 | 948 | 20241207 | 1049 | 2646459 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 244 | 35.3991 | -119.3164 | No | Partly Cloudy;32-90 F |  |  | 24-0143584 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1995342 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2101 | 255262101 | FUSE | 331549 | 20241207 | 1345 | 20241207 | 1503 | 2646610 | 78 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 702 | 35.3874 | -119.0963 | No | Clear;32-90 F | Fuse | Broken | 24-0143625 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995381 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2105 | 255262105 | TRANSFORMER | T8196 | 20241208 | 57 | 20241208 | 1415 | 2646763 | 798 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 8412 | 35.4017 | -119.1234 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0143656 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995410 | 0 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1104 | 253911104 | FUSE | 16539 | 20241208 | 418 | 20241208 | 2047 | 2646770 | 989 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 21 | 20769 | 35.3462 | -118.8667 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0143659 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1995413 | 0 | EPSS Ckt | N | 2024
KERN | KERN | RIO BRAVO-1106 | 252861106 | FUSE | 522365 | 20241208 | 952 | 20241208 | 1020 | 2646904 | 28 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 84 | 35.4418 | -119.2853 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0143698 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995474 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | 517395548553 | 20241208 | 2358 | 20241209 | 146 | 2647178 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 216 | 34.8316 | -118.8688 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0143782 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1995535 | 0 | EPSS Ckt | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 7496 | 20241209 | 346 | 20241209 | 945 | 2647203 | 359 | Distribution Circuit | 3rd Party | Vehicle | 9 | 3231 | 35.507 | -119.2588 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0143794 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995548 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1105 | 252821105 | RECLOSER | 684892 | 20241209 | 928 | 20241209 | 1244 | 2647573 | 196 | Distribution Circuit | Animal | Other | 32 | 6272 | 35.2104 | -119.1461 | No | Clear;32-90 F | Metering Equipment | Burned/flashed | 24-0143862 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1995706 | 0 | Non-EPSS | N | 2024 | ABC TIME OC
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | FUSE | 4016 | 20241209 | 1205 | 20241209 | 1317 | 2647769 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 72 | 35.5582 | -118.9445 | No | Clear;32-90 F |  |  | 24-0143956 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995801 | 1 | EPSS Ckt | N | 2024
KERN | KERN | CHARCA-1102 | 254501102 | OCB | 1102/2 | 20241209 | 1236 | 20241209 | 1339 | 2647797 | 63 | Distribution Circuit | Animal | Other | 284 | 14352 | 35.6081 | -119.3255 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0143932 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995782 | 0 | Non-EPSS | N | 2024 | AC INST OC
KERN | KERN | MC FARLAND-1104 | 253181104 | TRANSFORMER | 516262978850 | 20241209 | 1417 | 20241209 | 2210 | 2647810 | 473 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 473 | 35.66 | -119.2589 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143968 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995814 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | FUSE | 14544 | 20241209 | 1435 | 20241209 | 2330 | 2647947 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 650 | 35.2306 | -119.0739 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143987 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995831 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | RECLOSER | 1146 | 20241209 | 1851 | 20241209 | 1954 | 2648052 | 63 | Distribution Circuit | 3rd Party | Vehicle | 879 | 55377 | 35.3676 | -119.1809 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Normal | 24-0144032 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995854 | 0 | Non-EPSS | N | 2024 | B C
KERN | KERN | TEJON-1102 | 252931102 | SWITCH | 4782 | 20241209 | 2000 | 20241210 | 1859 | 2648125 | 1379 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 525 | 723975 | 34.8602 | -118.8819 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143773 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1995859 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 20241209 | 2001 | 20241210 | 1659 | s1995861 | 1258 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 41 | 51578 | 34.8817 | -118.9019 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143773 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1995861 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 3751 | 20241209 | 2003 | 20241210 | 1658 | s1995862 | 1255 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 51 | 64005 | 34.9321 | -118.9283 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143773 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1995862 | 0 | EPSS Ckt | N | 2024 | NA
KERN | KERN | LAMONT-1104 | 253911104 | SWITCH | 809792 | 20241209 | 2046 | 20241210 | 1653 | 2648149 | 1207 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 6035 | 35.334 | -118.7348 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143771 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1995865 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TWISSELMAN-2105 | 254402105 | FUSE | 13898 | 20241210 | 731 | 20241210 | 935 | 2648352 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 124 | 35.6882 | -119.763 | No | Clear;32-90 F |  |  | 24-0144140 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1996135 | 1 | Non-EPSS | N | 2024
KERN | KERN | LAMONT-1102 | 253911102 | OTHER | 8172 | 20241210 | 1328 | 20241210 | 2000 | 2648943 | 392 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 13368 | 35.288 | -118.9145 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0143827 | UG | Sus | 35593167 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1996219 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1106 | 253701106 | JUMPER | FB 2 W/OF 1828 | 20241211 | 818 | 20241211 | 1357 | 2649369 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 6102 | 35.3758 | -119.0303 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0144096 | OH | Sus | 35603417 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1996361 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1103 | 253391103 | TRANSFORMER | 516676868559 | 20241211 | 946 | 20241211 | 1410 | 2649582 | 264 | Transformer only | Unknown Cause | Patrol - not conducted | 6 | 1584 | 35.3785 | -119.1156 | No | Overcast;32-90 F |  |  | 24-0144371 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1996496 | 0 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1116 | 253491116 | FUSE | 18387 | 20241211 | 1434 | 20241211 | 1852 | 2649957 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 516 | 35.5296 | -119.1716 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 24-0144447 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1996599 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1104 | 252821104 | OTHER | WIRE DOWN 2 W/OF CGC 516619363442 | 20241211 | 1740 | 20241212 | 240 | 2650203 | 540 | Distribution Circuit | 3rd Party | Vehicle | 878 | 6336 | 35.2381 | -119.133 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on object | 24-0144492 | OH | Sus | 35605187 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | Yes | 1996633 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241211 | 1901 | 20241211 | 2009 | 2650209 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2176 | 35.3618 | -119.1627 | No | Clear;32-90 F |  |  | 24-0144504 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1996644 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 730862 | 20241212 | 1022 | 20241212 | 1209 | 2650799 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 3531 | 35.6271 | -118.9849 | No | Overcast;32-90 F |  |  | 24-0144605 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1996846 | 0 | EPSS Ckt | N | 2024 | B- GRD- INST OC
KERN | KERN | MCKITTRICK-1101 | 252781101 | JUMPER | BURNED OPEN JPR 2P E/OF 9166 | 20241213 | 1207 | 20241213 | 1618 | 2651874 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 251 | 35.2998 | -119.6299 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0144885 | OH | Sus | 46417798 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1997185 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1111 | 253701111 | TRANSFORMER | 516882167730 | 20241213 | 1413 | 20241213 | 1502 | 2652010 | 49 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 245 | 35.3565 | -119.0466 | No | Clear;32-90 F |  |  | 24-0144900 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1997199 | 0 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2103 | 254582103 | FUSE | 15895 | 20241213 | 2310 | 20241214 | 1351 | 2652468 | 881 | Distribution Circuit | 3rd Party | Vehicle | 1252 | 71136 | 35.438 | -119.1097 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0145005 | OH | Sus | 35605654 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1997310 | 1 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2102 | 254582102 | OCB | 2102/2/NORM | 20241214 | 834 | 20241214 | 923 | 2655253 | 49 | Distribution Circuit | 3rd Party | Vehicle | 503 | 24647 | 35.4397 | -119.1313 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0145060 | OH | Sus | 31719984 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1997598 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | BLACKWELL-1102 | 254681102 | FUSE | 19261 | 20241214 | 857 | 20241214 | 1146 | 2655940 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 7267 | 35.6155 | -119.8544 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145604 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997928 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN POWER-2104 | 255262104 | FUSE | 8008 | 20241214 | 947 | 20241214 | 1049 | 2656797 | 62 | Distribution Circuit | Animal | Bird found | 80 | 4960 | 35.3491 | -119.0845 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0145532 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997856 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | RECLOSER | 1034 | 20241214 | 949 | 20241215 | 26 | 2656889 | 0 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 5543 | 35.3678 | -119.6851 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | On Ground | 24-0145409 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 1997731 | 0 | EPSS Ckt | N | 2024 | A- B- GRD
KERN | KERN | TWISSELMAN-2105 | 254402105 | OCB | 2105/2 | 20241214 | 1017 | 20241214 | 1359 | s1997954 | 222 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 152 | 27868 | 35.7305 | -119.8581 | Yes | Clear;32-90 F |  |  | 24-0145629 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997954 | 0 | Non-EPSS | N | 2024 | A- C- TIME
KERN | KERN | LAKEVIEW-1107 | 253411107 | TRANSFORMER | 516442456954 | 20241214 | 1036 | 20241214 | 2103 | 2657685 | 627 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 627 | 35.0589 | -119.1897 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 24-0146089 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998432 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | TRIP-SAVER | 9126 | 20241214 | 1108 | 20241215 | 1214 | 2660730 | 1506 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 49698 | 35.3913 | -119.703 | Yes | Partly Cloudy;32-90 F |  |  | 24-0146115 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 1998461 | 0 | EPSS Ckt | N | 2024 | NONE
KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 20241214 | 1117 | 20241214 | 1242 | 2658263 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 566 | 48110 | 34.8817 | -118.9019 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145573 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997896 | 0 | EPSS Ckt | Y | 2024 | B C
KERN | KERN | NORCO-1101 | 254691101 | FUSE | 49723 | 20241214 | 1135 | 20241214 | 2203 | 2660687 | 628 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 1256 | 35.3105 | -119.3178 | Yes | Partly Cloudy;32-90 F |  |  | 24-0146106 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998451 | 0 | Non-EPSS | N | 2024
KERN | KERN | TAFT-1104 | 252081104 | OTHER | HOT WIRE DOWN 2P S/OF 15444 | 20241214 | 1148 | 20241214 | 2257 | 2660186 | 669 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 32488 | 35.1324 | -119.4691 | Yes | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0145947 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | Yes | 1998277 | 1 | Non-EPSS | N | 2024
KERN | KERN | ELK HILLS-1104 | 252441104 | RECLOSER | 3522 | 20241214 | 1202 | 20241214 | 1809 | 2658664 | 367 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 149 | 54683 | 35.2297 | -119.3762 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145631 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997956 | 0 | Non-EPSS | N | 2024 | B C
KERN | KERN | LERDO-1111 | 253491111 | FUSE | 7573 | 20241214 | 1209 | 20241214 | 1315 | 2658896 | 66 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 26 | 1717 | 35.4852 | -119.243 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0145720 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998049 | 1 | Non-EPSS | N | 2024
KERN | KERN | LERDO-1112 | 253491112 | OCB | 1112/2 | 20241214 | 1213 | 20241214 | 1428 | 2658795 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 230 | 31050 | 35.5004 | -119.1519 | Yes | Overcast;32-90 F |  |  | 24-0145654 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997978 | 0 | Non-EPSS | N | 2024 | AC INST
KERN | KERN | LAKEVIEW-1102 | 253411102 | FUSE | 16169 | 20241214 | 1216 | 20241215 | 1045 | 2658802 | 1349 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 4047 | 35.0946 | -119.1072 | Yes | Clear;32-90 F |  |  | 24-0146239 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998611 | 0 | Non-EPSS | N | 2024
KERN | KERN | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20241214 | 1216 | 20241215 | 1226 | 2658818 | 1450 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 28029 | 35.5593 | -118.9575 | Yes | Overcast;32-90 F |  |  | 24-0145651 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997975 | 0 | EPSS Ckt | N | 2024 | AB
KERN | KERN | STOCKDALE-2110 | 254072110 | FUSE | 17107 | 20241214 | 1238 | 20241214 | 1618 | 2659040 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 110 | 23752 | 35.3339 | -119.0566 | Yes | Overcast;32-90 F |  |  | 24-0145872 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998206 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1102 | 252821102 | RECLOSER | 1646 | 20241214 | 1257 | 20241214 | 1427 | 2659149 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 248 | 22320 | 35.2097 | -119.0029 | Yes | Clear;32-90 F |  |  | 24-0145706 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998034 | 0 | Non-EPSS | N | 2024 | AC
KERN | KERN | ANTELOPE-1102 | 252021102 | OCB | 1102/2 | 20241214 | 1311 | 20241214 | 1600 | 2659220 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 112 | 13744 | 35.6579 | -119.9968 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0145731 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998061 | 0 | EPSS Ckt | N | 2024 | BC TIME
KERN | KERN | SMYRNA-1105 | 253551105 | RECLOSER | 98496 | 20241214 | 1730 | 20241215 | 1254 | 2660299 | 1164 | Distribution Circuit | 3rd Party | Vandalism | 15 | 5812 | 35.79 | -119.3924 | Yes | Partly Cloudy;32-90 F | Pole-Wood | On Ground | 24-0145975 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1998313 | 0 | Non-EPSS | N | 2024 | ABC
KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | 514938652977 | 20241214 | 2131 | 20241215 | 120 | 2660664 | 229 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1374 | 34.9436 | -119.6894 | Yes | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0146114 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998460 | 0 | EPSS Ckt | N | 2024
KERN | KERN | TAFT-1106 | 252081106 | FUSE | 58901 | 20241215 | 1333 | 20241215 | 1453 | 2661744 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 80 | 35.1512 | -119.4715 | No | Clear;32-90 F |  |  | 24-0146343 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998714 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 14684 | 20241215 | 1342 | 20241215 | 1641 | 2661658 | 179 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 1477 | 35.2091 | -119.249 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146369 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998739 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | TRANSFORMER | 514939269075 | 20241215 | 1523 | 20241215 | 1637 | 2661791 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 74 | 35.3865 | -119.6989 | No | Clear;32-90 F | Fuse | Broken | 24-0146382 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998751 | 0 | EPSS Ckt | N | 2024
KERN | KERN | WESTPARK-1103 | 253701103 | FUSE | 14899 | 20241215 | 1726 | 20241215 | 1745 | 2661985 | 19 | Distribution Circuit | 3rd Party | Kite | 99 | 1881 | 35.3498 | -119.0433 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146400 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1998764 | 0 | Non-EPSS | N | 2024
KERN | KERN | ANTELOPE-1102 | 252021102 | FUSE | 7060 | 20241216 | 22 | 20241216 | 229 | 2662265 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1355 | 35.6559 | -119.9389 | No | Partly Cloudy;32-90 F |  |  | 24-0146478 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998847 | 1 | EPSS Ckt | N | 2024
KERN | KERN | MC FARLAND-1105 | 253181105 | FUSE | 673501 | 20241216 | 812 | 20241216 | 933 | 2662417 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1620 | 35.7178 | -119.2942 | No | Fog;32-90 F |  |  | 24-0146530 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998915 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 18299 | 20241216 | 851 | 20241216 | 1104 | 2662502 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 532 | 35.0763 | -118.9676 | No | Clear;32-90 F |  |  | 24-0146651 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999035 | 1 | EPSS Ckt | N | 2024
KERN | KERN | TUPMAN-1104 | 254561104 | TRANSFORMER | 515910270173 | 20241216 | 934 | 20241216 | 1721 | 2662674 | 467 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 467 | 35.4204 | -119.3736 | No | Clear;32-90 F | Transformer | Broken | 24-0146612 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998993 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | OCB | 2104/2 | 20241216 | 1342 | 20241216 | 1420 | 2663153 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 3532 | 35.1948 | -119.5861 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0146611 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1998995 | 0 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | MCKITTRICK-1101 | 252781101 | FUSE | 1686 | 20241216 | 1539 | 20241216 | 1645 | 2663350 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 440 | 35.3125 | -119.7135 | No | Partly Cloudy;32-90 F |  |  | 24-0146679 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999058 | 1 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | 516547368758 | 20241216 | 1633 | 20241216 | 1704 | 2663459 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 93 | 35.3833 | -119.1592 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0146674 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999053 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2113 | 254072113 | TRANSFORMER | 516969766260 | 20241216 | 1634 | 20241216 | 2345 | 2663617 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 5828 | 35.3163 | -119.016 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0146694 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | Yes | 1999071 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | JUMPER | FLYING BELLS 3 W/OF & 1 N/OF 54276 | 20241217 | 1829 | 20241218 | 43 | 2664571 | 374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 374 | 35.4863 | -119.4393 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0146826 | OH | Sus | 35605820 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999353 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | FUSE | 464269 | 20241217 | 2303 | 20241218 | 54 | 2664668 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 555 | 35.3739 | -119.4677 | No | Clear;32-90 F |  |  | 24-0146892 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1999394 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2103 | 254572103 | TRANSFORMER | 516547368758 | 20241218 | 802 | 20241218 | 944 | 2664768 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 306 | 35.3833 | -119.1592 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146916 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999422 | 0 | Non-EPSS | N | 2024
KERN | KERN | SEMITROPIC-1104 | 252901104 | JUMPER | WIRE DOWN @ CGC 515724675736 | 20241218 | 806 | 20241218 | 1149 | 2664779 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 888 | 35.5725 | -119.4385 | No | Overcast-Fog;32-90 F | Insulator | Broken- wire on ground | 24-0146936 | OH | Sus | 31720398 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | Yes | No | 1999539 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2107 | 254072107 | TRANSFORMER | 516785467287 | 20241218 | 1150 | 20241218 | 1247 | 2665154 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 171 | 35.3442 | -119.0786 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0146969 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999589 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | TRANSFORMER | 516317266275 | 20241218 | 1218 | 20241218 | 2346 | 2665193 | 688 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 688 | 35.3151 | -119.2354 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146976 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999607 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | FUSE | 7101 | 20241218 | 2014 | 20241219 | 106 | 2665548 | 292 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 974 | 35.4557 | -119.5169 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147062 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999712 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 41346 | 20241218 | 2046 | 20241218 | 2106 | 2665564 | 20 | Distribution Circuit | 3rd Party | Vehicle | 1 | 20 | 35.3279 | -118.9852 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Broken | 24-0147052 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999695 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241218 | 2344 | 20241219 | 150 | 2665618 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 4032 | 35.3618 | -119.1627 | No | Overcast;32-90 F |  |  | 24-0147064 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999715 | 0 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-2112 | 254072112 | OTHER | T302231 TWD T457211 | 20241219 | 105 | 20241219 | 215 | 2665624 | 70 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 2170 | 35.2862 | -119.0854 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0146911 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999711 | 0 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2103 | 254582103 | FUSE | 18866 | 20241219 | 726 | 20241219 | 833 | 2665676 | 67 | Distribution Circuit | Animal | Bird found | 48 | 1284 | 35.4416 | -119.1084 | No | Partly Cloudy-Fog;32-90 F | Jumper | Normal | 24-0147077 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999737 | 1 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | TRANSFORMER | 517081057445 | 20241219 | 849 | 20241219 | 1123 | 2665750 | 154 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 154 | 35.0761 | -118.9759 | No | Partly Cloudy;32-90 F |  |  | 24-0147108 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1999825 | 0 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | FUSE | 13417 | 20241219 | 1902 | 20241219 | 1914 | 2666252 | 12 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 108 | 35.3721 | -118.9991 | No | Clear;32-90 F | Customer Equipment | Broken | 24-0147164 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999892 | 0 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1108 | 252771108 | FUSE | 18692 | 20241220 | 49 | 20241220 | 931 | 2666316 | 522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 33495 | 35.3691 | -118.9056 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0147180 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999919 | 1 | EPSS Ckt | N | 2024
KERN | KERN | COLUMBUS-1103 | 253951103 | OCB | 1103/2 | 20241220 | 559 | 20241220 | 702 | 2666362 | 63 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1685 | 106155 | 35.3985 | -118.9399 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0147189 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1999928 | 0 | Non-EPSS | N | 2024 | B- C
KERN | KERN | MAGUNDEN-2108 | 252772108 | FUSE | 14499 | 20241220 | 808 | 20241220 | 1322 | 2666444 | 314 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 6908 | 35.329 | -118.9321 | No | Clear;32-90 F |  |  | 24-0147235 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000138 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | TRANSFORMER | 516410666930 | 20241220 | 943 | 20241221 | 316 | 2666616 | 1053 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1053 | 35.3335 | -119.2043 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0147229 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000118 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEVIS-2104 | 255322104 | TRANSFORMER | 516524367213 | 20241220 | 944 | 20241220 | 1800 | 2666619 | 496 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 496 | 35.3413 | -119.166 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147233 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000128 | 0 | Non-EPSS | N | 2024
KERN | KERN | COPUS-1103 | 253871103 | TRANSFORMER | 516333260335 | 20241220 | 1317 | 20241220 | 1606 | 2666838 | 169 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 169 | 35.1518 | -119.226 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0147236 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000142 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1101 | 252821101 | RECLOSER | 3570 | 20241221 | 521 | 20241221 | 707 | 2667178 | 106 | Distribution Circuit | Animal | Other | 15 | 1590 | 35.179 | -119.1461 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0147286 | OH | Sus | 46423374 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000199 | 0 | Non-EPSS | N | 2024 | B PWR FACTOR TGT
KERN | KERN | WEEDPATCH-1102 | 252971102 | FUSE | 14667 | 20241221 | 722 | 20241221 | 907 | 2667204 | 105 | Distribution Circuit | Animal | Bird found | 41 | 4305 | 35.1946 | -118.8337 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0147308 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000247 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1106 | 254561106 | FUSE | 9908 | 20241222 | 1257 | 20241222 | 1451 | 2667772 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 152 | 35.3446 | -119.2163 | No | Clear;32-90 F |  |  | 24-0147394 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000378 | 1 | Non-EPSS | N | 2024
KERN | KERN | MC FARLAND-1105 | 253181105 | TRANSFORMER | 516209680189 | 20241222 | 1853 | 20241222 | 2007 | 2667902 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 74 | 35.6966 | -119.2773 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0147417 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000402 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241223 | 1108 | 20241223 | 1233 | 2668280 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2720 | 35.3618 | -119.1627 | No | Clear;32-90 F |  |  | 24-0147483 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000530 | 0 | Non-EPSS | N | 2024
KERN | KERN | FELLOWS-2104 | 254242104 | RECLOSER | 1052 | 20241223 | 1730 | 20241223 | 2032 | 2668557 | 182 | Distribution Circuit | 3rd Party | Vandalism | 111 | 20202 | 35.189 | -119.5722 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0147503 | UG | Sus | 46438430 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000551 | 0 | EPSS Ckt | N | 2024 | A GRD
KERN | KERN | PANAMA-2101 | 253422101 | FUSE | 14555 | 20241224 | 604 | 20241224 | 709 | 2668842 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 2210 | 35.2664 | -119.0028 | No | Clear;32-90 F |  |  | 24-0147566 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000618 | 0 | Non-EPSS | N | 2024
KERN | KERN | SHAFTER-1111 | 253651111 | FUSE | 7505 | 20241224 | 945 | 20241224 | 1027 | 2669059 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 1401 | 35.5072 | -119.2733 | No | Overcast-Drizzle;32-90 F |  |  | 24-0147626 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000684 | 1 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | MTR#1008623095 | 20241224 | 947 | 20241224 | 1133 | 2669062 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 212 | 35.2012 | -119.0041 | No | Clear-Rain;32-90 F | Fuse | Failed/Faulted | 24-0147629 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000687 | 0 | Non-EPSS | N | 2024
KERN | KERN | BAKERSFIELD-2106 | 253372106 | OCB | 2106/2 | 20241224 | 1020 | 20241224 | 1131 | 2669098 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4529 | 260119 | 35.3885 | -119.0046 | No | Overcast-Drizzle;32-90 F |  |  | 24-0147621 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000679 | 0 | Non-EPSS | N | 2024 | AB INST OC
KERN | KERN | SMYRNA-1102 | 253551102 | FUSE | 18451 | 20241224 | 1025 | 20241224 | 1210 | 2669123 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 840 | 35.6884 | -119.5087 | No | Overcast-Fog;32-90 F |  |  | 24-0147646 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000702 | 0 | Non-EPSS | N | 2024
KERN | KERN | OLD RIVER-1103 | 252821103 | FUSE | 8694 | 20241224 | 1029 | 20241230 | 225 | 2669134 | 8156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 48960 | 35.2236 | -119.2072 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 24-0147676 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000736 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1101 | 252771101 | TRANSFORMER | 517216868077 | 20241224 | 1030 | 20241224 | 1500 | 2669137 | 270 | Transformer only | Vegetation | Tree - grew into line | 10 | 2700 | 35.3674 | -118.9339 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0147635 | OH | Sus | 46438631 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000693 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 8915 | 20241224 | 1056 | 20241224 | 1243 | 2669166 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1499 | 35.0244 | -118.7702 | No | Overcast-Fog;32-90 F |  |  | 24-0147649 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000707 | 1 | EPSS Ckt | N | 2024
KERN | KERN | RENFRO-2102 | 254572102 | TRANSFORMER | 516572168184 | 20241224 | 1119 | 20241224 | 1630 | 2669178 | 311 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1244 | 35.368 | -119.1505 | No | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147648 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000704 | 0 | Non-EPSS | N | 2024
KERN | KERN | WELLFIELD-1102 | 254291102 | OCB | 1102/2 | 20241224 | 1154 | 20241224 | 1519 | 2669205 | 205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 173 | 35465 | 35.2249 | -118.7784 | No | Overcast-Rain;32-90 F | Regulator | Burned/flashed | 24-0147662 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 2000720 | 0 | EPSS Ckt | N | 2024 | AC GRD
KERN | KERN | MC FARLAND-1105 | 253181105 | FUSE | 7467 | 20241224 | 1229 | 20241224 | 1350 | 2669235 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 567 | 35.718 | -119.2764 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0147668 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000726 | 0 | Non-EPSS | N | 2024
KERN | KERN | 7TH STANDARD-2103 | 254582103 | OCB | 2103/2/NORM | 20241224 | 1353 | 20241224 | 2115 | 2669265 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1373 | 100008 | 35.4397 | -119.1312 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken | 24-0147664 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000722 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | KERN OIL-1106 | 252721106 | TRANSFORMER | 517396370810 | 20241225 | 1050 | 20241226 | 54 | 2669621 | 844 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1688 | 35.4428 | -118.8725 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0147729 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000790 | 0 | EPSS Ckt | N | 2024
KERN | KERN | CARRIZO PLAINS-1101 | 253461101 | RECLOSER | 384116 | 20241225 | 1527 | 20241226 | 344 | 2669703 | 737 | Distribution Circuit | 3rd Party | Vehicle | 332 | 243691 | 35.3805 | -120.0405 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0147742 | OH | Sus | 35607526 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 2000802 | 0 | EPSS Ckt | N | 2024 | ABC
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241226 | 133 | 20241226 | 335 | 2669817 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 3904 | 35.3618 | -119.1627 | No | Overcast;32-90 F |  |  | 24-0147770 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000830 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1101 | 253481101 | FUSE | 18299 | 20241226 | 938 | 20241226 | 1107 | 2669981 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 534 | 35.0763 | -118.9676 | No | Clear;32-90 F |  |  | 24-0147803 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000890 | 0 | EPSS Ckt | N | 2024
KERN | KERN | ANTELOPE-1102 | 252021102 | SWITCH | 3256 | 20241226 | 1316 | 20241226 | 1922 | 2669992 | 366 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 40 | 11508 | 35.6582 | -119.9252 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0147807 | OH | Sus | 35607625 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000904 | 0 | EPSS Ckt | N | 2024
KERN | KERN | PANAMA-2101 | 253422101 | RECLOSER | 1393 | 20241226 | 1456 | 20241226 | 2224 | 2670208 | 448 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 347 | 4254 | 35.2647 | -119.0215 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147821 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | Yes | No | 2000919 | 0 | Non-EPSS | N | 2024 | N/A
KERN | KERN | LERDO-1112 | 253491112 | RECLOSER | 4323 | 20241226 | 1808 | 20241226 | 1824 | 2670300 | 16 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 124 | 1984 | 35.5151 | -119.0819 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0147836 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000930 | 0 | Non-EPSS | N | 2024 | NONE
KERN | KERN | LAMONT-1103 | 253911103 | TRANSFORMER | 517293764179 | 20241227 | 809 | 20241228 | 257 | 2670577 | 1128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 10722 | 35.2602 | -118.9075 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147907 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001026 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241227 | 1056 | 20241227 | 1304 | 2670753 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 4096 | 35.3618 | -119.1627 | No | Clear;32-90 F | Insulator | Failed/Faulted | 24-0147948 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001076 | 0 | Non-EPSS | N | 2024
KERN | KERN | KERN OIL-1114 | 252721114 | FUSE | 18174 | 20241227 | 1142 | 20241227 | 2005 | 2670806 | 503 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 23 | 11569 | 35.41 | -119.0187 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147943 | OH | Sus | 31720918 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | Yes | 2001070 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241228 | 43 | 20241228 | 145 | 2671125 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 1984 | 35.3618 | -119.1627 | No | Partly Cloudy;32-90 F |  |  | 24-0148005 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001136 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEMBLOR-1104 | 252551104 | TRIP-SAVER | 9126 | 20241228 | 943 | 20241228 | 1305 | 2671255 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 4446 | 35.3913 | -119.703 | No | Partly Cloudy;32-90 F |  |  | 24-0148040 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001179 | 1 | EPSS Ckt | N | 2024 | N/A
KERN | KERN | BAKERSFIELD-1116 | 253371116 | OCB | 1116/2 | 20241228 | 1603 | 20241228 | 1710 | 2671436 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3031 | 140185 | 35.3886 | -119.0042 | No | Partly Cloudy;32-90 F |  |  | 24-0148056 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2001197 | 0 | Non-EPSS | N | 2024 | AC TIME OC
KERN | KERN | MC FARLAND-1104 | 253181104 | FUSE | 2621 | 20241228 | 1618 | 20241228 | 1711 | s2001208 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 177 | 35.6604 | -119.1065 | No | Clear;32-90 F |  |  | 24-0148067 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001208 | 1 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241229 | 210 | 20241229 | 305 | 2671568 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 1760 | 35.3618 | -119.1627 | No | Fog;32-90 F |  |  | 24-0148071 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001213 | 0 | Non-EPSS | N | 2024
KERN | KERN | RENFRO-2101 | 254572101 | FUSE | 65897 | 20241229 | 659 | 20241229 | 1903 | 2671614 | 724 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 19632 | 35.3618 | -119.1627 | No | Clear;32-90 F |  |  | 24-0148094 | OH | Sus | 31721160 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2001239 | 0 | Non-EPSS | N | 2024
KERN | KERN | WHEELER RIDGE-1102 | 253481102 | FUSE | 15723 | 20241229 | 1012 | 20241229 | 1120 | 2671719 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 340 | 35.0934 | -118.9648 | No | Clear;32-90 F |  |  | 24-0148120 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2001267 | 0 | Non-EPSS | N | 2024
KERN | KERN | FRUITVALE-1104 | 253391104 | FUSE | 17264 | 20241229 | 1056 | 20241229 | 1133 | 2671765 | 37 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 2443 | 35.4195 | -119.079 | No | Clear;32-90 F |  |  | 24-0148121 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001268 | 1 | Non-EPSS | N | 2024
KERN | KERN | STOCKDALE-1108 | 254071108 | TRANSFORMER | 516933467153 | 20241229 | 1622 | 20241229 | 1653 | 2671915 | 31 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 186 | 35.3409 | -119.0289 | No | Overcast;32-90 F |  |  | 24-0148149 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 2001299 | 0 | Non-EPSS | N | 2024
KERN | KERN | SMYRNA-1101 | 253551101 | OCB | 1101/2 | 20241229 | 1627 | 20241230 | 1326 | 2671916 | 1259 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 24115 | 35.7178 | -119.4554 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148147 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 2001297 | 0 | Non-EPSS | N | 2024 | B-GRD
KERN | KERN | SAN BERNARD-1101 | 253191101 | FUSE | 15966 | 20241230 | 144 | 20241230 | 606 | 2672129 | 262 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 524 | 35.1072 | -118.8492 | No | Overcast-Fog;32-90 F |  |  | 24-0148179 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001332 | 1 | EPSS Ckt | N | 2024
KERN | KERN | BAKERSFIELD-1106 | 253371106 | FUSE | 14440 | 20241230 | 854 | 20241230 | 1204 | 2672318 | 190 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 176 | 15314 | 35.3835 | -118.99 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 24-0148200 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2001428 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1101 | 252611101 | TRANSFORMER | 515769271517 | 20241230 | 1105 | 20241230 | 2010 | 2672472 | 545 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 545 | 35.4569 | -119.4218 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148219 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001458 | 0 | Non-EPSS | N | 2024
KERN | KERN | TEJON-1103 | 252931103 | FUSE | 8915 | 20241230 | 1403 | 20241230 | 1648 | 2672623 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2311 | 35.0244 | -118.7702 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0148232 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001480 | 1 | EPSS Ckt | N | 2024
KERN | KERN | WHEELER RIDGE-1103 | 253481103 | TRANSFORMER | 517013560070 | 20241230 | 1412 | 20241230 | 1818 | 2672629 | 246 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 246 | 35.1465 | -119.0001 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148225 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001471 | 0 | Non-EPSS | N | 2024
KERN | KERN | TUPMAN-1103 | 254561103 | FUSE | 13287 | 20241230 | 1549 | 20241231 | 205 | 2672699 | 616 | Distribution Circuit | 3rd Party | Vehicle | 10 | 2208 | 35.368 | -119.2343 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0148234 | OH | Sus | 31721305 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | Yes | No | 2001482 | 0 | Non-EPSS | N | 2024
KERN | KERN | SAN BERNARD-1102 | 253191102 | FUSE | 80537 | 20241230 | 1753 | 20241230 | 2212 | 2672786 | 259 | Distribution Circuit | 3rd Party | Vehicle | 1 | 259 | 35.1289 | -118.8779 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0148242 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001491 | 1 | Non-EPSS | N | 2024
KERN | KERN | MAGUNDEN-1104 | 252771104 | FUSE | 13925 | 20241231 | 1500 | 20241231 | 1627 | 2673340 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2697 | 35.3792 | -118.9186 | No | Partly Cloudy;32-90 F |  |  | 24-0148318 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001616 | 0 | Non-EPSS | N | 2024
KERN | KERN | MIDWAY-1102 | 252611102 | SWITCH | 1404 | 20241231 | 1856 | 20250101 | 1021 | 2673484 | 925 | Distribution Circuit | 3rd Party | Vehicle | 26 | 24050 | 35.3475 | -119.4463 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0148327 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2001627 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO 1104 | 183101104 | FUSE | 6345 | 20230101 | 0 | 20230101 | 1742 | 1907547 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 13022 | 34.6409 | -120.5021 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1794824 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO 1103 | 182601103 | FUSE | 14721 | 20230101 | 1042 | 20230101 | 1058 | 1908145 | 16 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 26 | 416 | 35.1085 | -120.5918 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0004352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1794946 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY 1101 | 183011101 | JUMPER | OJ 2 W/OF CGC 511525468747 | 20230101 | 1547 | 20230101 | 2109 | 1908838 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2862 | 35.3561 | -120.844 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0004564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795165 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | JUMPER | JUMPERS 1 SPAN SS OF CGC 512467443154 | 20230102 | 1403 | 20230102 | 1445 | 1909881 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 42 | 34.6614 | -120.5061 | No | Clear;32-90F | Conductor- Overhead | Deteriorated | 23-0004776 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795378 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO 1101 | 182631101 | RECLOSER | V12 | 20230102 | 1713 | 20230102 | 1847 | 1910411 | 94 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 205 | 19270 | 35.2947 | -120.636 | No | Clear;32-90F |  |  | 23-0004824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795427 | 0 | EPSS Ckt | N | 2023 | SG
LOS PADRES | SAN LUIS OBISPO | FOOTHILL 1101 | 182951101 | FUSE | 13003 | 20230102 | 1805 | 20230103 | 1142 | 1910493 | 1057 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 5285 | 35.2853 | -120.7111 | No | Clear;32-90F | Elbow | Failed/Faulted | 23-0004929 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795534 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY 1101 | 183071101 | FUSE | 9191 | 20230103 | 1136 | 20230103 | 2108 | 1911153 | 572 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 37752 | 35.5471 | -121.0943 | No | Clear;32-90F | Pole-Wood | Broken | 23-0005092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795656 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 9777 | 20230103 | 1321 | 20230103 | 1617 | 1911485 | 176 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 26224 | 35.5631 | -121.089 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0005157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795695 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON 2110 | 183052110 | FUSE | 7359 | 20230104 | 216 | 20230105 | 1737 | 1921581 | 2361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 30693 | 35.6228 | -120.8555 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797481 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE 1103 | 182571103 | RECLOSER | 567884 | 20230104 | 649 | 20230104 | 1814 | 1912370 | 685 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 57047 | 34.8453 | -120.5126 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0005541 | OH | Sus | 35419616 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1796006 | 0 | EPSS Ckt | N | 2023 | A- B- C
LOS PADRES | PASO ROBLES | OILFIELDS 1103 | 182391103 | FUSE | 3413 | 20230104 | 825 | 20230104 | 1437 | 1912955 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5952 | 35.834 | -121.0258 | Yes | Clear;32-90F | Conductor- Overhead | Arcing | 23-0005782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796184 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO 1102 | 182631102 | FUSE | 9491 | 20230104 | 1221 | 20230105 | 1301 | 1921929 | 1480 | Distribution Circuit | Environmental/External | Flood/Erosion | 245 | 362600 | 35.2695 | -120.6646 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0007066 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797583 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO 1104 | 182631104 | FUSE | 9557 | 20230104 | 1245 | 20230104 | 1522 | 1913858 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 524 | 35.1476 | -120.6352 | Yes | Clear;32-90F |  |  | 23-0006031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796370 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON 1101 | 183041101 | FUSE | 7175 | 20230104 | 1252 | 20230105 | 37 | 1913872 | 705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 6263 | 34.5323 | -120.1893 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1796408 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5931 | 20230104 | 1321 | 20230104 | 1520 | 1914042 | 119 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 50 | 5950 | 35.5769 | -120.9724 | Yes | Clear;32-90F |  |  | 23-0006067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796398 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE 1108 | 182581108 | FUSE | 9793 | 20230104 | 1439 | 20230104 | 2028 | 1914562 | 349 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 49907 | 35.2918 | -120.6781 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796452 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | V12 | 20230104 | 1510 | 20230104 | 1520 | 1914725 | 10 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 205 | 2050 | 35.2947 | -120.636 | Yes | Clear;32-90F |  |  | 23-0006110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796433 | 0 | EPSS Ckt | N | 2023 | SG
LOS PADRES | PASO ROBLES | CHOLAME 2102 | 182562102 | FUSE | 5595 | 20230104 | 1535 | 20230104 | 1649 | 1914853 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1380 | 35.9016 | -120.4446 | Yes | Clear;32-90F |  |  | 23-0006261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796565 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO 1101 | 182541101 | FUSE | 7525 | 20230104 | 1602 | 20230104 | 1715 | 1915034 | 73 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 3573 | 35.4843 | -120.6747 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796622 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON 2113 | 183052113 | FUSE | 30695 | 20230104 | 1628 | 20230105 | 1112 | 1915239 | 1124 | Distribution Circuit | Vegetation | Tree - fell into line | 222 | 84468 | 35.5045 | -120.6663 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796795 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL 1102 | 182951102 | TRANSFORMER | 511831565241 | 20230104 | 1634 | 20230106 | 1706 | 1915605 | 2912 | Transformer only | Environmental/External | Water | 1 | 2912 | 35.261 | -120.7368 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0006986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797289 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO 1103 | 182541103 | FUSE | 3997 | 20230104 | 1641 | 20230104 | 1913 | 1915477 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 13376 | 35.4584 | -120.6836 | Yes | Clear;32-90F |  |  | 23-0006480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796778 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1103 | 182571103 | TRANSFORMER | 512622149138 | 20230104 | 1658 | 20230104 | 1733 | 1914594 | 35 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 35 | 34.8259 | -120.4596 | Yes | Clear;32-90F |  |  | 23-0006362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1796661 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 75931 | 20230104 | 1700 | 20230105 | 1316 | 1915944 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 40554 | 35.3627 | -120.8343 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796746 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON 1102 | 183041102 | SWITCH | 464123 | 20230104 | 1816 | 20230104 | 2044 | 1916962 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 5328 | 34.6129 | -120.1835 | Yes | Clear;32-90F | Other | Broken | 23-0006419 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796717 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC 1104 | 182811104 | FUSE | 12077 | 20230104 | 1840 | 20230105 | 1538 | 1917069 | 1258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 5032 | 34.8794 | -120.3327 | Yes | Clear;32-90F | Pole-Wood | On Ground | 23-0006542 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796840 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | 838078 | 20230104 | 1850 | 20230104 | 2017 | 1917262 | 87 | Distribution Circuit | Vegetation | Tree - branch fell on line | 161 | 14007 | 34.6455 | -120.4608 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1796738 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 9557 | 20230104 | 1851 | 20230104 | 2255 | 1917276 | 244 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1220 | 35.1476 | -120.6352 | Yes | Clear;32-90F |  |  | 23-0006820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797122 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ 1102 | 182721102 | FUSE | 20615 | 20230104 | 1933 | 20230104 | 2151 | 1917733 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3036 | 34.5989 | -120.1285 | Yes | Clear;32-90F |  |  | 23-0006733 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797035 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY SUB | 18301 | RECLOSER | TEMP LR 1102/2 | 20230104 | 1947 | 20230105 | 1424 | 1917857 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 6758 | 3056886 | 35.3745 | -120.8556 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1796819 | 0 | Non-EPSS | N | 2023 | A B C INST T
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1101 | 182771101 | FUSE | 789803 | 20230104 | 1956 | 20230107 | 1531 | 1921945 | 4055 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 170142 | 35.6948 | -121.2905 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1797935 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | OTHER | W52 | 20230104 | 2011 | 20230105 | 1215 | 1918067 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 3006 | 104753 | 35.5577 | -121.0774 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1796849 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | V74 | 20230104 | 2108 | 20230105 | 1755 | 1918674 | 1247 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 120349 | 35.5459 | -121.0678 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796918 | 0 | EPSS Ckt | N | 2023 | A B C GRD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | OTHER | WIRE DOWN 1 W/OF 14831 | 20230104 | 2108 | 20230105 | 1951 | 1922889 | 1363 | Distribution Circuit | Animal | Bird found | 231 | 211518 | 35.5461 | -121.0726 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1797826 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 306275 | 20230104 | 2114 | 20230105 | 325 | 1920460 | 371 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 16332 | 35.5721 | -121.1068 | Yes | Clear;32-90F |  |  | 23-0006969 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797272 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 3865 | 20230104 | 2115 | 20230105 | 1021 | 1920461 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 65238 | 35.5742 | -121.1038 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797262 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA 1102 | 182771102 | FUSE | 888151 | 20230104 | 2120 | 20230106 | 901 | 1918763 | 2112 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 81634 | 35.5715 | -121.1066 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006943 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1797245 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1101 | 182771101 | FUSE | 678931 | 20230104 | 2141 | 20230105 | 1919 | 1919015 | 1298 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 6060 | 35.6552 | -121.1869 | Yes | Clear;32-90 F |  |  | 23-0007951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798086 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE 1105 | 182581105 | TRANSFORMER | 512084166302 | 20230104 | 2229 | 20230105 | 2300 | 1919459 | 1471 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 16181 | 35.2932 | -120.6538 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0006997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797299 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 20615 | 20230104 | 2255 | 20230105 | 1249 | 1919587 | 831 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 18282 | 34.5989 | -120.1285 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797171 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS 1102 | 182551102 | TRANSFORMER | 511376272042 | 20230105 | 138 | 20230105 | 1750 | 1919169 | 972 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 24300 | 35.4457 | -120.8958 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0006920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797220 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | JUMPER | BURNT OPEN JUMPER | 20230105 | 151 | 20230105 | 835 | 1920300 | 404 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 13332 | 34.8801 | -120.4445 | Yes | Clear;32-90 F |  |  | 23-0007076 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1797370 | 1 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | TRANSFORMER | 512618852932 | 20230105 | 209 | 20230105 | 926 | 1920994 | 437 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 437 | 34.9294 | -120.4638 | Yes | Clear;32-90 F | Customer Equipment | Arcing | 23-0007165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797451 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES 1103 | 182611103 | RECLOSER | N02 | 20230105 | 235 | 20230105 | 1819 | 1920397 | 944 | Distribution Circuit | Equipment Failure/Involved | Underground | 828 | 320116 | 35.7193 | -120.8646 | Yes | Clear;32-90F | Switch (UG) | Failed/Faulted | 23-0006946 | UG | Sus | 35419614 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797248 | 0 | EPSS Ckt | N | 2023 | B-GRD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5931 | 20230105 | 323 | 20230105 | 1609 | 1921560 | 766 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 38300 | 35.5769 | -120.9724 | Yes | Clear;32-90 F |  |  | 23-0007703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797888 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO 1104 | 182601104 | FUSE | 15185 | 20230105 | 421 | 20230105 | 1329 | 1920579 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 15892 | 35.1492 | -120.5716 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797387 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO 1106 | 182601106 | FUSE | 14803 | 20230105 | 458 | 20230105 | 1123 | 1921890 | 385 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 19635 | 35.0981 | -120.6022 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797596 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512002266414 | 20230105 | 731 | 20230106 | 219 | 1920935 | 1128 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 15792 | 35.2956 | -120.6814 | Yes | Clear;32-90F | Woodpin | Broken | 23-0008007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798139 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA 1101 | 182771101 | FUSE | 15155 | 20230105 | 822 | 20230106 | 1425 | 1920735 | 1803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 7212 | 35.6185 | -121.1451 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797369 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ 1101 | 182721101 | FUSE | 20863 | 20230105 | 855 | 20230105 | 2335 | 1921323 | 880 | Distribution Circuit | Vegetation | Tree - branch fell on line | 73 | 19096 | 34.6193 | -120.0989 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797628 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 10729 | 20230105 | 1053 | 20230106 | 2121 | 1921808 | 2068 | Distribution Circuit | Equipment Failure/Involved | Overhead | 190 | 45712 | 35.2876 | -120.656 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0007501 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797719 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON 2111 | 183052111 | FUSE | 5973 | 20230105 | 1138 | 20230105 | 1420 | 1922001 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1944 | 35.5505 | -120.6925 | Yes | Clear;32-90 F |  |  | 23-0007507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797726 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | TRANSFORMER | 511788066058 | 20230105 | 1225 | 20230107 | 1115 | 1922174 | 2810 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2810 | 35.2839 | -120.7529 | Yes | Clear;32-90F | Transformer (OH) | Deteriorated | 23-0008008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798140 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | FUSE | 45939 | 20230105 | 1232 | 20230105 | 2130 | 1922192 | 538 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1076 | 34.9012 | -120.473 | Yes | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0007824 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797989 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | MESA 1103 | 182821103 | RECLOSER | M92 | 20230105 | 1312 | 20230105 | 1716 | 1922348 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 1206 | 254904 | 35.0168 | -120.4802 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797760 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | SANTA MARIA | SANTA MARIA 1108 | 182671108 | RECLOSER | M80 | 20230105 | 1313 | 20230106 | 2209 | s1797751 | 1868 | Distribution Circuit | Vegetation | Tree - fell into line | 385 | 213404 | 35.0146 | -120.3607 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797751 | 0 | EPSS Ckt | N | 2023 | A/C
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 1441 | 20230105 | 1604 | 20230105 | 1941 | 1923154 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 868 | 34.6716 | -120.5622 | Yes | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0007697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797885 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PERRY-1101 | 183071101 | FUSE | 30251 | 20230105 | 1648 | 20230106 | 45 | 1924056 | 477 | Distribution Circuit | Animal | Bird found | 1 | 477 | 35.5672 | -120.9086 | Yes | Clear;32-90F | Fuse | Broken | 23-0008052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798180 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 32305 | 20230105 | 1732 | 20230106 | 1203 | 1923400 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5555 | 35.5532 | -120.7509 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798071 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2291 | 20230105 | 2047 | 20230105 | 2203 | 1923868 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 304 | 35.2985 | -120.7834 | Yes | Clear;32-90F |  |  | 23-0008011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798144 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO 1108 | 182631108 | SWITCH | 5480 | 20230106 | 130 | 20230106 | 155 | 1924081 | 25 | Distribution Circuit | Company Initiated | Return Circuit Normal | 245 | 6125 | 35.267 | -120.6608 | No | Clear;32-90F | Switch (UG) | Normal | 23-0007066 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798187 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 5789 | 20230106 | 602 | 20230106 | 1014 | 1924126 | 252 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 22680 | 35.7865 | -120.9396 | No | Clear;32-90F |  |  | 23-0008114 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798214 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14831 | 20230106 | 1014 | 20230106 | 1358 | 1924460 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 4928 | 35.5463 | -121.0723 | No | Clear;32-90F | Pole-Wood | Broken | 23-0008153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798242 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512779452947 | 20230106 | 1112 | 20230107 | 1017 | 1924646 | 1385 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1385 | 34.931 | -120.4103 | No | Clear;32-90F | Transformer (OH) | Arcing | 23-0008511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798438 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 6713 | 20230106 | 1340 | 20230107 | 1619 | 1924967 | 1599 | Distribution Circuit | Equipment Failure/Involved | Underground | 90 | 116812 | 35.7591 | -120.9433 | No | Clear;32-90F | Conductor- Underground | Burned/flashed | 23-0008507 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798434 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512709651666 | 20230106 | 1549 | 20230106 | 2101 | 1925297 | 312 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 4992 | 34.8955 | -120.4325 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0008528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798457 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA 1110 | 182671110 | TRANSFORMER | 512289554133 | 20230106 | 1827 | 20230106 | 2201 | 1925551 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2140 | 34.9603 | -120.5746 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0008566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798487 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | SWITCH | 386844 | 20230106 | 1847 | 20230107 | 630 | 1925568 | 701 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 54163 | 35.3044 | -120.8054 | No | Clear;32-90F | Pole-Wood | Broken | 23-0008224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798480 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512536355172 | 20230107 | 757 | 20230107 | 1243 | 1926086 | 286 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 286 | 34.9911 | -120.4944 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0008721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798604 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | JUMPER | FB 1 SPAN S/E CGC511735566285 | 20230107 | 1423 | 20230107 | 1731 | 1926824 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 188 | 35.2905 | -120.7702 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0008839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798698 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | OCB | 1109/2 | 20230107 | 1915 | 20230107 | 2025 | 1927809 | 70 | Distribution Circuit | 3rd Party | Vehicle | 1480 | 48680 | 34.9503 | -120.4442 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0009041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1798868 | 0 | Non-EPSS | N | 2023 | ABC
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 6345 | 20230108 | 1258 | 20230108 | 2137 | 1933594 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6607 | 34.6409 | -120.5021 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800083 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO 1107 | 182631107 | FUSE | 2417 | 20230108 | 1443 | 20230108 | 2031 | 1933801 | 348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 6264 | 35.1893 | -120.7004 | Yes | Clear;32-90F | Cutout- fuse holder | Failed/Faulted | 23-0010475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800322 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA 1102 | 182681102 | TRANSFORMER | 513753044013 | 20230108 | 1954 | 20230109 | 24 | 1934305 | 270 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 270 | 34.6921 | -120.0767 | Yes | Clear;32-90F | Connector or Splice (OH) | Deteriorated | 23-0010461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800307 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA 1101 | 182821101 | OCB | 1101/2/NORM | 20230108 | 2006 | 20230108 | 2108 | 1934655 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2072 | 86145 | 35.0079 | -120.4539 | Yes | Clear;32-90F | Regulator | Failed/Faulted | 23-0010473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800320 | 1 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14865 | 20230109 | 59 | 20230109 | 1618 | 1935160 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10109 | 35.5505 | -121.0726 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800580 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | OTHER | N32 | 20230109 | 232 | 20230112 | 1533 | 1935234 | 5101 | Distribution Circuit | Vegetation | Tree - fell into line | 420 | 2089365 | 35.6814 | -120.9368 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1800585 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | OCB | 1104/2 | 20230109 | 253 | 20230109 | 553 | 1935389 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1465 | 263499 | 34.6432 | -120.4374 | Yes | Clear;32-90F | Lightning Arrestor | Burned/flashed | 23-0010731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1800594 | 0 | EPSS Ckt | N | 2023 | BC GRD
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 306275 | 20230109 | 328 | 20230110 | 1824 | 1935452 | 2336 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 200752 | 35.5721 | -121.1068 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010758 | OH | Sus | 35419613 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800624 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 635958 | 20230109 | 406 | 20230109 | 732 | 1935561 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 27398 | 35.3248 | -120.5176 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800620 | 0 | EPSS Ckt | N | 2023 | B-C
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20230109 | 447 | 20230109 | 1106 | 1935703 | 212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 279 | 59148 | 35.7984 | -120.9741 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0010772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800636 | 0 | EPSS Ckt | N | 2023 | AB
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6095 | 20230109 | 505 | 20230109 | 1904 | 1935730 | 839 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 38594 | 35.536 | -120.8438 | Yes | Clear;32-90F |  |  | 23-0011248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801036 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 2353 | 20230109 | 530 | 20230113 | 1555 | 1935809 | 6385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 172395 | 35.6807 | -120.9518 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0012706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802344 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | W06 | 20230109 | 544 | 20230109 | 1910 | 1935889 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 590 | 464287 | 35.3641 | -120.8503 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1800658 | 0 | EPSS Ckt | N | 2023 | ABC GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 64121 | 20230109 | 556 | 20230109 | 1530 | 1937177 | 574 | Distribution Circuit | Vegetation | Tree - bark fell into line | 7 | 4018 | 35.6065 | -120.6067 | Yes | Clear;32-90F | Service conductor | Broken | 23-0010950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800789 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V60 | 20230109 | 600 | 20230110 | 2243 | 1935969 | 2443 | Distribution Circuit | Vegetation | Tree - fell into line | 1257 | 3070851 | 35.1846 | -120.7042 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800665 | 0 | EPSS Ckt | N | 2023 | BC
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5031 | 20230109 | 615 | 20230111 | 1515 | 1936040 | 3420 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 157515 | 35.5561 | -121.0828 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801442 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 4595 | 20230109 | 628 | 20230109 | 1354 | 1937180 | 446 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 18732 | 35.5334 | -121.0161 | Yes | Clear;32-90F |  |  | 23-0011110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800921 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | RECLOSER | W18 | 20230109 | 711 | 20230109 | 1258 | 1936442 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2383 | 800181 | 35.4245 | -120.8785 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1800694 | 0 | EPSS Ckt | N | 2023 | ABC- GROUND- TIME OC
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 10149 | 20230109 | 740 | 20230111 | 1258 | 1945024 | 3198 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3198 | 35.5746 | -121.1112 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012391 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802116 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | JUMPER | OJ @ MAINLINE SS CGC 511717676370 | 20230109 | 800 | 20230111 | 1903 | 1938146 | 3543 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 10629 | 35.5663 | -120.7868 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0011203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801002 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 7277 | 20230109 | 800 | 20230109 | 2041 | 1935908 | 761 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2788 | 35.6223 | -120.8529 | Yes | Clear;32-90F |  |  | 23-0011601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801364 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | FUSE | 469377 | 20230109 | 801 | 20230109 | 1050 | 1936704 | 169 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2704 | 35.245 | -120.6827 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800869 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 307832 | 20230109 | 801 | 20230113 | 1555 | 1936686 | 6234 | Distribution Circuit | Vegetation | Tree - fell into line | 815 | 608858 | 35.5578 | -120.7747 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800724 | 0 | EPSS Ckt | N | 2023 | B- C- GRD
LOS PADRES | PASO ROBLES | TEMPLETON 2109 | 183052109 | RECLOSER | R74 | 20230109 | 810 | 20230109 | 2031 | 1936770 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 2414 | 461769 | 35.5922 | -120.6471 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1800773 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512034166411 | 20230109 | 817 | 20230109 | 1447 | 1936780 | 390 | Transformer only | Equipment Failure/Involved | Overhead | 55 | 21450 | 35.2959 | -120.6708 | Yes | Clear;32-90F | Fuse | Broken | 23-0011347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801122 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL 1105 | 182661105 | FUSE | 5441 | 20230109 | 819 | 20230111 | 1745 | 1936836 | 3446 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 20254 | 35.7556 | -120.6979 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0011282 | OH | Sus | 35419613 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801058 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 5287 | 20230109 | 821 | 20230109 | 1759 | 1937021 | 578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 24288 | 35.3721 | -120.6469 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0010995 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800830 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N64 | 20230109 | 823 | 20230110 | 1606 | 1936937 | 1903 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1976 | 415294 | 35.8134 | -120.8465 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1800806 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | PASO ROBLES | PASO ROBLES 1106 | 182611106 | RECLOSER | R70 | 20230109 | 823 | 20230109 | 1914 | 1936970 | 651 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2683 | 987501 | 35.6026 | -120.6687 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0010911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800755 | 0 | EPSS Ckt | N | 2023 | A & G
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | JUMPER | OJ @ 618168 | 20230109 | 823 | 20230109 | 2128 | 1939659 | 785 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 118535 | 35.5455 | -121.076 | Yes | Clear;32-90F | Jumper | Broken | 23-0011628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1801392 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9419 | 20230109 | 824 | 20230112 | 1850 | 1936882 | 4946 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 60318 | 35.1348 | -120.5045 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801329 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | TRANSFORMER | 512022264758 | 20230109 | 827 | 20230109 | 1534 | 1936985 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1281 | 35.2502 | -120.6717 | Yes | Clear;32-90F | Service conductor | Broken | 23-0011394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801160 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 4145 | 20230109 | 848 | 20230109 | 2100 | 1937074 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 18300 | 35.2031 | -120.6 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | Yes | 1801007 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 6577 | 20230109 | 850 | 20230110 | 1312 | 1937086 | 1702 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 6808 | 35.4962 | -120.7472 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0012471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802176 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES 1104 | 182611104 | FUSE | 30379 | 20230109 | 853 | 20230110 | 1830 | 1937185 | 2017 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 10085 | 35.6604 | -120.7549 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011554 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801317 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | JUMPER | 6305 | 20230109 | 855 | 20230109 | 1348 | 1937114 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2397 | 34.9574 | -120.5498 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0011250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1801038 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL 1104 | 182661104 | FUSE | 4169 | 20230109 | 856 | 20230109 | 2010 | 1937099 | 674 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 3147 | 35.7312 | -120.6242 | Yes | Clear;32-90F |  |  | 23-0011590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801355 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 511996166382 | 20230109 | 909 | 20230109 | 1427 | 1937196 | 318 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 3498 | 35.2948 | -120.6834 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0011312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801088 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1101 | 182771101 | TRANSFORMER | 510599579190 | 20230109 | 915 | 20230111 | 1243 | 1945017 | 3088 | Transformer only | Environmental/External | Water | 1 | 3088 | 35.6355 | -121.1646 | Yes | Clear;32-90 F | Transformer | Burned Open | 23-0012386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1802112 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 2499 | 20230109 | 951 | 20230112 | 1301 | 1937403 | 4510 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 22550 | 35.1851 | -120.4615 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012789 | OH | Sus | 35419613 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802379 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY 1102 | 183011102 | RECLOSER | W22 | 20230109 | 1105 | 20230110 | 1605 | 1944731 | 1740 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5871 | 4526865 | 35.3291 | -120.8245 | Yes | Clear;32-90 F |  |  | 23-0012614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1802283 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 5789 | 20230109 | 1125 | 20230110 | 1517 | 1937849 | 1672 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 150480 | 35.7865 | -120.9396 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801196 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511383671873 | 20230109 | 1155 | 20230110 | 1253 | 1938024 | 1498 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 17976 | 35.441 | -120.8934 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0011706 | OH | Sus | 35419613 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801466 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30977 | 20230109 | 1202 | 20230110 | 1908 | 1938047 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 13604 | 35.4479 | -120.6179 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0011519 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801277 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6489 | 20230109 | 1256 | 20230109 | 1725 | 1938198 | 269 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1075 | 35.5612 | -120.774 | Yes | Clear;32-90F |  |  | 23-0011461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801219 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON 2108 | 183052108 | OTHER | WIRE DOWN @ CGC# 512080773145 | 20230109 | 1258 | 20230110 | 930 | 1938189 | 1232 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 54130 | 35.4809 | -120.6615 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | No | 1801204 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME 1101 | 182561101 | TRANSFORMER | 512919579212 | 20230109 | 1322 | 20230111 | 1819 | 1938277 | 3177 | Transformer only | Vegetation | Tree - fell into line | 10 | 31770 | 35.6532 | -120.3841 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801178 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | TRANSFORMER | 512038374193 | 20230109 | 1334 | 20230110 | 537 | 1942023 | 963 | Transformer only | Vegetation | Tree - fell into line | 4 | 3852 | 35.5097 | -120.6768 | Yes | Clear;32-90F | Service conductor | Broken- wire on ground | 23-0011927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801698 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | 838078 | 20230109 | 1435 | 20230110 | 1634 | 1938475 | 1559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 116984 | 34.6455 | -120.4608 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1801098 | 0 | EPSS Ckt | N | 2023 | ABC- TIME OC
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | RECLOSER | 56012 | 20230109 | 1448 | 20230109 | 1553 | 1938527 | 65 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 2207 | 143455 | 35.1254 | -120.5995 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801115 | 0 | EPSS Ckt | N | 2023 | B & C
LOS PADRES | SANTA MARIA | DIVIDE 1102 | 182571102 | FUSE | 8983 | 20230109 | 1524 | 20230109 | 1551 | 1938141 | 27 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 180 | 34.8715 | -120.4682 | Yes | Clear;32-90F |  |  | 23-0011379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801147 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | M68 | 20230109 | 1618 | 20230109 | 2328 | 1938804 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 16340 | 35.0479 | -120.564 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0011426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1801188 | 0 | EPSS Ckt | N | 2023 | ABC GRD
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | JUMPER | FLYERS 1 SPAN N/OF CGC 512338757457 | 20230109 | 1619 | 20230110 | 1501 | 1939618 | 1362 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 5448 | 35.0534 | -120.5604 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | No | 1801374 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9403 | 20230109 | 1719 | 20230109 | 2327 | 1939029 | 368 | Distribution Circuit | Vegetation | Tree - bark fell into line | 96 | 35328 | 35.143 | -120.5462 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801456 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | FUSE | 22079 | 20230109 | 1734 | 20230110 | 2219 | 1938912 | 1725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 418 | 27132 | 34.6077 | -120.1794 | Yes | Clear;32-90F | Pothead(Riser Termination) | Failed/Faulted | 23-0011482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801240 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 10795 | 20230109 | 1742 | 20230110 | 959 | 1939124 | 977 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5854 | 35.1654 | -120.5848 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1801275 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES 1107 | 182611107 | RECLOSER | 826368 | 20230109 | 1812 | 20230116 | 1712 | 1939281 | 10020 | Distribution Circuit | Environmental/External | Flood/Erosion | 336 | 184113 | 35.6692 | -120.6893 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011526 | OH | Sus | 35419613 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801285 | 0 | EPSS Ckt | N | 2023 | SENSITIVE GRD
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | Q18 | 20230109 | 1822 | 20230110 | 1610 | 1939267 | 1308 | Distribution Circuit | Vegetation | Tree - fell into line | 1933 | 594848 | 35.0401 | -120.525 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011522 | OH | Sus | 35419613 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1801281 | 0 | EPSS Ckt | N | 2023 | B & C- GROUND
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | TRANSFORMER | 511873279404 | 20230109 | 1941 | 20230112 | 1109 | 1939509 | 3808 | Transformer only | Environmental/External | Lightning | 1 | 3808 | 35.6515 | -120.7356 | Yes | Clear;32-90 F | Transformer | Burned/flashed | 23-0013885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803246 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6095 | 20230109 | 1946 | 20230111 | 1448 | 1948077 | 2582 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 39551 | 35.536 | -120.8438 | Yes | Clear;32-90F |  |  | 23-0013690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803111 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | FUSE | 7405 | 20230109 | 2024 | 20230116 | 1707 | 1958333 | 9883 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 9883 | 35.6708 | -120.6911 | Yes | Clear;32-90F | Secondary | Broken | 23-0017261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805934 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO 1103 | 182631103 | TRANSFORMER | 512162963297 | 20230109 | 2030 | 20230110 | 1020 | 1939587 | 830 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 9960 | 35.2115 | -120.6249 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0011799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801560 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 397559 | 20230109 | 2037 | 20230110 | 914 | 1939595 | 757 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 42854 | 35.6289 | -120.554 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0012127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801899 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 20230109 | 2108 | 20230115 | 756 | 1939662 | 7848 | Distribution Circuit | Environmental/External | Flood/Erosion | 56 | 76103 | 35.4345 | -120.2869 | Yes | Clear;32-90F | Pole-Wood | On Ground | 23-0011630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801394 | 0 | EPSS Ckt | N | 2023 | A GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | RECLOSER | A50 | 20230109 | 2148 | 20230111 | 1318 | 1939726 | 2370 | Distribution Circuit | Vegetation | Tree - fell into line | 1425 | 1029186 | 35.4654 | -120.6712 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1801434 | 0 | EPSS Ckt | N | 2023 | B & C- GROUND
LOS PADRES | SANTA MARIA | SISQUOC 1102 | 182811102 | FUSE | 6845 | 20230109 | 2332 | 20230111 | 1149 | 1939779 | 2177 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 88012 | 34.8317 | -120.2332 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1802586 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 635958 | 20230110 | 252 | 20230111 | 2159 | 1941081 | 2587 | Distribution Circuit | Environmental/External | Flood/Erosion | 133 | 91087 | 35.3248 | -120.5176 | Yes | Clear;32-90F | Pole-Wood | On Ground | 23-0011813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801574 | 0 | EPSS Ckt | N | 2023 | A-B-GRD
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1101 | 182771101 | RECLOSER | 175422 | 20230110 | 314 | 20230112 | 1605 | 1941166 | 3651 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 205239 | 35.6473 | -121.191 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0011824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801585 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD
LOS PADRES | SAN LUIS OBISPO | CAYUCOS 1101 | 182551101 | RECLOSER | W14 | 20230110 | 340 | 20230111 | 38 | 1943228 | 1258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 89807 | 35.4716 | -120.9799 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802432 | 0 | EPSS Ckt | N | 2023 | B-GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 469377 | 20230110 | 351 | 20230110 | 1459 | 1943487 | 668 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 10416 | 35.245 | -120.6827 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012112 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801885 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 511488278689 | 20230110 | 352 | 20230112 | 1806 | 1941381 | 3734 | Transformer only | Vegetation | Tree - fell into line | 2 | 7468 | 35.6284 | -120.8636 | Yes | Clear;32-90 F | Transformer | Broken | 23-0013946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803302 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD 1101 | 182801101 | TRANSFORMER | 511514569004 | 20230110 | 402 | 20230110 | 1827 | 1944951 | 863 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 18986 | 35.363 | -120.8472 | Yes | Clear;32-90F | Bushing | Broken | 23-0012360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802096 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | OCB | 2102/2 | 20230110 | 406 | 20230111 | 1852 | 1941579 | 2326 | Distribution Circuit | Environmental/External | Flood/Erosion | 540 | 372525 | 35.6864 | -120.336 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1801622 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SANTA MARIA | SISQUOC 1103 | 182811103 | FUSE | 6487 | 20230110 | 616 | 20230110 | 1906 | 1943029 | 770 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 13860 | 34.9126 | -120.2248 | Yes | Clear;32-90F |  |  | 23-0012928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802494 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | OCB | 1101/2/NORM | 20230110 | 640 | 20230116 | 1317 | 1943104 | 9037 | Distribution Circuit | Environmental/External | Flood/Erosion | 2071 | 188975 | 35.0079 | -120.4539 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1801739 | 0 | EPSS Ckt | N | 2023 | ABC- TIME OC
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 8459 | 20230110 | 650 | 20230110 | 1847 | 1943140 | 717 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 30 | 21510 | 34.9578 | -120.5705 | Yes | Clear;32-90F |  |  | 23-0012922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802488 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | TRANSFORMER | 511513468769 | 20230110 | 715 | 20230110 | 2000 | 1943235 | 765 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 6120 | 35.3565 | -120.8474 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0012945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802510 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | R96 | 20230110 | 802 | 20230113 | 1432 | 1943472 | 4710 | Distribution Circuit | Equipment Failure/Involved | Overhead | 343 | 82764 | 35.6593 | -120.4952 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0012023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1801805 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | JUMPER | 2 POLES LS OF CGC 511830565132 | 20230110 | 906 | 20230112 | 1053 | 1948240 | 2987 | Distribution Circuit | Environmental/External | Flood/Erosion | 2 | 5974 | 35.2581 | -120.7407 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0013740 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | Yes | 1803139 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 11573 | 20230110 | 910 | 20230110 | 1647 | 1944058 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 143 | 41201 | 34.9208 | -120.4405 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0012136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801906 | 1 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20230110 | 916 | 20230110 | 1249 | 1944103 | 213 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 279 | 59427 | 35.7984 | -120.9741 | Yes | Clear;32-90F |  |  | 23-0012086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801875 | 0 | EPSS Ckt | N | 2023 | A & B
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 45411 | 20230110 | 937 | 20230110 | 1813 | 1946236 | 516 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 47988 | 34.9703 | -120.5727 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0012905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802474 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO 1102 | 182541102 | TRANSFORMER | 512145372162 | 20230110 | 953 | 20230113 | 609 | 1947722 | 4096 | Transformer only | Environmental/External | Lightning | 1 | 4096 | 35.4547 | -120.6386 | Yes | Clear;32-90 F | Transformer | Burned/flashed | 23-0013554 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803033 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 9201 | 20230110 | 1007 | 20230112 | 1420 | 1944383 | 3133 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 31330 | 35.2375 | -120.4731 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0013605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803068 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2989 | 20230110 | 1015 | 20230111 | 1550 | 1944429 | 1775 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1775 | 35.5292 | -120.6841 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803207 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 34413 | 20230110 | 1035 | 20230110 | 1545 | 1944573 | 310 | Distribution Circuit | Environmental/External | Lightning | 42 | 12420 | 35.4591 | -120.7502 | Yes | Clear;32-90F | Transformer (OH) | Normal | 23-0012904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802473 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2695 | 20230110 | 1102 | 20230110 | 2022 | 1944677 | 560 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 19600 | 35.4997 | -120.6008 | Yes | Clear;32-90F |  |  | 23-0012997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802556 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | TRANSFORMER | 511727469752 | 20230110 | 1204 | 20230111 | 903 | 1944954 | 1259 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1259 | 35.3856 | -120.7764 | Yes | Clear;32-90F | Service conductor | Broken- wire on ground | 23-0013418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802947 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | JUMPER | 5931 | 20230110 | 1413 | 20230110 | 1436 | 1945440 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 1150 | 35.5769 | -120.9724 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0012560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1802243 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | OTHER | WIRE DOWN AT CGC 512435178260 | 20230110 | 1419 | 20230112 | 1300 | s1803121 | 2801 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 7461 | 35.6243 | -120.5461 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1803121 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 511639777641 | 20230110 | 1855 | 20230111 | 1112 | 1946338 | 977 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 977 | 35.6028 | -120.8139 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0013548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803029 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X04 | 20230110 | 1922 | 20230111 | 1929 | 1948767 | 1447 | Distribution Circuit | Company Initiated | Return Circuit Normal | 285 | 412337 | 35.6554 | -120.3668 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803312 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 511808072363 | 20230110 | 1943 | 20230112 | 1950 | 1946408 | 2887 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 5774 | 35.4575 | -120.752 | Yes | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0013859 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803227 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES 1108 | 182611108 | TRANSFORMER | 512088877966 | 20230110 | 2044 | 20230111 | 1744 | 1946510 | 1260 | Transformer only | Equipment Failure/Involved | Underground | 6 | 7560 | 35.6133 | -120.6626 | Yes | Clear;32-90F | Cutout- fuse holder | Broken | 23-0013458 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802970 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512478141975 | 20230111 | 819 | 20230111 | 1904 | 1947148 | 641 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3205 | 34.6278 | -120.501 | No | Clear;32-90F | Pole-Wood | Broken | 23-0013677 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803103 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 2717 | 20230111 | 913 | 20230112 | 1320 | 1947255 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 51781 | 35.5898 | -120.7832 | No | Clear;32-90F | Pole-Wood | Broken | 23-0013416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802944 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510817376072 | 20230111 | 1110 | 20230111 | 1924 | 1947678 | 494 | Transformer only | Environmental/External | Water | 11 | 5434 | 35.5515 | -121.0884 | No | Clear;32-90 F | Transformer | Broken | 23-0013589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803056 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | SWITCH | 2431 | 20230111 | 1520 | 20230111 | 1812 | 1948452 | 172 | Distribution Circuit | 3rd Party | Vehicle | 142 | 24407 | 35.128 | -120.5705 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0013405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803181 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1101 | 182771101 | FUSE | 678931 | 20230111 | 1608 | 20230111 | 1730 | 1948858 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 383 | 35.6552 | -121.1869 | No | Clear;32-90 F |  |  | 23-0013918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803276 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | FUSE | 15875 | 20230111 | 1744 | 20230112 | 1000 | 1948840 | 976 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 5208 | 35.5259 | -120.9662 | No | Clear;32-90F |  |  | 23-0014365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803677 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | W08 | 20230111 | 2238 | 20230112 | 0 | 1949152 | 82 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1994 | 163508 | 35.3902 | -120.8556 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0010838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803470 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | RECLOSER | V92 | 20230112 | 801 | 20230112 | 1002 | 1949519 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1124 | 133364 | 35.2474 | -120.6734 | No | Clear;32-90F | Recloser | Malfunctioning | 23-0014284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803625 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 9999 | 20230112 | 942 | 20230112 | 1544 | 1949673 | 362 | Distribution Circuit | Environmental/External | Flood/Erosion | 28 | 10136 | 35.1876 | -120.5569 | No | Clear;32-90F | Transformer (UG) | Deteriorated | 23-0014317 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803645 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512305755970 | 20230112 | 1005 | 20230112 | 1723 | 1949780 | 438 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 438 | 35.0116 | -120.5706 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0014378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803694 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | OTHER | T957498 TWD T491864 | 20230112 | 1006 | 20230112 | 1012 | 1949769 | 6 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 6 | 34.855 | -120.4292 | No | Partly Cloudy;32-90 F | Transformer (UG) | Deteriorated | 23-0014335 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803671 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 6147 | 20230112 | 1145 | 20230113 | 1113 | 1950021 | 1408 | Distribution Circuit | Environmental/External | Flood/Erosion | 5 | 7040 | 34.9616 | -120.6221 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0014468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1803751 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 3945 | 20230112 | 1213 | 20230112 | 1513 | 1950136 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 10260 | 35.4394 | -120.4877 | No | Clear;32-90F | Secondary | Broken | 23-0014564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803790 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 14859 | 20230112 | 1413 | 20230112 | 1704 | 1950352 | 171 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 14193 | 35.1938 | -120.4327 | No | Clear;32-90F | Conductor- Overhead | On Ground | 23-0014615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1803805 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | FUSE | 1023 | 20230112 | 1548 | 20230112 | 2012 | 1950524 | 264 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1320 | 34.8703 | -120.2615 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0014709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1803861 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 512022064426 | 20230112 | 1655 | 20230113 | 735 | 1950490 | 880 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1760 | 35.2412 | -120.6734 | No | Clear;32-90F | Jumper | Broken | 23-0014746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803877 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | JUMPER | OJ 3 SPANS E/O CGC 511977965236 | 20230112 | 1705 | 20230112 | 2150 | 1950692 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4560 | 35.263 | -120.6873 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0014730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803868 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 7433 | 20230112 | 1744 | 20230112 | 1920 | 1950773 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 9216 | 35.4689 | -120.6972 | No | Clear;32-90F | Fuse | Broken | 23-0014790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803904 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | SWITCH | 334403 | 20230112 | 1832 | 20230112 | 2055 | 1950833 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 4576 | 35.6821 | -120.739 | No | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0014771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803893 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | M54 | 20230113 | 518 | 20230113 | 1034 | 1951306 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 21206 | 34.8627 | -120.2773 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1804166 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9421 | 20230113 | 811 | 20230113 | 1900 | 1951659 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1947 | 35.1295 | -120.5089 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804217 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 6307 | 20230113 | 907 | 20230113 | 1138 | 1951471 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 705 | 34.9561 | -120.5583 | No | Clear;32-90F |  |  | 23-0015236 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804237 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 511794172205 | 20230113 | 1002 | 20230113 | 1711 | 1951619 | 429 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 429 | 35.4535 | -120.7562 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0015280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804258 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 10973 | 20230113 | 1019 | 20230113 | 1235 | 1951555 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 5032 | 35.5436 | -121.0745 | No | Clear;32-90F | Recloser | Failed/Faulted | 23-0011628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804204 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 511798372180 | 20230113 | 1049 | 20230113 | 1713 | 1951709 | 384 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 384 | 35.452 | -120.7537 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0015312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804268 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | R34 | 20230113 | 1442 | 20230114 | 108 | 1952128 | 626 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 318 | 192194 | 35.5716 | -120.5425 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0015431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1804317 | 0 | EPSS Ckt | N | 2023 | AB GRD
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | V66 | 20230113 | 1658 | 20230113 | 1737 | 1952354 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 327 | 12753 | 35.3759 | -120.8526 | No | Clear;32-90F | Pole-Wood | Broken | 23-0015498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804354 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 32285 | 20230113 | 1658 | 20230114 | 1218 | 1952357 | 1160 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 126912 | 35.5581 | -120.7626 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1804370 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SANTA MARIA-1108 | 182671108 | FUSE | 42819 | 20230114 | 717 | 20230114 | 940 | 1952979 | 143 | Distribution Circuit | Animal | Bird found | 3 | 429 | 35.177 | -120.4305 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0015968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804795 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO 1103 | 183101103 | RECLOSER | Y10 | 20230114 | 1140 | 20230114 | 1325 | 1954168 | 105 | Distribution Circuit | 3rd Party | Vehicle | 236 | 24780 | 34.665 | -120.4225 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0015941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804917 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 7911 | 20230114 | 1223 | 20230114 | 1418 | 1954294 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 230 | 35.5573 | -120.8393 | Yes | Clear;32-90F |  |  | 23-0016257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805018 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA 1101 | 182681101 | TRANSFORMER | 513165945936 | 20230114 | 1321 | 20230114 | 1750 | 1954536 | 269 | Transformer only | Vegetation | Tree - fell into line | 12 | 3228 | 34.741 | -120.2761 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0016254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805014 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 834556 | 20230114 | 1332 | 20230114 | 1613 | 1954467 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 8855 | 35.194 | -120.7339 | Yes | Clear;32-90F |  |  | 23-0016283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805039 | 0 | EPSS Ckt | N | 2023 | B&C
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 32287 | 20230114 | 1358 | 20230114 | 1557 | 1954497 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 357 | 35.5641 | -120.7576 | Yes | Clear;32-90F |  |  | 23-0016295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805051 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO 1102 | 182601102 | FUSE | 8631 | 20230114 | 1421 | 20230114 | 1835 | 1954545 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 5588 | 35.0679 | -120.5939 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1805036 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | TEMP LR 1101/2 | 20230114 | 1755 | 20230114 | 1801 | 1954961 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1022 | 6132 | 34.6967 | -120.1518 | Yes | Clear;32-90F |  |  | 23-0016361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805116 | 0 | EPSS Ckt | N | 2023 | C-GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 511804171940 | 20230114 | 1807 | 20230114 | 2258 | 1954988 | 291 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 291 | 35.4455 | -120.7527 | Yes | Clear;32-90F | Pole-Wood | Contaminated | 23-0016488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805243 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512522662094 | 20230114 | 1840 | 20230115 | 1830 | 1955054 | 1430 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1430 | 35.181 | -120.5038 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0016382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805133 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | RECLOSER | R58 | 20230115 | 221 | 20230115 | 440 | 1955374 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 508 | 70612 | 35.7208 | -120.6846 | No | Clear;32-90F |  |  | 23-0016504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805262 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 511804171940 | 20230115 | 922 | 20230115 | 1120 | 1955702 | 118 | Transformer only | Environmental/External | Lightning | 1 | 118 | 35.4455 | -120.7527 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0016592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805338 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 14519 | 20230115 | 1136 | 20230115 | 1648 | 1956104 | 312 | Distribution Circuit | Environmental/External | Water | 20 | 6240 | 35.1823 | -120.5036 | No | Clear;32-90F | Fuse | Normal | 23-0016728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805439 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 46111 | 20230115 | 1344 | 20230115 | 1619 | 1956023 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 155 | 35.0276 | -120.528 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0016717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805434 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1103 | 182571103 | RECLOSER | 48160 | 20230115 | 2117 | 20230116 | 1042 | 1956403 | 805 | Distribution Circuit | Vegetation | Tree - branch fell on line | 107 | 86073 | 34.8293 | -120.4499 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1805519 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 307832 | 20230116 | 41 | 20230116 | 57 | 1956467 | 16 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 902 | 12495 | 35.5578 | -120.7747 | Yes | Clear;32-90F |  |  | 23-0016860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805558 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 32285 | 20230116 | 108 | 20230116 | 1314 | 1956567 | 726 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 87120 | 35.5581 | -120.7626 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1805574 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | JUMPER | OJ 7 SPANS L/S 64323 | 20230116 | 307 | 20230116 | 944 | 1956928 | 397 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 53726 | 35.6337 | -120.5469 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0016952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1805657 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511569167522 | 20230116 | 315 | 20230116 | 837 | 1956668 | 322 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 3220 | 35.3228 | -120.8277 | Yes | Clear;32-90F | Cutout- fuse holder | Broken | 23-0016971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805676 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 15273 | 20230116 | 327 | 20230116 | 441 | 1956672 | 74 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1110 | 35.5483 | -121.0846 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805591 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 5595 | 20230116 | 358 | 20230116 | 928 | 1956751 | 330 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 18480 | 35.9016 | -120.4446 | Yes | Clear;32-90F |  |  | 23-0017097 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805789 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 4539 | 20230116 | 415 | 20230116 | 727 | 1956774 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 415 | 79680 | 35.1471 | -120.6354 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0016981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805685 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 603067 | 20230116 | 421 | 20230116 | 1219 | 1957157 | 478 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 478 | 35.1452 | -120.6392 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0016981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805689 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X16 | 20230116 | 443 | 20230116 | 718 | 1956803 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 229 | 33957 | 35.6868 | -120.3362 | Yes | Clear;32-90F |  |  | 23-0016920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805627 | 0 | EPSS Ckt | N | 2023 | AB
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14047 | 20230116 | 446 | 20230116 | 1255 | 1956822 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 12225 | 35.553 | -121.0875 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016940 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805646 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2259 | 20230116 | 458 | 20230116 | 1300 | 1956839 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 13978 | 35.5553 | -120.5349 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1805723 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30977 | 20230116 | 503 | 20230116 | 649 | 1956848 | 106 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1378 | 35.4479 | -120.6179 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805680 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 9179 | 20230116 | 655 | 20230116 | 1245 | 1957129 | 350 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 6300 | 35.5438 | -121.0719 | Yes | Clear;32-90F |  |  | 23-0017189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805872 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 7409 | 20230116 | 656 | 20230116 | 934 | 1957121 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 300 | 47400 | 35.7065 | -120.7056 | Yes | Clear;32-90F |  |  | 23-0017002 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805706 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL 1106 | 182661106 | FUSE | 5707 | 20230116 | 737 | 20230116 | 1132 | 1957220 | 235 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 784 | 35.9307 | -120.6774 | Yes | Clear;32-90F |  |  | 23-0017169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805857 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6291 | 20230116 | 818 | 20230116 | 1140 | 1957311 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 471 | 35.6715 | -120.9914 | Yes | Clear;32-90F |  |  | 23-0017165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805853 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | JUMPER | OJ 1 W/OF CGC#512133665480 | 20230116 | 830 | 20230116 | 2000 | 1957335 | 690 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 9660 | 35.2709 | -120.6366 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0017030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805734 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1103 | 182571103 | RECLOSER | 48160 | 20230116 | 1303 | 20230116 | 1414 | 1958115 | 71 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 7597 | 34.8293 | -120.4499 | Yes | Clear;32-90F | Insulator | Broken | 23-0017161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805880 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | JUMPER | OJ SS OF CGC #512118965126 | 20230116 | 1530 | 20230116 | 2000 | 1958468 | 270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 9990 | 35.2614 | -120.6414 | Yes | Clear;32-90F | Jumper | Broken | 23-0017333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1806007 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 20791 | 20230116 | 2233 | 20230118 | 132 | 1958982 | 1617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 11319 | 34.6505 | -120.1158 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0017446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806114 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 511979865095 | 20230117 | 309 | 20230117 | 1138 | 1959046 | 509 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 6617 | 35.2594 | -120.6874 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0017452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806122 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | FUSE | 1019 | 20230117 | 852 | 20230118 | 1055 | 1959263 | 1563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 9378 | 34.8825 | -120.2772 | No | Clear;32-90F | Pole-Wood | Broken | 23-0017510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806152 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X10 | 20230117 | 1132 | 20230117 | 1158 | 1959560 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 2704 | 35.5847 | -120.3364 | No | Clear;32-90F | Pole-Wood | Broken | 23-0017627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806201 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SANTA MARIA | PURISIMA 1101 | 182971101 | JUMPER | 8275 | 20230117 | 1733 | 20230117 | 2258 | 1960192 | 325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 46800 | 34.7047 | -120.4657 | No | Clear;32-90F | Jumper | Burned Open | 23-0017883 | OH | Sus | 31634749 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1806293 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 3211 | 20230117 | 1954 | 20230118 | 145 | 1960319 | 351 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 28431 | 35.1497 | -120.6001 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017904 | OH | Sus | 31634691 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1806316 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 10615 | 20230118 | 640 | 20230118 | 1315 | 1960521 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 7110 | 35.3548 | -120.7864 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0018271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1806553 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512715751764 | 20230118 | 1234 | 20230118 | 1550 | 1960822 | 196 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1764 | 34.8981 | -120.4305 | No | Clear;32-90F | Cutout- fuse holder | Broken | 23-0018351 | OH | Sus | 31634820 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806576 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 10111 | 20230119 | 33 | 20230119 | 249 | 1961729 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2176 | 35.0991 | -120.6143 | No | Clear;32-90F |  |  | 23-0018650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806711 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1101 | 182771101 | JUMPER | UNNUMBER SOLID BLADES SS OF CGC 510159484026 | 20230119 | 958 | 20230119 | 1710 | 1961972 | 432 | Distribution Circuit | Environmental/External | Flood/Erosion | 35 | 15120 | 35.7618 | -121.3185 | No | Clear;32-90F | Pole-Wood | Normal | 23-0018763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806761 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 939545 | 20230119 | 1111 | 20230119 | 1720 | 1962060 | 369 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 369 | 35.2349 | -120.6441 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0018937 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1806805 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | SWITCH | 491460 | 20230119 | 1410 | 20230120 | 220 | 1962251 | 730 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 730 | 34.922 | -120.4326 | No | Clear;32-90F | Elbow | Burned/flashed | 23-0018954 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806809 | 1 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5047 | 20230119 | 2205 | 20230119 | 2233 | 1962814 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 3050 | 35.5474 | -121.0898 | No | Clear;32-90F | Cutout- fuse holder | Failed/Faulted | 23-0019114 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806887 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | TRANSFORMER | 512031572629 | 20230120 | 424 | 20230120 | 928 | 1962880 | 304 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 912 | 35.4666 | -120.6776 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0019194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806968 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 3941 | 20230120 | 829 | 20230120 | 1233 | 1963021 | 244 | Distribution Circuit | 3rd Party | Vehicle | 52 | 12688 | 35.571 | -120.5607 | No | Clear;32-90F | Pole-Wood | Broken | 23-0019252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806988 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 7479 | 20230120 | 839 | 20230120 | 1144 | 1963026 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 185 | 34.9573 | -120.5528 | No | Clear;32-90F |  |  | 23-0019383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807049 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T1523 | 20230120 | 1007 | 20230121 | 1723 | 1963124 | 1876 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 15145 | 35.0166 | -120.4985 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0019493 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807063 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 9927 | 20230120 | 1334 | 20230120 | 1634 | 1963356 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1554 | 35.3151 | -120.8358 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0019514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807066 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 4169 | 20230121 | 908 | 20230121 | 1019 | 1963880 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 331 | 35.7312 | -120.6242 | No | Clear;32-90F |  |  | 23-0019708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807187 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 14283 | 20230121 | 937 | 20230121 | 959 | 1963900 | 22 | Distribution Circuit | 3rd Party | Other | 250 | 5500 | 35.4423 | -120.8953 | No | Clear;32-90F | Jumper | Normal | 23-0019695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807175 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 7297 | 20230121 | 1250 | 20230122 | 1341 | 1964069 | 1491 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 10437 | 34.6629 | -120.3648 | No | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0019732 | OH | Sus | 45646899 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807204 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512687153216 | 20230121 | 1325 | 20230122 | 1244 | 1964210 | 1399 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 13990 | 34.9379 | -120.4415 | No | Clear;32-90F | Connector or Splice (OH) | Burned/flashed | 23-0019761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807224 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 20913 | 20230121 | 1409 | 20230122 | 1402 | 1964095 | 1433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7165 | 34.6649 | -120.409 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0019746 | OH | Sus | 31634912 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | Yes | 1807216 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512221758471 | 20230121 | 1500 | 20230121 | 1704 | 1963832 | 124 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 372 | 35.0795 | -120.5995 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0019771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807233 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512204559347 | 20230121 | 1748 | 20230122 | 1244 | 1964220 | 1136 | Transformer only | Equipment Failure/Involved | Overhead | 39 | 44304 | 35.1032 | -120.6074 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0019781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807239 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 156857 | 20230122 | 238 | 20230122 | 501 | 1964420 | 143 | Distribution Circuit | 3rd Party | Vehicle | 45 | 6391 | 35.0981 | -120.5963 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0019816 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807276 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2519 | 20230122 | 512 | 20230122 | 705 | 1964437 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 3955 | 35.5268 | -120.6745 | No | Clear;32-90F |  |  | 23-0019821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807280 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512154771425 | 20230122 | 1030 | 20230122 | 1425 | 1964628 | 235 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 705 | 35.4345 | -120.6345 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807329 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | FUSE | 7887 | 20230122 | 1927 | 20230122 | 2044 | 1965032 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 847 | 34.7563 | -120.1195 | No | Clear;32-90F |  |  | 23-0019941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807375 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | T0234 | 20230122 | 1956 | 20230123 | 509 | 1965026 | 553 | Distribution Circuit | 3rd Party | Vehicle | 10 | 4594 | 34.9683 | -120.4223 | No | Clear;32-90F | Transformer (UG) | Broken | 23-0019956 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807389 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 7421 | 20230123 | 1147 | 20230123 | 1310 | 1965784 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 83 | 34.9415 | -120.5746 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0020280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807608 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512682253557 | 20230123 | 1618 | 20230124 | 28 | 1966158 | 490 | Transformer only | Equipment Failure/Involved | Electrical Overload | 7 | 3430 | 34.9473 | -120.4433 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0020459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807654 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 15751 | 20230123 | 2116 | 20230124 | 424 | 1966340 | 428 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 14559 | 35.3655 | -120.8437 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0020486 | OH | Sus | 31634998 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807681 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | FUSE | 15875 | 20230124 | 1106 | 20230124 | 1224 | 1966930 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 624 | 35.5259 | -120.9662 | No | Clear;32-90F |  |  | 23-0020778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807886 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | OCB | 1105/2 | 20230124 | 1126 | 20230124 | 1134 | 1966946 | 8 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4771 | 38168 | 34.9503 | -120.444 | No | Clear;32-90F | Capacitor | Failed/Faulted | 23-0020708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807852 | 0 | Non-EPSS | N | 2023 | N/A
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | T1333 | 20230124 | 1839 | 20230125 | 38 | 1967255 | 359 | Transformer only | Equipment Failure/Involved | Underground | 17 | 6103 | 34.9779 | -120.4511 | No | Clear;32-90F | Secondary | Broken | 23-0020958 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807941 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | JUMPER | BURNT OJ 2 SPANS SS CGC 512326676027 | 20230125 | 703 | 20230125 | 1220 | 1967728 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 3850 | 35.5643 | -120.5799 | No | Clear;32-90F | Jumper | Burned Open | 23-0021109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1808083 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | T0766 | 20230125 | 927 | 20230125 | 1224 | 1967769 | 177 | Transformer only | Equipment Failure/Involved | Underground | 1 | 177 | 34.9019 | -120.4496 | No | Clear;32-90F | Fuse | Burned Open | 23-0021239 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808138 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512044572090 | 20230125 | 1019 | 20230125 | 1403 | 1967852 | 224 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 672 | 35.4535 | -120.6721 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0018159 | OH | Sus | 45500992 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1808111 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 724437 | 20230125 | 1040 | 20230125 | 1415 | 1967871 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 7740 | 35.2541 | -120.6279 | No | Clear;32-90F |  |  | 23-0021234 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808136 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512420740601 | 20230125 | 1546 | 20230125 | 2323 | 1968198 | 457 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 914 | 34.5881 | -120.5239 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0021441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808191 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512414555228 | 20230125 | 1914 | 20230126 | 250 | 1968261 | 456 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 456 | 34.9917 | -120.5339 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0021446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808194 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 7581 | 20230125 | 2134 | 20230125 | 2223 | 1968409 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 121 | 5929 | 35.499 | -120.7022 | No | Clear;32-90F |  |  | 23-0021516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808255 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | FUSE | 43903 | 20230126 | 850 | 20230126 | 907 | 1968686 | 17 | Distribution Circuit | Animal | Other | 5 | 85 | 35.0694 | -120.5051 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0021632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808352 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 45107 | 20230126 | 1119 | 20230126 | 1627 | 1968850 | 308 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1232 | 34.5925 | -120.0555 | No | Clear;32-90F |  |  | 23-0021981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808474 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 45333 | 20230127 | 932 | 20230127 | 1041 | 1969672 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 184 | 34.9706 | -120.5216 | No | Clear;32-90F |  |  | 23-0022220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808650 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | RECLOSER | 605393 | 20230127 | 1423 | 20230128 | 1632 | 1970011 | 1569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 21618 | 35.8451 | -120.7004 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0022452 | OH | Sus | 31635712 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1808704 | 0 | EPSS Ckt | N | 2023 | A-B-GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO 1105 | 182601105 | TRANSFORMER | 512030461265 | 20230127 | 1612 | 20230128 | 1701 | 1970163 | 1489 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 16379 | 35.1545 | -120.6675 | No | Clear;32-90F | Transformer (OH) | Leaking | 23-0022548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1808727 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 94117 | 20230128 | 1426 | 20230129 | 208 | 1970578 | 702 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4914 | 35.4835 | -120.6763 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0022646 | OH | Sus | 35423904 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808837 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | FUSE | 11499 | 20230129 | 800 | 20230129 | 902 | 1970828 | 62 | Distribution Circuit | 3rd Party | Metallic Balloon | 166 | 10292 | 34.9714 | -120.4334 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0022714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808912 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511364772173 | 20230129 | 927 | 20230129 | 1756 | 1970889 | 509 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3054 | 35.4494 | -120.8996 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0022730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808928 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 1875 | 20230129 | 1042 | 20230130 | 1832 | 1970883 | 1910 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 1910 | 34.6649 | -120.3904 | No | Clear;32-90F | Pothead(Riser Termination) | Failed/Faulted | 23-0022722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808922 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512039965989 | 20230129 | 1545 | 20230130 | 230 | 1971039 | 645 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 9675 | 35.2842 | -120.6683 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0022766 | OH | Sus | 31635905 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808964 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | TRANSFORMER | T3033 | 20230129 | 2035 | 20230130 | 541 | 1971198 | 546 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 6552 | 35.1408 | -120.6226 | No | Clear;32-90F | Secondary | Deteriorated | 23-0022798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1809001 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 5589 | 20230130 | 748 | 20230130 | 1008 | 1971407 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 840 | 35.4181 | -120.6268 | No | Clear;32-90F |  |  | 23-0022891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1809159 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 9671 | 20230130 | 905 | 20230130 | 1243 | 1971531 | 218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1090 | 35.0828 | -120.5686 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0022847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1809093 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20230130 | 917 | 20230130 | 2303 | 1971636 | 826 | Distribution Circuit | 3rd Party | Vehicle | 544 | 61554 | 35.2197 | -120.5967 | No | Clear;32-90F | Anchor or Guy | Broken- wire on ground | 23-0022856 | OH | Sus | 35424119 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1809122 | 0 | EPSS Ckt | N | 2023 | B GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6233 | 20230130 | 1252 | 20230130 | 1414 | 1971970 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 246 | 35.5434 | -120.7436 | No | Clear;32-90F |  |  | 23-0023058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809229 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | RECLOSER | M46 | 20230131 | 1354 | 20230131 | 1841 | 1973007 | 287 | Distribution Circuit | 3rd Party | Vehicle | 1009 | 54647 | 34.8616 | -120.4506 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0023516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1809501 | 0 | EPSS Ckt | N | 2023 | BC GRD
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | TRANSFORMER | 513118052475 | 20230131 | 2128 | 20230201 | 308 | 1973263 | 340 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1020 | 34.9211 | -120.2981 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0023711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809562 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512402461147 | 20230131 | 2153 | 20230201 | 1510 | 1973306 | 1037 | Transformer only | 3rd Party | Vehicle | 2 | 2074 | 35.1541 | -120.5431 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0023720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809570 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | OTHER | J52591 TWD T0247 | 20230201 | 204 | 20230201 | 550 | 1973371 | 226 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 2938 | 35.2816 | -120.6637 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0023710 | UG | Sus | 31636085 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1809578 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | FUSE | 46251 | 20230201 | 911 | 20230201 | 1330 | 1973647 | 259 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 259 | 34.9207 | -120.4948 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0023855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809736 | 1 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 7945 | 20230202 | 1135 | 20230202 | 1521 | 1974903 | 226 | Distribution Circuit | 3rd Party | Vehicle | 7 | 1582 | 34.6446 | -120.5106 | No | Clear;32-90F | Pole-Wood | Broken | 23-0024402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810039 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | TRANSFORMER | T3445 | 20230202 | 1731 | 20230203 | 354 | 1975306 | 623 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 21805 | 34.9194 | -120.4226 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0024635 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810115 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 5927 | 20230203 | 652 | 20230203 | 1140 | 1975648 | 288 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 14112 | 35.4604 | -120.7525 | No | Clear;32-90F |  |  | 23-0024878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810319 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A18 | 20230203 | 1227 | 20230203 | 1901 | 1976011 | 389 | Distribution Circuit | 3rd Party | Vehicle | 1669 | 134768 | 35.449 | -120.6492 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0024956 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810344 | 0 | EPSS Ckt | N | 2023 | A-GRD
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | OTHER | WIRE DOWN 1 LD SIDE OF 98187 | 20230204 | 1120 | 20230204 | 1715 | 1976588 | 355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1400 | 35.5254 | -121.0606 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0025211 | OH | Sus | 45658702 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1810521 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T1475 | 20230204 | 2119 | 20230204 | 2227 | 1977068 | 68 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 204 | 35.0454 | -120.5539 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0025301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810604 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512362057222 | 20230204 | 2128 | 20230204 | 2224 | 1977072 | 56 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 56 | 35.0459 | -120.5533 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0025300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810603 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | TEMP LR 1101/2 | 20230205 | 215 | 20230205 | 253 | 1977173 | 38 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1022 | 38836 | 34.6967 | -120.1518 | No | Clear;32-90F |  |  | 23-0025321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810625 | 0 | EPSS Ckt | N | 2023 | C GRD TIME OC
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 5975 | 20230205 | 735 | 20230205 | 1745 | 1977284 | 610 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 6 | 3660 | 35.7104 | -120.381 | No | Clear;32-90F | Pole-Wood | Burned/flashed | 23-0025382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1810675 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | JUMPER | OJ 1 N/OF 45387 | 20230205 | 1611 | 20230205 | 2220 | 1977576 | 369 | Distribution Circuit | 3rd Party | Metallic Balloon | 42 | 15498 | 34.9678 | -120.4321 | No | Clear;32-90F | Jumper | Burned Open | 23-0025457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1810742 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | T1034 | 20230206 | 6 | 20230206 | 755 | 1977767 | 464 | Transformer only | Equipment Failure/Involved | Underground | 21 | 9744 | 35.13 | -120.5651 | No | Clear;32-90F | Conductor- Underground | Burned/flashed | 23-0025518 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810801 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | T3088 | 20230206 | 45 | 20230206 | 452 | 1977822 | 247 | Transformer only | Equipment Failure/Involved | Underground | 2 | 494 | 35.145 | -120.5201 | No | Clear;32-90F | Secondary | Broken | 23-0025528 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810811 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512219353251 | 20230206 | 958 | 20230206 | 1321 | 1978124 | 203 | Transformer only | Company Initiated | Coordination failure | 1 | 203 | 34.9359 | -120.5971 | No | Clear;32-90F | Transformer (OH) |  | 23-0025764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811005 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y12 | 20230206 | 1527 | 20230207 | 51 | 1978516 | 564 | Distribution Circuit | Equipment Failure/Involved | Overhead | 306 | 16362 | 34.6648 | -120.4223 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0025846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811029 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 6289 | 20230207 | 707 | 20230208 | 1519 | 1978825 | 1932 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 4784 | 34.9539 | -120.47 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0026064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1811158 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 512037264529 | 20230207 | 1224 | 20230207 | 1410 | 1979133 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 848 | 35.2441 | -120.6678 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0026243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811317 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 512041164537 | 20230207 | 1240 | 20230207 | 1410 | 1979206 | 90 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 540 | 35.2439 | -120.6669 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0026253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811323 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512304254163 | 20230208 | 105 | 20230208 | 152 | 1979632 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 705 | 34.9613 | -120.5698 | No | Partly Cloudy-Fog;32-90 F | PGs- Kearneys | Broken | 23-0026494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811419 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 14283 | 20230208 | 959 | 20230208 | 1300 | 1979937 | 181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 230 | 41630 | 35.4423 | -120.8953 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0026590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811599 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5655 | 20230209 | 802 | 20230209 | 1028 | 1980513 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2674 | 35.4572 | -120.4631 | No | Clear;32-90F |  |  | 23-0027047 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811907 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 724437 | 20230209 | 1317 | 20230209 | 1450 | 1981049 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 3348 | 35.2541 | -120.6279 | No | Clear;32-90F |  |  | 23-0027209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1811962 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512181759194 | 20230210 | 1027 | 20230210 | 1420 | 1981647 | 233 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 466 | 35.0987 | -120.615 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0027547 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812217 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V60 | 20230210 | 1031 | 20230211 | 134 | 1981749 | 719 | Distribution Circuit | Equipment Failure/Involved | Underground | 1257 | 224337 | 35.1846 | -120.7042 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0027522 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1812209 | 0 | EPSS Ckt | N | 2023 | AC GRD
LOS PADRES | SANTA MARIA | SANTA YNEZ 1104 | 182721104 | TRANSFORMER | 513822342218 | 20230210 | 2030 | 20230210 | 2350 | 1981919 | 200 | Transformer only | 3rd Party | Vehicle | 1 | 200 | 34.6427 | -120.0549 | No | Overcast-Fog;32-90 F | Pole - Tower- steel | Broken | 23-0027771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812327 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512436876818 | 20230210 | 2341 | 20230210 | 2351 | 1982131 | 10 | Transformer only | Equipment Failure/Involved | Underground | 2 | 20 | 35.5844 | -120.5448 | No | Clear;32-90F | Secondary | Burned Open | 23-0027769 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812325 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512435976858 | 20230210 | 2353 | 20230211 | 2243 | 1982130 | 1370 | Transformer only | Equipment Failure/Involved | Underground | 1 | 1370 | 35.5855 | -120.5451 | No | Clear;32-90 F | Secondary | Burned Open | 23-0027770 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812326 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | 511867880645 | 20230211 | 1424 | 20230211 | 1728 | 1982507 | 184 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 184 | 35.6855 | -120.739 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0027860 | OH | Sus | 31636587 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812445 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | 511867880645 | 20230212 | 1133 | 20230212 | 1217 | 1982908 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 44 | 35.6855 | -120.739 | No | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0027928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812519 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | 511867880645 | 20230212 | 1221 | 20230212 | 1735 | 1982927 | 314 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 314 | 35.6855 | -120.739 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0027929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812520 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 511987066328 | 20230212 | 1833 | 20230213 | 202 | 1983045 | 449 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 5388 | 35.2931 | -120.6865 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0027956 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812554 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 99195 | 20230212 | 2039 | 20230213 | 6 | 1983122 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1656 | 35.3927 | -120.8352 | No | Clear;32-90F |  |  | 23-0027993 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1812587 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 491705 | 20230213 | 557 | 20230213 | 740 | 1983214 | 103 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 137 | 35.6559 | -120.561 | No | Clear;32-90F | Metering Equipment | Broken | 23-0028059 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812666 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | TRANSFORMER | T65909 | 20230213 | 1055 | 20230213 | 1205 | 1983585 | 70 | Transformer only | Company Initiated | Return Circuit Normal | 18 | 1260 | 35.2589 | -120.6817 | No | Clear;32-90F | Transformer (UG) | Normal | 23-0028118 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812768 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512364957585 | 20230213 | 1256 | 20230213 | 2159 | 1983706 | 543 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1086 | 35.0556 | -120.5516 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0028283 | OH | Sus | 45670926 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812856 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 14055 | 20230213 | 1258 | 20230213 | 2022 | 1983688 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 15555 | 35.5649 | -121.1039 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0028167 | OH | Sus | 45670820 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812801 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 12079 | 20230213 | 1318 | 20230213 | 1457 | 1983735 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 660 | 34.8792 | -120.3095 | No | Clear;32-90F |  |  | 23-0028252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812832 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | OCB | 2113/2 | 20230214 | 624 | 20230214 | 1642 | 1984322 | 618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5539 | 387086 | 35.555 | -120.6803 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0028422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1812962 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511621867272 | 20230214 | 1109 | 20230214 | 1603 | 1984747 | 294 | Transformer only | Vegetation | Tree - fell into line | 2 | 588 | 35.3169 | -120.8099 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0028718 | OH | Sus | 45671843 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813190 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | JUMPER | 1965 | 20230214 | 1211 | 20230214 | 1416 | 1984860 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 3536 | 34.9091 | -120.4402 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0028747 | OH | Sus | 45671827 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1813201 | 1 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | FUSE | 352867 | 20230214 | 1219 | 20230214 | 1243 | 1984883 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 48 | 34.9006 | -120.5272 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0028695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1813182 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5031 | 20230214 | 1428 | 20230214 | 1610 | 1985137 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 15198 | 35.5561 | -121.0828 | No | Clear;32-90F |  |  | 23-0028868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813239 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510784176685 | 20230214 | 1612 | 20230214 | 2335 | 1985156 | 443 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4430 | 35.5681 | -121.0998 | No | Clear;32-90F | Cutout- fuse holder | Broken | 23-0028911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813265 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6889 | 20230214 | 1702 | 20230214 | 1925 | 1985331 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1859 | 35.4691 | -120.5003 | No | Overcast;32-90 F |  |  | 23-0028933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813278 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 4539 | 20230214 | 1731 | 20230214 | 2057 | 1985357 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 415 | 83000 | 35.1471 | -120.6354 | No | Clear;32-90F |  |  | 23-0028951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813291 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 10149 | 20230214 | 1805 | 20230215 | 614 | 1985379 | 729 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 729 | 35.5746 | -121.1112 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0028921 | OH | Sus | 45672140 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1813271 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 11075 | 20230214 | 2343 | 20230215 | 442 | 1985499 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 598 | 35.04 | -120.5458 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0028950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1813290 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | Y70 | 20230215 | 259 | 20230215 | 548 | 1985652 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 9464 | 34.7348 | -120.126 | No | Clear;32-90F |  |  | 23-0028981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813320 | 0 | EPSS Ckt | N | 2023 | B & C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | T3590 | 20230215 | 425 | 20230215 | 1257 | 1985660 | 512 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 6656 | 35.2418 | -120.676 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0028984 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813325 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512021666463 | 20230215 | 651 | 20230215 | 1420 | 1985702 | 449 | Transformer only | Equipment Failure/Involved | Overhead | 32 | 14368 | 35.2971 | -120.6751 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0029028 | OH | Sus | 31636905 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1813364 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | TRANSFORMER | 512699552112 | 20230215 | 955 | 20230215 | 1028 | 1986008 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 132 | 34.9077 | -120.4363 | No | Clear;32-90F | Fuse | Broken | 23-0029146 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813495 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y12 | 20230215 | 1318 | 20230215 | 1345 | 1986131 | 27 | Distribution Circuit | Vegetation | Tree - branch fell on line | 306 | 8262 | 34.6648 | -120.4223 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0029280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813532 | 0 | EPSS Ckt | N | 2023 | NA
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | FUSE | 14491 | 20230215 | 1828 | 20230215 | 2259 | 1986434 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 6233 | 35.4748 | -120.9134 | No | Clear;32-90F |  |  | 23-0029498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813614 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | SWITCH | 1235 | 20230215 | 1922 | 20230215 | 2126 | 1986472 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2521 | 307452 | 34.921 | -120.4369 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0029450 | OH | Sus | 31636865 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813581 | 1 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20230215 | 2352 | 20230216 | 613 | 1986537 | 381 | Distribution Circuit | 3rd Party | Vehicle | 930 | 293087 | 35.4622 | -120.6221 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0029501 | OH | Sus | 31636889 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1813618 | 0 | EPSS Ckt | N | 2023 | A-C
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5475 | 20230216 | 642 | 20230216 | 815 | 1986585 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2046 | 35.5643 | -120.5874 | No | Clear;32-90F |  |  | 23-0029578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813673 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512429943496 | 20230216 | 1140 | 20230217 | 716 | 1986905 | 1176 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1176 | 34.6687 | -120.519 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0029749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813768 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512157859950 | 20230217 | 23 | 20230217 | 740 | 1987248 | 437 | Transformer only | Equipment Failure/Involved | Overhead | 37 | 16169 | 35.1195 | -120.6234 | No | Clear;32-90F | Connector or Splice (OH) | Arcing | 23-0029963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813832 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 7543 | 20230217 | 822 | 20230217 | 1851 | 1987413 | 629 | Distribution Circuit | 3rd Party | Vehicle | 160 | 28145 | 34.6651 | -120.1137 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0030041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813925 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | 511922774606 | 20230217 | 939 | 20230217 | 1037 | 1987560 | 58 | Transformer only | Animal | Bird found | 9 | 522 | 35.5195 | -120.7169 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0030115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813993 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | TRANSFORMER | 512693553708 | 20230217 | 1018 | 20230217 | 1120 | 1987606 | 62 | Transformer only | Equipment Failure/Involved | Electrical Overload | 26 | 1612 | 34.9515 | -120.4396 | No | Clear;32-90 F | Fuse | Broken | 23-0030147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814009 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X24 | 20230217 | 2204 | 20230218 | 1336 | 1987974 | 932 | Distribution Circuit | Equipment Failure/Involved | Overhead | 257 | 62125 | 35.6532 | -120.3636 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0030384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814111 | 0 | EPSS Ckt | N | 2023 | NA
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 11315 | 20230218 | 848 | 20230218 | 1251 | 1988117 | 243 | Distribution Circuit | Animal | Bird found | 23 | 5511 | 34.6069 | -120.1253 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0030447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814175 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | MTR#1006257318 | 20230218 | 1546 | 20230219 | 1154 | 1988299 | 0 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 20536 | 35.384 | -120.8515 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0030490 | OH | Sus | 45678381 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814224 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 511660977707 | 20230218 | 1639 | 20230218 | 1829 | 1988316 | 110 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 220 | 35.6035 | -120.8078 | No | Clear;32-90F |  |  | 23-0030488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1814222 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 64141 | 20230219 | 620 | 20230219 | 1717 | 1988504 | 657 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1971 | 34.9576 | -120.5635 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0030524 | OH | Sus | 31638741 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814264 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 6997 | 20230219 | 900 | 20230219 | 1119 | 1988574 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 181 | 25159 | 34.5985 | -120.1926 | Yes | Clear;32-90F |  |  | 23-0030539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814289 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 6997 | 20230219 | 1543 | 20230219 | 1820 | 1988939 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 181 | 28417 | 34.5985 | -120.1926 | Yes | Clear;32-90F |  |  | 23-0030558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814310 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | TRANSFORMER | 510760976631 | 20230220 | 830 | 20230220 | 1901 | 1989245 | 631 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4417 | 35.5666 | -121.1078 | No | Clear;32-90F | Conductor- Overhead | Arcing | 23-0030651 | OH | Sus | 31638805 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814457 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5203 | 20230221 | 1224 | 20230222 | 1615 | 1995312 | 1671 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 6684 | 35.3517 | -120.3499 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0031983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815580 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | V74 | 20230221 | 1359 | 20230221 | 1513 | 1991198 | 74 | Distribution Circuit | Vegetation | Tree - branch fell on line | 382 | 14639 | 35.5459 | -121.0678 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0031155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814851 | 0 | EPSS Ckt | N | 2023 | A/C T
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 9187 | 20230221 | 1504 | 20230222 | 1950 | 1992112 | 1726 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 45814 | 35.5523 | -121.0773 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815009 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | RECLOSER | W14 | 20230221 | 1549 | 20230222 | 1246 | 1992794 | 1257 | Distribution Circuit | Vegetation | Tree - branch fell on line | 75 | 94275 | 35.4716 | -120.9799 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0031405 | OH | Sus | 31638768 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815044 | 0 | EPSS Ckt | N | 2023 | A/GRD
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 306275 | 20230221 | 1608 | 20230222 | 1703 | 1993039 | 1495 | Distribution Circuit | Vegetation | Tree - fell into line | 1253 | 237107 | 35.5721 | -121.1068 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031648 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815266 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 4539 | 20230221 | 1620 | 20230221 | 1842 | 1993096 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 415 | 58930 | 35.1471 | -120.6354 | Yes | Clear;32-90 F |  |  | 23-0031566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815190 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5031 | 20230221 | 1640 | 20230222 | 1007 | 1993318 | 1047 | Distribution Circuit | Vegetation | Tree - bark fell into line | 149 | 156003 | 35.5561 | -121.0828 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0032159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815746 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 986322 | 20230221 | 1702 | 20230222 | 2109 | 1993593 | 1623 | Distribution Circuit | Vegetation | Tree - fell into line | 1526 | 525303 | 35.5505 | -121.0725 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031545 | OH | Sus | 31638752 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1815171 | 0 | EPSS Ckt | N | 2023 | ABC/T
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 156519 | 20230221 | 1712 | 20230221 | 2233 | 1995864 | 321 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1605 | 35.035 | -120.5325 | Yes | Clear;32-90 F |  |  | 23-0031938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815537 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14127 | 20230221 | 1717 | 20230222 | 1626 | 1993748 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 34029 | 35.5578 | -121.0812 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032241 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815795 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 4979 | 20230221 | 1751 | 20230222 | 1049 | 1994306 | 1018 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 25394 | 35.36 | -120.8487 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1815406 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512015866220 | 20230221 | 1754 | 20230222 | 1626 | 1994427 | 1341 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 18774 | 35.2903 | -120.6765 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815575 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512012266204 | 20230221 | 1754 | 20230222 | 1615 | 1994426 | 1341 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 5364 | 35.2899 | -120.6779 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0032554 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815975 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 3081 | 20230221 | 1755 | 20230222 | 1519 | 1994464 | 1284 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 114276 | 35.3591 | -120.8415 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815441 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 2463 | 20230221 | 1755 | 20230221 | 2243 | 1994514 | 288 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 302 | 86976 | 35.31 | -120.8302 | Yes | Clear;32-90 F |  |  | 23-0031902 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815500 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO 1105 | 182631105 | RECLOSER | 512313 | 20230221 | 1801 | 20230222 | 1126 | 1994618 | 1045 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 127 | 125575 | 35.2791 | -120.6501 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0032177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815755 | 0 | EPSS Ckt | N | 2023 | A & B
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | FUSE | 6627 | 20230221 | 1803 | 20230223 | 1523 | 1994694 | 2720 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 23552 | 35.0547 | -120.5782 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815605 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | JUMPER | OJ 1 SPAN SE 14355 | 20230221 | 1809 | 20230223 | 1800 | 1997870 | 2871 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5742 | 35.062 | -120.5811 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1816019 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | JUMPER | JUMPERS 2P SW/OF CGC# 512036166409 | 20230221 | 1822 | 20230222 | 2012 | 1993953 | 1550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 18600 | 35.2956 | -120.6705 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0031749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815351 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1106 | 182061106 | OCB | 1106/2 | 20230221 | 1829 | 20230222 | 151 | 1994936 | 442 | Distribution Circuit | 3rd Party | Other | 2367 | 199186 | 34.9106 | -120.4462 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815319 | 0 | Non-EPSS | N | 2023 | PH OC - GRD OC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | 42344 | 20230221 | 1836 | 20230222 | 1320 | 1995012 | 1124 | Distribution Circuit | Vegetation | Tree - branch fell on line | 329 | 197204 | 35.2316 | -120.6362 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815326 | 0 | EPSS Ckt | N | 2023 | A-GRD
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | FUSE | 6963 | 20230221 | 1842 | 20230222 | 1210 | 1995063 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3728 | 35.9985 | -120.645 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031956 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815554 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 59719 | 20230221 | 1907 | 20230222 | 1404 | 1995364 | 1137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 4548 | 35.0528 | -120.564 | Yes | Clear;32-90 F |  |  | 23-0032462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815912 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 4539 | 20230221 | 1924 | 20230221 | 2334 | 1995689 | 250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 416 | 104000 | 35.1471 | -120.6354 | Yes | Clear;32-90 F |  |  | 23-0031973 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815570 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 1609 | 20230221 | 1928 | 20230221 | 2146 | 1995509 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 100 | 13800 | 34.6126 | -119.9879 | Yes | Overcast;32-90 F |  |  | 23-0031906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815505 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512557251771 | 20230221 | 1938 | 20230222 | 2109 | 1993876 | 1531 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 22965 | 34.8973 | -120.4834 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0032722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816103 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | TRANSFORMER | 512586345089 | 20230221 | 1944 | 20230222 | 1221 | 1995680 | 997 | Transformer only | Vegetation | Tree - grew into line | 12 | 11964 | 34.7133 | -120.4674 | Yes | Clear;32-90 F | Secondary | Arcing | 23-0032123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815711 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | JUMPER | WIRE DOWN @ 5393 | 20230221 | 1958 | 20230222 | 1600 | 1995724 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 8002 | 35.2837 | -120.8834 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | No | 1815517 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 14827 | 20230221 | 2009 | 20230222 | 1218 | 1996989 | 969 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 25194 | 35.3126 | -120.8462 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0032151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815741 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 2817 | 20230221 | 2115 | 20230222 | 121 | 1996021 | 246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 28290 | 35.3163 | -120.823 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815610 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 10793 | 20230221 | 2150 | 20230222 | 1117 | 1996106 | 807 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 11 | 8877 | 35.2273 | -120.6491 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815785 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | JUMPER | WIRE DOWN HOT @ 5187 | 20230222 | 644 | 20230223 | 1515 | 1996486 | 1951 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1951 | 35.3529 | -120.8439 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1815977 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | FUSE | 780907 | 20230222 | 647 | 20230222 | 1414 | 1997904 | 447 | Distribution Circuit | Environmental/External | Lightning | 5 | 2235 | 34.9208 | -120.4875 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Burned/flashed | 23-0032469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815917 | 1 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 20911 | 20230222 | 817 | 20230222 | 1321 | 1996796 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2736 | 34.6659 | -120.4137 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032211 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815778 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 156519 | 20230222 | 1109 | 20230222 | 1729 | 1997332 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1900 | 35.035 | -120.5325 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0032339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815844 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | Q18 | 20230222 | 1110 | 20230222 | 2042 | 1997194 | 572 | Distribution Circuit | Vegetation | Tree - fell into line | 1977 | 169494 | 35.0401 | -120.525 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815800 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 3849 | 20230222 | 1223 | 20230223 | 138 | 1997554 | 795 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 615 | 48269 | 35.5627 | -121.1006 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0032333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815843 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2493 | 20230222 | 2011 | 20230222 | 2241 | 1998197 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1650 | 35.2919 | -120.7532 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0032719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816100 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | SWITCH | 46191 | 20230222 | 2033 | 20230222 | 2041 | s1816116 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 167 | 1336 | 35.0277 | -120.5392 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1816116 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6309 | 20230223 | 114 | 20230223 | 935 | 1998762 | 478 | Distribution Circuit | 3rd Party | Vehicle | 88 | 14848 | 34.9591 | -120.5583 | Yes | Overcast-Fog;32-90 F | Crossarm- Wood | Broken | 23-0032826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816172 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | FUSE | 45789 | 20230223 | 250 | 20230223 | 1105 | 1998825 | 495 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 49 | 24432 | 34.9604 | -120.4416 | Yes | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0032840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816182 | 1 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511489069968 | 20230223 | 628 | 20230223 | 1301 | 1998867 | 393 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 5502 | 35.3892 | -120.8566 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0032980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816227 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y10 | 20230223 | 650 | 20230223 | 758 | 1998893 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1075 | 73100 | 34.665 | -120.4225 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0032860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1816188 | 0 | EPSS Ckt | N | 2023 | BC/GRD
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 91481 | 20230223 | 735 | 20230223 | 1518 | 1998940 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4630 | 35.443 | -120.8896 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1816222 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510857776050 | 20230223 | 933 | 20230223 | 1645 | 1999128 | 432 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2872 | 35.5511 | -121.0747 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0033111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816290 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 206195 | 20230223 | 951 | 20230223 | 1625 | 1999199 | 394 | Distribution Circuit | 3rd Party | Vehicle | 18 | 3652 | 34.9444 | -120.5113 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0033006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816241 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510833076452 | 20230223 | 1229 | 20230224 | 1130 | 1999300 | 1381 | Transformer only | Environmental/External | Water | 1 | 1381 | 35.5623 | -121.0838 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0033145 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816304 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y10 | 20230223 | 1239 | 20230223 | 1440 | 1999497 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1083 | 131043 | 34.665 | -120.4225 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0033154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816306 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | FUSE | 512733253226 | 20230223 | 2019 | 20230224 | 701 | 2000440 | 638 | Distribution Circuit | 3rd Party | Vehicle | 75 | 24684 | 34.9385 | -120.426 | Yes | Overcast;32-90 F | Pole-Wood | Broken | 23-0033264 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816447 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V60 | 20230223 | 2120 | 20230223 | 2301 | 2000674 | 101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1256 | 126856 | 35.1846 | -120.7042 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816480 | 0 | EPSS Ckt | N | 2023 | A & B
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 20741 | 20230224 | 34 | 20230224 | 736 | 2001318 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2954 | 34.6551 | -120.5377 | Yes | Clear;32-90 F | Jumper | Broken | 23-0033568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816601 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 3561 | 20230224 | 438 | 20230224 | 1402 | 2002560 | 564 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 6204 | 35.2923 | -120.7158 | Yes | Clear;32-90 F | Insulator | Broken | 23-0034003 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816974 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512120065569 | 20230224 | 445 | 20230224 | 838 | 2002602 | 233 | Transformer only | Vegetation | Tree - palm frond fell into line | 8 | 1864 | 35.2732 | -120.6413 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816847 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | 512102664116 | 20230224 | 454 | 20230224 | 1652 | 2002687 | 718 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1436 | 35.2335 | -120.6457 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0034136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817067 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 834556 | 20230224 | 456 | 20230224 | 953 | 2002680 | 297 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 16335 | 35.194 | -120.7339 | Yes | Clear;32-90 F |  |  | 23-0033918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1816907 | 0 | EPSS Ckt | N | 2023 | B/C
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 15377 | 20230224 | 509 | 20230224 | 829 | 2002714 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 369 | 73770 | 35.0517 | -120.5267 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0033796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816812 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 20139 | 20230224 | 511 | 20230224 | 1215 | 2003221 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 4240 | 34.73 | -120.4364 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0033704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816741 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | 512106864089 | 20230224 | 519 | 20230224 | 1225 | 2002751 | 426 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 2130 | 35.2329 | -120.6442 | Yes | Clear;32-90 F |  |  | 23-0034111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1817053 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | RECLOSER | V28 | 20230224 | 524 | 20230225 | 1915 | 2002795 | 2271 | Distribution Circuit | Vegetation | Tree - fell into line | 512 | 214283 | 35.0973 | -120.6074 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1816706 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | RECLOSER | V32 | 20230224 | 525 | 20230225 | 1725 | 2002818 | 2160 | Distribution Circuit | Vegetation | Tree - fell into line | 2050 | 565622 | 35.1042 | -120.6199 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033669 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1816707 | 0 | EPSS Ckt | N | 2023 | A-B-C
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | RECLOSER | V26 | 20230224 | 527 | 20230224 | 2004 | 2002836 | 877 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2483 | 287366 | 35.0985 | -120.6074 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033671 | OH | Sus | 35427605 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816709 | 0 | EPSS Ckt | N | 2023 | B C GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5203 | 20230224 | 527 | 20230224 | 1023 | 2002887 | 296 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1184 | 35.3517 | -120.3499 | Yes | Clear;32-90 F |  |  | 23-0034068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817017 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | RECLOSER | M30 | 20230224 | 539 | 20230224 | 1749 | 2002995 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 39070 | 34.9566 | -120.5089 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0033681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816718 | 0 | Non-EPSS | N | 2023 | SGF
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 45807 | 20230224 | 543 | 20230224 | 1335 | 2005307 | 472 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 472 | 35.0211 | -120.5058 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Fuse | Broken | 23-0034092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817036 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 11051 | 20230224 | 546 | 20230224 | 1238 | 2003024 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 574 | 195364 | 35.0269 | -120.4913 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1816757 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 1609 | 20230224 | 553 | 20230224 | 912 | 2003053 | 199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 100 | 19900 | 34.6126 | -119.9879 | Yes | Partly Cloudy-Heavy Rain;32-90 F |  |  | 23-0033834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816846 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 511959466168 | 20230224 | 643 | 20230224 | 1307 | 2003533 | 384 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 768 | 35.2883 | -120.6958 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0033753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816781 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | T0247 | 20230224 | 828 | 20230224 | 1029 | 2004224 | 121 | Transformer only | Equipment Failure/Involved | Underground | 21 | 2541 | 34.8718 | -120.4415 | Yes | Clear;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0033881 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816882 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | TRANSFORMER | 512263357529 | 20230224 | 903 | 20230224 | 1118 | 2004440 | 135 | Transformer only | Environmental/External | Water | 2 | 270 | 35.0538 | -120.5854 | Yes | Clear;32-90 F | Transformer | Burned Open | 23-0034024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816987 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 1461 | 20230224 | 929 | 20230224 | 1153 | 2004705 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 6048 | 35.0209 | -120.5049 | Yes | Clear;32-90 F |  |  | 23-0034036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816997 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512304054108 | 20230224 | 1027 | 20230224 | 1258 | 2002765 | 151 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 2567 | 34.9598 | -120.5698 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0033971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816948 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512169859406 | 20230224 | 1030 | 20230224 | 1907 | 2004971 | 517 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1551 | 35.1047 | -120.6193 | Yes | Clear;32-90 F | Secondary | Burned/flashed | 23-0034257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817149 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | FUSE | 20269 | 20230224 | 1132 | 20230224 | 1243 | 2005213 | 71 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 1065 | 34.6014 | -120.1642 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817039 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 11395 | 20230224 | 1507 | 20230224 | 2210 | 2005939 | 423 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 846 | 34.5956 | -120.0662 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Elbow | Burned/flashed | 23-0034366 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817236 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512210159345 | 20230224 | 1641 | 20230224 | 1717 | 2006267 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 540 | 35.1031 | -120.6056 | Yes | Clear;32-90 F | Fuse | Broken | 23-0034428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817281 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512855052379 | 20230224 | 1801 | 20230224 | 2224 | 2006534 | 263 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 789 | 34.9161 | -120.3847 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0034513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817363 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20230224 | 2122 | 20230227 | 1655 | 2007224 | 4037 | Distribution Circuit | Environmental/External | Ice or snow | 394 | 545003 | 35.3806 | -120.4438 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817520 | 0 | EPSS Ckt | N | 2023 | B-C- GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | JUMPER | OJ 3 SPANS W/O MTR 1007996385 | 20230224 | 2122 | 20230226 | 1540 | 2009475 | 2538 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 2538 | 35.3402 | -120.3546 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0035568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1818418 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30681 | 20230224 | 2122 | 20230227 | 1454 | 2009484 | 3932 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 19660 | 35.3678 | -120.3989 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1818420 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5143 | 20230224 | 2122 | 20230226 | 1900 | 2009787 | 2738 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 38332 | 35.3109 | -120.3215 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818476 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 7047 | 20230224 | 2122 | 20230228 | 1557 | 2009895 | 5435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 16305 | 35.3807 | -120.419 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818518 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5203 | 20230224 | 2122 | 20230301 | 1402 | 2010199 | 6760 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 27040 | 35.3517 | -120.3499 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818606 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | SWITCH | 6535 | 20230224 | 2122 | 20230301 | 1715 | 2010827 | 6953 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 27812 | 35.2555 | -120.2714 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818755 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 20230224 | 2126 | 20230226 | 2130 | 2007226 | 2884 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 156400 | 35.4345 | -120.2869 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817541 | 0 | EPSS Ckt | N | 2023 | C GRD
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | JUMPER | OJ CGC 511472570177 | 20230224 | 2157 | 20230225 | 1017 | 2007332 | 740 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3533 | 1351848 | 35.3949 | -120.8623 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0034906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1817767 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 796386 | 20230224 | 2232 | 20230225 | 2127 | 2007344 | 1375 | Distribution Circuit | Environmental/External | Ice or snow | 18 | 24750 | 35.8461 | -120.3793 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0034996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1817862 | 0 | EPSS Ckt | N | 2023 | A- B- GRD- 51 TIME
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | JUMPER | FLYING BELLS N/OF & E/OF CGC# 41579520062 | 20230224 | 2232 | 20230226 | 1757 | 2009454 | 2605 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 221425 | 35.8801 | -120.4222 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818413 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 10264 | 20230224 | 2232 | 20230301 | 1520 | 2010229 | 6768 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 25227 | 35.9053 | -120.4339 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035797 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818617 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 2781 | 20230224 | 2238 | 20230302 | 713 | 2009452 | 7715 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 15430 | 35.8653 | -120.4003 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1818412 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | JUMPER | FB 1 E OF 30299 | 20230224 | 2238 | 20230227 | 1430 | 2010398 | 3832 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 76640 | 35.9207 | -120.4923 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818679 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRIP-SAVER | 5597 | 20230224 | 2238 | 20230227 | 1106 | 2010405 | 3628 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 65304 | 35.9127 | -120.4393 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818682 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | R82 | 20230224 | 2317 | 20230225 | 1735 | 2007390 | 1098 | Distribution Circuit | 3rd Party | Vehicle | 897 | 521024 | 35.5299 | -120.523 | Yes | Partly Cloudy-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817872 | 0 | EPSS Ckt | N | 2023 | B C GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 635958 | 20230225 | 49 | 20230226 | 23 | 2007447 | 1414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 153471 | 35.3248 | -120.5176 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0035007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1817874 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | JUMPER | OJ 2 POLES SS CGC 513347454906 | 20230225 | 57 | 20230228 | 1245 | 2013587 | 5028 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 15084 | 34.9893 | -120.222 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0036737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1819297 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M52 | 20230225 | 58 | 20230227 | 1929 | 2007453 | 3991 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 267397 | 34.9254 | -120.3465 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0035009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817876 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 64223 | 20230225 | 157 | 20230225 | 1819 | 2007479 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 22098 | 35.1231 | -120.5669 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1817906 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X08 | 20230225 | 218 | 20230225 | 2049 | 2007511 | 1111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 66660 | 35.7094 | -120.3018 | Yes | Clear;32-90F |  |  | 23-0035018 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817885 | 0 | EPSS Ckt | N | 2023 | A C
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 5591 | 20230225 | 218 | 20230226 | 1210 | 2009184 | 2032 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 28448 | 35.6437 | -120.2095 | Yes | Clear;32-90F |  |  | 23-0035439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818287 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 3683 | 20230225 | 703 | 20230225 | 1610 | 2007764 | 547 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6564 | 35.6589 | -120.3638 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0035373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818210 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 452469 | 20230225 | 806 | 20230227 | 1412 | 2007842 | 3246 | Distribution Circuit | 3rd Party | Other | 14 | 18584 | 34.6645 | -120.029 | Yes | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035146 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1818005 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | M70 | 20230225 | 827 | 20230225 | 1126 | 2007815 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 2892 | 35.0285 | -120.4965 | Yes | Partly Cloudy-Fog;32-90 F | Cutout- fuse holder | Arcing | 23-0035066 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1817930 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X06 | 20230225 | 840 | 20230225 | 1811 | 2007913 | 571 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 13704 | 35.7373 | -120.2882 | Yes | Clear;32-90F |  |  | 23-0035080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1817943 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | JUMPER | OJ 2 SPANS W/OF CGC 513521840499 | 20230225 | 1127 | 20230225 | 1930 | 2008329 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6762 | 34.5944 | -120.1545 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0035176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1818026 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 30053 | 20230225 | 1439 | 20230225 | 2251 | 2008737 | 492 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 7872 | 35.6553 | -120.3704 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0035307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1818153 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 30019 | 20230225 | 1615 | 20230228 | 1755 | 2008905 | 4420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 11086 | 35.291 | -120.4757 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818344 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T3439 | 20230225 | 1637 | 20230225 | 1847 | 2008945 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 130 | 35.0207 | -120.5063 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0035442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818290 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | FUSE | 8633 | 20230225 | 1638 | 20230225 | 1753 | 2008976 | 75 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 31 | 2325 | 35.0417 | -120.5696 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0035421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818267 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5655 | 20230225 | 1656 | 20230226 | 1229 | 2009187 | 1173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 64515 | 35.4572 | -120.4631 | Yes | Overcast-Rain;32-90 F | Insulator | Broken | 23-0035491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818338 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 30395 | 20230225 | 1811 | 20230226 | 1521 | 2009103 | 1270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2540 | 35.6779 | -120.3949 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0035428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818276 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512333062665 | 20230225 | 1936 | 20230226 | 1223 | 2009333 | 1007 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1007 | 35.1941 | -120.5676 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0035571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818422 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6095 | 20230226 | 627 | 20230226 | 1100 | 2009631 | 273 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 12558 | 35.536 | -120.8438 | Yes | Overcast-Fog;32-90 F |  |  | 23-0035680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818523 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9303 | 20230226 | 1315 | 20230226 | 1501 | 2010006 | 106 | Distribution Circuit | Vegetation | Tree - grew into line | 8 | 848 | 35.1472 | -120.6003 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0035734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1818568 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | TRANSFORMER | 510762876772 | 20230227 | 932 | 20230227 | 956 | 2011603 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 264 | 35.5704 | -121.1072 | Yes | Partly Cloudy;32-90 F | Sectionalizer | Broken | 23-0036189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1818925 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 11347 | 20230227 | 1237 | 20230227 | 1309 | 2012194 | 32 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 192 | 34.6244 | -120.1875 | Yes | Overcast;32-90 F | Cutout- fuse holder | Broken | 23-0036363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819029 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20230227 | 1306 | 20230227 | 1401 | 2012423 | 55 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 279 | 15345 | 35.7984 | -120.9741 | Yes | Clear;32-90F |  |  | 23-0036493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1819101 | 0 | EPSS Ckt | N | 2023 | AB
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 6845 | 20230227 | 1348 | 20230227 | 1658 | 2012572 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 10260 | 34.8317 | -120.2332 | Yes | Clear;32-90F |  |  | 23-0036545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1819133 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6525 | 20230227 | 1350 | 20230228 | 115 | 2012570 | 685 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 13 | 3205 | 35.0008 | -120.532 | Yes | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0036592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1819168 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | JUMPER | OJ @ R531 | 20230227 | 1716 | 20230227 | 2033 | 2013256 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2685 | 65657 | 34.9526 | -120.5742 | Yes |  | Jumper | Burned Open | 23-0036683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1819245 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511535168873 | 20230228 | 301 | 20230228 | 935 | 2014093 | 394 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 3940 | 35.3595 | -120.8401 | Yes | Clear;32-90F |  |  | 23-0037052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819589 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 30225 | 20230228 | 450 | 20230228 | 940 | 2014129 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 19720 | 35.4909 | -120.7302 | Yes | Clear;32-90F | Insulator | Broken | 23-0037063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1819594 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512209271510 | 20230228 | 1253 | 20230228 | 1615 | 2015216 | 202 | Transformer only | Equipment Failure/Involved | Underground | 1 | 202 | 35.4372 | -120.6162 | Yes | Clear;32-90F | Conductor- Underground | Deteriorated | 23-0037414 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819820 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | FUSE | 790635 | 20230228 | 1253 | 20230228 | 1300 | 2015035 | 7 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 413 | 35.1575 | -120.6726 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0037353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819761 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 7921 | 20230228 | 1650 | 20230301 | 1325 | 2016258 | 1235 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1235 | 34.6473 | -119.9737 | Yes | Clear;32-90F | Conductor- Underground | Deteriorated | 23-0037695 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820027 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 64029 | 20230228 | 1724 | 20230228 | 1828 | 2016340 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 5632 | 34.9526 | -120.4285 | Yes | Clear;32-90F |  |  | 23-0037646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819982 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | TRANSFORMER | 510762276810 | 20230228 | 2335 | 20230301 | 1047 | 2017256 | 672 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 6720 | 35.5714 | -121.1075 | Yes | Clear;32-90F | Cutout- fuse holder | Broken | 23-0037876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820208 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 45241 | 20230301 | 30 | 20230301 | 1425 | 2017293 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 52605 | 35.0671 | -120.3919 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1820243 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 4539 | 20230301 | 59 | 20230301 | 303 | 2017322 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 415 | 51460 | 35.1471 | -120.6354 | No | Clear;32-90F |  |  | 23-0037898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1820231 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | FUSE | 469377 | 20230301 | 218 | 20230301 | 425 | 2017406 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2032 | 35.245 | -120.6827 | No | Clear;32-90F |  |  | 23-0037905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1820240 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5475 | 20230301 | 617 | 20230301 | 842 | 2017621 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3190 | 35.5643 | -120.5874 | No | Clear;32-90F |  |  | 23-0037985 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1820291 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 6091 | 20230301 | 1027 | 20230302 | 42 | 2018027 | 855 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3420 | 34.5858 | -120.5241 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0038160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1820393 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | TRANSFORMER | 512675552987 | 20230301 | 1108 | 20230301 | 1344 | 2018134 | 156 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 156 | 34.9317 | -120.445 | No | Clear;32-90F | Cutout- fuse holder | Broken | 23-0038195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820425 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | JUMPER | OJ 15 SS/OF CGC ENDING IN 8996 | 20230301 | 1528 | 20230301 | 1731 | 2018597 | 123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 246 | 35.6511 | -120.177 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0038304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820504 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 3417 | 20230302 | 808 | 20230302 | 1341 | 2019432 | 333 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2997 | 35.3861 | -120.7747 | No | Clear;32-90F |  |  | 23-0038838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1820882 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9419 | 20230302 | 819 | 20230302 | 2018 | 2019496 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 11109 | 35.1348 | -120.5045 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0038658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1820785 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 93151 | 20230302 | 1446 | 20230302 | 1643 | 2020068 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 7371 | 35.3028 | -120.8494 | No | Clear;32-90F |  |  | 23-0038959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1820966 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 12103 | 20230302 | 1546 | 20230302 | 1807 | 2020153 | 141 | Distribution Circuit | 3rd Party | Metallic Balloon | 9 | 1269 | 34.9153 | -120.3374 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0039030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821024 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | OTHER | J9585 TWD T506914 | 20230302 | 1914 | 20230302 | 2135 | 2020520 | 141 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 141 | 35.5221 | -121.0614 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0038822 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821048 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30681 | 20230303 | 658 | 20230303 | 1058 | 2020743 | 238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1190 | 35.3678 | -120.3989 | No | Clear;32-90F |  |  | 23-0039414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821272 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512506743098 | 20230303 | 1035 | 20230303 | 1515 | 2021118 | 280 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 280 | 34.6585 | -120.4928 | No | Clear;32-90F | Transformer (OH) | Deteriorated | 23-0039401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821259 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9421 | 20230303 | 1329 | 20230304 | 1722 | 2021386 | 1673 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5019 | 35.1295 | -120.5089 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1821374 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | TRANSFORMER | 513333852318 | 20230303 | 1600 | 20230305 | 1840 | 2024050 | 3040 | Transformer only | Equipment Failure/Involved | Underground | 2 | 6080 | 34.917 | -120.2248 | No | Clear;32-90F | Conductor- Underground | Deteriorated | 23-0040445 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1822178 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 20145 | 20230304 | 718 | 20230304 | 1055 | 2022109 | 217 | Distribution Circuit | Animal | Other | 43 | 9331 | 34.583 | -120.4122 | No | Overcast-Fog;32-90 F | Anchor or Guy | Normal | 23-0039887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821650 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | FUSE | 15875 | 20230304 | 722 | 20230304 | 808 | 2022113 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 245 | 35.5259 | -120.9662 | No | Clear;32-90F |  |  | 23-0039888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821651 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | OCB | 1110/2 | 20230304 | 1923 | 20230305 | 1427 | 2022881 | 1144 | Distribution Circuit | Equipment Failure/Involved | Underground | 3168 | 20146 | 34.9503 | -120.4442 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 23-0040077 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821821 | 0 | EPSS Ckt | N | 2023 | NA
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | 55374 | 20230304 | 1936 | 20230304 | 2052 | 2022889 | 76 | Distribution Circuit | Equipment Failure/Involved | Overhead | 519 | 28322 | 35.6203 | -120.6962 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0040079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821824 | 0 | EPSS Ckt | N | 2023 | A&GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | FUSE | 6422 | 20230305 | 446 | 20230305 | 1207 | 2023227 | 441 | Distribution Circuit | Equipment Failure/Involved | Underground | 194 | 46654 | 35.6158 | -120.6732 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Broken | 23-0040227 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821976 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512663753609 | 20230306 | 906 | 20230306 | 1752 | 2024413 | 526 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1578 | 34.9486 | -120.4495 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0040611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822320 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 2417 | 20230306 | 1052 | 20230307 | 144 | 2024567 | 892 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 16056 | 35.1893 | -120.7004 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 23-0040685 | OH | Sus | 35427605 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1822352 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | TRANSFORMER | 512061066010 | 20230306 | 2228 | 20230307 | 1210 | 2025147 | 822 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 4110 | 35.285 | -120.6613 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0040998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822533 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 5177 | 20230307 | 1431 | 20230307 | 1646 | 2025741 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1755 | 35.2894 | -120.7467 | No | Clear;32-90F |  |  | 23-0041327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1822667 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | T2511 | 20230307 | 1553 | 20230307 | 1741 | 2025822 | 108 | Transformer only | Equipment Failure/Involved | Underground | 20 | 2160 | 35.5553 | -120.7087 | No | Clear;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0041334 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822672 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | FUSE | 45903 | 20230308 | 1029 | 20230308 | 1041 | 2026557 | 12 | Distribution Circuit | Animal | Other | 143 | 1716 | 34.9054 | -120.4355 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0041629 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1822892 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 20793 | 20230308 | 1435 | 20230308 | 1646 | 2026819 | 131 | Distribution Circuit | Animal | Squirrel | 5 | 655 | 34.6499 | -120.1154 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0041780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1822954 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | TRANSFORMER | 513002552469 | 20230308 | 1617 | 20230308 | 1638 | 2026831 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 21 | 34.9194 | -120.335 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0041810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822964 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 5591 | 20230308 | 1630 | 20230308 | 1817 | 2026917 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1498 | 35.6437 | -120.2095 | No | Partly Cloudy;32-90 F |  |  | 23-0041837 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1822978 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512655754293 | 20230308 | 1801 | 20230308 | 2334 | 2026937 | 333 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1665 | 34.9674 | -120.4526 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0041836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822977 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512878643482 | 20230308 | 1814 | 20230309 | 145 | 2026959 | 451 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 451 | 34.6717 | -120.3686 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0041840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822981 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 2107 | 20230308 | 2102 | 20230308 | 2245 | 2027083 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 7313 | 35.2309 | -120.7463 | No | Clear;32-90F |  |  | 23-0041900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823039 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512425260958 | 20230309 | 640 | 20230309 | 1009 | 2027191 | 209 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 627 | 35.149 | -120.5348 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0042034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823083 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | FUSE | 45209 | 20230309 | 1123 | 20230309 | 1326 | 2027672 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 369 | 34.9651 | -120.3031 | Yes | Clear;32-90F |  |  | 23-0042177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823135 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 12103 | 20230309 | 1159 | 20230310 | 732 | 2027470 | 1173 | Distribution Circuit | 3rd Party | Other | 9 | 10557 | 34.9153 | -120.3374 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0042221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823149 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | TRANSFORMER | 511688768692 | 20230309 | 1215 | 20230309 | 1600 | 2027346 | 225 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 225 | 35.3562 | -120.789 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0042123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823115 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512261255729 | 20230309 | 1335 | 20230309 | 1603 | 2027509 | 148 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 148 | 35.004 | -120.5862 | Yes | Clear;32-90F | Transformer (OH) | Deteriorated | 23-0042181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823137 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512309754466 | 20230309 | 1629 | 20230309 | 1919 | 2028099 | 170 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 850 | 34.9699 | -120.5683 | Yes | Clear;32-90F | Cutout- fuse holder | Broken | 23-0042364 | OH | Sus | 31639768 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823205 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 2453 | 20230309 | 2056 | 20230310 | 954 | 2028625 | 778 | Distribution Circuit | Equipment Failure/Involved | Overhead | 433 | 23462 | 35.3865 | -120.8534 | Yes | Clear;32-90 F | Secondary | Broken | 23-0042576 | OH | Sus | 31639770 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823394 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 2797 | 20230309 | 2224 | 20230310 | 34 | 2029555 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 9360 | 35.4782 | -120.709 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0042661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823469 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 31913 | 20230309 | 2241 | 20230310 | 323 | 2029622 | 282 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 846 | 35.5088 | -120.5153 | Yes | Clear;32-90F |  |  | 23-0042716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823528 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5203 | 20230309 | 2316 | 20230310 | 1411 | 2031203 | 895 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 3580 | 35.3517 | -120.3499 | Yes | Clear;32-90F |  |  | 23-0043159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823765 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 7339 | 20230310 | 0 | 20230310 | 130 | 2029720 | 90 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 2160 | 35.4685 | -120.6986 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0042686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823494 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2233 | 20230310 | 9 | 20230310 | 224 | 2029763 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 82 | 11070 | 35.5021 | -120.4709 | No | Clear;32-90F |  |  | 23-0042693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823503 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 618168 | 20230310 | 39 | 20230310 | 1350 | 2029805 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 45041 | 35.5454 | -121.076 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042684 | OH | Sus | 31639699 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823492 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 3997 | 20230310 | 109 | 20230310 | 231 | 2029849 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 7216 | 35.4584 | -120.6836 | No | Clear;32-90F |  |  | 23-0042685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823493 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1103 | 182571103 | JUMPER | OJ LD SIDE OF 567884 | 20230310 | 117 | 20230310 | 310 | 2029892 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 9379 | 34.8453 | -120.5127 | No | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 23-0042701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1823514 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 5925 | 20230310 | 209 | 20230310 | 715 | 2030041 | 306 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 6732 | 35.459 | -120.7357 | No | Clear-Strong Winds;32-90 F |  |  | 23-0042785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823582 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 3635 | 20230310 | 230 | 20230310 | 1045 | 2029951 | 495 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 1980 | 35.445 | -120.6298 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0042722 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823534 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | R52 | 20230310 | 301 | 20230310 | 519 | 2029983 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 703 | 97014 | 35.6376 | -120.5775 | No | Clear;32-90F |  |  | 23-0042707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823519 | 0 | EPSS Ckt | N | 2023 | A GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 6635 | 20230310 | 341 | 20230310 | 637 | 2030022 | 176 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 49984 | 35.3924 | -120.6076 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0042751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823565 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 79696 | 20230310 | 430 | 20230311 | 1709 | 2030069 | 2199 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 16878 | 35.5731 | -121.0414 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042736 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823550 | 0 | EPSS Ckt | N | 2023 | A-C-SGF
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512165271683 | 20230310 | 433 | 20230310 | 1054 | 2030068 | 381 | Transformer only | 3rd Party | Customer Equipment | 3 | 1143 | 35.4416 | -120.6313 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0042972 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823684 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | R94 | 20230310 | 434 | 20230310 | 1408 | 2030078 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 104468 | 35.5605 | -120.7743 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823555 | 0 | EPSS Ckt | N | 2023 | A-B-GRD
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | JUMPER | OJ 5 LD SIDE OF 6417 | 20230310 | 545 | 20230310 | 1045 | 2030554 | 300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 4746 | 34.9092 | -120.5287 | No | Clear;32-90F | Jumper | Burned Open | 23-0042865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1823626 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 7387 | 20230310 | 712 | 20230311 | 1043 | 2030285 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 420 | 532300 | 35.7073 | -120.9713 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823730 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 4751 | 20230310 | 1041 | 20230310 | 1914 | 2030719 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 22390 | 35.5487 | -121.0749 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0043197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823790 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 306275 | 20230310 | 1121 | 20230310 | 1634 | 2030796 | 313 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 46637 | 35.5721 | -121.1068 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043082 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823726 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 14679 | 20230310 | 1328 | 20230310 | 1442 | 2031068 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 3552 | 35.1233 | -120.5706 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0043136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823750 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | V66 | 20230310 | 1352 | 20230312 | 1327 | 2031104 | 2855 | Distribution Circuit | Environmental/External | Flood/Erosion | 329 | 746743 | 35.3759 | -120.8526 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823744 | 0 | EPSS Ckt | N | 2023 | B GRD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 618168 | 20230310 | 1409 | 20230310 | 1515 | 2031133 | 66 | Distribution Circuit | Company Initiated | Improper Construction | 27 | 1782 | 35.5454 | -121.076 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0042684 | OH | Sus | 31639699 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823751 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 5201 | 20230310 | 1411 | 20230313 | 2330 | 2031223 | 4879 | Distribution Circuit | Environmental/External | Flood/Erosion | 47 | 229313 | 35.4804 | -120.8412 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823830 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 618168 | 20230310 | 1522 | 20230310 | 1532 | 2031271 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 151 | 1386 | 35.5454 | -121.076 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0042684 | OH | Sus | 31639699 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823777 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 986322 | 20230310 | 1713 | 20230311 | 1615 | 2031458 | 1382 | Distribution Circuit | Environmental/External | Flood/Erosion | 25 | 7730 | 35.5505 | -121.0725 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0043219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823812 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 5595 | 20230310 | 1822 | 20230311 | 1759 | 2031531 | 1417 | Distribution Circuit | Environmental/External | Flood/Erosion | 56 | 22696 | 35.9016 | -120.4446 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823893 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 30053 | 20230310 | 2031 | 20230311 | 1445 | 2031663 | 1094 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 17504 | 35.6553 | -120.3704 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0043316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1823900 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 511976061495 | 20230310 | 2127 | 20230311 | 1029 | 2031650 | 782 | Transformer only | Vegetation | Tree - fell into line | 8 | 6256 | 35.1601 | -120.6857 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0043313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823898 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 460229 | 20230311 | 657 | 20230311 | 1350 | 2031990 | 413 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 5369 | 35.5795 | -120.9671 | No | Clear;32-90F |  |  | 23-0043477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824030 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 14859 | 20230311 | 1309 | 20230311 | 1510 | 2032188 | 121 | Distribution Circuit | Environmental/External | Flood/Erosion | 83 | 10043 | 35.1938 | -120.4327 | No | Clear;32-90F | Pole-Wood | Broken | 23-0043404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823970 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512812744039 | 20230311 | 1505 | 20230311 | 1755 | 2032579 | 170 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 340 | 34.6864 | -120.3918 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0043534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824075 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | RECLOSER | M16 | 20230311 | 1809 | 20230311 | 1832 | 2032752 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2122 | 48806 | 34.9603 | -120.4226 | No | Clear;32-90F | Regulator | Failed/Faulted | 23-0043546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824086 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | JUMPER | OJ @ CGC# 413760018157 | 20230312 | 1050 | 20230312 | 1356 | 2033134 | 186 | Distribution Circuit | Environmental/External | Flood/Erosion | 13 | 2418 | 35.8157 | -121.1022 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0043655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824190 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 78269 | 20230312 | 1321 | 20230312 | 1730 | 2033316 | 249 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 498 | 35.5738 | -121.0397 | No | Clear;32-90F | Pole-Wood | Broken | 23-0043734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824250 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 15845 | 20230312 | 1343 | 20230312 | 1432 | 2033380 | 49 | Distribution Circuit | Company Initiated | Improper Construction | 328 | 10152 | 35.3872 | -120.8388 | No | Clear;32-90F | Fuse | Burned Open | 23-0043743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824260 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | T1881 | 20230312 | 2029 | 20230313 | 2117 | 2033707 | 1488 | Distribution Circuit | Equipment Failure/Involved | Underground | 61 | 45601 | 35.2487 | -120.6373 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 23-0043908 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824422 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | RECLOSER | 605393 | 20230313 | 46 | 20230313 | 451 | 2033865 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 22050 | 35.8451 | -120.7004 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0043923 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824437 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512350260858 | 20230313 | 50 | 20230313 | 1329 | 2033864 | 759 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 4554 | 35.1457 | -120.56 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0044009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824490 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 7513 | 20230313 | 900 | 20230313 | 1303 | 2034286 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 243 | 35.5921 | -120.7957 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824505 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SANTA MARIA-1108 | 182671108 | FUSE | 15693 | 20230313 | 1513 | 20230317 | 1554 | 2035088 | 5801 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 23204 | 35.1421 | -120.3568 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824643 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PERRY-1101 | 183071101 | FUSE | 7913 | 20230313 | 1531 | 20230314 | 432 | 2034779 | 781 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1562 | 35.6116 | -120.9121 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824646 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511518067086 | 20230313 | 2049 | 20230314 | 245 | 2035071 | 356 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 6764 | 35.3102 | -120.8445 | No | Clear;32-90F | Transformer (OH) | Leaking | 23-0044376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824641 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5203 | 20230314 | 706 | 20230314 | 1035 | 2035206 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 836 | 35.3517 | -120.3499 | Yes | Clear;32-90F |  |  | 23-0044731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824870 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5741 | 20230314 | 740 | 20230314 | 856 | 2035240 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 380 | 35.5721 | -120.5832 | Yes | Clear;32-90F |  |  | 23-0044568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824770 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 5925 | 20230314 | 955 | 20230314 | 1621 | 2042866 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 8426 | 35.459 | -120.7357 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0045465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825438 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 9211 | 20230314 | 1028 | 20230314 | 1812 | 2035944 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4640 | 35.5467 | -121.0762 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824943 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 31913 | 20230314 | 1032 | 20230314 | 1310 | 2035934 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 474 | 35.5088 | -120.5153 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Together | 23-0044854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824963 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 30929 | 20230314 | 1034 | 20230314 | 1205 | 2035945 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 910 | 35.49 | -120.6473 | Yes | Clear;32-90F |  |  | 23-0045010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825086 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | V74 | 20230314 | 1140 | 20230314 | 1812 | 2037502 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 66360 | 35.5459 | -121.0678 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824987 | 0 | EPSS Ckt | N | 2023 | A B & C PH
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5203 | 20230314 | 1233 | 20230315 | 1215 | 2039163 | 1422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 5688 | 35.3517 | -120.3499 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0045238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825266 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 8907 | 20230314 | 1259 | 20230314 | 1614 | 2039717 | 195 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1365 | 35.035 | -120.5269 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0045156 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825205 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | OCB | 1103/2 | 20230314 | 1359 | 20230314 | 1539 | 2041586 | 100 | Distribution Circuit | Vegetation | Tree - fell into line | 2410 | 128500 | 35.4652 | -120.6713 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0045277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825294 | 0 | EPSS Ckt | N | 2023 | GRD OC CTR
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | SWITCH | 9263 | 20230314 | 1410 | 20230314 | 1904 | 2041211 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 29988 | 35.1932 | -120.6925 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0045239 | OH | Sus | 45699380 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825267 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 3559 | 20230314 | 1419 | 20230314 | 2329 | 2042016 | 550 | Distribution Circuit | Equipment Failure/Involved | Underground | 184 | 61892 | 35.2445 | -120.6763 | Yes | Overcast-Heavy Rain;32-90 F | Transformer (UG) | Failed/Faulted | 23-0045636 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825579 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | SWITCH | 6667 | 20230314 | 1519 | 20230315 | 1530 | 2042637 | 1451 | Distribution Circuit | Environmental/External | Flood/Erosion | 45 | 3947 | 34.9791 | -120.4537 | Yes |  | Pole-Wood | Deteriorated | 23-0045416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825397 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 2659 | 20230314 | 1852 | 20230314 | 2038 | 2044284 | 106 | Distribution Circuit | Animal | Squirrel | 24 | 2506 | 35.5155 | -120.7082 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0045879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825803 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512687054446 | 20230314 | 1924 | 20230315 | 1156 | 2044471 | 992 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 24800 | 34.9718 | -120.4423 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0045917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825840 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 32285 | 20230314 | 2105 | 20230315 | 935 | 2044825 | 750 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 90000 | 35.5581 | -120.7626 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1825863 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 426061 | 20230315 | 405 | 20230315 | 1418 | 2045192 | 613 | Distribution Circuit | Environmental/External | Water | 16 | 9808 | 35.3829 | -120.1551 | No | Overcast-Drizzle;32-90 F | Pole-Wood | On Ground | 23-0046090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826005 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511518767144 | 20230315 | 1219 | 20230315 | 1410 | 2045704 | 111 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 2331 | 35.3118 | -120.8443 | No | Clear;32-90 F | Transformer (OH) | Arcing | 23-0046312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826139 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 15751 | 20230315 | 1406 | 20230316 | 240 | 2046347 | 754 | Distribution Circuit | Environmental/External | Water | 17 | 2018 | 35.5401 | -121.0111 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0046399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826198 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | TRANSFORMER | 514116639985 | 20230315 | 1407 | 20230315 | 2044 | 2046343 | 397 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 794 | 34.5826 | -119.9581 | No | Overcast;32-90 F |  |  | 23-0046693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826374 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | FUSE | 9375 | 20230315 | 1436 | 20230315 | 1713 | 2046411 | 157 | Distribution Circuit | Environmental/External | Flood/Erosion | 14 | 2198 | 35.2637 | -120.7334 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0046513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826260 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | JUMPER | BURNED OJ 625 UNIVERSITY | 20230315 | 1531 | 20230316 | 115 | 2046837 | 584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 39128 | 34.6286 | -120.4551 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0046556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1826288 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512341861676 | 20230315 | 1556 | 20230315 | 1930 | 2046625 | 214 | Transformer only | Environmental/External | Flood/Erosion | 1 | 214 | 35.168 | -120.5629 | No | Clear-Drizzle;32-90 F | Pole-Wood | Normal | 23-0046499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826251 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON 2112 | 183052112 | FUSE | 6003 | 20230315 | 1645 | 20230315 | 1807 | 2046728 | 82 | Distribution Circuit | Environmental/External | Flood/Erosion | 3 | 246 | 35.5814 | -120.6814 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0046526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826269 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | JUMPER | JPRS 1 N/OF CGC 100000003015 | 20230315 | 1819 | 20230315 | 2051 | 2046924 | 152 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 456 | 35.5454 | -121.0769 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0046591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1826311 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 14991 | 20230315 | 1920 | 20230315 | 2352 | 2046803 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 9248 | 35.4071 | -120.8659 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0046640 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826345 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PERRY-1101 | 183071101 | FUSE | 7913 | 20230315 | 1922 | 20230316 | 1457 | 2047137 | 1175 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2350 | 35.6116 | -120.9121 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826474 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46059 | 20230316 | 959 | 20230316 | 1344 | 2048075 | 225 | Distribution Circuit | 3rd Party | Metallic Balloon | 36 | 8100 | 34.9618 | -120.4099 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0046986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826544 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 79696 | 20230316 | 1040 | 20230316 | 1456 | 2048181 | 256 | Distribution Circuit | Environmental/External | Flood/Erosion | 130 | 32565 | 35.5731 | -121.0414 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0046903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826522 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 45333 | 20230316 | 1504 | 20230316 | 1616 | 2048763 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 192 | 34.9706 | -120.5216 | No | Overcast;32-90 F |  |  | 23-0047161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826645 | 1 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512201858895 | 20230316 | 1835 | 20230317 | 229 | 2048857 | 474 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 474 | 35.091 | -120.6075 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0047235 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826698 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | TRANSFORMER | 512609652634 | 20230317 | 1536 | 20230318 | 1630 | 2050004 | 1494 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 4482 | 34.9214 | -120.4663 | No | Partly Cloudy;32-90 F |  |  | 23-0047708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826955 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | V74 | 20230317 | 1809 | 20230319 | 1748 | 2050642 | 2859 | Distribution Circuit | 3rd Party | Vehicle | 382 | 185328 | 35.5459 | -121.0678 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0047742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1826983 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 4757 | 20230318 | 926 | 20230318 | 1550 | 2050989 | 384 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 17280 | 35.3416 | -120.7646 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0048268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827491 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 7299 | 20230318 | 933 | 20230318 | 2040 | 2050992 | 667 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 9681 | 34.6579 | -120.3228 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048274 | OH | Sus | 45702075 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | No | 1827498 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 6321 | 20230318 | 1335 | 20230319 | 1945 | 2051215 | 1810 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 5430 | 34.9613 | -120.6136 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0048321 | OH | Sus | 35432599 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827530 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512269174866 | 20230318 | 1526 | 20230318 | 1640 | 2051406 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 74 | 35.5289 | -120.5988 | No | Partly Cloudy;32-90 F | Other | Burned/flashed | 23-0048346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827550 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511490569766 | 20230318 | 2335 | 20230319 | 24 | 2051559 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 24 | 1176 | 35.3837 | -120.8559 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0048414 | OH | Sus | 45702781 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827620 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5649 | 20230319 | 826 | 20230319 | 1500 | 2051805 | 394 | Distribution Circuit | 3rd Party | Vehicle | 229 | 90226 | 35.522 | -120.4948 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0048458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827669 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | RECLOSER | V84 | 20230319 | 911 | 20230320 | 1244 | 2051851 | 1653 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2440 | 487056 | 35.3169 | -120.8248 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048457 | OH | Sus | 35432784 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827668 | 0 | EPSS Ckt | N | 2023 | B & GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 8805 | 20230319 | 1800 | 20230320 | 336 | 2052251 | 576 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 23616 | 35.2213 | -120.6326 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0048543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827752 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | TRANSFORMER | 512694553830 | 20230319 | 1944 | 20230320 | 1121 | 2052340 | 937 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 10307 | 34.9549 | -120.4394 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 23-0048559 | OH | Sus | 35432731 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827767 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512732651164 | 20230319 | 2141 | 20230319 | 2304 | 2052474 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 1743 | 34.8817 | -120.4245 | No | Overcast;32-90 F | Fuse | Broken | 23-0048589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827797 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 45865 | 20230320 | 620 | 20230320 | 929 | 2052564 | 189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 6615 | 34.9523 | -120.4471 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Broken | 23-0048621 | OH | Sus | 31640127 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827816 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 511995266456 | 20230320 | 820 | 20230320 | 1130 | 2052574 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2470 | 35.2967 | -120.6838 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0048658 | OH | Sus | 45702772 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827827 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | SWITCH | 2075 | 20230320 | 1254 | 20230320 | 1308 | 2053056 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 34 | 476 | 35.3118 | -120.8362 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0048457 | OH | Sus | 35432784 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1827920 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | FUSE | 15875 | 20230320 | 1702 | 20230320 | 1920 | 2053339 | 138 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 1104 | 35.5259 | -120.9662 | No | Overcast;32-90 F |  |  | 23-0049012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827969 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512759250697 | 20230320 | 1942 | 20230320 | 2037 | 2053435 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 880 | 34.8691 | -120.4152 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0049018 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827976 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512021261322 | 20230320 | 2055 | 20230320 | 2213 | 2053479 | 78 | Transformer only | Unknown Cause | Patrol - not conducted | 12 | 936 | 35.156 | -120.6705 | No | Partly Cloudy;32-90 F |  |  | 23-0049046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1828002 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512682853183 | 20230321 | 14 | 20230321 | 221 | 2053506 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1524 | 34.937 | -120.4428 | Yes | Partly Cloudy;32-90 F | Fuse | Broken | 23-0049063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828019 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20149 | 20230321 | 702 | 20230322 | 1744 | 2053592 | 2082 | Distribution Circuit | Environmental/External | Flood/Erosion | 37 | 77034 | 34.5309 | -120.2908 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0049257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828105 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9403 | 20230321 | 723 | 20230321 | 1930 | 2053608 | 727 | Distribution Circuit | Environmental/External | Water | 96 | 69792 | 35.143 | -120.5462 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0049125 | OH | Sus | 35432789 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828046 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 7437 | 20230321 | 821 | 20230321 | 1425 | 2053661 | 364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 6552 | 34.9324 | -120.5689 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0049321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828126 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 378599 | 20230321 | 831 | 20230321 | 1031 | 2053675 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 7920 | 35.2657 | -120.6402 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0049246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828100 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 834556 | 20230321 | 840 | 20230321 | 1511 | 2053692 | 391 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 21505 | 35.194 | -120.7339 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1828111 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 7525 | 20230321 | 846 | 20230321 | 956 | 2053701 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 147 | 9996 | 35.4843 | -120.6747 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828092 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | P60 | 20230321 | 859 | 20230321 | 1735 | 2053737 | 516 | Distribution Circuit | Equipment Failure/Involved | Overhead | 435 | 71440 | 35.6117 | -120.6326 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Deteriorated | 23-0049155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828065 | 0 | EPSS Ckt | N | 2023 | A&B
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | RECLOSER | 826368 | 20230321 | 907 | 20230321 | 1019 | 2053763 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 337 | 13257 | 35.6692 | -120.6893 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828075 | 0 | EPSS Ckt | N | 2023 | AC
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5931 | 20230321 | 907 | 20230321 | 1643 | 2053900 | 456 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 22800 | 35.5769 | -120.9724 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0049477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828243 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5293 | 20230321 | 908 | 20230321 | 1609 | 2053755 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 5909 | 35.3811 | -120.449 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828161 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | JUMPER | OJ 5 POLE S LD SIDE OF 20721 | 20230321 | 1030 | 20230321 | 1500 | 2054141 | 270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 23664 | 34.6938 | -120.4665 | Yes | Overcast-Strong Winds;32-90 F | Jumper | Burned Open | 23-0049337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1828136 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511540169051 | 20230321 | 1051 | 20230321 | 1322 | 2053758 | 151 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 3322 | 35.3644 | -120.8385 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Arcing | 23-0049280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828109 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20230321 | 1106 | 20230321 | 1806 | 2054045 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 279 | 117180 | 35.7984 | -120.9741 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0049305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828118 | 0 | EPSS Ckt | N | 2023 | A&B
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | RECLOSER | M46 | 20230321 | 1119 | 20230321 | 1641 | 2054078 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1007 | 109158 | 34.8616 | -120.4506 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Deteriorated | 23-0049315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828122 | 0 | EPSS Ckt | N | 2023 | A GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | RECLOSER | 826368 | 20230321 | 1120 | 20230321 | 1419 | 2054096 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 337 | 34253 | 35.6692 | -120.6893 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828125 | 0 | EPSS Ckt | N | 2023 | A & C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512092266079 | 20230321 | 1125 | 20230321 | 1149 | 2053817 | 24 | Transformer only | Vegetation | Tree - grew into line | 15 | 360 | 35.2869 | -120.651 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Arcing | 23-0049322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828127 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | R52 | 20230321 | 1219 | 20230321 | 1907 | 2054324 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1500 | 113629 | 35.6376 | -120.5775 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0049403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828181 | 0 | EPSS Ckt | N | 2023 | A GRD
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | TRANSFORMER | 512568844882 | 20230321 | 1227 | 20230321 | 1740 | 2054317 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2817 | 34.7075 | -120.473 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0049412 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828187 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | OCB | 1104/2 | 20230321 | 1325 | 20230321 | 1957 | 2055421 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 3642 | 594095 | 34.9106 | -120.4461 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0049526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828285 | 0 | Non-EPSS | N | 2023 | A&B & SET A RLY TRIP
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | 513805638161 | 20230321 | 1547 | 20230321 | 2018 | 2057371 | 271 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 271 | 34.5296 | -120.0564 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0050137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828802 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 5763 | 20230321 | 1640 | 20230322 | 149 | 2058869 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11529 | 35.3025 | -120.4043 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0049927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828614 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 7525 | 20230321 | 1649 | 20230321 | 1956 | 2058715 | 187 | Distribution Circuit | Equipment Failure/Involved | Overhead | 226 | 27647 | 35.4843 | -120.6747 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0049977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828663 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 722131 | 20230321 | 1853 | 20230322 | 1855 | 2060150 | 1442 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 80750 | 35.307 | -120.8139 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828811 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 834556 | 20230321 | 2111 | 20230321 | 2234 | 2060985 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 4565 | 35.194 | -120.7339 | Yes | Overcast;32-90 F |  |  | 23-0050243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828903 | 0 | EPSS Ckt | N | 2023 | UNKNOWN
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 834556 | 20230322 | 258 | 20230322 | 917 | 2061517 | 379 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 20845 | 35.194 | -120.7339 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0050401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1829018 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512690251739 | 20230322 | 733 | 20230322 | 1135 | 2061780 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1936 | 34.8973 | -120.4389 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828993 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | FUSE | 5707 | 20230322 | 1014 | 20230322 | 1212 | 2062246 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 394 | 35.9307 | -120.6774 | No | Clear;32-90 F |  |  | 23-0050674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829164 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T1488 | 20230322 | 1122 | 20230322 | 1145 | 2062242 | 23 | Transformer only | Equipment Failure/Involved | Underground | 1 | 23 | 35.0257 | -120.5078 | No | Overcast-Rain;32-90 F | Fuse | Failed/Faulted | 23-0050596 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829121 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 8645 | 20230322 | 1749 | 20230323 | 135 | 2063431 | 466 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 1634 | 35.0348 | -120.5006 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829347 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10329 | 20230323 | 713 | 20230323 | 923 | 2064091 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2340 | 35.225 | -120.7319 | No | Partly Cloudy;32-90 F |  |  | 23-0051262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829574 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 30453 | 20230323 | 856 | 20230323 | 1334 | 2064247 | 278 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 278 | 35.5433 | -120.7415 | No | Clear;32-90 F | Bus | Burned/flashed | 23-0051299 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829591 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 30017 | 20230323 | 1119 | 20230323 | 1522 | 2064546 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 243 | 35.2993 | -120.4896 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1829610 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512745753908 | 20230323 | 1631 | 20230323 | 2339 | 2065035 | 428 | Transformer only | Vegetation | Tree - grew into line | 14 | 5992 | 34.9573 | -120.4223 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0051544 | OH | Sus | 45707666 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829728 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512415056348 | 20230323 | 1647 | 20230324 | 916 | 2065125 | 989 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1978 | 35.0223 | -120.5346 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0051667 | OH | Sus | 31640319 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829818 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 15327 | 20230323 | 1800 | 20230324 | 710 | 2065348 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1580 | 35.0757 | -120.5427 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829766 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512220659421 | 20230324 | 106 | 20230324 | 1045 | 2065496 | 579 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 6369 | 35.1054 | -120.6022 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0051664 | OH | Sus | 31640288 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829815 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | SWITCH | 719657 | 20230324 | 716 | 20230324 | 1409 | 2065624 | 413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 54516 | 35.2633 | -120.6338 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0051689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829831 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | SWITCH | 658059 | 20230324 | 1130 | 20230324 | 1711 | 2065848 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3751 | 34.6327 | -120.5005 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0051802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829878 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | JUMPER | 22079 #2 JMPR BLOWN | 20230324 | 1428 | 20230324 | 1609 | 2066190 | 101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1278 | 34.6077 | -120.1793 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0051978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1829956 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | TRANSFORMER | 513842542268 | 20230324 | 1650 | 20230326 | 2237 | 2066506 | 3227 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3227 | 34.6441 | -120.0485 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829997 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 6997 | 20230325 | 647 | 20230326 | 1607 | 2066754 | 2000 | Distribution Circuit | Equipment Failure/Involved | Overhead | 181 | 190772 | 34.5985 | -120.1926 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052438 | OH | Sus | 45708739 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1830397 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 6323 | 20230325 | 648 | 20230325 | 804 | 2066755 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 152 | 34.9609 | -120.6059 | No | Clear;32-90 F |  |  | 23-0052441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830401 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | TRANSFORMER | 513259541598 | 20230325 | 1454 | 20230326 | 1915 | 2067045 | 1701 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 5103 | 34.6224 | -120.2416 | No | Clear;32-90 F | Transformer (OH) | Arcing | 23-0052524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830475 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9361 | 20230327 | 206 | 20230327 | 1048 | 2068082 | 522 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 7857 | 35.1205 | -120.5715 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052758 | OH | Sus | 45709126 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1830693 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRIP-SAVER | 6111 | 20230327 | 551 | 20230327 | 1110 | 2068107 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 259 | 29215 | 35.0643 | -120.4971 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1830697 | 1 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512925943636 | 20230327 | 1910 | 20230328 | 949 | 2069350 | 879 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 879 | 34.6756 | -120.353 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0053171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830928 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | RECLOSER | M46 | 20230328 | 712 | 20230328 | 1431 | 2069540 | 439 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1008 | 157369 | 34.8616 | -120.4506 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0053246 | OH | Sus | 31640506 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1830982 | 0 | EPSS Ckt | N | 2023 | C GRD
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | FUSE | 1287 | 20230328 | 957 | 20230328 | 1701 | 2070063 | 424 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 87 | 36888 | 34.8725 | -120.4573 | No | Partly Cloudy;32-90 F |  |  | 23-0053813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831323 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 3021 | 20230329 | 108 | 20230329 | 316 | 2071912 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 37376 | 35.1196 | -120.6258 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0053978 | OH | Sus | 45710754 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831458 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511419871525 | 20230329 | 1005 | 20230329 | 1129 | 2072779 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 420 | 35.4313 | -120.8815 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 23-0054282 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831597 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | JUMPER | OJ 2 E/OF CGC 511540267390 | 20230329 | 1047 | 20230329 | 1151 | 2072731 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 128 | 35.319 | -120.8366 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0054195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831559 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512357753608 | 20230329 | 1202 | 20230329 | 1514 | 2072993 | 192 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 384 | 34.9463 | -120.5514 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0054465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831669 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | SWITCH | 1289 | 20230329 | 1245 | 20230329 | 1305 | 2073061 | 20 | Distribution Circuit | Company Initiated | Return Circuit Normal | 27 | 540 | 34.8725 | -120.4593 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0053246 | OH | Sus | 31640506 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1831625 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 834556 | 20230329 | 1812 | 20230329 | 2033 | 2073579 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 7755 | 35.194 | -120.7339 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0054664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831759 | 0 | EPSS Ckt | N | 2023 | B-C
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512688853631 | 20230329 | 1839 | 20230329 | 2330 | 2073448 | 291 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 3783 | 34.9494 | -120.4411 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0054635 | OH | Sus | 45711176 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831736 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | TRANSFORMER | 512740253353 | 20230329 | 1852 | 20230330 | 149 | 2073612 | 417 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4170 | 34.942 | -120.4238 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0054642 | OH | Sus | 31640699 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831745 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | Q12 | 20230330 | 639 | 20230330 | 1625 | 2073870 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 26263 | 35.1396 | -120.5208 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0054743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1831825 | 0 | EPSS Ckt | N | 2023 | ABC INST
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | SWITCH | 78635 | 20230330 | 940 | 20230330 | 1636 | 2074139 | 416 | Distribution Circuit | 3rd Party | Vehicle | 186 | 77376 | 34.6262 | -120.1175 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0054721 | OH | Sus | 35434800 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831902 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | RECLOSER | 707662 | 20230330 | 1017 | 20230330 | 1601 | 2074194 | 344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3096 | 34.9526 | -120.3852 | No | Clear;32-90 F | Other | Broken- wire on ground | 23-0055025 | OH | Sus | 45711854 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1831974 | 0 | Non-EPSS | N | 2023 | COULD NOT READ
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512750553674 | 20230331 | 917 | 20230331 | 1336 | 2075300 | 259 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 4749 | 34.9498 | -120.4206 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055501 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832200 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | SWITCH | 5633 | 20230331 | 1231 | 20230331 | 1305 | 2075449 | 34 | Distribution Circuit | 3rd Party | Other | 1683 | 54138 | 35.5011 | -120.6892 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0055504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1832216 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | RECLOSER | 613456 | 20230331 | 1759 | 20230401 | 1520 | 2075746 | 1281 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 70119 | 35.448 | -120.8707 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0055671 | OH | Sus | 45713212 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1832268 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X22 | 20230401 | 636 | 20230401 | 851 | 2076465 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 11475 | 35.6009 | -120.3242 | No | Fog;32-90 F | Capacitor | Broken | 23-0055798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832398 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511368972112 | 20230401 | 1004 | 20230401 | 2136 | 2076624 | 692 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2076 | 35.4477 | -120.8982 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832467 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | 512265164302 | 20230403 | 735 | 20230403 | 1600 | 2077889 | 505 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 505 | 35.2398 | -120.5916 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0056342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832855 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20230403 | 1229 | 20230403 | 1351 | 2078325 | 82 | Distribution Circuit | 3rd Party | Customer Equipment | 187 | 15070 | 34.7206 | -120.4308 | No | Clear-Strong Winds;32-90 F | Recloser | Malfunctioning | 23-0056338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832853 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512440042995 | 20230403 | 1311 | 20230403 | 1820 | 2078366 | 309 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 309 | 34.6554 | -120.5155 | No | Strong Winds-Clear;32-90 F | Transformer | Deteriorated | 23-0056446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832897 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512614050856 | 20230403 | 1343 | 20230403 | 1730 | 2078421 | 227 | Transformer only | Vegetation | Tree - fell into line | 1 | 227 | 34.8725 | -120.4638 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0056401 | OH | Sus | 31641344 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1832878 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 7751 | 20230403 | 1401 | 20230403 | 2205 | 2078440 | 484 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 5808 | 34.6418 | -119.973 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056514 | OH | Sus | 45714929 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832935 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512666253736 | 20230403 | 1406 | 20230403 | 1713 | 2078450 | 187 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1683 | 34.9521 | -120.4488 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0056544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832951 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 4539 | 20230403 | 1431 | 20230403 | 1717 | 2078514 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 416 | 69056 | 35.1471 | -120.6354 | No | Clear-Strong Winds;32-90 F |  |  | 23-0056535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832947 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 10793 | 20230403 | 1619 | 20230403 | 1744 | 2078897 | 85 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 11 | 935 | 35.2273 | -120.6491 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0056561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832964 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 4539 | 20230403 | 1733 | 20230403 | 1849 | 2079075 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 416 | 31616 | 35.1471 | -120.6354 | No | Clear-Strong Winds;32-90 F |  |  | 23-0056563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832965 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512100560908 | 20230403 | 1923 | 20230403 | 2006 | 2079125 | 43 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 215 | 35.1452 | -120.6436 | No | Clear-Strong Winds;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0056620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833004 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | FUSE | 32015 | 20230404 | 235 | 20230404 | 520 | 2079496 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 4785 | 35.4643 | -120.6536 | No | Clear;32-90 F |  |  | 23-0056709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833074 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5475 | 20230404 | 628 | 20230404 | 837 | 2079536 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 945 | 35.5643 | -120.5874 | No | Clear;32-90 F |  |  | 23-0056802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833142 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | JUMPER | OJ 2/P SS OF CGC 1496 | 20230404 | 1427 | 20230404 | 1900 | 2080062 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 10920 | 35.4307 | -120.8839 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0057096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833259 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 392049 | 20230404 | 1626 | 20230405 | 500 | 2080202 | 754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1508 | 35.4809 | -120.2262 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0057207 | OH | Sus | 45715669 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833294 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512418061075 | 20230404 | 1925 | 20230405 | 1017 | 2080275 | 892 | Transformer only | 3rd Party | Other | 1 | 892 | 35.1522 | -120.537 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0057218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833304 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512108960743 | 20230404 | 2205 | 20230405 | 1308 | 2080328 | 903 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 14448 | 35.1406 | -120.6408 | No | Clear;32-90 F | Secondary | Burned/flashed | 23-0057244 | OH | Sus | 31641426 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833329 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512693252939 | 20230405 | 13 | 20230405 | 133 | 2080279 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 1360 | 34.9304 | -120.4391 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 23-0057217 | OH | Sus | 31641335 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833303 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1105 | 182581105 | FUSE | 9393 | 20230405 | 633 | 20230405 | 2200 | 2080384 | 927 | Distribution Circuit | Equipment Failure/Involved | Underground | 137 | 126999 | 35.2968 | -120.6665 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0057375 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833461 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9347 | 20230405 | 1238 | 20230405 | 1613 | 2080834 | 215 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 6450 | 35.1542 | -120.5988 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0057524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833515 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6053 | 20230405 | 2230 | 20230406 | 6 | 2081213 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2400 | 35.5084 | -120.4863 | No | Clear;32-90 F |  |  | 23-0057743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833605 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | 10264 | 20230406 | 124 | 20230406 | 1206 | 2081285 | 642 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3210 | 35.9053 | -120.4339 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0057747 | OH | Sus | 45716452 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833610 | 0 | EPSS Ckt | N | 2023 | A/GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 5927 | 20230406 | 1133 | 20230406 | 1825 | 2081749 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 9979 | 35.4604 | -120.7525 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058080 | OH | Sus | 45717765 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1833837 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 513053576740 | 20230406 | 1208 | 20230406 | 1405 | 2081787 | 117 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 234 | 35.5868 | -120.3362 | No | Clear;32-90 F |  |  | 23-0057979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833812 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 12113 | 20230406 | 1450 | 20230407 | 332 | 2082065 | 762 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1524 | 34.9665 | -120.5962 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0058193 | UG | Sus | 31641514 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1833883 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512305654192 | 20230406 | 1627 | 20230406 | 1723 | 2081858 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 616 | 34.9621 | -120.5694 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Arcing | 23-0058156 | OH | Sus | 45717764 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833855 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | OTHER | WIRE DOWN | 20230406 | 1951 | 20230407 | 347 | 2082153 | 476 | Distribution Circuit | Animal | Bird found | 1469 | 23338 | 34.6169 | -120.4627 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058196 | OH | Sus | 31641515 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | Yes | Yes | 1833886 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 5521 | 20230407 | 624 | 20230407 | 749 | 2082337 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1644 | 35.7047 | -120.6226 | No | Clear;32-90 F |  |  | 23-0058325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833991 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512876452379 | 20230408 | 906 | 20230408 | 1435 | 2083107 | 329 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 329 | 34.9161 | -120.3773 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0058751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834211 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512353158580 | 20230408 | 1207 | 20230411 | 319 | 2083220 | 3792 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3792 | 35.0829 | -120.5567 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0058805 | OH | Sus | 35436960 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834257 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | RECLOSER | TEMP LR 1101/2 | 20230408 | 1400 | 20230409 | 1526 | 2083293 | 1526 | Distribution Circuit | 3rd Party | Vehicle | 381 | 96348 | 35.2865 | -120.7064 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0058785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | Yes | No | 1834241 | 0 | EPSS Ckt | N | 2023 | A/C GRD T
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | TRANSFORMER | 512085077943 | 20230408 | 1827 | 20230409 | 1000 | 2083391 | 933 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 7464 | 35.6126 | -120.6638 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0058812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834264 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2695 | 20230409 | 624 | 20230409 | 755 | 2083537 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 3185 | 35.4997 | -120.6008 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0058850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834299 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512131760379 | 20230409 | 659 | 20230409 | 1737 | 2083550 | 638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1914 | 35.1311 | -120.6326 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0058857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834306 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | TRANSFORMER | 512106366313 | 20230409 | 900 | 20230409 | 1514 | 2083588 | 374 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 1122 | 35.2936 | -120.6463 | No | Clear;32-90 F |  |  | 23-0058873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1834323 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511335072893 | 20230410 | 48 | 20230410 | 945 | 2083984 | 537 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 537 | 35.4676 | -120.9099 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0058930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834383 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512382054286 | 20230410 | 1230 | 20230410 | 1444 | 2084378 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 134 | 34.9652 | -120.5439 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834580 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511379671875 | 20230410 | 1510 | 20230410 | 1643 | 2084656 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 1674 | 35.4411 | -120.8947 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0059213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834601 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | 512134463661 | 20230410 | 1613 | 20230410 | 1623 | 2084734 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 50 | 35.2213 | -120.6348 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0059248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834619 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | 512134463661 | 20230410 | 1706 | 20230410 | 1854 | 2084790 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 540 | 35.2213 | -120.6348 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834623 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | TRANSFORMER | 511859576480 | 20230411 | 1143 | 20230411 | 1743 | 2085257 | 360 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 360 | 35.571 | -120.7381 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834909 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512353158580 | 20230411 | 1656 | 20230411 | 2215 | 2085747 | 319 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 319 | 35.0829 | -120.5567 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834938 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | SWITCH | 6184 | 20230412 | 1029 | 20230412 | 1044 | 2086556 | 15 | Distribution Circuit | Company Initiated | Return Circuit Normal | 63 | 945 | 35.6217 | -120.6713 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0040227 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1835203 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512701051625 | 20230412 | 1106 | 20230412 | 2315 | 2086586 | 729 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 5832 | 34.8941 | -120.4353 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0060420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835329 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6301 | 20230412 | 1718 | 20230412 | 1801 | 2086510 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 172 | 34.9579 | -120.5398 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0060376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1835293 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512675554128 | 20230412 | 2343 | 20230413 | 119 | 2087171 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 1632 | 34.963 | -120.4459 | No | Clear;32-90 F | Fuse | Broken | 23-0060443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835350 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 11837 | 20230413 | 1529 | 20230414 | 1336 | 2087862 | 1327 | Distribution Circuit | Equipment Failure/Involved | Underground | 134 | 54182 | 34.8573 | -120.4364 | No | Clear-Strong Winds;32-90 F | Conductor- Underground | Burned/flashed | 23-0060827 | UG | Sus | 45729377 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835599 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512206853261 | 20230413 | 1755 | 20230413 | 1945 | 2087967 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 110 | 34.9361 | -120.6009 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0060864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1835613 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 52489 | 20230413 | 1848 | 20230413 | 2009 | 2088009 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 2997 | 35.4705 | -120.6672 | No | Clear;32-90 F |  |  | 23-0060890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1835631 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46059 | 20230413 | 1921 | 20230414 | 246 | 2088023 | 445 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 16020 | 34.9618 | -120.4099 | No | Clear;32-90 F |  |  | 23-0060942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1835698 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512695650370 | 20230413 | 2046 | 20230414 | 1044 | 2088080 | 838 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3352 | 34.8597 | -120.436 | No | Clear;32-90 F | Insulator | Arcing | 23-0060902 | OH | Sus | 31642238 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835640 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512325058275 | 20230415 | 1057 | 20230415 | 1912 | 2089217 | 495 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 495 | 35.0742 | -120.5662 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0061361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836047 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | FUSE | 46135 | 20230415 | 1719 | 20230415 | 2055 | 2089301 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1296 | 34.9036 | -120.2272 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0061370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1836054 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512200871919 | 20230416 | 731 | 20230416 | 1013 | 2089555 | 162 | Transformer only | Vegetation | Tree - fell into line | 6 | 972 | 35.4484 | -120.6195 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0061449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836153 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9315 | 20230416 | 1523 | 20230416 | 1848 | 2089725 | 205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 4510 | 35.1302 | -120.5571 | No | Partly Cloudy;32-90 F | Jumper | Broken | 23-0061486 | OH | Sus | 45731808 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1836175 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 30931 | 20230417 | 45 | 20230417 | 220 | 2089914 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 4750 | 35.4889 | -120.6471 | No | Overcast;32-90 F |  |  | 23-0061526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1836218 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 5177 | 20230417 | 1637 | 20230417 | 1839 | 2090750 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1586 | 35.2894 | -120.7467 | No | Clear;32-90 F |  |  | 23-0061817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1836499 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | JUMPER | 11047 ROADPHSE BURNT OPEN JPR | 20230418 | 900 | 20230418 | 2207 | 2091677 | 787 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 787 | 35.0276 | -120.5225 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0062250 | OH | Sus | 31642579 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1836806 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512694653063 | 20230419 | 1223 | 20230419 | 1440 | 2092532 | 137 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1781 | 34.9338 | -120.4388 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0062501 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837047 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | OCB | 1107/2 | 20230419 | 2132 | 20230420 | 6 | 2092834 | 154 | Distribution Circuit | 3rd Party | Vandalism | 1356 | 208824 | 34.9503 | -120.4441 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0062725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1837102 | 0 | Non-EPSS | N | 2023 | PH TIME- GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 10337 | 20230419 | 2136 | 20230419 | 2349 | 2092833 | 133 | Distribution Circuit | Animal | Other | 6 | 798 | 35.1543 | -120.5646 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0062749 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837124 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 5521 | 20230420 | 650 | 20230420 | 853 | 2092906 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2379 | 35.7047 | -120.6226 | No | Clear;32-90 F |  |  | 23-0062843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837195 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | TEMPLETON-2110 | 183052110 | FUSE | 10591 | 20230420 | 1223 | 20230420 | 1437 | 2093180 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 670 | 35.5724 | -121.0481 | No | Clear;32-90 F |  |  | 23-0063091 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837278 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | OCB | 1104/2 | 20230420 | 1301 | 20230420 | 1311 | 2093199 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 3447 | 34470 | 34.6255 | -120.1193 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0047470 | OH | Sus | 31611513 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837264 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | 673618 | 20230420 | 1313 | 20230420 | 1324 | 2093213 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 154 | 34.6287 | -120.1272 | No | Clear;32-90 F |  |  | 23-0063029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837269 | 0 | EPSS Ckt | N | 2023 | BC
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 511707576550 | 20230420 | 1334 | 20230420 | 1852 | 2093217 | 318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 636 | 35.5715 | -120.7898 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0063105 | OH | Sus | 31642785 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837281 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 100000005175 | 20230420 | 1351 | 20230420 | 2352 | 2093233 | 601 | Transformer only | Animal | Bird found | 1 | 601 | 35.5798 | -120.3499 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0063190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837296 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 30607 | 20230421 | 650 | 20230421 | 1135 | 2093492 | 285 | Distribution Circuit | Animal | Other | 1 | 380 | 35.4953 | -120.2285 | No | Clear;32-90 F | Crossarm- Wood | Normal | 23-0063488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837549 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511182475310 | 20230421 | 651 | 20230421 | 1330 | 2093493 | 399 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 399 | 35.5303 | -120.9587 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0063311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837370 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | JUMPER | OJ 1 POLE W/ OF 511941472963 | 20230421 | 946 | 20230421 | 1241 | 2093696 | 175 | Distribution Circuit | 3rd Party | Vehicle | 26 | 4550 | 35.475 | -120.7081 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0063373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837485 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 38991 | 20230422 | 440 | 20230422 | 603 | 2094403 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1245 | 34.9692 | -120.5636 | No | Partly Cloudy;32-90 F |  |  | 23-0063710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837683 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511546767741 | 20230422 | 833 | 20230422 | 1017 | 2094633 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1352 | 35.3286 | -120.8354 | No | Partly Cloudy;32-90 F | Service conductor | Together | 23-0063760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837777 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 4049 | 20230423 | 553 | 20230423 | 808 | 2094911 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1350 | 35.5564 | -120.5362 | No | Clear;32-90 F |  |  | 23-0063820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837848 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | TRANSFORMER | 510721477438 | 20230423 | 944 | 20230423 | 2012 | 2094985 | 628 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 628 | 35.5881 | -121.1223 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0063836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837866 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | RECLOSER | 273892 | 20230423 | 1040 | 20230424 | 220 | 2095044 | 940 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 17 | 7860 | 34.9162 | -120.3731 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0063849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | No | No | 1837876 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | JUMPER | WIRE DOWN 3 N/OF 12103 | 20230424 | 441 | 20230424 | 844 | 2095239 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1692 | 34.9183 | -120.3373 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0063923 | OH | Sus | 45739018 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1837934 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 7947 | 20230424 | 949 | 20230424 | 1104 | 2095554 | 75 | Distribution Circuit | 3rd Party | Customer Equipment | 6 | 450 | 34.6426 | -120.5082 | No | Clear;32-90 F | Metering Equipment | Failed/Faulted | 23-0064063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838120 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 3983 | 20230424 | 952 | 20230426 | 1238 | 2095557 | 398 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 54490 | 35.098 | -120.603 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0064073 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838124 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | SWITCH | 31499 | 20230425 | 925 | 20230425 | 1411 | 2096452 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 3030 | 35.6301 | -120.3746 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0064388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1838373 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | TEMPLETON-2110 | 183052110 | FUSE | 9173 | 20230426 | 618 | 20230426 | 926 | 2097163 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1316 | 35.5727 | -121.0551 | No | Partly Cloudy;32-90 F |  |  | 23-0064848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838638 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511494669958 | 20230427 | 354 | 20230427 | 625 | 2097999 | 151 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 2265 | 35.3889 | -120.8547 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Arcing | 23-0065273 | OH | Sus | 45741966 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838845 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | SWITCH | 6267 | 20230427 | 1539 | 20230427 | 2032 | 2098640 | 293 | Distribution Circuit | 3rd Party | Vehicle | 224 | 65632 | 34.9403 | -120.4356 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0065657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839067 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | OCB | 2109/2 | 20230427 | 1614 | 20230428 | 111 | 2098672 | 537 | Distribution Circuit | 3rd Party | Vehicle | 3527 | 317677 | 35.555 | -120.6804 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0065703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | Yes | No | 1839071 | 0 | EPSS Ckt | N | 2023 | A B C GR TIME
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 14281 | 20230428 | 1540 | 20230428 | 1649 | 2099546 | 69 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 4071 | 35.4446 | -120.8966 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 23-0066144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839359 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9419 | 20230429 | 624 | 20230429 | 833 | 2099867 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 8127 | 35.1348 | -120.5045 | No | Clear;32-90 F |  |  | 23-0066242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839461 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | T32011 | 20230429 | 1449 | 20230429 | 1704 | 2100137 | 135 | Transformer only | Equipment Failure/Involved | Underground | 4 | 540 | 34.9438 | -120.4559 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0066322 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839542 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 511133575555 | 20230430 | 232 | 20230430 | 1634 | 2100356 | 842 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2526 | 35.5397 | -120.9822 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066412 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839639 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | V74 | 20230430 | 233 | 20230430 | 1258 | 2100357 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 382 | 55000 | 35.5459 | -121.0678 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0066370 | OH | Sus | 45745363 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1839589 | 0 | EPSS Ckt | N | 2023 | C- GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5655 | 20230430 | 402 | 20230430 | 556 | 2100366 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2088 | 35.4572 | -120.4631 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0066378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839598 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 6807 | 20230430 | 820 | 20230430 | 915 | 2100409 | 55 | Distribution Circuit | Animal | Bird found | 46 | 2530 | 35.5739 | -120.6983 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0066396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839623 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | RECLOSER | W14 | 20230430 | 2248 | 20230501 | 54 | 2100969 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5062 | 519687 | 35.4716 | -120.9799 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0066507 | OH | Sus | 45745393 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839716 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 5253 | 20230501 | 1634 | 20230501 | 2017 | 2101873 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 164 | 10410 | 35.1017 | -120.6075 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 23-0066817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1839955 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | JUMPER | BURNED OJ 1 LD SIDE OF CGC# 414608920507 | 20230502 | 920 | 20230502 | 1740 | 2102584 | 500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 500 | 35.8843 | -120.8209 | No | Clear;32-90 F | Jumper | Burned Open | 23-0067163 | OH | Sus | 45746476 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1840217 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 114631 | 20230502 | 950 | 20230502 | 1340 | 2102943 | 230 | Distribution Circuit | Animal | Other | 1 | 230 | 35.7323 | -120.5734 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0067200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1840230 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 7975 | 20230503 | 1858 | 20230503 | 2125 | 2104122 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 3381 | 34.6568 | -120.0898 | No | Overcast-Rain;32-90 F |  |  | 23-0067874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1840602 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X20 | 20230503 | 2125 | 20230503 | 2233 | 2104205 | 68 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 47 | 3196 | 35.5238 | -120.2128 | No | Overcast-Drizzle;32-90 F |  |  | 23-0067882 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840604 | 0 | EPSS Ckt | N | 2023 | C GRD
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 30609 | 20230503 | 2233 | 20230504 | 30 | 2104235 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1989 | 35.4934 | -120.2276 | No | Overcast-Rain;32-90 F |  |  | 23-0067933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1840643 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 4695 | 20230504 | 349 | 20230504 | 2110 | 2104317 | 1041 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 6121 | 35.6446 | -120.3782 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0067966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | Yes | No | 1840674 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | OCB | 1110/2 | 20230504 | 437 | 20230504 | 1309 | 2104337 | 512 | Distribution Circuit | 3rd Party | Vehicle | 2397 | 87480 | 34.9503 | -120.4442 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0067958 | OH | Sus | 31644105 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | No | 1840665 | 0 | EPSS Ckt | N | 2023 | AB
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V14 | 20230504 | 1645 | 20230505 | 257 | 2104982 | 612 | Distribution Circuit | Environmental/External | Flood/Erosion | 547 | 54099 | 35.1791 | -120.6181 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0068431 | OH | Sus | 35441459 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840918 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 6217 | 20230504 | 2036 | 20230504 | 2219 | 2105110 | 103 | Distribution Circuit | 3rd Party | Other | 5 | 515 | 35.8433 | -120.3805 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0068495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840956 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512779952648 | 20230504 | 2100 | 20230505 | 1227 | 2105118 | 927 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 927 | 34.923 | -120.41 | No | Overcast;32-90 F | Sectionalizer | Burned/flashed | 23-0068532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840988 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2287 | 20230505 | 654 | 20230505 | 928 | 2105203 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 308 | 35.2848 | -120.7328 | No | Clear;32-90 F |  |  | 23-0068615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841065 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 14883 | 20230505 | 1454 | 20230505 | 1535 | 2105697 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 82 | 35.141 | -120.5253 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0068941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841200 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 32285 | 20230505 | 1610 | 20230506 | 231 | 2105742 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 17848 | 35.5581 | -120.7626 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0068989 | OH | Sus | 31644118 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | Yes | No | 1841215 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512779952648 | 20230505 | 1650 | 20230505 | 2100 | 2105761 | 250 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 250 | 34.923 | -120.41 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0068995 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841221 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2291 | 20230505 | 2219 | 20230506 | 1106 | 2105868 | 767 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3068 | 35.2985 | -120.7834 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0069100 | OH | Sus | 45750837 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841277 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | T0282 | 20230506 | 1354 | 20230507 | 1646 | 2106277 | 1612 | Distribution Circuit | Equipment Failure/Involved | Underground | 126 | 147908 | 35.7169 | -120.8774 | No | Clear;32-90 F | Transformer (UG) | Arcing | 23-0069208 | UG | Sus | 35441738 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841400 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | Q08 | 20230507 | 702 | 20230507 | 1018 | 2106601 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 879 | 177287 | 35.148 | -120.5897 | No | Fog;32-90 F | Jumper | Burned Open | 23-0062435 | OH | Sus | 35316393 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841458 | 0 | EPSS Ckt | N | 2023 | B & GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512684753236 | 20230507 | 1013 | 20230507 | 2254 | 2106647 | 761 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3805 | 34.9385 | -120.4422 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0069279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841477 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 513407374483 | 20230507 | 1743 | 20230507 | 2318 | 2106889 | 335 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 670 | 35.5268 | -120.2167 | No | Clear;32-90 F |  |  | 23-0069367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1841562 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | T0282 | 20230507 | 1941 | 20230508 | 2342 | 2106891 | 1681 | Transformer only | Equipment Failure/Involved | Underground | 89 | 149609 | 35.7169 | -120.8774 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0069334 | UG | Sus | 45751311 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841529 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512869551845 | 20230508 | 1027 | 20230508 | 1414 | 2107322 | 227 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 227 | 34.9017 | -120.3794 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0069622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841756 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | JUMPER | OJ @ CGC# 512073173819 | 20230508 | 1921 | 20230508 | 2034 | 2108103 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2798 | 164027 | 35.4996 | -120.6649 | No | Clear;32-90 F | Jumper | Burned Open | 23-0069722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1841793 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5475 | 20230509 | 806 | 20230509 | 935 | 2108319 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 652 | 35.5643 | -120.5874 | No | Clear;32-90 F |  |  | 23-0069886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841966 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512611760185 | 20230509 | 921 | 20230509 | 1417 | 2108469 | 296 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 592 | 35.1303 | -120.4751 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0069870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841954 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | TRANSFORMER | T0522 | 20230509 | 1910 | 20230510 | 1127 | 2108952 | 940 | Distribution Circuit | Equipment Failure/Involved | Underground | 297 | 34045 | 35.2657 | -120.6614 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0070186 | UG | Sus | 35442598 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842114 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30911 | 20230510 | 248 | 20230510 | 425 | 2109081 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 872 | 35.5035 | -120.6027 | No | Partly Cloudy;32-90 F |  |  | 23-0070244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842131 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 343821 | 20230510 | 431 | 20230510 | 816 | 2109088 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 4725 | 35.2469 | -120.6824 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 23-0070246 | OH | Sus | 31644861 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842132 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 6439 | 20230510 | 1549 | 20230510 | 1708 | 2109701 | 79 | Distribution Circuit | 3rd Party | Metallic Balloon | 370 | 29192 | 34.7046 | -120.4654 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0070630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842357 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 1147 | 20230510 | 1636 | 20230511 | 254 | 2109720 | 618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 67362 | 34.62 | -120.1048 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0070644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842366 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 6997 | 20230511 | 1817 | 20230512 | 33 | 2110637 | 376 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 182 | 68416 | 34.5987 | -120.1926 | No | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0071114 | OH | Sus | 45760075 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1842648 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 8797 | 20230511 | 2024 | 20230511 | 2213 | 2110711 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2289 | 35.0618 | -120.5937 | No | Partly Cloudy;32-90 F |  |  | 23-0071157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842691 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511568467164 | 20230512 | 1337 | 20230515 | 628 | 2111316 | 3891 | Transformer only | Equipment Failure/Involved | Underground | 6 | 23346 | 35.313 | -120.8276 | No | Clear;32-90 F | Other | Broken | 23-0071455 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842919 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 2101 | 20230512 | 1343 | 20230512 | 2310 | 2111317 | 567 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 20412 | 35.3129 | -120.8275 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0071445 | UG | Sus | 31644868 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842914 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | TRANSFORMER | 513048151392 | 20230513 | 450 | 20230513 | 2110 | 2111712 | 980 | Transformer only | Animal | Bird found | 1 | 980 | 34.8901 | -120.3191 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0071583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843040 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 52489 | 20230513 | 954 | 20230513 | 1054 | 2111718 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 2220 | 35.4705 | -120.6672 | No | Clear;32-90 F |  |  | 23-0071551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843013 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | TRANSFORMER | 511643969033 | 20230514 | 1650 | 20230514 | 1837 | 2112259 | 107 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 107 | 35.3646 | -120.8044 | No | Clear;32-90 F |  |  | 23-0071693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1843141 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511506367118 | 20230515 | 1058 | 20230515 | 1408 | 2113038 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2280 | 35.3111 | -120.8484 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0071853 | OH | Sus | 31645441 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843299 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 45867 | 20230515 | 1507 | 20230515 | 2119 | 2113323 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 6082 | 34.9527 | -120.4475 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0072065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843402 | 1 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 513067374420 | 20230516 | 1008 | 20230516 | 1301 | 2114016 | 173 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 173 | 35.5226 | -120.3309 | No | Partly Cloudy;32-90 F |  |  | 23-0072369 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1843648 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC 1101 | 182811101 | OTHER | 6723 | 20230516 | 1253 | 20230516 | 1852 | 2114129 | 359 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 4179 | 34.7509 | -120.312 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0072326 | OH | Sus | 45765067 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | Yes | Yes | 1843631 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | TRANSFORMER | 513289041797 | 20230516 | 1709 | 20230516 | 1820 | 2114373 | 71 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 142 | 34.6281 | -120.2322 | No | Clear;32-90 F |  |  | 23-0072467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1843683 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 511235581736 | 20230516 | 1816 | 20230516 | 2150 | 2114416 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 214 | 35.71 | -120.953 | No | Clear;32-90 F | Fuse | Normal | 23-0072489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843713 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | 513616239274 | 20230517 | 837 | 20230518 | 1100 | 2114746 | 1583 | Transformer only | Equipment Failure/Involved | Underground | 2 | 3166 | 34.5483 | -120.1233 | No | Overcast-Fog;32-90 F | Conductor- Underground | Broken | 23-0072666 | UG | Sus | 45765975 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843940 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512375743296 | 20230517 | 1030 | 20230517 | 1603 | 2114824 | 333 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 333 | 34.6631 | -120.5367 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0072665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843939 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512735050579 | 20230517 | 1418 | 20230517 | 2102 | 2115122 | 404 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3232 | 34.8657 | -120.4232 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0072839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843999 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512025072374 | 20230517 | 1659 | 20230517 | 2340 | 2115198 | 401 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 401 | 35.4596 | -120.6796 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0072854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844006 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | T67261 | 20230517 | 2316 | 20230518 | 709 | 2115485 | 473 | Transformer only | 3rd Party | Customer Equipment | 9 | 4257 | 34.9729 | -120.4359 | No | Clear;32-90 F | Transformer | Normal | 23-0072930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844060 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512539553307 | 20230518 | 254 | 20230519 | 609 | 2116290 | 1635 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1635 | 34.9392 | -120.4904 | No | Overcast-Fog;32-90 F | Transformer (OH) | Leaking | 23-0073325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844327 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 5433 | 20230518 | 2305 | 20230519 | 706 | 2116541 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 962 | 35.3831 | -120.857 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0073311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1844319 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | OCB | 1103/2 | 20230518 | 2352 | 20230519 | 1218 | 2116554 | 746 | Distribution Circuit | 3rd Party | Vehicle | 2966 | 665412 | 35.2617 | -120.6346 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0073314 | OH | Sus | 31645948 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | Yes | No | 1844322 | 0 | EPSS Ckt | N | 2023 | A-B-C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | OCB | 1104/2 | 20230518 | 2352 | 20230519 | 1219 | 2116558 | 747 | Distribution Circuit | 3rd Party | Vehicle | 2259 | 184641 | 35.2617 | -120.6345 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0073315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1844323 | 0 | EPSS Ckt | N | 2023 | A-B GRD
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 1619 | 20230519 | 1330 | 20230519 | 1550 | 2117118 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1401 | 34.5701 | -119.9536 | No | Clear;32-90 F | Jumper | Bent or Twisted | 23-0073668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844533 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | FUSE | 15591 | 20230519 | 1435 | 20230520 | 1542 | 2117171 | 1507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7535 | 35.0634 | -120.4985 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0073664 | OH | Sus | 45769705 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1844531 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 1619 | 20230519 | 1610 | 20230519 | 1652 | 2117263 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 420 | 34.5701 | -119.9536 | No | Partly Cloudy;32-90 F |  |  | 23-0073714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844548 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | TRANSFORMER | 512602157141 | 20230519 | 1939 | 20230520 | 1508 | 2117326 | 1169 | Transformer only | Animal | Bird found | 11 | 12859 | 35.0455 | -120.4728 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073738 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844563 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 52489 | 20230520 | 822 | 20230520 | 902 | 2117506 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 1480 | 35.4705 | -120.6672 | No | Clear;32-90 F |  |  | 23-0073812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1844650 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | TRANSFORMER | 100000077139 | 20230520 | 1316 | 20230520 | 1400 | 2117651 | 44 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 44 | 34.6637 | -120.336 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0073847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1844694 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 7519 | 20230520 | 1604 | 20230520 | 2358 | 2117726 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3792 | 35.5988 | -120.8052 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0073886 | OH | Sus | 31646031 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1844716 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | FUSE | 5441 | 20230521 | 718 | 20230521 | 957 | 2117908 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 4772 | 35.7556 | -120.6979 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0073952 | OH | Sus | 45770082 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844777 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 248566 | 20230521 | 1640 | 20230521 | 1941 | 2118088 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 9412 | 35.1805 | -120.7403 | No | Partly Cloudy;32-90 F |  |  | 23-0073998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1844830 | 0 | EPSS Ckt | N | 2023 | AC GRD
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1101 | 182771101 | FUSE | 15157 | 20230521 | 1719 | 20230521 | 1902 | 2118098 | 103 | Distribution Circuit | 3rd Party | Kite | 74 | 7622 | 35.6164 | -121.1436 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0074009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1844837 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | SWITCH | 5866 | 20230522 | 1127 | 20230522 | 1141 | 2118720 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 92 | 1288 | 35.6199 | -120.6535 | No | Clear;32-90 F | Other | Normal | 23-0049155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845064 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 6513 | 20230522 | 1134 | 20230522 | 1715 | 2118721 | 341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 14119 | 34.7061 | -120.4573 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0074247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845078 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5655 | 20230522 | 1627 | 20230522 | 2302 | 2118906 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 21725 | 35.4572 | -120.4631 | No | Clear;32-90 F | Insulator | Broken | 23-0074365 | OH | Sus | 31646246 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845105 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512969566647 | 20230522 | 2205 | 20230523 | 1657 | 2119257 | 1132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1132 | 35.3077 | -120.3575 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0074513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845230 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 45731 | 20230523 | 545 | 20230523 | 710 | 2119305 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 4592 | 35.0401 | -120.5361 | No | Overcast-Fog;32-90 F |  |  | 23-0074484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845183 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 7559 | 20230523 | 1150 | 20230523 | 1929 | 2119745 | 459 | Distribution Circuit | 3rd Party | Vehicle | 85 | 39015 | 35.6266 | -120.5512 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0074658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845354 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | JUMPER | DOUBLE DEAD ENDS LD SIDE OF CGC #512969266740 | 20230523 | 1358 | 20230523 | 1657 | 2119867 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 179 | 35.3104 | -120.3575 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0074771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845393 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 7195 | 20230524 | 1607 | 20230524 | 2239 | 2120562 | 392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1568 | 34.6084 | -120.3652 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0075257 | OH | Sus | 45773929 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | Yes | No | 1845694 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | TRANSFORMER | 513674441208 | 20230524 | 2002 | 20230525 | 2100 | 2120848 | 1498 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 7364 | 34.6141 | -120.1033 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0075307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845711 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | SWITCH | 11501 | 20230524 | 2203 | 20230525 | 53 | 2118970 | 170 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 340 | 34.9186 | -120.4007 | No | Overcast;32-90 F | Transformer (UG) | Deteriorated | 23-0075318 | UG | Sus | 45770688 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1845722 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | TRANSFORMER | 511631379415 | 20230525 | 645 | 20230525 | 1830 | 2121140 | 705 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 705 | 35.6495 | -120.8178 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0075441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845861 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 511991065070 | 20230525 | 1357 | 20230525 | 2034 | 2121385 | 397 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 9126 | 35.2587 | -120.6836 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0075696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845951 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | JUMPER | OJ 1 S/OF CGC 9180 | 20230525 | 1512 | 20230525 | 1645 | 2121418 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 372 | 35.6463 | -120.6675 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0075662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845940 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | SWITCH | 2755 | 20230525 | 1602 | 20230525 | 1724 | 2121425 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 3198 | 35.4053 | -120.2577 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0075673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845945 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRANSFORMER | 512498858587 | 20230525 | 1622 | 20230525 | 2340 | 2121471 | 438 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 438 | 35.0847 | -120.508 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0075739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845969 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 30315 | 20230526 | 548 | 20230526 | 651 | 2121848 | 63 | Distribution Circuit | Animal | Bird found | 1 | 63 | 35.6722 | -120.6053 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0075828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846053 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 3933 | 20230526 | 721 | 20230526 | 1241 | 2121884 | 320 | Distribution Circuit | 3rd Party | Vehicle | 53 | 7027 | 35.5247 | -120.6432 | No | Overcast;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0075875 | OH | Sus | 31650271 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1846088 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 7385 | 20230526 | 909 | 20230526 | 1106 | 2121988 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1287 | 35.4325 | -120.4912 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0075905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846114 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 45731 | 20230526 | 924 | 20230526 | 1021 | 2122034 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 3192 | 35.0401 | -120.5361 | No | Overcast;32-90 F |  |  | 23-0075968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846155 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512208754265 | 20230526 | 938 | 20230526 | 1226 | 2122058 | 168 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 168 | 34.9635 | -120.6016 | No | Clear;32-90 F | Fuse | Broken | 23-0076079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846193 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | TRANSFORMER | 513290241265 | 20230526 | 1121 | 20230526 | 1950 | 2122150 | 509 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 509 | 34.6141 | -120.2318 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0076087 | OH | Sus | 31649150 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1846195 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 31927 | 20230527 | 910 | 20230527 | 1111 | 2122604 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 242 | 35.4764 | -120.5038 | No | Overcast;32-90 F |  |  | 23-0076297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846322 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 1147 | 20230527 | 1109 | 20230527 | 1210 | 2122655 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 6649 | 34.62 | -120.1048 | No | Overcast;32-90 F |  |  | 23-0076306 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846329 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 7057 | 20230527 | 1242 | 20230527 | 1622 | 2122700 | 220 | Distribution Circuit | Animal | Squirrel | 4 | 880 | 35.4527 | -120.5049 | No | Clear;32-90 F | Fuse | Burned Open | 23-0076346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1846352 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 68557 | 20230527 | 1840 | 20230527 | 1854 | 2122811 | 14 | Distribution Circuit | 3rd Party | Kite | 49 | 686 | 35.4409 | -120.8945 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0076358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846360 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y06 | 20230528 | 1025 | 20230528 | 1623 | 2122996 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 345 | 19245 | 34.6201 | -120.2103 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0076433 | OH | Sus | 31650480 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | Yes | No | 1846420 | 0 | EPSS Ckt | N | 2023 | A B C G TIME
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 8173 | 20230528 | 1100 | 20230528 | 1310 | 2123048 | 130 | Distribution Circuit | Animal | Squirrel | 2 | 260 | 34.7068 | -120.0612 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0076453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846433 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 10509 | 20230528 | 1725 | 20230528 | 1817 | 2123151 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 260 | 35.3839 | -120.8401 | No | Partly Cloudy;32-90 F |  |  | 23-0076479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846449 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1101 | 182771101 | FUSE | 14049 | 20230529 | 1554 | 20230529 | 1656 | 2123454 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 62 | 35.6576 | -121.2244 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 23-0076568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846527 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 30297 | 20230529 | 1630 | 20230529 | 1744 | 2123546 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 4810 | 35.5022 | -120.7217 | No | Partly Cloudy;32-90 F |  |  | 23-0076604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846552 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | T1581 | 20230530 | 731 | 20230530 | 1500 | 2123704 | 449 | Transformer only | Equipment Failure/Involved | Underground | 19 | 8531 | 34.9729 | -120.4512 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0076699 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846667 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512178573607 | 20230530 | 838 | 20230530 | 1102 | 2123770 | 144 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 144 | 35.4944 | -120.6288 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0076682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846641 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | TRANSFORMER | 512601057768 | 20230530 | 1505 | 20230530 | 2215 | 2124205 | 430 | Transformer only | 3rd Party | Contact with High Voltage- 3rd party | 1 | 430 | 35.0621 | -120.4736 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0076966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846815 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 100000005176 | 20230530 | 1617 | 20230530 | 2148 | 2124249 | 331 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 662 | 35.5703 | -120.3505 | No | Partly Cloudy;32-90 F |  |  | 23-0077021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1846834 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 1459 | 20230530 | 2250 | 20230531 | 111 | 2124387 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 23265 | 34.8964 | -120.4185 | No | Overcast;32-90 F |  |  | 23-0077042 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846854 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2939 | 20230531 | 753 | 20230531 | 908 | 2124513 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 675 | 35.513 | -120.639 | No | Overcast;32-90 F |  |  | 23-0077275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1847046 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512275280574 | 20230531 | 1437 | 20230531 | 1937 | 2124917 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1200 | 35.6861 | -120.6023 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0077410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1847079 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | OTHER | J911 TWD T3453 | 20230531 | 1606 | 20230531 | 1741 | 2124971 | 95 | Distribution Circuit | Equipment Failure/Involved | Underground | 32 | 3040 | 34.9861 | -120.4507 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0077371 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1847080 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512000866500 | 20230531 | 2123 | 20230601 | 209 | 2125127 | 286 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 4576 | 35.2979 | -120.6821 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0077551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1847133 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | FUSE | 962673 | 20230601 | 547 | 20230601 | 730 | 2125208 | 103 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 1099 | 35.6844 | -120.7299 | No | Clear;32-90 F |  |  | 23-0077626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1847161 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | FUSE | 11185 | 20230601 | 1556 | 20230601 | 1716 | 2126854 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1840 | 34.9339 | -120.4271 | No | Overcast;32-90 F |  |  | 23-0077991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847358 | 1 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 11361 | 20230601 | 1626 | 20230601 | 1802 | 2126878 | 96 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 58 | 5568 | 34.6362 | -119.9744 | No | Clear;32-90 F | Other | Normal | 23-0077989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1847357 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512693376057 | 20230602 | 755 | 20230602 | 1021 | 2127100 | 146 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 292 | 35.5651 | -120.4624 | No | Overcast;32-90 F |  |  | 23-0078216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1847558 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 415561721879 | 20230602 | 1124 | 20230602 | 1435 | 2127369 | 191 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 191 | 35.9242 | -120.4989 | No | Clear;32-90 F |  |  | 23-0078387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1847597 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | FUSE | 5977 | 20230603 | 753 | 20230604 | 2017 | 2127782 | 2184 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 4368 | 35.6157 | -120.655 | No | Overcast;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0078539 | OH | Sus | 31650926 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847678 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 14673 | 20230603 | 1341 | 20230603 | 1834 | 2127960 | 293 | Distribution Circuit | 3rd Party | Vehicle | 2 | 586 | 35.1167 | -120.5822 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0078599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1847720 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 3015 | 20230603 | 1814 | 20230603 | 1926 | 2128073 | 72 | Distribution Circuit | Animal | Bird found | 1 | 72 | 35.3203 | -120.8422 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0078630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847744 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511151674795 | 20230604 | 939 | 20230604 | 1755 | 2128374 | 496 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 496 | 35.5192 | -120.975 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847811 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 30527 | 20230605 | 907 | 20230605 | 1245 | 2129010 | 218 | Distribution Circuit | Animal | Bird found | 2 | 363 | 35.5731 | -120.5966 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0078955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848057 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 9491 | 20230605 | 1609 | 20230605 | 1640 | 2129460 | 31 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 221 | 6844 | 35.2695 | -120.6646 | No | Overcast;32-90 F | Connector or Splice (UG) | Normal | 23-0073371 | UG | Sus | 35342624 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848100 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | TRANSFORMER | 511999874380 | 20230605 | 1622 | 20230605 | 1658 | 2129466 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 108 | 35.5144 | -120.6902 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 23-0079059 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848096 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 3403 | 20230605 | 1807 | 20230605 | 1947 | 2129595 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1334 | 35.7467 | -120.6183 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0079112 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848123 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1105 | 182581105 | FUSE | 3239 | 20230605 | 2233 | 20230606 | 1445 | 2130064 | 972 | Distribution Circuit | Environmental/External | Lightning | 4 | 2835 | 35.3115 | -120.6761 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848291 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1105 | 182581105 | FUSE | 9389 | 20230605 | 2240 | 20230606 | 903 | 2130066 | 623 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1246 | 35.3267 | -120.6619 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0079168 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848174 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1105 | 182581105 | FUSE | 15881 | 20230605 | 2243 | 20230606 | 16 | 2130068 | 93 | Distribution Circuit | Environmental/External | Lightning | 4 | 279 | 35.2932 | -120.6653 | No | Overcast-Rain;32-90 F | Lightning Arrestor | Burned/flashed | 23-0079159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848165 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9311 | 20230605 | 2306 | 20230606 | 615 | 2130072 | 429 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 3432 | 35.139 | -120.5746 | No | Overcast-Rain;32-90 F |  |  | 23-0079195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848200 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 7051 | 20230605 | 2351 | 20230606 | 1507 | 2130080 | 916 | Distribution Circuit | Environmental/External | Lightning | 27 | 14286 | 35.0477 | -120.3014 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0079221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848216 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 7645 | 20230606 | 28 | 20230606 | 1333 | 2130094 | 785 | Distribution Circuit | Environmental/External | Lightning | 47 | 21737 | 35.0623 | -120.392 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079252 | OH | Sus | 45825124 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848257 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9413 | 20230606 | 123 | 20230606 | 2032 | 2130103 | 1149 | Distribution Circuit | Environmental/External | Lightning | 29 | 32954 | 35.1379 | -120.5166 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079178 | OH | Sus | 45824901 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848182 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2291 | 20230606 | 522 | 20230606 | 713 | 2130139 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 444 | 35.2985 | -120.7834 | No | Clear;32-90 F |  |  | 23-0079220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848213 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | OCB | 2102/2 | 20230606 | 705 | 20230606 | 833 | 2130200 | 88 | Distribution Circuit | Animal | Other | 595 | 52360 | 35.6864 | -120.336 | No | Overcast;32-90 F | Regulator | Burned/flashed | 23-0079208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848206 | 0 | EPSS Ckt | N | 2023 | NOTHING ON ADMS OR SCADA
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | FUSE | 6055 | 20230606 | 708 | 20230607 | 1043 | 2130204 | 1655 | Distribution Circuit | Environmental/External | Lightning | 12 | 7474 | 35.0032 | -120.571 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848402 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | OCB | 2102/2 | 20230606 | 851 | 20230606 | 906 | 2130339 | 15 | Distribution Circuit | Equipment Failure/Involved | Overhead | 595 | 8925 | 35.6864 | -120.336 | No | Overcast;32-90 F | Regulator | Malfunctioning | 23-0079208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848280 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRIP-SAVER | 6111 | 20230606 | 858 | 20230606 | 1235 | 2130346 | 217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 260 | 56420 | 35.0643 | -120.4971 | No | Overcast;32-90 F |  |  | 23-0079360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848391 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1105 | 182581105 | TRANSFORMER | 512021966940 | 20230606 | 859 | 20230606 | 1359 | 2130353 | 300 | Transformer only | Environmental/External | Lightning | 1 | 300 | 35.3104 | -120.6751 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848289 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 513200558075 | 20230606 | 1004 | 20230607 | 1016 | 2130515 | 1452 | Transformer only | Environmental/External | Lightning | 1 | 1452 | 35.0764 | -120.2732 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079572 | OH | Sus | 35454687 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848488 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512837357463 | 20230606 | 1112 | 20230607 | 509 | 2130570 | 1077 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1077 | 35.0555 | -120.3945 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0079560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848478 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512380053445 | 20230606 | 1329 | 20230606 | 1613 | 2130691 | 164 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 164 | 34.9426 | -120.544 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0079484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848441 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512519051200 | 20230606 | 1429 | 20230606 | 1623 | 2130990 | 114 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 114 | 34.8833 | -120.4958 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0079531 | OH | Sus | 45825462 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848458 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 15915 | 20230606 | 1457 | 20230606 | 1622 | 2131063 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 85 | 35.1752 | -120.6202 | No | Overcast;32-90 F |  |  | 23-0079526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848457 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | T3088 | 20230607 | 148 | 20230607 | 1513 | 2131350 | 805 | Distribution Circuit | Environmental/External | Lightning | 2 | 1610 | 35.145 | -120.5201 | No | Overcast;32-90 F | Transformer (UG) | Broken | 23-0079641 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848554 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512827557605 | 20230607 | 610 | 20230607 | 1203 | 2131473 | 353 | Transformer only | Environmental/External | Lightning | 1 | 353 | 35.06 | -120.3969 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0079828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848752 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 10745 | 20230607 | 704 | 20230608 | 125 | 2131540 | 1101 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 4404 | 35.1515 | -120.5172 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0079803 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848731 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512491460688 | 20230607 | 709 | 20230607 | 1652 | 2131552 | 583 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 583 | 35.1411 | -120.5128 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0079743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848687 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512822457485 | 20230607 | 734 | 20230607 | 1323 | 2131574 | 349 | Transformer only | Environmental/External | Lightning | 1 | 349 | 35.0574 | -120.3991 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0079825 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848748 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512956458859 | 20230607 | 1109 | 20230607 | 2245 | 2131894 | 696 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 696 | 35.095 | -120.3551 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0079980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848810 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | TRANSFORMER | 512679053398 | 20230607 | 1322 | 20230608 | 303 | 2132010 | 821 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1642 | 34.9429 | -120.4442 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848793 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 11221 | 20230607 | 1600 | 20230608 | 1436 | 2132874 | 1356 | Distribution Circuit | 3rd Party | Vandalism | 1 | 1356 | 34.6115 | -120.3679 | No | Overcast;32-90 F | Secondary | Broken | 23-0080442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849103 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512821657445 | 20230607 | 1748 | 20230608 | 1030 | 2132137 | 1002 | Transformer only | Environmental/External | Lightning | 1 | 1002 | 35.0557 | -120.4002 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0080119 | OH | Sus | 35455725 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848876 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512820657375 | 20230608 | 45 | 20230608 | 1133 | 2132265 | 648 | Transformer only | Environmental/External | Lightning | 1 | 648 | 35.0553 | -120.4023 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0080120 | OH | Sus | 35455711 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848878 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5483 | 20230608 | 1241 | 20230608 | 1521 | 2132762 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 6280 | 35.5724 | -120.5886 | No | Clear;32-90 F | Fuse | Normal | 23-0080440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849102 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512959260566 | 20230608 | 1733 | 20230609 | 1434 | 2133009 | 1261 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 1261 | 35.1383 | -120.3542 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0080555 | OH | Sus | 45836020 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849161 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 81805 | 20230609 | 1014 | 20230609 | 1203 | 2133513 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1090 | 35.5595 | -120.8191 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0080743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849358 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511526468851 | 20230609 | 1630 | 20230610 | 1351 | 2133824 | 1268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 17752 | 35.3589 | -120.8431 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0081047 | OH | Sus | 31651491 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849465 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 12143 | 20230609 | 2117 | 20230610 | 1121 | 2134009 | 844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 7596 | 34.9825 | -120.572 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 23-0081079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849495 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | FUSE | 5573 | 20230610 | 910 | 20230610 | 1047 | 2134161 | 97 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 41 | 3977 | 35.6582 | -120.8721 | No | Clear;32-90 F |  |  | 23-0081119 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849583 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512948460532 | 20230610 | 1134 | 20230610 | 1302 | 2134237 | 88 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 88 | 35.1385 | -120.3574 | No | Clear;32-90 F |  |  | 23-0081138 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1849597 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1106 | 182061106 | FUSE | 40159 | 20230610 | 1844 | 20230611 | 1122 | 2134427 | 998 | Distribution Circuit | 3rd Party | Vehicle | 274 | 65992 | 34.928 | -120.4522 | No | Overcast;32-90 F | Transformer (UG) | Broken | 23-0081183 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849629 | 1 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y36 | 20230611 | 934 | 20230611 | 1856 | 2134581 | 562 | Distribution Circuit | Animal | Bird found | 290 | 32804 | 34.6026 | -120.1931 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849706 | 0 | EPSS Ckt | N | 2023 | AB TIME OC
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510839075952 | 20230611 | 1718 | 20230611 | 2304 | 2134698 | 346 | Transformer only | Vegetation | Tree - fell into line | 3 | 1038 | 35.5483 | -121.081 | No | Overcast;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0081319 | OH | Sus | 45843390 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849737 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512690750760 | 20230613 | 1428 | 20230613 | 1813 | 2136239 | 225 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 15 | 3375 | 34.8705 | -120.438 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0082019 | OH | Sus | 31652228 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1850357 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512947661131 | 20230613 | 1624 | 20230613 | 2017 | 2136303 | 233 | Transformer only | Environmental/External | Lightning | 1 | 233 | 35.1547 | -120.3571 | No | Clear;32-90 F | CT | Burned/flashed | 23-0082069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850385 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A20 | 20230614 | 911 | 20230614 | 920 | 2136766 | 9 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 3134 | 28206 | 35.5005 | -120.6607 | No | Partly Cloudy;32-90 F | PT/CCVT | Failed/Faulted | 23-0082207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850560 | 0 | EPSS Ckt | N | 2023 | A- GRD
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | TRANSFORMER | 100000003731 | 20230615 | 645 | 20230615 | 1332 | 2137608 | 407 | Transformer only | 3rd Party | Vehicle | 1 | 407 | 34.9285 | -120.539 | No | Overcast;32-90 F | Service conductor | Broken- wire on ground | 23-0082729 | OH | Sus | 31652371 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850848 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | RECLOSER | P28 | 20230615 | 1438 | 20230615 | 1948 | 2137795 | 310 | Distribution Circuit | Animal | Bird found | 505 | 32299 | 35.6289 | -120.6608 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0082811 | OH | Sus | 31652430 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1850877 | 0 | EPSS Ckt | N | 2023 | B PHASE GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 4485 | 20230616 | 1422 | 20230616 | 1536 | 2138691 | 74 | Distribution Circuit | Animal | Bird found | 54 | 3996 | 35.5058 | -120.6832 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0083259 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851180 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2519 | 20230616 | 1735 | 20230616 | 1843 | 2138836 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 2380 | 35.5268 | -120.6745 | No | Clear;32-90 F |  |  | 23-0083284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851195 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | JUMPER | UNUMBERED SBCO 1 S/OF CGC#511630573295 | 20230617 | 930 | 20230617 | 1601 | 2139171 | 391 | Distribution Circuit | Environmental/External | Flood/Erosion | 12 | 4692 | 35.4819 | -120.8124 | No | Overcast;32-90 F | Conductor- Underground | Contaminated | 23-0083334 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1851261 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 14259 | 20230617 | 958 | 20230617 | 1739 | 2139253 | 197 | Distribution Circuit | Animal | Bird found | 31 | 6107 | 35.078 | -120.5489 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 23-0083383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851337 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N42 | 20230617 | 1755 | 20230618 | 1409 | 2139508 | 1214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2271 | 2272816 | 35.8683 | -120.843 | No | Clear;32-90 F |  |  | 23-0083419 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851362 | 0 | EPSS Ckt | Y | 2023 | DCD/ SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 31947 | 20230618 | 902 | 20230618 | 1548 | 2139733 | 406 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1624 | 35.5313 | -120.5845 | No | Partly Cloudy;32-90 F |  |  | 23-0083524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851468 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | TRANSFORMER | 512248659506 | 20230618 | 935 | 20230618 | 1211 | 2139747 | 156 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1404 | 35.1075 | -120.593 | No | Overcast;32-90 F | Fuse | Broken | 23-0083500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851447 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 76265 | 20230619 | 555 | 20230619 | 747 | 2140192 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 896 | 35.5431 | -120.7041 | No | Clear;32-90 F |  |  | 23-0083600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851542 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N42 | 20230619 | 1526 | 20230619 | 1613 | 2140620 | 47 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2271 | 106737 | 35.8683 | -120.843 | No | Clear;32-90 F |  |  | 23-0083686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851660 | 0 | EPSS Ckt | Y | 2023 | DCD
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | RECLOSER | Y18 | 20230620 | 810 | 20230620 | 1005 | 2140916 | 115 | Distribution Circuit | 3rd Party | Vehicle | 537 | 60210 | 34.5941 | -120.1409 | No | Overcast;32-90 F | Recloser | Malfunctioning | 23-0083789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1851795 | 0 | EPSS Ckt | Y | 2023 | NONE
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512330859085 | 20230620 | 1111 | 20230620 | 1523 | 2141300 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 504 | 35.0965 | -120.5653 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0083900 | OH | Sus | 31652707 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851917 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 2657 | 20230620 | 1701 | 20230620 | 1938 | 2141654 | 157 | Distribution Circuit | 3rd Party | Vehicle | 24 | 3768 | 35.5799 | -120.5518 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0084035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851966 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 4695 | 20230621 | 1213 | 20230621 | 1350 | 2142317 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 3104 | 35.6446 | -120.3782 | No | Clear;32-90 F |  |  | 23-0084334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1852202 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 30223 | 20230621 | 1505 | 20230621 | 1818 | 2142379 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1351 | 35.4661 | -120.7723 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0084394 | OH | Sus | 31652718 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1852213 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | 513583140609 | 20230622 | 628 | 20230622 | 910 | 2142776 | 162 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1296 | 34.5972 | -120.1336 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0084522 | OH | Sus | 45855627 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852297 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | T2857 | 20230622 | 821 | 20230622 | 1942 | 2142908 | 681 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 3777 | 35.3947 | -120.63 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0084748 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852472 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 3929 | 20230622 | 914 | 20230622 | 1027 | 2143012 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 4088 | 35.531 | -120.6256 | No | Clear;32-90 F |  |  | 23-0084629 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1852432 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512713651678 | 20230622 | 1119 | 20230622 | 1440 | 2143115 | 201 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 11 | 2211 | 34.8957 | -120.4311 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0084667 | OH | Sus | 31653163 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852447 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y48 | 20230622 | 1502 | 20230622 | 1511 | 2143320 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 826 | 7434 | 34.6653 | -120.1182 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0084794 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1852484 | 0 | EPSS Ckt | Y | 2023 | NA
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | Y24 | 20230622 | 2218 | 20230623 | 1238 | 2143654 | 860 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 22519 | 34.6331 | -120.4541 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0084885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Multi-Fault | 0 | No | No | No | 1852550 | 0 | EPSS Ckt | N | 2023 | ABC/GRD T
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 64223 | 20230623 | 1820 | 20230623 | 2036 | 2144384 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 5848 | 35.1231 | -120.5669 | No | Partly Cloudy;32-90 F |  |  | 23-0085236 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1852770 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | TRANSFORMER | 512573744859 | 20230624 | 835 | 20230624 | 1354 | 2144586 | 319 | Transformer only | Equipment Failure/Involved | Overhead | 24 | 7656 | 34.7072 | -120.471 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0085322 | OH | Sus | 45858439 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852875 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 4483 | 20230624 | 1001 | 20230624 | 1103 | 2144671 | 62 | Distribution Circuit | Animal | Squirrel | 45 | 2790 | 35.5061 | -120.6779 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Normal | 23-0085319 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852874 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | FUSE | 6422 | 20230624 | 1008 | 20230625 | 742 | 2144674 | 1294 | Distribution Circuit | Equipment Failure/Involved | Underground | 106 | 95719 | 35.6158 | -120.6732 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0085335 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852885 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2291 | 20230625 | 2106 | 20230625 | 2313 | 2145536 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 508 | 35.2985 | -120.7834 | No | Clear;32-90 F |  |  | 23-0085467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853021 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 6023 | 20230626 | 508 | 20230626 | 1341 | 2145575 | 513 | Distribution Circuit | Animal | Bird found | 14 | 1852 | 35.5204 | -120.7115 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0085484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853039 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 30527 | 20230626 | 957 | 20230626 | 1105 | 2145837 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 113 | 35.5731 | -120.5966 | No | Clear;32-90 F |  |  | 23-0085598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853198 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y48 | 20230626 | 1348 | 20230626 | 1404 | 2146210 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 826 | 13216 | 34.6653 | -120.1182 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0085703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1853235 | 0 | EPSS Ckt | Y | 2023 | NA
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 1863 | 20230626 | 1538 | 20230626 | 2123 | 2146296 | 345 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 34 | 10153 | 34.5514 | -119.9703 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0085841 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853297 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y48 | 20230626 | 1631 | 20230626 | 1642 | 2146337 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 826 | 9086 | 34.6653 | -120.1182 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0085791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1853273 | 0 | EPSS Ckt | Y | 2023 | NA
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 1133 | 20230627 | 413 | 20230627 | 610 | 2146579 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 3393 | 34.6249 | -120.1192 | No | Overcast;32-90 F |  |  | 23-0085881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853338 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | FUSE | 1263 | 20230627 | 1318 | 20230627 | 1536 | 2147084 | 138 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 138 | 34.7906 | -120.2611 | No | Clear;32-90 F | Metering Equipment | Broken | 23-0086212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853516 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | FUSE | 1263 | 20230627 | 1824 | 20230627 | 1940 | 2147283 | 76 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 76 | 34.7906 | -120.2611 | No | Clear;32-90 F | Metering Equipment | Burned/flashed | 23-0086307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853540 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | JUMPER | JPRS 2 SSD OF GCG 512166875644 | 20230627 | 1950 | 20230627 | 2229 | 2147307 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 5088 | 35.5503 | -120.6341 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0086315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853546 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20230628 | 22 | 20230628 | 851 | s1853583 | 509 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 729 | 140669 | 35.7811 | -120.9891 | No | Clear;32-90 F |  |  | 23-0086353 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853583 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | FUSE | 45903 | 20230628 | 333 | 20230628 | 542 | 2147399 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 143 | 18447 | 34.9054 | -120.4355 | No | Overcast-Fog;32-90 F |  |  | 23-0086364 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853597 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y04 | 20230628 | 804 | 20230628 | 935 | 2147490 | 91 | Distribution Circuit | Company Initiated | Personnel- company | 447 | 40677 | 34.6354 | -120.0656 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0086413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853636 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 11623 | 20230628 | 836 | 20230628 | 1736 | 2147848 | 540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 647 | 34.9824 | -120.5784 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0086509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853775 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | OCB | 2113/2 | 20230628 | 940 | 20230628 | 1308 | 2147790 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7088 | 1234064 | 35.555 | -120.6803 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0086489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853766 | 0 | EPSS Ckt | Y | 2023 | PH INST OC & RLY TGT GRD
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | TRANSFORMER | 513402538633 | 20230628 | 947 | 20230628 | 1245 | 2147821 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 178 | 34.5415 | -120.1916 | No | Partly Cloudy;32-90 F | Metering Equipment | Malfunctioning | 23-0086625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853818 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 31623 | 20230628 | 1213 | 20230628 | 1521 | s1854216 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 33732 | 35.5124 | -120.6703 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0086489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854216 | 1 | EPSS Ckt | Y | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511364272199 | 20230629 | 510 | 20230629 | 837 | 2148596 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1242 | 35.4502 | -120.8998 | No | Overcast;32-90 F | Fuse | Broken | 23-0086993 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853969 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46037 | 20230629 | 1430 | 20230629 | 1510 | 2149058 | 40 | Distribution Circuit | Animal | Bird found | 154 | 6160 | 34.9548 | -120.4288 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0087278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854129 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | R56 | 20230629 | 1448 | 20230629 | 1918 | 2149089 | 270 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 422 | 68864 | 35.6443 | -120.7067 | No | Clear;Above 90 |  |  | 23-0087270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854124 | 0 | EPSS Ckt | Y | 2023 | A & C PH
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | Y24 | 20230629 | 1615 | 20230629 | 1844 | 2149189 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 68 | 10132 | 34.6331 | -120.4541 | No | Partly Cloudy;32-90 F |  |  | 23-0087319 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854137 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | 838078 | 20230629 | 1618 | 20230629 | 1839 | 2149168 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1398 | 182986 | 34.6455 | -120.4608 | No | Partly Cloudy;32-90 F |  |  | 23-0087317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854135 | 0 | EPSS Ckt | Y | 2023 | A PHASE
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 1371 | 20230629 | 2012 | 20230629 | 2050 | 2149340 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 76 | 34.5832 | -120.0996 | No | Clear;32-90 F |  |  | 23-0087365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854173 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512127673575 | 20230630 | 812 | 20230630 | 1157 | 2149585 | 225 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 225 | 35.4935 | -120.6462 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0087510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1854331 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | JUMPER | VERT JPRS 1 W/OF CGC 511358972076 | 20230630 | 839 | 20230630 | 1020 | 2149633 | 101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 505 | 35.4467 | -120.9015 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken | 23-0087482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854306 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512929578590 | 20230630 | 1001 | 20230630 | 1222 | 2149740 | 141 | Transformer only | Animal | Bird found | 1 | 141 | 35.6362 | -120.3799 | No | Clear;32-90 F | Transformer (OH) |  | 23-0087633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854392 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 45083 | 20230630 | 1114 | 20230630 | 1213 | 2149808 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 944 | 34.86 | -120.401 | No | Clear;32-90 F |  |  | 23-0087626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854387 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512500942732 | 20230630 | 1449 | 20230701 | 26 | 2150005 | 577 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 577 | 34.6484 | -120.4945 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854513 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 21260 | 20230701 | 400 | 20230703 | 0 | 2151363 | 2640 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 69144 | 34.6174 | -120.2032 | No | Clear;32-90 F | Bushing | Leaking | 23-0088062 | UG | Sus | 35464204 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854703 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512300074070 | 20230701 | 644 | 20230701 | 834 | 2150595 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 220 | 35.5085 | -120.5878 | No | Clear;32-90 F | Fuse | Deteriorated | 23-0087860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854549 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | RECLOSER | A28 | 20230701 | 1515 | 20230701 | 1647 | 2150904 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1795 | 165140 | 35.4622 | -120.6453 | No | Clear;32-90 F |  |  | 23-0087952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854601 | 0 | EPSS Ckt | Y | 2023 | 3-4 & 5-6
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N44 | 20230701 | 1523 | 20230701 | 1918 | 2150913 | 228 | Distribution Circuit | Company Initiated | Personnel- company | 1188 | 270864 | 35.7755 | -120.8971 | No | Clear;32-90 F | Recloser | Normal | 23-0087948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854599 | 0 | EPSS Ckt | Y | 2023 | AC
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | RECLOSER | A28 | 20230701 | 1705 | 20230702 | 235 | 2151029 | 570 | Distribution Circuit | Equipment Failure/Involved | Underground | 1795 | 121246 | 35.4622 | -120.6453 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0087963 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | No | No | 1854610 | 0 | EPSS Ckt | Y | 2023 | 1-2- 5-6- & GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | TRANSFORMER | T3140 | 20230701 | 1803 | 20230701 | 1949 | 2151154 | 106 | Transformer only | Equipment Failure/Involved | Underground | 19 | 2014 | 35.6047 | -120.6447 | No | Clear;Above 90 | Secondary | Burned/flashed | 23-0087979 | UG | Sus | 45867218 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1854624 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 30053 | 20230701 | 1829 | 20230701 | 2224 | 2151178 | 235 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2508 | 35.6553 | -120.3704 | No | Clear;Above 90 |  |  | 23-0088064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854704 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512742450618 | 20230701 | 2146 | 20230702 | 1159 | 2151571 | 853 | Transformer only | Vegetation | Tree - branch fell on line | 21 | 17913 | 34.8668 | -120.4207 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0088036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854677 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | SWITCH | 22053 | 20230702 | 507 | 20230702 | 848 | 2151861 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3757 | 34.6005 | -120.1909 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0088102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854746 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y36 | 20230702 | 508 | 20230702 | 649 | 2151824 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 273 | 27573 | 34.6026 | -120.1931 | No | Partly Cloudy;32-90 F |  |  | 23-0088102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854740 | 0 | EPSS Ckt | Y | 2023 | A&C
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y26 | 20230702 | 508 | 20230702 | 950 | s1854742 | 282 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 191 | 29110 | 34.625 | -120.1892 | No | Clear;32-90 F |  |  | 23-0088103 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854742 | 0 | EPSS Ckt | Y | 2023 | A&B
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20230702 | 1813 | 20230703 | 325 | 2152345 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 1723 | 176420 | 35.5213 | -120.7125 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0088215 | OH | Sus | 31654204 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | Yes | No | 1854835 | 0 | EPSS Ckt | Y | 2023 | AB GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A16 | 20230703 | 136 | 20230703 | 1021 | 2152888 | 525 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 225 | 74701 | 35.392 | -120.5975 | No | Clear;32-90 F |  |  | 23-0088294 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854935 | 0 | EPSS Ckt | Y | 2023 | A-B
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | SWITCH | 20008 | 20230703 | 1154 | 20230703 | 1247 | 2153350 | 53 | Distribution Circuit | Equipment Failure/Involved | Underground | 51 | 2703 | 34.6164 | -120.2014 | No | Clear-Drizzle;32-90 F | Transformer (UG) | Broken | 23-0088452 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855031 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | TRANSFORMER | 514109539640 | 20230703 | 1402 | 20230703 | 1555 | 2153476 | 113 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 113 | 34.5732 | -119.96 | No | Clear;32-90 F |  |  | 23-0088618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1855060 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511365772024 | 20230703 | 1805 | 20230703 | 1857 | 2153686 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 416 | 35.4453 | -120.8994 | No | Clear;32-90 F | Transformer (OH) | Arcing | 23-0088653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855075 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X08 | 20230704 | 851 | 20230704 | 1604 | 2153997 | 433 | Distribution Circuit | Animal | Other | 73 | 31609 | 35.7094 | -120.3018 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0088732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855144 | 0 | EPSS Ckt | Y | 2023 | A- B PHASE
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | RECLOSER | 605393 | 20230704 | 938 | 20230704 | 1457 | 2154010 | 319 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 18510 | 35.8451 | -120.7004 | No | Clear;32-90 F |  |  | 23-0088741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855148 | 0 | EPSS Ckt | Y | 2023 | INSTANT OC- GRD
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 1643 | 20230704 | 1016 | 20230704 | 1323 | 2154023 | 187 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 6545 | 34.5941 | -120.1394 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0088734 | UG | Sus | 35465641 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855151 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | OCB | 1102/2 | 20230704 | 2328 | 20230705 | 202 | 2154293 | 154 | Distribution Circuit | Animal | Other | 2346 | 361284 | 34.6255 | -120.1193 | No | Partly Cloudy-Fog;32-90 F | Cutout- fuse holder | Normal | 23-0088807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855215 | 0 | EPSS Ckt | Y | 2023 | B-GRD
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512395056877 | 20230705 | 329 | 20230705 | 1629 | 2154334 | 780 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 780 | 35.0369 | -120.5418 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0088845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855232 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2709 | 20230705 | 728 | 20230705 | 1024 | 2154375 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 5632 | 35.5192 | -120.6404 | No | Overcast;32-90 F |  |  | 23-0088926 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855315 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | FUSE | 10735 | 20230705 | 914 | 20230705 | 1112 | 2154609 | 118 | Distribution Circuit | Animal | Squirrel | 1 | 118 | 35.2504 | -120.6702 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 23-0088938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855318 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | SWITCH | 20008 | 20230705 | 958 | 20230705 | 1009 | 2154562 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 51 | 561 | 34.6164 | -120.2014 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0088452 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855309 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | TRANSFORMER | 512506055845 | 20230705 | 1142 | 20230705 | 1433 | 2154641 | 171 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 171 | 35.008 | -120.5048 | No | Clear;32-90 F | Fuse | Burned Open | 23-0089090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855343 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | TRANSFORMER | 513840841752 | 20230705 | 1533 | 20230706 | 208 | 2154809 | 635 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 635 | 34.6298 | -120.0482 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0089183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855399 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | TRANSFORMER | 512304355262 | 20230705 | 1659 | 20230705 | 2003 | 2154772 | 184 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 184 | 34.9916 | -120.5708 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0089150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855368 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A80 | 20230706 | 659 | 20230706 | 1217 | 2155101 | 318 | Distribution Circuit | 3rd Party | Vehicle | 511 | 101110 | 35.4259 | -120.6312 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0089232 | OH | Sus | 31654257 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855418 | 0 | EPSS Ckt | Y | 2023 | B/C
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | SWITCH | 83341 | 20230706 | 1118 | 20230706 | 1313 | 2155398 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 230 | 35.4158 | -120.8564 | No | Clear;32-90 F | Insulator | Broken | 23-0089371 | OH | Sus | 45872428 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855518 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 11205 | 20230706 | 1239 | 20230706 | 1320 | 2155458 | 41 | Distribution Circuit | Animal | Squirrel | 49 | 2009 | 34.6025 | -120.1282 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0089449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855544 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512289554222 | 20230706 | 1343 | 20230706 | 1824 | 2155706 | 281 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1405 | 34.9627 | -120.5748 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0089565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855576 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y46 | 20230706 | 1404 | 20230706 | 1838 | 2155539 | 274 | Distribution Circuit | 3rd Party | Vehicle | 275 | 16382 | 34.6448 | -120.429 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0089483 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855555 | 0 | EPSS Ckt | N | 2023 | A/ GRD
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y46 | 20230706 | 2118 | 20230706 | 2225 | 2155832 | 67 | Distribution Circuit | 3rd Party | Other | 275 | 18425 | 34.6448 | -120.429 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0089605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855597 | 0 | EPSS Ckt | N | 2023 | B-GRD INST OC
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 46131 | 20230707 | 1411 | 20230708 | 0 | 2156385 | 589 | Distribution Circuit | 3rd Party | Vehicle | 1 | 786 | 34.9453 | -120.4538 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0090029 | UG | Sus | 31654571 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855773 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 45305 | 20230708 | 1412 | 20230708 | 1611 | 2157217 | 119 | Distribution Circuit | 3rd Party | Vehicle | 1 | 119 | 35.0206 | -120.5213 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0090123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855877 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | TRANSFORMER | 512113965137 | 20230708 | 1545 | 20230708 | 1654 | 2157274 | 69 | Transformer only | 3rd Party | Vehicle | 11 | 759 | 35.2614 | -120.6431 | No | Clear;32-90 F | Fuse | Normal | 23-0090158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855901 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512582656689 | 20230708 | 1939 | 20230708 | 1948 | 2157343 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 45 | 35.033 | -120.4793 | No | Partly Cloudy-Rain;32-90 F | Connector or Splice (OH) | Contaminated | 23-0090163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855906 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | RECLOSER | 613456 | 20230708 | 2052 | 20230709 | 1930 | 2157408 | 1036 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 129758 | 35.448 | -120.8707 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0090168 | OH | Sus | 45875860 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1855911 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A16 | 20230709 | 522 | 20230709 | 1653 | 2157569 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 37805 | 35.392 | -120.5975 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0090193 | OH | Sus | 31654902 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1855935 | 0 | EPSS Ckt | Y | 2023 | A-B
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 76144 | 20230709 | 1706 | 20230709 | 1737 | 2157790 | 31 | Distribution Circuit | Company Initiated | Return Circuit Normal | 84 | 2604 | 35.3143 | -120.3558 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090193 | OH | Sus | 31654902 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1855980 | 0 | EPSS Ckt | N | 2023 | NA
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511433771180 | 20230709 | 2149 | 20230710 | 207 | 2157758 | 258 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2580 | 35.4218 | -120.8771 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0090266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855997 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | Y24 | 20230710 | 1757 | 20230710 | 1959 | 2158928 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 68 | 8296 | 34.6331 | -120.4541 | No | Clear;32-90 F |  |  | 23-0090620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856244 | 0 | EPSS Ckt | Y | 2023 | A-C INST OC
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N42 | 20230710 | 2113 | 20230711 | 8 | 2159010 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2271 | 393418 | 35.8683 | -120.843 | No | Clear;32-90 F | Regulator | Broken | 23-0090636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856261 | 0 | EPSS Ckt | Y | 2023 | B- INST OC
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N42 | 20230711 | 23 | 20230711 | 121 | 2159147 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2271 | 131718 | 35.8683 | -120.843 | No | Clear;32-90 F | Regulator | Failed/Faulted | 23-0090663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856293 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 986322 | 20230711 | 609 | 20230711 | 800 | 2159268 | 111 | Distribution Circuit | Animal | Bird found | 1575 | 174825 | 35.5505 | -121.0725 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0090671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856308 | 0 | EPSS Ckt | Y | 2023 | A-C
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | R94 | 20230711 | 1419 | 20230711 | 1534 | 2159943 | 75 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 13725 | 35.5605 | -120.7743 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090924 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856566 | 0 | EPSS Ckt | Y | 2023 | NONE
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | SWITCH | 1899BP | 20230712 | 1713 | 20230713 | 527 | 2161102 | 663 | Distribution Circuit | 3rd Party | Vehicle | 2692 | 245797 | 34.9772 | -120.4442 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0091500 | OH | Sus | 35467225 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1856920 | 1 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | JUMPER | 30221 HIGH JUMPERS | 20230714 | 1201 | 20230714 | 1424 | 2162561 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 858 | 35.4968 | -120.7211 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0091698 | OH | Sus | 31637012 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1857500 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | SWITCH | 8534 | 20230714 | 1354 | 20230714 | 1417 | 2162709 | 23 | Distribution Circuit | Company Initiated | Operating error | 225 | 5175 | 34.9773 | -120.448 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0091500 | OH | Sus | 35467225 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1857523 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | 511933674471 | 20230714 | 1614 | 20230715 | 30 | 2162826 | 496 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 992 | 35.5163 | -120.7125 | No | Clear;Above 90 | Transformer (OH) | Deteriorated | 23-0092472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857547 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A20 | 20230715 | 211 | 20230715 | 1033 | 2163075 | 502 | Distribution Circuit | 3rd Party | Vehicle | 3133 | 497393 | 35.5005 | -120.6607 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0092524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857591 | 0 | EPSS Ckt | Y | 2023 | BC
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9407 | 20230715 | 518 | 20230715 | 702 | 2163155 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2704 | 35.1344 | -120.5395 | No | Overcast;32-90 F |  |  | 23-0092536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857602 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20230715 | 755 | 20230715 | 1635 | 2163249 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 51470 | 35.1757 | -120.5255 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0092542 | OH | Sus | 45887992 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1857612 | 0 | EPSS Ckt | Y | 2023 | B PHASE- GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 6631 | 20230715 | 1204 | 20230715 | 1411 | 2163430 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 635 | 35.3964 | -120.6147 | No | Clear;32-90 F |  |  | 23-0092638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857691 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | TRANSFORMER | 512094678215 | 20230715 | 2220 | 20230715 | 2245 | 2163929 | 25 | Transformer only | 3rd Party | Fire- house or bldg. | 8 | 200 | 35.6204 | -120.661 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0092743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857761 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | FUSE | 45445 | 20230716 | 1153 | 20230716 | 1326 | 2164198 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 837 | 34.8655 | -120.3832 | No | Partly Cloudy-Heat Wave;32-90 F |  |  | 23-0092818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857845 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y04 | 20230717 | 803 | 20230717 | 814 | 2165102 | 11 | Distribution Circuit | Company Initiated | Personnel- company | 444 | 4884 | 34.6354 | -120.0656 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0093022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858029 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 6293 | 20230717 | 913 | 20230717 | 1005 | 2165260 | 52 | Distribution Circuit | 3rd Party | Vehicle | 5 | 260 | 34.951 | -120.4896 | No | Overcast;32-90 F | Pole-Wood | Normal | 23-0093091 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858139 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | 705596 | 20230717 | 1337 | 20230717 | 1432 | 2165627 | 55 | Distribution Circuit | Company Initiated | Personnel- company | 106 | 5830 | 34.5986 | -120.1926 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Normal | 23-0093263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1858216 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | TRANSFORMER | 513809043574 | 20230717 | 1844 | 20230718 | 215 | 2165957 | 451 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 451 | 34.6799 | -120.0602 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858283 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | T0622 | 20230717 | 1908 | 20230717 | 2348 | 2165894 | 280 | Transformer only | Equipment Failure/Involved | Underground | 52 | 14560 | 34.9287 | -120.439 | No | Clear-Heat Wave;32-90 F | Secondary | Burned Open | 23-0093407 | UG | Sus | 31656020 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858268 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 10615 | 20230717 | 1946 | 20230717 | 2144 | 2165998 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2124 | 35.3548 | -120.7864 | No | Partly Cloudy-Heat Wave;32-90 F |  |  | 23-0093431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858287 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 5025 | 20230718 | 341 | 20230718 | 639 | 2166164 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 3560 | 35.6001 | -121.1172 | No | Clear;32-90 F |  |  | 23-0093487 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858327 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512701150887 | 20230718 | 1728 | 20230718 | 2237 | 2166647 | 309 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1854 | 34.8741 | -120.4346 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0093913 | OH | Sus | 31656057 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858563 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | TRANSFORMER | 512720251896 | 20230718 | 1819 | 20230718 | 2034 | 2166820 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1620 | 34.9017 | -120.4292 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0093924 | OH | Sus | 45892960 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858569 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512664650495 | 20230718 | 1952 | 20230719 | 313 | 2167262 | 441 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 5292 | 34.863 | -120.4466 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0093984 | OH | Sus | 45892973 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858620 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | OTHER | T600 TWD T373 | 20230718 | 2044 | 20230718 | 2305 | 2167307 | 141 | Distribution Circuit | Equipment Failure/Involved | Underground | 112 | 15792 | 35.7546 | -120.9821 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0093872 | UG | Sus | 35470267 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858585 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A10 | 20230719 | 23 | 20230719 | 1310 | 2167359 | 767 | Distribution Circuit | Equipment Failure/Involved | Overhead | 408 | 92616 | 35.4109 | -120.5655 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0093986 | OH | Sus | 31656143 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858624 | 0 | EPSS Ckt | Y | 2023 | C GRD
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | TRANSFORMER | 513105651983 | 20230719 | 643 | 20230719 | 1028 | 2167439 | 225 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 225 | 34.9073 | -120.3005 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0094150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858824 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | TRANSFORMER | 512019381632 | 20230719 | 1050 | 20230719 | 2040 | 2167856 | 590 | Transformer only | Environmental/External | Flood/Erosion | 1 | 590 | 35.7138 | -120.6881 | No | Clear;32-90 F | Pole-Wood | On Ground | 23-0094154 | OH | Sus | 45893928 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858826 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | JUMPER | M124 | 20230719 | 1351 | 20230720 | 255 | 2168083 | 784 | Distribution Circuit | Equipment Failure/Involved | Overhead | 973 | 127593 | 34.9206 | -120.4642 | No | Clear;32-90 F | Jumper | Burned Open | 23-0094271 | OH | Sus | 31656281 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1858875 | 1 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512259858705 | 20230719 | 1616 | 20230719 | 1739 | 2168359 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 166 | 35.0866 | -120.5885 | No | Clear;32-90 F | Secondary | Broken | 23-0094341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858906 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | RECLOSER | M88 | 20230720 | 24 | 20230720 | 1746 | 2168538 | 1042 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 26540 | 34.8325 | -120.3062 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0094463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1858969 | 0 | EPSS Ckt | Y | 2023 | A&GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | RECLOSER | M80 | 20230720 | 319 | 20230720 | 2025 | 2168558 | 1026 | Distribution Circuit | Equipment Failure/Involved | Underground | 445 | 375896 | 35.0146 | -120.3607 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0094485 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858977 | 0 | EPSS Ckt | Y | 2023 | B&GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1101 | 182611101 | TRANSFORMER | 512031578705 | 20230720 | 551 | 20230720 | 1026 | 2168716 | 275 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 825 | 35.6335 | -120.6822 | No | Clear;32-90 F |  |  | 23-0094597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1859078 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES 1101 | 182611101 | FUSE | 32439 | 20230720 | 556 | 20230720 | 737 | 2168570 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1111 | 35.6316 | -120.6827 | No | Clear;32-90 F |  |  | 23-0094517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858993 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | FUSE | 46251 | 20230720 | 740 | 20230720 | 1221 | 2168631 | 281 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 281 | 34.9207 | -120.4948 | No | Overcast-Fog;32-90 F |  |  | 23-0094687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859104 | 1 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 511715074970 | 20230720 | 1440 | 20230720 | 1920 | 2168807 | 280 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 280 | 35.5283 | -120.7871 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0094806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859137 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | FUSE | 263525 | 20230721 | 304 | 20230721 | 327 | 2169470 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 496 | 11408 | 34.9603 | -120.435 | No | Overcast-Fog;32-90 F | Jumper | Arcing | 23-0094992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859239 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512422953825 | 20230721 | 714 | 20230721 | 1013 | 2169552 | 179 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 179 | 34.953 | -120.53 | No | Overcast-Fog;32-90 F |  |  | 23-0095143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1859402 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y04 | 20230721 | 732 | 20230721 | 938 | 2169561 | 126 | Distribution Circuit | Company Initiated | Personnel- company | 814 | 102564 | 34.6354 | -120.0656 | No | Partly Cloudy-Fog;32-90 F | Recloser | Normal | 23-0095024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859263 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | R06 | 20230721 | 1805 | 20230722 | 1401 | 2170232 | 1196 | Distribution Circuit | Equipment Failure/Involved | Underground | 2180 | 838245 | 35.5543 | -120.7222 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0095417 | UG | Sus | 45897254 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859484 | 0 | EPSS Ckt | Y | 2023 | A&GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | Q08 | 20230722 | 110 | 20230722 | 311 | 2170504 | 121 | Distribution Circuit | Animal | Bird found | 373 | 45133 | 35.148 | -120.5897 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0095486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859545 | 0 | EPSS Ckt | Y | 2023 | B&C
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X14 | 20230722 | 549 | 20230722 | 1801 | 2170547 | 732 | Distribution Circuit | Animal | Bird found | 572 | 130295 | 35.6554 | -120.3806 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0095499 | OH | Sus | 31656289 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | Yes | No | 1859560 | 0 | EPSS Ckt | Y | 2023 | ABC-GRD
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | RECLOSER | 320270 | 20230722 | 607 | 20230722 | 922 | 2170592 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 229 | 44655 | 34.5995 | -120.1277 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0095502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859564 | 0 | EPSS Ckt | Y | 2023 | AB
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 469333 | 20230722 | 1118 | 20230722 | 2208 | 2170798 | 650 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2600 | 34.8731 | -120.3046 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0095585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859677 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | OTHER | WIRE DOWN HOT 2 LD SIDE OF 67619 | 20230722 | 1133 | 20230722 | 1932 | 2170838 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 479 | 34.9323 | -120.3804 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0095553 | OH | Sus | 31656458 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1859655 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 20177 | 20230722 | 1305 | 20230722 | 1543 | 2170889 | 158 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 6478 | 34.6874 | -120.0882 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0095572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859666 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | TRANSFORMER | 512099373147 | 20230722 | 1701 | 20230722 | 2226 | 2171028 | 325 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 4225 | 35.4814 | -120.6554 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0095599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859690 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | FUSE | 6060 | 20230722 | 1927 | 20230723 | 1629 | 2171116 | 1262 | Distribution Circuit | Equipment Failure/Involved | Underground | 132 | 73652 | 35.6077 | -120.6487 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0095644 | UG | Sus | 35472100 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859733 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X22 | 20230723 | 757 | 20230723 | 1210 | 2171337 | 253 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 21505 | 35.6009 | -120.3242 | No | Partly Cloudy;32-90 F |  |  | 23-0095661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859754 | 0 | EPSS Ckt | Y | 2023 | A
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | R56 | 20230723 | 1730 | 20230724 | 933 | 2171820 | 963 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 422 | 231048 | 35.6443 | -120.7067 | No | Partly Cloudy-Heat Wave;32-90 F |  |  | 23-0095713 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859813 | 0 | EPSS Ckt | Y | 2023 | B&GRD
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 451760 | 20230724 | 246 | 20230724 | 524 | 2172054 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1001 | 111733 | 35.7334 | -120.8797 | No | Partly Cloudy;32-90 F |  |  | 23-0095768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859865 | 0 | EPSS Ckt | Y | 2023 | C&GRD
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20230724 | 527 | 20230724 | 1033 | 2172069 | 306 | Distribution Circuit | Company Initiated | Coordination failure | 730 | 223380 | 35.7811 | -120.9891 | No | Clear;32-90 F | Recloser | Normal | 23-0095771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859868 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 6182SW | 20230724 | 545 | 20230724 | 829 | 2172079 | 164 | Distribution Circuit | Equipment Failure/Involved | Underground | 100 | 16400 | 35.7272 | -120.8946 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0095776 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859872 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 492068 | 20230724 | 1023 | 20230724 | 1124 | 2172437 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1738 | 106018 | 35.4579 | -120.6602 | No | Clear;32-90 F |  |  | 23-0095904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860018 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512664650495 | 20230724 | 1901 | 20230725 | 126 | 2172839 | 385 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 4620 | 34.863 | -120.4466 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0096214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860131 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 8577 | 20230724 | 2154 | 20230725 | 322 | 2172686 | 328 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 5429 | 34.6234 | -120.1887 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0096223 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1860138 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512200075920 | 20230725 | 837 | 20230725 | 1236 | 2173233 | 239 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 239 | 35.5578 | -120.6233 | No | Clear;32-90 F |  |  | 23-0096516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1860391 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512550654983 | 20230725 | 841 | 20230726 | 718 | 2173248 | 1357 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1357 | 34.9815 | -120.4879 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Deteriorated | 23-0096443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860373 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512290454299 | 20230725 | 1049 | 20230725 | 1337 | 2173299 | 168 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 504 | 34.9649 | -120.5745 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Annealed | 23-0096450 | OH | Sus | 45900583 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860375 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 942274 | 20230725 | 1126 | 20230725 | 1535 | 2173473 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 7968 | 35.5192 | -120.6406 | No | Clear;32-90 F |  |  | 23-0096540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1860397 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 45083 | 20230725 | 1216 | 20230725 | 1437 | 2173514 | 141 | Distribution Circuit | Animal | Bird found | 16 | 2256 | 34.86 | -120.401 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0096618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860419 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | RECLOSER | R88 | 20230725 | 1307 | 20230725 | 1446 | 2173569 | 99 | Distribution Circuit | Animal | Other | 241 | 19915 | 35.7084 | -120.6137 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0096535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860396 | 0 | EPSS Ckt | Y | 2023 | B PH & GRD
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 3971 | 20230725 | 1644 | 20230726 | 257 | 2173758 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1635 | 35.3609 | -120.8063 | No | Clear;32-90 F | Insulator | Broken | 23-0096755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860444 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | V12 | 20230725 | 1932 | 20230726 | 840 | 2173858 | 788 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 205 | 161540 | 35.2947 | -120.636 | No | Clear;32-90 F |  |  | 23-0096757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860445 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512200075920 | 20230726 | 1046 | 20230726 | 1203 | 2174342 | 77 | Transformer only | 3rd Party | Customer Equipment | 1 | 77 | 35.5578 | -120.6233 | No | Clear;32-90 F | Fuse | Normal | 23-0097058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860695 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | TRANSFORMER | T1146 | 20230726 | 1508 | 20230726 | 1829 | 2174598 | 201 | Transformer only | Equipment Failure/Involved | Underground | 23 | 4623 | 34.9087 | -120.4227 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0097172 | UG | Sus | 45902790 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860734 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | RECLOSER | A64 | 20230727 | 708 | 20230727 | 1110 | 2175017 | 242 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3079 | 637270 | 35.5233 | -120.6936 | No | Clear;32-90 F |  |  | 23-0097388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860807 | 0 | EPSS Ckt | Y | 2023 | A GRD
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | FUSE | 11175 | 20230727 | 1731 | 20230728 | 235 | 2175040 | 544 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 544 | 34.878 | -120.2593 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Leaking | 23-0097437 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860876 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | TRANSFORMER | 413764118450 | 20230727 | 2244 | 20230728 | 240 | 2175864 | 236 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 236 | 35.8233 | -121.0989 | No | Clear;32-90 F | Service conductor | Broken | 23-0097880 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861097 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | RECLOSER | TEMP LR 1101/2 | 20230728 | 42 | 20230728 | 233 | 2175889 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 381 | 28179 | 35.2865 | -120.7064 | No | Clear;32-90 F |  |  | 23-0097874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861091 | 0 | EPSS Ckt | Y | 2023 | B- C PHASE
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 20230728 | 848 | 20230728 | 905 | s1861224 | 17 | Distribution Circuit | Company Initiated | Personnel- company | 16 | 272 | 35.4345 | -120.2869 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0093280 | OH | Sus | 31622825 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1861224 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | FUSE | 1123 | 20230728 | 1603 | 20230728 | 1741 | 2176568 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 9800 | 35.0023 | -120.4392 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0098163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861314 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | OCB | 1102/2 | 20230729 | 232 | 20230729 | 1206 | 2176870 | 574 | Distribution Circuit | 3rd Party | Vehicle | 8399 | 819506 | 35.1017 | -120.581 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0098260 | OH | Sus | 35473236 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | Yes | No | 1861374 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | Q10 | 20230729 | 232 | 20230729 | 842 | 2176876 | 370 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 781 | 288970 | 35.1349 | -120.5694 | No | Clear;32-90 F |  |  | 23-0098262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861376 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | FUSE | 6257 | 20230729 | 757 | 20230729 | 1345 | 2176921 | 348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 12528 | 34.7292 | -120.0951 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0098274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861390 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | R82 | 20230729 | 2046 | 20230730 | 20 | 2177388 | 214 | Distribution Circuit | Animal | Bird found | 899 | 168032 | 35.5299 | -120.523 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0098383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861519 | 0 | EPSS Ckt | Y | 2023 | B C
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 6011 | 20230730 | 30 | 20230730 | 232 | 2177479 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 366 | 35.531 | -120.7079 | No | Clear;32-90 F |  |  | 23-0098415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861550 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 32049 | 20230730 | 859 | 20230730 | 1203 | 2177604 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 184 | 35.5251 | -120.6929 | No | Clear;32-90 F |  |  | 23-0098448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861595 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 14033 | 20230730 | 1138 | 20230730 | 1928 | 2177657 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1410 | 35.0726 | -120.5974 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0098447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861594 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 3815 | 20230730 | 1315 | 20230730 | 2252 | 2177696 | 577 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 46160 | 35.088 | -120.5641 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0098453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861601 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 30389 | 20230730 | 1709 | 20230730 | 2133 | 2177896 | 264 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 135 | 31220 | 35.5468 | -120.7082 | No | Clear;32-90 F | Fuse | Normal | 23-0098476 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861616 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | V12 | 20230730 | 1839 | 20230731 | 916 | 2177934 | 877 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 205 | 145729 | 35.2947 | -120.636 | No | Partly Cloudy;32-90 F |  |  | 23-0098478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861618 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512675754183 | 20230731 | 640 | 20230731 | 839 | 2178137 | 119 | Transformer only | 3rd Party | Metallic Balloon | 21 | 2499 | 34.9645 | -120.4459 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0098596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861759 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | TRANSFORMER | 513111946113 | 20230731 | 1117 | 20230731 | 1444 | 2178357 | 207 | Transformer only | Company Initiated | Other Circuits | 3 | 621 | 34.7456 | -120.2944 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0098673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861832 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510820475889 | 20230801 | 23 | 20230801 | 701 | 2179055 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 4776 | 35.5465 | -121.0873 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0098926 | OH | Sus | 31657746 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1861945 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512235858182 | 20230801 | 841 | 20230801 | 934 | 2179241 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 159 | 35.0712 | -120.595 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Deteriorated | 23-0098971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1862028 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 4719 | 20230801 | 1833 | 20230802 | 550 | 2179861 | 677 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 23018 | 35.6078 | -121.091 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0099349 | OH | Sus | 31657592 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | Yes | No | 1862236 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512775066160 | 20230801 | 2243 | 20230802 | 1825 | 2180020 | 1182 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1182 | 35.2922 | -120.4217 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0099370 | OH | Sus | 35474136 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862249 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A70 | 20230801 | 2318 | 20230802 | 305 | 2180042 | 227 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1711 | 188269 | 35.5023 | -120.649 | No | Partly Cloudy;32-90 F |  |  | 23-0099373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862252 | 0 | EPSS Ckt | Y | 2023 | B- C
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A32 | 20230802 | 211 | 20230802 | 812 | 2180064 | 361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1255 | 145461 | 35.5007 | -120.662 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0099383 | OH | Sus | 31657830 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1862259 | 0 | EPSS Ckt | Y | 2023 | A GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 66283 | 20230802 | 1329 | 20230802 | 1502 | 2180782 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 93 | 34.9499 | -120.5074 | No | Clear;32-90 F |  |  | 23-0099692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862519 | 1 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | JUMPER | 32149/ 2993 HIGH SIDE JUMPERS | 20230802 | 1517 | 20230802 | 1715 | 2180726 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1062 | 35.5435 | -120.7012 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0099640 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862506 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 66283 | 20230803 | 1022 | 20230803 | 1147 | 2181434 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 85 | 34.9499 | -120.5074 | No | Partly Cloudy;32-90 F |  |  | 23-0100102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862801 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511423171546 | 20230804 | 328 | 20230804 | 849 | 2182044 | 321 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3852 | 35.4318 | -120.8803 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862934 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 5257 | 20230804 | 732 | 20230804 | 1151 | 2182086 | 259 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 6734 | 35.3286 | -120.8398 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100472 | OH | Sus | 31659035 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863024 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 510914074578 | 20230804 | 919 | 20230804 | 1334 | 2182268 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 441 | 35.5112 | -121.0541 | No | Overcast;32-90 F | Jumper | Broken | 23-0100541 | OH | Sus | 45911216 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863083 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | T3351 | 20230804 | 1217 | 20230804 | 1813 | 2182429 | 356 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 356 | 35.5156 | -120.7173 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0100702 | UG | Sus | 35474913 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863147 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 7006 | 20230805 | 946 | 20230805 | 1406 | 2182998 | 260 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 258 | 53378 | 35.8689 | -120.8458 | No | Clear;32-90 F |  |  | 23-0100863 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863290 | 0 | EPSS Ckt | Y | 2023 | A & GRD PHASE
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | OTHER | J758 TWD T2724 | 20230805 | 1200 | 20230805 | 1336 | 2183079 | 96 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 5376 | 35.0283 | -120.4893 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0100869 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863310 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 79696 | 20230806 | 526 | 20230806 | 846 | 2183492 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 132 | 26400 | 35.5731 | -121.0414 | No | Partly Cloudy;32-90 F |  |  | 23-0100981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863384 | 0 | EPSS Ckt | Y | 2023 | B-C INST PC
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | V38 | 20230806 | 1040 | 20230806 | 1619 | 2183581 | 339 | Distribution Circuit | 3rd Party | Metallic Balloon | 1501 | 242373 | 35.1274 | -120.5689 | No | Partly Cloudy;32-90 F | Jumper | Burned/flashed | 23-0101005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863415 | 0 | EPSS Ckt | Y | 2023 | B & C PH
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | 49394 | 20230806 | 1223 | 20230806 | 2150 | 2183613 | 415 | Distribution Circuit | Equipment Failure/Involved | Underground | 2102 | 388740 | 34.7035 | -120.461 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0101011 | UG | Sus | 31662120 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863423 | 0 | EPSS Ckt | Y | 2023 | B PH & GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 64121 | 20230807 | 636 | 20230807 | 900 | 2184034 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1008 | 35.6065 | -120.6067 | No | Clear;32-90 F |  |  | 23-0101146 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863554 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | OTHER | WIRE DWN BET 1477 & 14251 | 20230807 | 645 | 20230807 | 1100 | 2184035 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 544 | 115822 | 35.0745 | -120.5774 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0101119 | OH | Sus | 45915434 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1863514 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 52783 | 20230807 | 739 | 20230807 | 1953 | 2184077 | 734 | Distribution Circuit | 3rd Party | Vehicle | 6 | 4404 | 34.9708 | -120.5674 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 23-0101151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1863562 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | 55374 | 20230807 | 752 | 20230807 | 1253 | 2184091 | 301 | Distribution Circuit | Animal | Squirrel | 519 | 81736 | 35.6203 | -120.6962 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0101130 | OH | Sus | 45915523 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1863524 | 0 | EPSS Ckt | Y | 2023 | BC
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M54 | 20230807 | 1339 | 20230807 | 1632 | 2184717 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 127 | 21971 | 34.8627 | -120.2773 | No | Clear;32-90 F |  |  | 23-0101303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863732 | 0 | EPSS Ckt | Y | 2023 | A GRD
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | RECLOSER | V74 | 20230808 | 604 | 20230808 | 741 | 2185190 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 332 | 32204 | 35.5459 | -121.0678 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0101517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863845 | 0 | EPSS Ckt | Y | 2023 | AC
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511412471556 | 20230808 | 705 | 20230808 | 1035 | 2185208 | 210 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 4830 | 35.4322 | -120.8839 | No | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0101593 | OH | Sus | 31662358 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863925 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | TRANSFORMER | 513278749922 | 20230808 | 1019 | 20230808 | 1038 | 2185495 | 19 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 19 | 34.8512 | -120.2415 | No | Partly Cloudy;32-90 F |  |  | 23-0101671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864024 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 121629 | 20230808 | 1041 | 20230808 | 1419 | 2185639 | 218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 654 | 35.0331 | -120.4912 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0101709 | OH | Sus | 31662153 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1864035 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1105 | 182581105 | SWITCH | 551904 | 20230808 | 1117 | 20230808 | 1123 | 2185703 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 6 | 35.3205 | -120.6917 | No | Clear;32-90 F | Metering Equipment | Burned/flashed | 23-0101697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1864033 | 0 | EPSS Ckt | Y | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y04 | 20230808 | 1745 | 20230808 | 1948 | 2186063 | 123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 450 | 55350 | 34.6354 | -120.0656 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0101914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864100 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | TRANSFORMER | 513760941969 | 20230808 | 2243 | 20230809 | 450 | 2186168 | 367 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 367 | 34.6355 | -120.0753 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0101959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864126 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 31923 | 20230809 | 1845 | 20230809 | 1955 | 2187067 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 70 | 35.4852 | -120.5077 | No | Partly Cloudy;32-90 F | Jumper | Broken | 23-0102385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1864415 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20230810 | 11 | 20230810 | 647 | 2187195 | 396 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1188 | 155457 | 35.7811 | -120.9891 | No | Clear;32-90 F |  |  | 23-0102467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864450 | 0 | EPSS Ckt | Y | 2023 | B-C
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 6609 | 20230810 | 757 | 20230810 | 1053 | 2187415 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1232 | 35.7903 | -120.9199 | No | Clear;32-90 F |  |  | 23-0102643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864658 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512371680345 | 20230810 | 1113 | 20230810 | 1552 | 2187730 | 279 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 558 | 35.6807 | -120.5696 | No | Partly Cloudy;32-90 F | Transformer | Normal | 23-0102794 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864719 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | OCB | 1102/2 | 20230810 | 1555 | 20230810 | 1754 | 2188015 | 119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5962 | 134919 | 34.8288 | -120.4485 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0102888 | OH | Sus | 31662830 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1864735 | 0 | EPSS Ckt | N | 2023 | GRD
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 1827 | 20230810 | 1850 | 20230810 | 1859 | 2188169 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 23 | 207 | 34.8779 | -120.4541 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0102888 | OH | Sus | 31662830 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1864759 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | INTERRUPTER | 11156 | 20230810 | 1940 | 20230810 | 2050 | 2188199 | 27 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 484 | 13770 | 34.9165 | -120.4316 | No | Overcast;32-90 F | Switch (UG) | Normal | 23-0094092 | UG | Sus | 35422301 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864761 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 6679 | 20230811 | 40 | 20230811 | 343 | 2188299 | 183 | Distribution Circuit | Animal | Bird found | 15 | 2745 | 35.5726 | -120.6016 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0103055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864819 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 679461 | 20230811 | 1321 | 20230811 | 1909 | 2188693 | 348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 10008 | 35.0222 | -120.5171 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0103380 | OH | Sus | 31662837 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1865030 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 6917 | 20230812 | 906 | 20230812 | 1158 | 2189060 | 172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2236 | 34.7327 | -119.9963 | No | Clear;32-90 F | Other | Malfunctioning | 23-0103573 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1865160 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | RECLOSER | 798137 | 20230812 | 1006 | 20230812 | 1121 | 2189129 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1725 | 35.3054 | -120.8082 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0103596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1865202 | 0 | EPSS Ckt | Y | 2023 | BC
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 2657 | 20230813 | 552 | 20230813 | 807 | 2189513 | 135 | Distribution Circuit | Animal | Bird found | 24 | 3240 | 35.5799 | -120.5518 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Normal | 23-0103717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1865319 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | RECLOSER | W58 | 20230813 | 1323 | 20230813 | 1618 | 2189630 | 175 | Distribution Circuit | Animal | Bird found | 330 | 57750 | 35.4511 | -120.9069 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0103753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865342 | 0 | EPSS Ckt | Y | 2023 | A GRD
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | TRANSFORMER | 511841865295 | 20230813 | 1622 | 20230813 | 2329 | 2189694 | 427 | Transformer only | Vegetation | Tree - fell into line | 2 | 854 | 35.2636 | -120.7334 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103779 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865365 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512884040070 | 20230813 | 2133 | 20230813 | 2350 | 2189885 | 137 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 137 | 34.5774 | -120.3616 | No | Partly Cloudy;32-90 F |  |  | 23-0103829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1865407 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 236895 | 20230814 | 117 | 20230814 | 430 | 2189938 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 772 | 35.1761 | -120.535 | No | Partly Cloudy;32-90 F |  |  | 23-0103839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1865415 | 0 | EPSS Ckt | Y | 2023 | N/A
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 9025 | 20230814 | 833 | 20230814 | 1042 | 2190074 | 129 | Distribution Circuit | Animal | Squirrel | 16 | 2064 | 35.2532 | -120.7638 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0103977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865589 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 236895 | 20230814 | 836 | 20230814 | 1037 | 2190079 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 484 | 35.1761 | -120.535 | No | Overcast;32-90 F |  |  | 23-0103965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | No | No | 1865579 | 0 | EPSS Ckt | Y | 2023 | C
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | SWITCH | 6372 | 20230814 | 1312 | 20230814 | 1424 | 2190562 | 72 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 1152 | 34.7153 | -120.4717 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0103949 | UG | Sus | 35475580 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865632 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | RECLOSER | M88 | 20230814 | 1519 | 20230814 | 1802 | 2190691 | 163 | Distribution Circuit | 3rd Party | Other | 39 | 6357 | 34.8325 | -120.3062 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0104191 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1865648 | 0 | EPSS Ckt | Y | 2023 | BC
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | SWITCH | 11166 | 20230814 | 2058 | 20230814 | 2337 | 2190965 | 159 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 477 | 34.9333 | -120.4213 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0104259 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865691 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | Q12 | 20230815 | 617 | 20230815 | 820 | 2191238 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1501 | 76138 | 35.1396 | -120.5208 | No | Overcast-Fog;32-90 F |  |  | 23-0104333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1865736 | 0 | EPSS Ckt | Y | 2023 | AC
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512627343325 | 20230815 | 1109 | 20230815 | 1310 | 2191582 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 121 | 34.6656 | -120.4533 | No | Clear;32-90 F | Fuse | Burned Open | 23-0104597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865929 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | 511897580860 | 20230815 | 1123 | 20230815 | 1338 | 2191584 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 135 | 35.6913 | -120.7299 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0104490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865897 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20230815 | 1349 | 20230815 | 1707 | 2191764 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 191 | 37818 | 34.5979 | -120.0297 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0104635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1865937 | 0 | EPSS Ckt | Y | 2023 | AB
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | 277014 | 20230815 | 1833 | 20230815 | 2020 | 2192102 | 107 | Distribution Circuit | Vegetation | Tree - fell into line | 364 | 38948 | 34.5994 | -120.0979 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0104796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1865990 | 0 | EPSS Ckt | Y | 2023 | DCD & SGF
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | 277014 | 20230815 | 2034 | 20230816 | 1929 | 2192217 | 1375 | Distribution Circuit | Vegetation | Tree - fell into line | 364 | 302453 | 34.5994 | -120.0979 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0104820 | OH | Sus | 31663534 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1866009 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 3371 | 20230816 | 1337 | 20230816 | 1506 | 2192959 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 89 | 35.5586 | -120.335 | No | Clear;Above 90 |  |  | 23-0105171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866292 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | 483444 | 20230816 | 1720 | 20230816 | 1900 | 2193178 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2955 | 226094 | 35.2892 | -120.6524 | No | Clear;32-90 F |  |  | 23-0105268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866321 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2287 | 20230816 | 2038 | 20230816 | 2312 | 2193329 | 154 | Distribution Circuit | Animal | Bird found | 2 | 308 | 35.2848 | -120.7328 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0105331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866367 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y36 | 20230817 | 637 | 20230817 | 802 | 2193471 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 289 | 21845 | 34.6026 | -120.1931 | No | Partly Cloudy-Fog-Rain;32-90 F |  |  | 23-0105390 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866419 | 0 | EPSS Ckt | Y | 2023 | B&C INST
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 75697 | 20230817 | 1446 | 20230817 | 1510 | 2193890 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 312 | 34.9478 | -120.447 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0105671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866574 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRIP-SAVER | 6111 | 20230817 | 1627 | 20230818 | 1114 | 2193961 | 1127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 260 | 109020 | 35.0643 | -120.4971 | No | Partly Cloudy;32-90 F |  |  | 23-0105759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866590 | 1 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512236271292 | 20230817 | 1833 | 20230818 | 33 | 2194039 | 360 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 360 | 35.4315 | -120.6069 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0105746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866587 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 8753 | 20230817 | 2045 | 20230817 | 2344 | 2194182 | 179 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 3580 | 35.0192 | -120.5011 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0105790 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866613 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | 511895080745 | 20230818 | 803 | 20230818 | 1246 | 2194500 | 283 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1132 | 35.6886 | -120.7302 | No | Overcast-Fog;32-90 F | Pole-Wood | Normal | 23-0105910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866690 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | SWITCH | 868170 | 20230818 | 936 | 20230818 | 1057 | 2194761 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 372 | 30132 | 35.3112 | -120.8538 | No | Overcast;32-90 F |  |  | 23-0106007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866818 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512307954218 | 20230819 | 1203 | 20230819 | 1230 | 2195634 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 432 | 34.9628 | -120.5681 | No | Clear;32-90 F | Secondary | Broken | 23-0106353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867050 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | 512000173411 | 20230819 | 1208 | 20230819 | 1603 | 2195618 | 235 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 940 | 35.4879 | -120.6889 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0106368 | OH | Sus | 45933570 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867054 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | SWITCH | 20285 | 20230819 | 1331 | 20230819 | 1417 | 2195670 | 46 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 36 | 1656 | 34.657 | -120.3232 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867061 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512402776440 | 20230819 | 1359 | 20230819 | 1405 | 2195674 | 6 | Transformer only | Animal | Squirrel | 1 | 6 | 35.5739 | -120.5561 | No | Clear;32-90 F | Fuse | Burned Open | 23-0106387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867063 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 12079 | 20230819 | 1907 | 20230819 | 2201 | 2196237 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1740 | 34.8792 | -120.3095 | No | Partly Cloudy;32-90 F |  |  | 23-0106499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867168 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A46 | 20230820 | 1834 | 20230820 | 2036 | 2197258 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 808 | 44357 | 35.4018 | -120.6222 | No | Clear;32-90 F |  |  | 23-0106734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867382 | 0 | EPSS Ckt | Y | 2023 | A GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 6127 | 20230820 | 2203 | 20230821 | 21 | 2197385 | 138 | Distribution Circuit | Animal | Bird found | 5 | 690 | 35.5605 | -120.6717 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867425 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | RECLOSER | 320270 | 20230821 | 703 | 20230821 | 2358 | 2197599 | 1015 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 59251 | 34.5995 | -120.1277 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 23-0106828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867479 | 0 | EPSS Ckt | Y | 2023 | A-B- INST
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511393371783 | 20230821 | 852 | 20230821 | 907 | 2197626 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 210 | 35.4385 | -120.8902 | No | Fog;32-90 F | Secondary | Normal | 23-0106885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867547 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y02 | 20230821 | 946 | 20230821 | 1146 | 2197837 | 120 | Distribution Circuit | Vegetation | Tree - fell into line | 538 | 64560 | 34.6503 | -120.0946 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0106935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867596 | 0 | EPSS Ckt | Y | 2023 | A-B
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | TRANSFORMER | 510952578685 | 20230821 | 1242 | 20230821 | 2130 | 2198153 | 528 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 528 | 35.6236 | -121.0448 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867723 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512595156626 | 20230821 | 1400 | 20230822 | 100 | 2198303 | 660 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3300 | 35.0313 | -120.4752 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867772 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | SWITCH | 560665 | 20230821 | 2333 | 20230822 | 6 | 2198757 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 858 | 35.3802 | -120.8572 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0107316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867812 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A70 | 20230822 | 853 | 20230822 | 1216 | 2198982 | 203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1709 | 155440 | 35.5023 | -120.649 | No | Clear;32-90 F |  |  | 23-0107437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867918 | 0 | EPSS Ckt | Y | 2023 | A-B
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | TRANSFORMER | T0236 | 20230822 | 1107 | 20230822 | 1123 | 2199114 | 16 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 32 | 34.5845 | -120.0912 | No | Clear;32-90 F |  |  | 23-0107539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1868013 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | OCB | 1108/2 | 20230823 | 529 | 20230823 | 648 | 2199758 | 79 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 2894 | 228626 | 35.2617 | -120.6345 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 23-0107842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868154 | 0 | EPSS Ckt | N | 2023 | PHSE GRD INST
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | RECLOSER | A50 | 20230823 | 609 | 20230823 | 1029 | 2199766 | 260 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 680 | 169516 | 35.4654 | -120.6712 | No | Clear;32-90 F |  |  | 23-0107844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1868156 | 0 | EPSS Ckt | Y | 2023 | A-C
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512277859880 | 20230823 | 735 | 20230823 | 922 | 2199801 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 214 | 35.1179 | -120.5834 | No | Overcast-Fog-Drizzle;32-90 F | Cutout- fuse holder | Broken | 23-0107921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868286 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 4975 | 20230823 | 1121 | 20230823 | 1318 | 2200123 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 10179 | 35.3987 | -120.8285 | No | Clear;32-90 F |  |  | 23-0108095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868357 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | OTHER | T3492 TWD T3493 | 20230823 | 1141 | 20230823 | 1229 | 2200137 | 48 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 1680 | 34.9159 | -120.4204 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 23-0108005 | UG | Sus | 35483342 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868344 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 30937 | 20230823 | 1633 | 20230823 | 2006 | 2200401 | 213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1704 | 35.4892 | -120.6495 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0108279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868389 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512240171739 | 20230824 | 936 | 20230824 | 1504 | 2201135 | 328 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 656 | 35.4438 | -120.6063 | No | Clear;32-90 F | Service conductor | Broken | 23-0108724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868738 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512108160629 | 20230824 | 1207 | 20230824 | 1239 | 2200855 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 672 | 35.1375 | -120.641 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0108653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868705 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512689854142 | 20230824 | 1316 | 20230824 | 1550 | 2201381 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 3388 | 34.9634 | -120.4411 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0108767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868753 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 6607 | 20230824 | 1316 | 20230824 | 1410 | 2201377 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 138 | 7452 | 35.5107 | -120.7135 | No | Clear;32-90 F |  |  | 23-0108679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1868719 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512159359920 | 20230824 | 1354 | 20230824 | 1502 | 2201420 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 30 | 2040 | 35.1185 | -120.6229 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0108747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868746 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N42 | 20230824 | 1611 | 20230824 | 1910 | 2201529 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2171 | 300689 | 35.8683 | -120.843 | No | Clear;32-90 F |  |  | 23-0108772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1868756 | 0 | EPSS Ckt | Y | 2023 | B C PHASE
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V58 | 20230825 | 139 | 20230825 | 825 | 2201737 | 406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2816 | 268670 | 35.247 | -120.6494 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0108883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868847 | 0 | EPSS Ckt | Y | 2023 | A/SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 7231 | 20230825 | 449 | 20230825 | 715 | 2201774 | 143 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 1716 | 35.4972 | -120.6808 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0108889 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868853 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 350030 | 20230825 | 1503 | 20230825 | 1646 | 2202336 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 412 | 35.2139 | -120.5913 | No | Clear;32-90 F |  |  | 23-0109254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869077 | 0 | EPSS Ckt | Y | 2023 | A- C
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6139 | 20230825 | 1550 | 20230825 | 1609 | 2202365 | 19 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 76 | 35.5321 | -120.771 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869084 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y46 | 20230825 | 1652 | 20230826 | 1724 | 2202423 | 1472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 275 | 399027 | 34.6448 | -120.429 | No | Clear;32-90 F | Jumper | Bent or Twisted | 23-0109295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869097 | 0 | EPSS Ckt | Y | 2023 | C/GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 47765 | 20230826 | 1515 | 20230826 | 1745 | 2202931 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 600 | 35.4621 | -120.6665 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869251 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | OCB | 1110/2 | 20230826 | 1803 | 20230826 | 1829 | 2202972 | 26 | Distribution Circuit | 3rd Party | Vehicle | 2410 | 62660 | 34.9503 | -120.4442 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0109445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869252 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510835776091 | 20230826 | 1847 | 20230827 | 426 | 2202960 | 579 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1737 | 35.5521 | -121.0822 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0109451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869258 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 30449 | 20230827 | 1509 | 20230827 | 1637 | 2203372 | 88 | Distribution Circuit | 3rd Party | Metallic Balloon | 6 | 528 | 35.7241 | -120.6046 | No | Clear;Above 90 | Transformer (OH) | Normal | 23-0109553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869345 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 14275 | 20230828 | 107 | 20230828 | 450 | 2203552 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 297 | 35.2634 | -120.6427 | No | Clear;32-90 F |  |  | 23-0109593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869384 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 7006 | 20230828 | 2006 | 20230829 | 916 | 2204473 | 790 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 258 | 47526 | 35.8689 | -120.8458 | No | Clear;32-90 F |  |  | 23-0109957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869661 | 0 | EPSS Ckt | Y | 2023 | A/C
LOS PADRES | SANTA MARIA | DIVIDE 1101 | 182571101 | TRANSFORMER | 512747050230 | 20230828 | 2227 | 20230829 | 157 | 2204493 | 210 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 840 | 34.8562 | -120.4187 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869690 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1106 | 182061106 | OTHER | J852 TWD T3179 | 20230829 | 1217 | 20230829 | 1254 | 2205046 | 37 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 777 | 34.9294 | -120.4591 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0110188 | UG | Sus | 35484764 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869931 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512708753267 | 20230829 | 1246 | 20230829 | 1437 | 2204979 | 111 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1110 | 34.9395 | -120.4342 | No | Clear;32-90 F | Service conductor | Broken | 23-0110263 | OH | Sus | 45945019 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869940 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | RECLOSER | V84 | 20230829 | 1337 | 20230829 | 1607 | 2205115 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2440 | 108620 | 35.3169 | -120.8248 | No | Clear;32-90 F |  |  | 23-0110310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869960 | 0 | EPSS Ckt | Y | 2023 | BC
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 30957 | 20230829 | 1610 | 20230830 | 331 | 2205267 | 681 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 24516 | 35.477 | -120.6525 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0110445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869986 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20230829 | 1937 | 20230830 | 808 | 2205419 | 751 | Distribution Circuit | Animal | Bird found | 281 | 155513 | 35.7984 | -120.9741 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0110465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1870006 | 0 | EPSS Ckt | Y | 2023 | B/C
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 7006 | 20230830 | 1355 | 20230830 | 1532 | 2206109 | 97 | Distribution Circuit | Animal | Bird found | 258 | 25026 | 35.8689 | -120.8458 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0110860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1870256 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 7006 | 20230830 | 1554 | 20230830 | 1806 | 2206228 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 258 | 34056 | 35.8689 | -120.8458 | No | Clear;Above 90 |  |  | 23-0110955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870281 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | JUMPER | JUMPERS 1P W/OF MTR# 1008495394 | 20230830 | 2355 | 20230831 | 254 | 2206509 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 4117 | 34.9574 | -120.4445 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0111040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1870332 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20230831 | 202 | 20230831 | 1002 | 2206526 | 480 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 548 | 134809 | 35.2197 | -120.5967 | No | Partly Cloudy;32-90 F |  |  | 23-0111042 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870334 | 0 | EPSS Ckt | Y | 2023 | A SGF
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512105361012 | 20230831 | 512 | 20230831 | 1257 | 2206588 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 6045 | 35.1479 | -120.6417 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0111089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870376 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20230831 | 722 | 20230831 | 1103 | 2206618 | 221 | Distribution Circuit | Company Initiated | Personnel- company | 1722 | 380562 | 35.5213 | -120.7125 | No | Fog;32-90 F | Recloser | Normal | 23-0111076 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870356 | 0 | EPSS Ckt | Y | 2023 | GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 14157 | 20230831 | 807 | 20230901 | 25 | 2206714 | 978 | Distribution Circuit | 3rd Party | Vehicle | 211 | 28698 | 35.2632 | -120.6341 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 23-0111203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1870526 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X16 | 20230831 | 902 | 20230831 | 1204 | 2206824 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 283 | 20489 | 35.6868 | -120.3362 | No | Clear;32-90 F |  |  | 23-0111151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1870469 | 0 | EPSS Ckt | Y | 2023 | AB
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | 483444 | 20230831 | 909 | 20230831 | 1003 | 2206838 | 54 | Distribution Circuit | Animal | Bird found | 2950 | 159288 | 35.2892 | -120.6524 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0111165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870490 | 0 | EPSS Ckt | Y | 2023 | A GRD INST
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 6553 | 20230831 | 1123 | 20230831 | 1244 | 2207039 | 81 | Distribution Circuit | Animal | Squirrel | 10 | 810 | 35.5221 | -120.7135 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0111302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870581 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1106 | 182061106 | FUSE | 560001 | 20230831 | 2011 | 20230831 | 2145 | 2207383 | 94 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 470 | 34.9313 | -120.4543 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0111528 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870627 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | M72 | 20230901 | 202 | 20230901 | 1017 | 2207488 | 495 | Distribution Circuit | Vegetation | Tree - fell into line | 2966 | 262006 | 35.0397 | -120.5225 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0111574 | OH | Sus | 35486040 | SOUTH BAY AND CENTRAL COAST | SEP | Multi-Fault | 0 | No | Yes | No | 1870672 | 0 | EPSS Ckt | N | 2023 | AC GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 6375 | 20230901 | 1711 | 20230902 | 48 | 2208073 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 24240 | 35.4843 | -120.6515 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112008 | OH | Sus | 31666654 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1870856 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | FUSE | 4155 | 20230901 | 1739 | 20230901 | 1846 | 2208095 | 67 | Distribution Circuit | Animal | Bird found | 209 | 14003 | 35.2609 | -120.7018 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0111997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1870851 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | FUSE | 7485 | 20230901 | 1856 | 20230902 | 49 | 2208238 | 353 | Distribution Circuit | 3rd Party | Metallic Balloon | 1 | 353 | 35.6415 | -120.6565 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0112015 | OH | Sus | 31666996 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870866 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | FUSE | 10449 | 20230901 | 1903 | 20230901 | 2003 | 2208196 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 385 | 23092 | 35.2633 | -120.6988 | No | Partly Cloudy;32-90 F |  |  | 23-0112012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870860 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 2465 | 20230903 | 1537 | 20230903 | 1547 | 2209123 | 10 | Distribution Circuit | 3rd Party | Metallic Balloon | 403 | 4030 | 35.3114 | -120.8455 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0112254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871058 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | TRANSFORMER | T0335 | 20230904 | 2 | 20230904 | 1259 | 2209241 | 777 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 19662 | 35.5745 | -121.106 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0112282 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871085 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | RECLOSER | M38 | 20230904 | 1406 | 20230905 | 538 | 2209456 | 932 | Distribution Circuit | Vegetation | Tree - fell into line | 952 | 254947 | 34.8793 | -120.4367 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112350 | OH | Sus | 31667448 | SOUTH BAY AND CENTRAL COAST | SEP | Multi-Fault | 0 | No | Yes | No | 1871132 | 0 | Non-EPSS | N | 2023 | AC & GRD
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1101 | 182771101 | RECLOSER | 175422 | 20230904 | 1917 | 20230905 | 225 | 2209553 | 428 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 16111 | 35.6473 | -121.191 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0112382 | OH | Sus | 31667463 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871148 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 5521 | 20230905 | 618 | 20230905 | 842 | 2209661 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 4176 | 35.7047 | -120.6226 | No | Clear;32-90 F |  |  | 23-0112476 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871232 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | TRANSFORMER | 513542557915 | 20230905 | 627 | 20230905 | 1623 | 2209663 | 596 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 596 | 35.0714 | -120.1618 | No | Fog;32-90 F | Pole-Wood | Deteriorated | 23-0112430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871184 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511389271803 | 20230905 | 1034 | 20230905 | 1050 | 2209767 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 304 | 35.4391 | -120.8916 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0112570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871347 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | TRANSFORMER | 513551640629 | 20230905 | 1232 | 20230905 | 1347 | 2210105 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 600 | 34.5976 | -120.144 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0112618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871362 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512698442492 | 20230905 | 1248 | 20230905 | 1344 | 2210124 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 112 | 34.6427 | -120.4292 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0112673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871366 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | R12 | 20230905 | 1629 | 20230906 | 220 | 2210314 | 591 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 31732 | 35.6607 | -120.7652 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112778 | OH | Sus | 31667532 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1871388 | 0 | EPSS Ckt | Y | 2023 | B & GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30415 | 20230905 | 1950 | 20230905 | 2203 | 2210407 | 133 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1 | 133 | 35.4215 | -120.4655 | No | Clear;32-90 F | Secondary | Broken | 23-0112820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871399 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X08 | 20230906 | 502 | 20230906 | 1030 | 2210537 | 328 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 23616 | 35.7094 | -120.3018 | No | Partly Cloudy;32-90 F |  |  | 23-0112885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871432 | 0 | EPSS Ckt | Y | 2023 | AB
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | TRANSFORMER | 511680066085 | 20230906 | 832 | 20230906 | 917 | 2210661 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 45 | 35.2838 | -120.7875 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0112973 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871499 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | TRANSFORMER | 511683466044 | 20230906 | 929 | 20230906 | 1007 | 2210777 | 38 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 38 | 35.2833 | -120.788 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0113013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871567 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 307832 | 20230906 | 1049 | 20230906 | 1343 | 2210866 | 174 | Distribution Circuit | Animal | Squirrel | 1322 | 127518 | 35.5578 | -120.7747 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0113072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871602 | 0 | EPSS Ckt | Y | 2023 | A & GRD
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 7006 | 20230906 | 1618 | 20230906 | 2101 | 2211136 | 283 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 258 | 73014 | 35.8689 | -120.8458 | No | Clear;32-90 F |  |  | 23-0113330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871675 | 0 | EPSS Ckt | Y | 2023 | SGF RLY & DCD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512335076155 | 20230906 | 1739 | 20230906 | 1753 | 2211079 | 14 | Transformer only | Animal | Bird found | 1 | 14 | 35.5654 | -120.5785 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0113368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871688 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 7495 | 20230906 | 2113 | 20230907 | 1554 | 2211271 | 1121 | Distribution Circuit | Equipment Failure/Involved | Underground | 61 | 43293 | 35.0348 | -120.4966 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0113414 | UG | Sus | 35487029 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871717 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 721823 | 20230907 | 1000 | 20230907 | 1143 | 2211676 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1234 | 127102 | 35.1986 | -120.607 | No | Partly Cloudy;32-90 F |  |  | 23-0113560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871872 | 0 | EPSS Ckt | Y | 2023 | B PHASE
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 2981 | 20230907 | 1629 | 20230907 | 1759 | 2212039 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 540 | 35.5651 | -120.6878 | No | Clear;32-90 F |  |  | 23-0113846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871962 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | OTHER | GEN FEEDING T0363 | 20230907 | 2027 | 20230907 | 2040 | 2212159 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 14 | 182 | 35.0359 | -120.4966 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0113414 | UG | Sus | 35487029 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1871975 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20230908 | 1014 | 20230908 | 1208 | 2212673 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 730 | 83220 | 35.7811 | -120.9891 | No | Clear;32-90 F |  |  | 23-0114094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1872153 | 0 | EPSS Ckt | Y | 2023 | B/C
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | TRANSFORMER | 512020875289 | 20230908 | 1106 | 20230908 | 1515 | 2212716 | 249 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 249 | 35.5394 | -120.683 | No | Clear;32-90 F |  |  | 23-0114278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1872213 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | 511879073623 | 20230908 | 1156 | 20230908 | 1257 | 2212765 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 244 | 35.4923 | -120.7292 | No | Clear;32-90 F | Secondary | Broken | 23-0114165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872177 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46037 | 20230908 | 2146 | 20230909 | 922 | 2213253 | 696 | Distribution Circuit | 3rd Party | Vehicle | 155 | 41912 | 34.9548 | -120.4288 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0114349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | Yes | No | 1872251 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512696042533 | 20230909 | 1457 | 20230909 | 1736 | 2213814 | 159 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 318 | 34.6419 | -120.4283 | Yes | Partly Cloudy;32-90 F |  |  | 23-0114527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872456 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | RECLOSER | 858898 | 20230910 | 629 | 20230910 | 1157 | 2214512 | 328 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 160 | 40472 | 34.8684 | -120.2483 | No | Partly Cloudy;32-90 F |  |  | 23-0114620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1872557 | 0 | EPSS Ckt | Y | 2023 | AC
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | FUSE | 6417 | 20230911 | 1357 | 20230911 | 2218 | 2215660 | 501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 9018 | 34.9204 | -120.5224 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0115126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873035 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X06 | 20230911 | 1824 | 20230911 | 2136 | 2215942 | 192 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 172 | 33024 | 35.7373 | -120.2884 | No | Partly Cloudy;32-90 F |  |  | 23-0115213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873089 | 0 | EPSS Ckt | Y | 2023 | AB INST
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 30773 | 20230911 | 1940 | 20230911 | 2252 | 2215997 | 192 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1025 | 35.6772 | -120.6057 | No | Clear;32-90 F |  |  | 23-0115268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873123 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | FUSE | 30477 | 20230911 | 1951 | 20230912 | 749 | 2216000 | 718 | Distribution Circuit | Vegetation | Tree - branch fell on line | 189 | 50634 | 35.6309 | -120.6925 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0115242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | Yes | No | 1873102 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512286654323 | 20230912 | 45 | 20230912 | 258 | 2216063 | 133 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 2926 | 34.9655 | -120.5758 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0115281 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873134 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N42 | 20230912 | 959 | 20230912 | 1051 | 2216499 | 52 | Distribution Circuit | Company Initiated | Personnel- company | 3322 | 172744 | 35.8683 | -120.843 | No | Clear-Rain;32-90 F | Recloser | Malfunctioning | 23-0115413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1873319 | 0 | EPSS Ckt | Y | 2023 | DCD
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | FUSE | 32859 | 20230913 | 600 | 20230913 | 824 | 2217336 | 144 | Distribution Circuit | 3rd Party | Vehicle | 2 | 288 | 35.6522 | -120.6403 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Normal | 23-0115908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873603 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | V38 | 20230913 | 639 | 20230913 | 830 | 2217341 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1500 | 50494 | 35.1274 | -120.5689 | No | Overcast;32-90 F |  |  | 23-0115857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873521 | 0 | EPSS Ckt | Y | 2023 | A-C
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N40 | 20230913 | 946 | 20230913 | 1025 | 2217615 | 39 | Distribution Circuit | Company Initiated | Personnel- company | 900 | 35100 | 35.7571 | -120.8803 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0115965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1873695 | 0 | EPSS Ckt | Y | 2023 | DCD
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | JUMPER | OJ 1 S/OF 10639 | 20230913 | 1154 | 20230913 | 1244 | 2217750 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 250 | 35.3936 | -120.8508 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0116040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873719 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5371 | 20230913 | 1359 | 20230913 | 1527 | 2218014 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 7392 | 35.5555 | -120.6253 | No | Clear;32-90 F |  |  | 23-0116233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873762 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | TEMP LR 1101/2 | 20230913 | 1647 | 20230913 | 1845 | 2218189 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1022 | 120596 | 34.6967 | -120.1518 | No | Clear;32-90 F |  |  | 23-0116279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873776 | 0 | EPSS Ckt | Y | 2023 | A- B- INSTANT OC
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | OTHER | HOT WIRE DOWN 1 LS OF 7351 | 20230914 | 1238 | 20230914 | 1927 | 2218910 | 409 | Distribution Circuit | 3rd Party | Vehicle | 2132 | 16130 | 35.6503 | -120.6844 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0116655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1874062 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | R58 | 20230915 | 837 | 20230915 | 912 | 2219478 | 35 | Distribution Circuit | Company Initiated | Personnel- company | 1799 | 59659 | 35.7208 | -120.6846 | No | Overcast;32-90 F | Jumper | Normal | 23-0117027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1874246 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y36 | 20230915 | 1809 | 20230915 | 1913 | 2220085 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 272 | 17408 | 34.6026 | -120.1931 | No | Partly Cloudy;32-90 F |  |  | 23-0117356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1874417 | 0 | EPSS Ckt | Y | 2023 | A-C INST OC
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | FUSE | 10009 | 20230915 | 2106 | 20230915 | 2305 | 2220156 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 13573 | 35.2979 | -120.681 | No | Partly Cloudy;32-90 F |  |  | 23-0117380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874439 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512724654459 | 20230916 | 2227 | 20230916 | 2343 | 2220834 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 1368 | 34.9723 | -120.4297 | No | Clear;32-90 F | Fuse | Broken | 23-0117511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874591 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20230917 | 1540 | 20230917 | 1759 | 2221072 | 139 | Distribution Circuit | Animal | Bird found | 1724 | 161300 | 35.5213 | -120.7125 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0117560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1874641 | 0 | EPSS Ckt | Y | 2023 | A & C PHASE- INST
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | FUSE | 10009 | 20230917 | 1917 | 20230917 | 2204 | 2221111 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 19048 | 35.2979 | -120.681 | No | Clear;32-90 F |  |  | 23-0117580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874661 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | JUMPER | WIRE DOWN 3 S/S OF CGC#512851641940 | 20230918 | 840 | 20230918 | 1306 | 2221413 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 266 | 34.6277 | -120.3784 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0117685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1874811 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511563869818 | 20230918 | 1657 | 20230918 | 1900 | 2221886 | 123 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 369 | 35.3857 | -120.8314 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0117966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1874951 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N44 | 20230919 | 853 | 20230919 | 1117 | 2222267 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1189 | 64072 | 35.7755 | -120.8971 | No | Clear;32-90 F |  |  | 23-0118102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1875115 | 0 | EPSS Ckt | Y | 2023 | A & B
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 7061 | 20230919 | 941 | 20230919 | 1145 | 2222360 | 124 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 248 | 34.5879 | -120.0911 | No | Overcast;32-90 F | Customer Equipment | Failed/Faulted | 23-0118236 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1875233 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | OTHER | WIRE DWON @ CGC #512831566412 | 20230919 | 1042 | 20230919 | 2037 | 2222506 | 595 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 33762 | 35.3003 | -120.4027 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0118212 | OH | Sus | 31669309 | SOUTH BAY AND CENTRAL COAST | SEP | Open Circuit | 0 | No | Yes | Yes | 1875227 | 1 | EPSS Ckt | Y | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20230919 | 1721 | 20230920 | 255 | 2222733 | 574 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1189 | 142820 | 35.7984 | -120.9741 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0118415 | OH | Sus | 31669627 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1875284 | 0 | EPSS Ckt | Y | 2023 | AB
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 1459 | 20230919 | 2249 | 20230920 | 116 | 2222826 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 24255 | 34.8964 | -120.4185 | No | Overcast-Fog;32-90 F |  |  | 23-0118475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875318 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6307 | 20230920 | 749 | 20230920 | 910 | 2222956 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 378 | 34.9561 | -120.5583 | No | Overcast-Fog;32-90 F |  |  | 23-0118637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875495 | 1 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 423943 | 20230920 | 941 | 20230920 | 1108 | 2223242 | 87 | Distribution Circuit | Animal | Other | 1 | 87 | 35.6337 | -120.3922 | No | Overcast;32-90 F | Cutout- fuse holder | Normal | 23-0118720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875569 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | R82 | 20230920 | 1500 | 20230920 | 1725 | 2223536 | 145 | Distribution Circuit | Animal | Bird found | 899 | 39303 | 35.5299 | -120.523 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1875623 | 0 | EPSS Ckt | Y | 2023 | BC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512088265660 | 20230920 | 1636 | 20230920 | 2151 | 2223662 | 315 | Transformer only | 3rd Party | Metallic Balloon | 15 | 4725 | 35.2755 | -120.6521 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0118958 | OH | Sus | 31669317 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875652 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 3449 | 20230921 | 825 | 20230921 | 1608 | 2223874 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 18057 | 35.3061 | -120.8583 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0119119 | OH | Sus | 45985998 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875735 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6069 | 20230921 | 1258 | 20230921 | 1415 | 2224097 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1179 | 35.5341 | -120.5447 | No | Partly Cloudy;32-90 F |  |  | 23-0119330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875798 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | TEMP LR 1101/2 | 20230921 | 1315 | 20230921 | 1650 | 2224103 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1022 | 120485 | 34.6967 | -120.1518 | No | Partly Cloudy;32-90 F |  |  | 23-0119304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875789 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20230921 | 1322 | 20230921 | 1656 | 2224107 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 225 | 48150 | 35.1757 | -120.5255 | No | Partly Cloudy;32-90 F |  |  | 23-0119306 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1875790 | 0 | EPSS Ckt | Y | 2023 | B & C PH
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | FUSE | 7059 | 20230922 | 1014 | 20230922 | 1133 | 2224723 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1501 | 35.4653 | -120.6468 | No | Clear;32-90 F |  |  | 23-0119756 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876064 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 8473 | 20230922 | 1122 | 20230922 | 1158 | 2224839 | 36 | Distribution Circuit | Animal | Bird found | 33 | 1177 | 34.9238 | -120.4392 | No | Clear;32-90 F | Fuse | Normal | 23-0119770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876070 | 1 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | OCB | 2113/2 | 20230922 | 1843 | 20230922 | 2056 | 2225059 | 133 | Distribution Circuit | Animal | Bird found | 5584 | 386987 | 35.555 | -120.6803 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0119951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876122 | 0 | EPSS Ckt | Y | 2023 | OC & GRD
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511474870345 | 20230923 | 214 | 20230923 | 1240 | 2225164 | 626 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 8138 | 35.3994 | -120.8616 | No | Overcast-Fog;32-90 F | Transformer (OH) | Deteriorated | 23-0119991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876150 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6309 | 20230923 | 238 | 20230923 | 1127 | 2225169 | 520 | Distribution Circuit | 3rd Party | Vehicle | 88 | 8968 | 34.9591 | -120.5583 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0119986 | OH | Sus | 31669876 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | Yes | No | 1876145 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | V38 | 20230924 | 1316 | 20230924 | 1529 | 2225903 | 133 | Distribution Circuit | Animal | Bird found | 1500 | 99859 | 35.1274 | -120.5689 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0120149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876317 | 0 | EPSS Ckt | Y | 2023 | A- C- SGF
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20230925 | 1411 | 20230925 | 1741 | 2226749 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 225 | 45288 | 35.1757 | -120.5255 | No | Clear;32-90 F |  |  | 23-0120499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876647 | 0 | EPSS Ckt | Y | 2023 | B- C- INSTANT OC
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 5249 | 20230925 | 1518 | 20230925 | 2301 | 2226808 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 39724 | 35.1122 | -120.6159 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0120575 | OH | Sus | 45990026 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876669 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512486062060 | 20230925 | 1837 | 20230926 | 120 | 2226964 | 403 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 403 | 35.1795 | -120.5148 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0120617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876685 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512738862030 | 20230925 | 2144 | 20230926 | 237 | 2227022 | 293 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 293 | 35.177 | -120.4306 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0120655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876704 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512476860330 | 20230926 | 1003 | 20230926 | 1302 | 2227503 | 179 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 179 | 35.1309 | -120.517 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0120955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876967 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | RECLOSER | M98 | 20230926 | 1333 | 20230926 | 1455 | 2227717 | 82 | Distribution Circuit | Animal | Bird found | 35 | 2632 | 34.8946 | -120.3018 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0121022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876996 | 0 | EPSS Ckt | Y | 2023 | AC
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 7957 | 20230926 | 1607 | 20230927 | 337 | 2227862 | 690 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 16570 | 34.9389 | -120.455 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0121154 | UG | Sus | 31670500 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877028 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V14 | 20230926 | 1624 | 20230926 | 1632 | 2227875 | 8 | Distribution Circuit | 3rd Party | Vandalism | 1225 | 9800 | 35.1791 | -120.6181 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0121134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877018 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | RECLOSER | A28 | 20230926 | 1922 | 20230926 | 2033 | 2228001 | 71 | Distribution Circuit | Animal | Bird found | 1795 | 126857 | 35.4622 | -120.6453 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0121183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1877048 | 0 | EPSS Ckt | Y | 2023 | B-C
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | RECLOSER | M86 | 20230927 | 1437 | 20230927 | 1725 | 2228719 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 756 | 127008 | 35.0492 | -120.4827 | No | Clear;32-90 F |  |  | 23-0121647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1877347 | 0 | EPSS Ckt | Y | 2023 | AB INST
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | JUMPER | V82 | 20230927 | 1818 | 20230928 | 39 | 2228927 | 254 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1290 | 336108 | 35.2151 | -120.615 | No | Clear;32-90 F | Jumper | Burned Open | 23-0121763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Open Circuit | 0 | No | No | No | 1877374 | 1 | EPSS Ckt | Y | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | V82 | 20230928 | 47 | 20230928 | 54 | 2229036 | 7 | Distribution Circuit | Company Initiated | Operating error | 1290 | 9030 | 35.2151 | -120.615 | No | Clear;32-90 F | Recloser | Normal | 23-0121807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877403 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 6011 | 20230928 | 652 | 20230928 | 915 | 2229110 | 143 | Distribution Circuit | Animal | Bird found | 3 | 429 | 35.531 | -120.7079 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0121945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1877560 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | 277014 | 20230928 | 802 | 20230928 | 1453 | 2229172 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 364 | 47127 | 34.5994 | -120.0979 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0121881 | OH | Sus | 45992796 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1877454 | 0 | EPSS Ckt | Y | 2023 | A-B
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | TRANSFORMER | 512084165229 | 20230928 | 1443 | 20230929 | 56 | 2229658 | 613 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 9195 | 35.2636 | -120.653 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0122228 | OH | Sus | 45993764 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877678 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | FUSE | 45189 | 20230928 | 1444 | 20230928 | 1534 | 2229659 | 50 | Distribution Circuit | Animal | Bird found | 3 | 133 | 34.8649 | -120.3697 | No | Clear;32-90 F | Fuse | Burned Open | 23-0122242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877687 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 20613 | 20230928 | 2046 | 20230929 | 331 | 2229870 | 405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 5265 | 34.6068 | -120.1256 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0122309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877716 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | SWITCH | 903036 | 20230928 | 2148 | 20230929 | 110 | 2229918 | 202 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 8080 | 35.264 | -120.6537 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0122299 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877724 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | TRANSFORMER | 512751553220 | 20230929 | 713 | 20230929 | 912 | 2230054 | 119 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 357 | 34.9384 | -120.42 | No | Overcast-Fog;32-90 F | Fuse | Broken | 23-0122441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877871 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | N58 | 20230929 | 1146 | 20230929 | 1154 | 2230407 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 1939 | 15512 | 35.6286 | -120.6955 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0122576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1877931 | 0 | EPSS Ckt | Y | 2023 | NONE
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512659354292 | 20230929 | 1226 | 20230929 | 1636 | 2230469 | 250 | Transformer only | 3rd Party | Customer Equipment | 24 | 6000 | 34.9674 | -120.4514 | No | Clear;32-90 F | Secondary | Broken | 23-0122705 | OH | Sus | 31670903 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877976 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511492769873 | 20230929 | 2048 | 20230929 | 2055 | 2230766 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 154 | 35.3867 | -120.8553 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0122769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877998 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1105 | 182581105 | FUSE | 3549 | 20230929 | 2308 | 20230930 | 1024 | 2231088 | 676 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 16900 | 35.2956 | -120.6635 | No | Overcast;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0122802 | OH | Sus | 45994734 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1878033 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 618168 | 20230930 | 704 | 20230930 | 833 | 2231346 | 89 | Distribution Circuit | Animal | Other | 151 | 13439 | 35.5454 | -121.076 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0122845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1878088 | 0 | EPSS Ckt | Y | 2023 | A-B
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A70 | 20231001 | 110 | 20231001 | 407 | 2231986 | 177 | Distribution Circuit | Animal | Bird found | 1712 | 264549 | 35.5023 | -120.649 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0123062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1878289 | 0 | EPSS Ckt | Y | 2023 | A & B
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 407733 | 20231001 | 1322 | 20231001 | 1816 | 2232200 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2058 | 34.6046 | -120.2964 | No | Partly Cloudy;32-90 F |  |  | 23-0123131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1878369 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | SWITCH | 6229 | 20231001 | 1342 | 20231001 | 1854 | 2232201 | 312 | Distribution Circuit | 3rd Party | Vehicle | 851 | 265512 | 34.7239 | -120.2155 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0123106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1878346 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | FUSE | 573839 | 20231001 | 1513 | 20231001 | 1608 | 2232224 | 55 | Distribution Circuit | Animal | Bird found | 10 | 550 | 34.7127 | -120.1407 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0123118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878358 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 982992 | 20231001 | 1639 | 20231002 | 1006 | 2232246 | 1047 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 49209 | 35.1923 | -120.4565 | No | Partly Cloudy;32-90 F |  |  | 23-0123124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1878364 | 0 | EPSS Ckt | Y | 2023 | B-C
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y48 | 20231002 | 847 | 20231002 | 855 | 2232587 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 827 | 6616 | 34.6653 | -120.1182 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 23-0123239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1878494 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20231002 | 1027 | 20231002 | 1053 | 2232779 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 218 | 5668 | 35.1757 | -120.5255 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0123124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1878567 | 0 | EPSS Ckt | Y | 2023 | N/A
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20231002 | 1104 | 20231002 | 1132 | 2232814 | 28 | Distribution Circuit | Company Initiated | Personnel- company | 218 | 6104 | 35.1757 | -120.5255 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0123124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1878574 | 0 | EPSS Ckt | Y | 2023 | TIME OC
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 7497 | 20231002 | 2001 | 20231003 | 409 | 2233260 | 488 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1323 | 35.6236 | -120.6144 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0123595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878716 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6307 | 20231003 | 342 | 20231003 | 516 | 2233345 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 439 | 34.9561 | -120.5583 | No | Fog;32-90 F |  |  | 23-0123607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878736 | 1 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N44 | 20231003 | 1335 | 20231003 | 1517 | 2233825 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1189 | 92820 | 35.7755 | -120.8971 | No | Clear;32-90 F |  |  | 23-0123877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878969 | 0 | EPSS Ckt | Y | 2023 | B & GRD TGTS
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 256147 | 20231003 | 1345 | 20231003 | 1956 | 2233839 | 371 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1484 | 35.2251 | -120.6266 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0123891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1878972 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20231003 | 1414 | 20231003 | 1636 | 2233870 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 30956 | 35.1757 | -120.5255 | No | Clear;32-90 F |  |  | 23-0123912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1878977 | 0 | EPSS Ckt | Y | 2023 | B & C PH
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V02 | 20231003 | 1636 | 20231003 | 1828 | 2233974 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2013 | 215396 | 35.2377 | -120.6796 | No | Clear;32-90 F |  |  | 23-0124024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878999 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | JUMPER | 9657 BURNT OPEN JMPR | 20231003 | 2051 | 20231003 | 2134 | 2234113 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2404 | 19271 | 35.2617 | -120.6482 | No | Clear;32-90 F | Jumper | Burned Open | 23-0124082 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1879034 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 45289 | 20231004 | 840 | 20231004 | 914 | 2234327 | 34 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 1292 | 34.9613 | -120.5704 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0124251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879238 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 3683 | 20231004 | 1130 | 20231004 | 1327 | 2234581 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1404 | 35.6588 | -120.3637 | No | Clear;32-90 F |  |  | 23-0124422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1879342 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512692753513 | 20231004 | 1130 | 20231004 | 1146 | 2234351 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 41 | 656 | 34.9461 | -120.4397 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0124349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879305 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V02 | 20231004 | 1142 | 20231004 | 1210 | 2234629 | 28 | Distribution Circuit | Company Initiated | Personnel- company | 1993 | 55804 | 35.2377 | -120.6796 | No | Clear;32-90 F | Fuse | Normal | 23-0124357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879310 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | RECLOSER | TEMP LR 1102/2 | 20231004 | 1548 | 20231004 | 1825 | 2234850 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2033 | 319181 | 34.6251 | -120.1865 | No | Clear;32-90 F |  |  | 23-0124565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Multi-Fault | 0 | No | No | No | 1879368 | 0 | EPSS Ckt | Y | 2023 | A- B- C & GRD
LOS PADRES | SAN LUIS OBISPO | CAMBRIA-1102 | 182771102 | FUSE | 888151 | 20231004 | 1945 | 20231005 | 255 | 2235048 | 430 | Distribution Circuit | Equipment Failure/Involved | Overhead | 190 | 27079 | 35.5715 | -121.1066 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0124650 | OH | Sus | 31671474 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879398 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20231005 | 848 | 20231005 | 904 | 2235444 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 218 | 3488 | 35.1757 | -120.5255 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0124769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1879523 | 0 | EPSS Ckt | Y | 2023 | TIME OC
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 587564 | 20231005 | 1016 | 20231005 | 1140 | 2235578 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 1764 | 35.495 | -120.644 | No | Clear;32-90 F |  |  | 23-0124816 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879608 | 0 | EPSS Ckt | Y | 2023 | B GRD INST
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | N30 | 20231005 | 1420 | 20231005 | 1438 | 2235816 | 18 | Distribution Circuit | Company Initiated | Personnel- company | 451 | 8118 | 35.626 | -120.8965 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0124988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879686 | 0 | EPSS Ckt | Y | 2023 | SGF / DCD
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | OTHER | T2897 TWD T2898 | 20231005 | 2058 | 20231006 | 207 | 2236079 | 309 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 6180 | 34.8746 | -120.4567 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0125090 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879727 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 2355 | 20231006 | 51 | 20231006 | 1127 | 2236197 | 636 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 12735 | 35.5914 | -120.5828 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0125152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1879780 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 45137 | 20231006 | 949 | 20231006 | 1045 | 2236496 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 144 | 8064 | 34.8755 | -120.4316 | No | Clear;32-90 F |  |  | 23-0125316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879949 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | RECLOSER | 536076 | 20231006 | 1130 | 20231006 | 1222 | 2236613 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 884 | 35.7473 | -120.716 | No | Clear;32-90 F |  |  | 23-0125403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1879972 | 0 | EPSS Ckt | Y | 2023 | A&B INSTANT
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5049 | 20231006 | 1236 | 20231007 | 1430 | 2236697 | 1554 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 19143 | 35.5335 | -121.0503 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0125495 | OH | Sus | 31671511 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | Yes | No | 1880043 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 200598 | 20231006 | 1314 | 20231006 | 1615 | 2236755 | 181 | Distribution Circuit | Vegetation | Tree - fell into line | 2258 | 211507 | 35.5515 | -121.0724 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 23-0125495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | Yes | Yes | 1880003 | 0 | EPSS Ckt | N | 2023 | NONE
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20231007 | 841 | 20231007 | 911 | 2237435 | 30 | Distribution Circuit | Animal | Squirrel | 1734 | 33056 | 35.5213 | -120.7125 | No | Clear;32-90 F | Fuse | Normal | 23-0125694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880167 | 0 | EPSS Ckt | Y | 2023 | GRD
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 8473 | 20231007 | 1605 | 20231007 | 1822 | 2237829 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 4478 | 34.9238 | -120.4392 | No | Clear;32-90 F |  |  | 23-0125781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880248 | 1 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 467165 | 20231007 | 1845 | 20231008 | 710 | 2237845 | 745 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 29647 | 35.5422 | -121.089 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Deteriorated | 23-0125788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880256 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | RECLOSER | W58 | 20231008 | 1858 | 20231009 | 1216 | 2238379 | 1038 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 330 | 76368 | 35.4511 | -120.9069 | No | Clear;32-90 F |  |  | 23-0125876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880353 | 0 | EPSS Ckt | Y | 2023 | A- C
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | FUSE | 45759 | 20231009 | 1002 | 20231009 | 1050 | 2238852 | 48 | Distribution Circuit | 3rd Party | Metallic Balloon | 458 | 21984 | 34.9388 | -120.4501 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0126036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880607 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | RECLOSER | M98 | 20231009 | 1021 | 20231009 | 1921 | 2238872 | 540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 18900 | 34.8946 | -120.3018 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0126123 | OH | Sus | 46004146 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1880654 | 0 | EPSS Ckt | Y | 2023 | UNK
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 359656 | 20231009 | 1027 | 20231009 | 1121 | 2238884 | 54 | Distribution Circuit | Company Initiated | Personnel- company | 20 | 1080 | 35.247 | -120.6822 | No | Overcast;32-90 F | Cutout- fuse holder | Normal | 23-0126032 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880606 | 0 | EPSS Ckt | Y | 2023 | B & INST TGTS
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | TEMP LR 1103/2 | 20231009 | 1232 | 20231009 | 1526 | 2239024 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1696 | 174319 | 34.6432 | -120.4375 | No | Partly Cloudy;32-90 F |  |  | 23-0126102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880644 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20231009 | 1323 | 20231009 | 1603 | 2239080 | 160 | Distribution Circuit | Animal | Bird found | 186 | 22189 | 34.7206 | -120.4308 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0126131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880655 | 0 | EPSS Ckt | Y | 2023 | C PHASE & GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512657675286 | 20231009 | 1503 | 20231010 | 36 | 2238946 | 573 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 573 | 35.5438 | -120.4699 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0126186 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880677 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 6205 | 20231009 | 1907 | 20231010 | 140 | 2239214 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1572 | 35.5493 | -120.2355 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0126196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880679 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20231009 | 1915 | 20231010 | 816 | 2239382 | 781 | Distribution Circuit | Equipment Failure/Involved | Overhead | 186 | 23164 | 34.7206 | -120.4308 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0126264 | OH | Sus | 31672112 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880707 | 0 | EPSS Ckt | Y | 2023 | B GRD
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | FUSE | 1217 | 20231009 | 2006 | 20231009 | 2355 | 2239387 | 229 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 916 | 34.6154 | -120.1655 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0126267 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880709 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20231010 | 419 | 20231010 | 815 | 2239473 | 236 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 43660 | 34.7206 | -120.4308 | No | Clear;32-90 F |  |  | 23-0126322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880753 | 0 | EPSS Ckt | Y | 2023 | A- B
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512692753513 | 20231010 | 725 | 20231010 | 1210 | 2239571 | 285 | Transformer only | Equipment Failure/Involved | Overhead | 41 | 11685 | 34.9461 | -120.4397 | No | Overcast;32-90 F | Secondary | Broken | 23-0126539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880980 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | 351084 | 20231010 | 851 | 20231010 | 956 | 2239708 | 65 | Distribution Circuit | Animal | Squirrel | 355 | 20419 | 35.6223 | -120.7024 | No | Overcast;32-90 F | Pothead(Riser Termination) | Normal | 23-0126410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880876 | 0 | EPSS Ckt | Y | 2023 | B GRD
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | TRANSFORMER | 512822153018 | 20231010 | 1104 | 20231010 | 1250 | 2239885 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 106 | 34.9333 | -120.3962 | No | Overcast;32-90 F | Fuse | Broken | 23-0126558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880988 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | TEMP LR 1103/2 | 20231010 | 1138 | 20231010 | 2226 | 2239931 | 648 | Distribution Circuit | Equipment Failure/Involved | Overhead | 275 | 66576 | 34.6432 | -120.4375 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0126506 | OH | Sus | 46008791 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1880968 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20231010 | 1211 | 20231010 | 1218 | 2239954 | 6 | Distribution Circuit | Company Initiated | Personnel- company | 1681 | 10086 | 35.5213 | -120.7125 | No | Partly Cloudy;32-90 F | Switch (OH) | Normal | 23-0126525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880975 | 0 | EPSS Ckt | Y | 2023 | GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | FUSE | 14771 | 20231010 | 1253 | 20231010 | 1451 | 2239992 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 150 | 17700 | 35.1147 | -120.5961 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0126557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880987 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | FUSE | 11473 | 20231010 | 1345 | 20231010 | 2051 | 2240056 | 426 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 113 | 39857 | 34.9292 | -120.433 | No | Partly Cloudy;32-90 F |  |  | 23-0126762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881036 | 1 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512751253982 | 20231011 | 1625 | 20231011 | 2059 | 2241218 | 274 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 3836 | 34.9593 | -120.4205 | No | Clear-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0127233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881397 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512746653977 | 20231011 | 1625 | 20231011 | 2221 | 2241217 | 356 | Transformer only | Vegetation | Tree - grew into line | 15 | 5340 | 34.9592 | -120.422 | No | Clear-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0127235 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881399 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | RECLOSER | 38682 | 20231011 | 2351 | 20231012 | 537 | 2241367 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 225 | 77850 | 35.6136 | -120.6591 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0127224 | OH | Sus | 35495963 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881428 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | FUSE | 45905 | 20231012 | 344 | 20231012 | 550 | 2241382 | 126 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 11592 | 34.9018 | -120.428 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0127295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1881430 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 32389 | 20231012 | 906 | 20231012 | 1344 | 2241582 | 278 | Distribution Circuit | 3rd Party | Vehicle | 1 | 278 | 35.6436 | -120.2217 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0127586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881675 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | OCB | 1104/2 | 20231012 | 1431 | 20231012 | 1828 | 2241967 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2281 | 469414 | 35.2617 | -120.6345 | No | Clear;32-90 F | Jumper | Burned Open | 23-0127616 | OH | Sus | 46012113 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881683 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 10001 | 20231012 | 1538 | 20231012 | 1850 | s1881712 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 192 | 35.2482 | -120.6171 | No | Clear;32-90 F | Other | Broken | 23-0127616 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881712 | 0 | EPSS Ckt | Y | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | JUMPER | JPRS TWD CGC 511254072800 | 20231012 | 1612 | 20231012 | 1655 | 2242032 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 86 | 35.4657 | -120.9365 | No | Clear;32-90 F | Insulator | Broken | 23-0127676 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881694 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | V82 | 20231013 | 2047 | 20231014 | 1215 | 2243013 | 928 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1293 | 27424 | 35.2151 | -120.615 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0128211 | OH | Sus | 46013188 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882020 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | TRANSFORMER | 512025273025 | 20231014 | 757 | 20231014 | 900 | 2243176 | 63 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 126 | 35.4775 | -120.6802 | No | Fog;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0128262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882137 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512401943637 | 20231014 | 1049 | 20231014 | 1258 | 2243325 | 129 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 516 | 34.6726 | -120.5282 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0128292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882167 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512585641169 | 20231014 | 1107 | 20231014 | 1317 | 2243335 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 130 | 34.6062 | -120.4647 | No | Clear;32-90 F | Fuse | Broken | 23-0128315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882181 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512662754041 | 20231014 | 1301 | 20231015 | 1357 | 2243318 | 1496 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 13464 | 34.9605 | -120.4501 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0128307 | OH | Sus | 46013194 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882174 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X06 | 20231014 | 1539 | 20231014 | 2111 | 2243491 | 332 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 172 | 53624 | 35.7373 | -120.2884 | No | Clear;32-90 F |  |  | 23-0128337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882196 | 0 | EPSS Ckt | Y | 2023 | A- B & INST
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 20095 | 20231014 | 1719 | 20231014 | 1851 | 2243510 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 368 | 34.6444 | -120.4309 | No | Clear;32-90 F |  |  | 23-0128349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882203 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512513853851 | 20231015 | 1500 | 20231015 | 1725 | 2243828 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 145 | 34.9542 | -120.4997 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0128448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882287 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5783 | 20231015 | 1525 | 20231015 | 1704 | 2243839 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 198 | 35.5714 | -120.5586 | No | Clear;32-90 F | Fuse | Broken | 23-0128439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882285 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510804075782 | 20231015 | 2037 | 20231015 | 2140 | 2243824 | 63 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 63 | 35.5434 | -121.0927 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0128427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882276 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | 686138 | 20231016 | 250 | 20231016 | 703 | 2244052 | 253 | Distribution Circuit | Animal | Squirrel | 141 | 30097 | 35.5352 | -120.7228 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0128498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882330 | 0 | EPSS Ckt | Y | 2023 | A-C
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512990251943 | 20231016 | 1454 | 20231016 | 1735 | 2244669 | 161 | Transformer only | Animal | Bird found | 2 | 322 | 34.9049 | -120.3393 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0128889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882586 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X06 | 20231017 | 935 | 20231017 | 1310 | 2245213 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 172 | 31964 | 35.7373 | -120.2884 | No | Clear;32-90 F |  |  | 23-0129056 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882811 | 0 | EPSS Ckt | Y | 2023 | B&C
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510811375765 | 20231017 | 2105 | 20231018 | 59 | 2245675 | 234 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1638 | 35.543 | -121.0902 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0129353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882939 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512372054190 | 20231018 | 1441 | 20231018 | 1913 | 2246286 | 272 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 272 | 34.9626 | -120.5472 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0129879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883243 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y02 | 20231018 | 1446 | 20231018 | 1503 | 2246292 | 17 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 547 | 8207 | 34.6503 | -120.0946 | No | Clear;Above 90 | Metering Equipment | Burned/flashed | 23-0129745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883206 | 0 | EPSS Ckt | Y | 2023 | B&GRD
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y02 | 20231018 | 2058 | 20231018 | 2219 | 2246557 | 81 | Distribution Circuit | 3rd Party | Other | 547 | 28473 | 34.6503 | -120.0946 | No | Clear;32-90 F | Other | Normal | 23-0129896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883248 | 0 | EPSS Ckt | Y | 2023 | B & GRD
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511264072507 | 20231019 | 230 | 20231019 | 935 | 2246592 | 425 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 850 | 35.4574 | -120.9341 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0129945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883285 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | TRANSFORMER | 513757142494 | 20231019 | 1333 | 20231019 | 2205 | 2246979 | 512 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 512 | 34.65 | -120.0769 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0130247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883396 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | R56 | 20231020 | 912 | 20231020 | 1343 | 2247472 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 232 | 53093 | 35.6443 | -120.7067 | No | Clear;32-90 F |  |  | 23-0130523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1883614 | 0 | EPSS Ckt | Y | 2023 | BC
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512162275882 | 20231020 | 1309 | 20231020 | 1342 | 2247765 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 33 | 35.5565 | -120.6373 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0130731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883702 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | TRANSFORMER | 513840841752 | 20231020 | 1509 | 20231020 | 2120 | 2247820 | 371 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 371 | 34.6298 | -120.0482 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0130797 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883715 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | JUMPER | OJ JEO CGC 512058764340 | 20231020 | 1515 | 20231020 | 2023 | 2247789 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1232 | 35.2396 | -120.6607 | No | Clear;32-90 F | Jumper | Burned Open | 23-0130798 | OH | Sus | 46027196 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1883716 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | OCB | 1104/2 | 20231020 | 1843 | 20231021 | 853 | 2247878 | 850 | Distribution Circuit | 3rd Party | Vehicle | 1286 | 364376 | 35.7522 | -120.6838 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0130802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1883720 | 0 | EPSS Ckt | N | 2023 | A PH AND GRD
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRIP-SAVER | 6111 | 20231020 | 1943 | 20231020 | 2105 | 2247902 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 260 | 21320 | 35.0643 | -120.4971 | No | Partly Cloudy;32-90 F |  |  | 23-0130817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1883727 | 0 | EPSS Ckt | N | 2023 | A&B
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | FUSE | 45771 | 20231020 | 2313 | 20231021 | 100 | 2247941 | 107 | Distribution Circuit | 3rd Party | Metallic Balloon | 128 | 13696 | 34.9432 | -120.4383 | No | Fog;32-90 F | Conductor- Overhead | Normal | 23-0130843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1883751 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | W28 | 20231021 | 656 | 20231021 | 1030 | 2248004 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1633 | 103990 | 35.5681 | -121.1019 | No | Partly Cloudy;32-90 F |  |  | 23-0130851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1883763 | 0 | EPSS Ckt | Y | 2023 | A/B
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | OCB | 1104/2 | 20231021 | 1818 | 20231022 | 1501 | 2248451 | 1243 | Distribution Circuit | 3rd Party | Vehicle | 523 | 289939 | 34.8788 | -120.3307 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0130947 | OH | Sus | 35506114 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1883910 | 0 | EPSS Ckt | N | 2023 | PH OC & GRD OC
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 32771 | 20231022 | 1843 | 20231022 | 2038 | 2249136 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 230 | 35.7829 | -120.8836 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0131094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884055 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | TRANSFORMER | 511443784326 | 20231022 | 1843 | 20231023 | 403 | 2249321 | 560 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1120 | 35.7832 | -120.886 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0131100 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884061 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | RECLOSER | 317156 | 20231022 | 1855 | 20231022 | 2139 | 2249143 | 164 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 5735 | 35.4156 | -120.8725 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0131076 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884045 | 0 | EPSS Ckt | Y | 2023 | B&C PHASE INST OC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 8803 | 20231022 | 2121 | 20231023 | 4 | 2249320 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 10854 | 35.2961 | -120.658 | No | Overcast;32-90 F |  |  | 23-0131124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884082 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | RECLOSER | M108 | 20231023 | 856 | 20231023 | 1024 | 2249634 | 88 | Distribution Circuit | 3rd Party | Metallic Balloon | 1060 | 93280 | 34.9511 | -120.4405 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0131210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884209 | 0 | Non-EPSS | N | 2023 | A-B-
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 317796 | 20231023 | 2241 | 20231024 | 41 | 2250252 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1388 | 158655 | 35.5433 | -120.7453 | No | Clear;32-90 F |  |  | 23-0131606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Multi-Fault | 0 | No | No | No | 1884414 | 0 | EPSS Ckt | Y | 2023 | A- B- C- GRD- & INST OC
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | RECLOSER | 238418 | 20231024 | 804 | 20231024 | 956 | 2250406 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1344 | 35.5905 | -120.7299 | No | Clear;32-90 F |  |  | 23-0131665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884469 | 0 | EPSS Ckt | Y | 2023 | A-B
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | FUSE | 45763 | 20231024 | 1640 | 20231025 | 59 | 2250805 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 16467 | 34.9483 | -120.4435 | No | Clear;32-90 F | Insulator | Broken | 23-0132031 | OH | Sus | 31674004 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1884689 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 31623 | 20231024 | 1829 | 20231024 | 1904 | 2250995 | 35 | Distribution Circuit | Animal | Bird found | 269 | 9415 | 35.5124 | -120.6703 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0132057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884702 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | 514592 | 20231025 | 740 | 20231025 | 859 | 2251176 | 79 | Distribution Circuit | Animal | Bird found | 2053 | 158557 | 35.5368 | -120.7146 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0132162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884756 | 0 | EPSS Ckt | Y | 2023 | INST- GRD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | V88 | 20231025 | 1059 | 20231025 | 1318 | 2251541 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2360 | 248228 | 35.5597 | -121.0765 | No | Partly Cloudy;32-90 F |  |  | 23-0132325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884948 | 0 | EPSS Ckt | Y | 2023 | A-C
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | TRANSFORMER | 513306941707 | 20231025 | 1752 | 20231026 | 15 | 2251856 | 383 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 1149 | 34.6256 | -120.2258 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0132585 | OH | Sus | 46031445 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1885035 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | JUMPER | JMPRS 4 SPANS E/O CGC 512378675764 | 20231026 | 1132 | 20231026 | 1323 | 2252467 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 333 | 35.5558 | -120.5609 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0132834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1885318 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511472370195 | 20231026 | 1319 | 20231026 | 1827 | 2252558 | 296 | Transformer only | Equipment Failure/Involved | Fire- pole | 12 | 3552 | 35.3954 | -120.8624 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0132928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885362 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M52 | 20231026 | 2111 | 20231027 | 1023 | 2252862 | 792 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 55440 | 34.9254 | -120.3465 | No | Clear;32-90 F |  |  | 23-0133022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885409 | 0 | EPSS Ckt | Y | 2023 | C & INST
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | TRANSFORMER | T0799 | 20231027 | 1344 | 20231027 | 2246 | 2253440 | 542 | Distribution Circuit | Equipment Failure/Involved | Underground | 215 | 13216 | 35.2653 | -120.7053 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0133325 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885679 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | OCB | 1104/2 | 20231027 | 1641 | 20231027 | 1831 | 2253592 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2951 | 177183 | 35.6156 | -120.6793 | No | Clear;32-90 F |  |  | 23-0133401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885699 | 0 | EPSS Ckt | Y | 2023 | PH GRD INST
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | JUMPER | 2 SPANS WIRE DOWN 2 N/OF 8199 | 20231027 | 1655 | 20231027 | 2201 | 2253605 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 305 | 84755 | 34.9252 | -120.4372 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0133417 | OH | Sus | 31674362 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | Yes | 1885704 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512212359023 | 20231027 | 1707 | 20231027 | 1933 | 2253611 | 146 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 438 | 35.0941 | -120.6046 | No | Clear;32-90 F | Fuse | Broken | 23-0133431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885713 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | OCB | 1103/2 | 20231028 | 716 | 20231028 | 725 | 2253925 | 9 | Distribution Circuit | Company Initiated | Operating error | 1270 | 11430 | 35.2617 | -120.6346 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0124393 | OH | Sus | 35328985 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885754 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 7337 | 20231028 | 808 | 20231028 | 950 | 2254001 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 238 | 35.5819 | -120.5424 | No | Clear;32-90 F |  |  | 23-0133499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885816 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511554467288 | 20231028 | 1010 | 20231028 | 1303 | 2254169 | 173 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 3114 | 35.3163 | -120.8323 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0133556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885864 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512635669683 | 20231028 | 1115 | 20231028 | 1452 | 2254198 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 868 | 35.3899 | -120.472 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0133538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885850 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | OCB | 2102/2 | 20231029 | 520 | 20231029 | 1323 | 2254620 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 593 | 162205 | 35.6864 | -120.336 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0133653 | OH | Sus | 31674440 | SOUTH BAY AND CENTRAL COAST | OCT | Multi-Fault | 0 | No | Yes | No | 1885940 | 0 | EPSS Ckt | N | 2023 | BC GRD
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | OTHER | J1103 TWD T3734 | 20231029 | 1718 | 20231029 | 1912 | 2255032 | 114 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 798 | 35.0227 | -120.4904 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0133726 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1886026 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 20095 | 20231029 | 1725 | 20231029 | 1821 | 2255038 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 224 | 34.6444 | -120.4309 | No | Clear;32-90 F |  |  | 23-0133735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1886028 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | TRANSFORMER | 414788518610 | 20231030 | 808 | 20231030 | 1545 | 2255267 | 457 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2285 | 35.8316 | -120.7591 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0133930 | OH | Sus | 31674668 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886235 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M54 | 20231030 | 1511 | 20231030 | 1635 | 2255987 | 84 | Distribution Circuit | Animal | Bird found | 127 | 10668 | 34.8627 | -120.2773 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0134096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886311 | 0 | EPSS Ckt | Y | 2023 | A-GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | RECLOSER | 28088 | 20231030 | 1608 | 20231030 | 1622 | 2256035 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 225 | 3150 | 35.4646 | -120.6762 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0134108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886318 | 0 | EPSS Ckt | Y | 2023 | A
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | 483444 | 20231030 | 1912 | 20231031 | 1533 | 2256111 | 1210 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3135 | 201569 | 35.2892 | -120.6524 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0134153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1886336 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 31853 | 20231031 | 923 | 20231031 | 1015 | 2256489 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 398 | 35.4979 | -120.6834 | No | Partly Cloudy;32-90 F |  |  | 23-0134272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886549 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | 351084 | 20231101 | 959 | 20231101 | 1102 | 2257429 | 63 | Distribution Circuit | Animal | Squirrel | 355 | 13069 | 35.6223 | -120.7024 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0134609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1886882 | 0 | EPSS Ckt | Y | 2023 | B GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | TRANSFORMER | 511998373918 | 20231101 | 2029 | 20231102 | 322 | 2257853 | 413 | Transformer only | Vegetation | Tree - fell into line | 4 | 1652 | 35.5018 | -120.69 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0134934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1886983 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | INTERRUPTER | 45672 | 20231102 | 649 | 20231102 | 716 | 2257973 | 27 | Distribution Circuit | Company Initiated | Coordination failure | 21 | 567 | 35.2433 | -120.6405 | No | Clear;32-90 F | Interrupter | Malfunctioning | 23-0120240 | UG | Sus | 35331177 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1887031 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 7451 | 20231102 | 917 | 20231102 | 1001 | 2258162 | 44 | Distribution Circuit | Animal | Squirrel | 28 | 1232 | 35.4807 | -120.665 | No | Clear-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0135118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887201 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | RECLOSER | 1101/2 | 20231102 | 1105 | 20231102 | 1304 | 2258343 | 119 | Distribution Circuit | Animal | Bird found | 291 | 34629 | 35.361 | -120.8117 | No | Clear;32-90 F | Lightning Arrestor | Normal | 23-0135172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887225 | 0 | EPSS Ckt | Y | 2023 | B- GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | FUSE | 77625 | 20231102 | 1255 | 20231102 | 1321 | 2258435 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 52 | 34.9529 | -120.3957 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0135247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887253 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | INTERRUPTER | 21262 | 20231102 | 1433 | 20231102 | 1944 | 2258536 | 311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 5424 | 34.6158 | -120.1993 | No | Clear;32-90 F | Jumper | Burned Open | 23-0135330 | OH | Sus | 46046608 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887281 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1101 | 182571101 | TRANSFORMER | 512861050005 | 20231102 | 2234 | 20231103 | 632 | 2258714 | 478 | Transformer only | Equipment Failure/Involved | Underground | 4 | 1912 | 34.8513 | -120.3791 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0135416 | UG | Sus | 46046789 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887324 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y06 | 20231103 | 905 | 20231103 | 1421 | 2258941 | 316 | Distribution Circuit | Equipment Failure/Involved | Overhead | 345 | 21512 | 34.6201 | -120.2103 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0135514 | OH | Sus | 31675146 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1887457 | 0 | EPSS Ckt | Y | 2023 | INSTA- GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 31101 | 20231103 | 1017 | 20231103 | 1220 | 2259057 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 9845 | 35.4667 | -120.6707 | No | Clear;32-90 F |  |  | 23-0135641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887574 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 511967567115 | 20231103 | 1027 | 20231103 | 1520 | 2259163 | 293 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 293 | 35.3148 | -120.6937 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0135643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887578 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | RECLOSER | 320270 | 20231103 | 1236 | 20231103 | 1242 | 2259216 | 6 | Distribution Circuit | Company Initiated | Personnel- company | 209 | 1254 | 34.5995 | -120.1277 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0135650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887582 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 7131 | 20231103 | 1336 | 20231103 | 1639 | 2259298 | 183 | Distribution Circuit | Animal | Bird found | 1 | 183 | 34.963 | -120.4228 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0135754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887621 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | TEMP LR 1101/2 | 20231103 | 1542 | 20231103 | 1825 | 2259383 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1022 | 149306 | 34.6967 | -120.1518 | No | Clear;32-90 F |  |  | 23-0135734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887617 | 0 | EPSS Ckt | Y | 2023 | A- B- INSTANT
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46055 | 20231103 | 1806 | 20231103 | 1853 | 2259491 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 110 | 5173 | 34.9604 | -120.4232 | No | Clear;32-90 F |  |  | 23-0135790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887636 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | M92 | 20231104 | 455 | 20231104 | 1036 | 2259674 | 341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1209 | 162349 | 35.0168 | -120.4802 | No | Partly Cloudy-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0135838 | OH | Sus | 46047730 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | Yes | No | 1887673 | 0 | EPSS Ckt | N | 2023 | A/C GRD
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | SWITCH | 439515 | 20231104 | 2220 | 20231105 | 808 | 2260268 | 588 | Distribution Circuit | 3rd Party | Vehicle | 104 | 61152 | 35.6555 | -120.3887 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0135943 | OH | Sus | 35509640 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887838 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | 597930 | 20231104 | 2323 | 20231105 | 1925 | 2260278 | 1202 | Distribution Circuit | 3rd Party | Vehicle | 1239 | 143611 | 34.6603 | -120.4533 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 23-0135969 | OH | Sus | 35509721 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887844 | 0 | EPSS Ckt | Y | 2023 | A/C I
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | JUMPER | OJ @ CGC#512693854034 | 20231105 | 556 | 20231105 | 1842 | s1887899 | 766 | Distribution Circuit | 3rd Party | Vehicle | 475 | 284242 | 34.9607 | -120.4397 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0135981 | OH | Sus | 35509763 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1887899 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | TRANSFORMER | T0884 | 20231105 | 1209 | 20231105 | 1345 | 2260475 | 96 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 96 | 34.6689 | -120.0505 | No | Clear;32-90 F |  |  | 23-0136009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1887910 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | 873068 | 20231105 | 2003 | 20231105 | 2229 | 2260692 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 301 | 43946 | 35.138 | -120.5669 | No | Clear;32-90 F |  |  | 23-0136040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887937 | 0 | EPSS Ckt | Y | 2023 | A/C
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 3935 | 20231106 | 640 | 20231106 | 840 | 2261055 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2400 | 35.5518 | -120.5871 | No | Overcast;32-90 F |  |  | 23-0136160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888071 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 30609 | 20231107 | 504 | 20231107 | 702 | 2262250 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 668 | 35.4934 | -120.2276 | No | Partly Cloudy;32-90 F |  |  | 23-0136548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888346 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512309561132 | 20231107 | 856 | 20231107 | 1345 | 2262404 | 289 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 578 | 35.1535 | -120.5737 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888547 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 511501469823 | 20231107 | 2013 | 20231108 | 331 | 2263212 | 438 | Distribution Circuit | Equipment Failure/Involved | Overhead | 435 | 92175 | 35.3853 | -120.8523 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136907 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888681 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511519069383 | 20231107 | 2102 | 20231108 | 102 | 2263214 | 240 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 4800 | 35.3734 | -120.846 | No | Clear;32-90 F | Jumper | Arcing | 23-0136904 | OH | Sus | 46049818 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888673 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20231108 | 620 | 20231108 | 856 | 2263317 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 192 | 29952 | 34.5979 | -120.0297 | No | Clear;32-90 F |  |  | 23-0136924 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888697 | 0 | EPSS Ckt | Y | 2023 | AC
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 30609 | 20231108 | 657 | 20231108 | 2243 | 2263337 | 946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 9282 | 35.4934 | -120.2276 | No | Clear-Drizzle;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0137210 | OH | Sus | 31675577 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888985 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | N58 | 20231108 | 1123 | 20231108 | 1338 | 2264134 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2595 | 350325 | 35.6286 | -120.6955 | No | Clear;32-90 F |  |  | 23-0137117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888938 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 7451 | 20231108 | 1216 | 20231108 | 1445 | 2264188 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 4172 | 35.4807 | -120.665 | No | Clear;32-90 F |  |  | 23-0137206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888982 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | TEMP LR 1101/2 | 20231108 | 1513 | 20231108 | 1631 | 2264454 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1022 | 79716 | 34.6967 | -120.1518 | No | Clear;32-90 F |  |  | 23-0137223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888993 | 0 | EPSS Ckt | Y | 2023 | A- B- & INST OC
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 511997566220 | 20231108 | 1945 | 20231109 | 201 | 2264619 | 376 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3008 | 35.2902 | -120.6828 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0137301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889043 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | OCB | 1102/2 | 20231109 | 738 | 20231109 | 957 | 2264782 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1442 | 163658 | 34.6967 | -120.1519 | No | Clear;32-90 F |  |  | 23-0137359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889083 | 0 | EPSS Ckt | Y | 2023 | INST OC-GRD
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 100000048781 | 20231109 | 820 | 20231109 | 1520 | 2264845 | 420 | Transformer only | 3rd Party | Dig in- 3rd party | 1 | 420 | 34.8651 | -120.375 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0137484 | UG | Sus | 46054006 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889264 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MESA-1103 | 182821103 | TRANSFORMER | 512433457837 | 20231109 | 1311 | 20231109 | 1410 | 2265238 | 59 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 236 | 35.0631 | -120.5298 | No | Partly Cloudy;32-90 F |  |  | 23-0137571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1889312 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | TRANSFORMER | 512046073008 | 20231109 | 1500 | 20231110 | 136 | 2265256 | 636 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 5088 | 35.4771 | -120.6731 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0137591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889322 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | TRANSFORMER | 511910066107 | 20231109 | 1951 | 20231110 | 310 | 2265534 | 439 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 439 | 35.2863 | -120.7118 | No | Clear;32-90 F | Jumper | Arcing | 23-0137660 | OH | Sus | 46054175 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889355 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 2145 | 20231110 | 432 | 20231110 | 650 | 2265818 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 325 | 44850 | 35.33 | -120.8311 | No | Partly Cloudy;32-90 F |  |  | 23-0137711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1889410 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | T0227 | 20231110 | 941 | 20231110 | 1314 | 2266008 | 213 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 2589 | 34.874 | -120.4395 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0137860 | UG | Sus | 46055687 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889579 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 511996664391 | 20231110 | 1207 | 20231110 | 1239 | 2266246 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 32 | 35.2403 | -120.6818 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0137888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889594 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | RECLOSER | M86 | 20231110 | 1323 | 20231110 | 1438 | 2266301 | 75 | Distribution Circuit | 3rd Party | Vehicle | 756 | 47276 | 35.0492 | -120.4827 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0137927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1889609 | 0 | EPSS Ckt | Y | 2023 | A-C-SGF
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | FUSE | 30541 | 20231111 | 1048 | 20231111 | 1443 | 2266751 | 235 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 780 | 35.663 | -120.6275 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0138071 | UG | Sus | 35510755 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889748 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20231112 | 1306 | 20231112 | 1531 | 2267217 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1189 | 117915 | 35.7811 | -120.9891 | No | Clear;32-90 F |  |  | 23-0138210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889882 | 0 | EPSS Ckt | Y | 2023 | B-GRD INST
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | TRANSFORMER | 512686852717 | 20231113 | 932 | 20231113 | 1017 | 2267478 | 45 | Transformer only | Equipment Failure/Involved | Underground | 2 | 90 | 34.9243 | -120.4412 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0138357 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890109 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 469333 | 20231113 | 1156 | 20231113 | 1542 | 2267841 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 904 | 34.8731 | -120.3046 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0138432 | OH | Sus | 46057369 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890168 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | OTHER | T0734 TWD J268 | 20231113 | 1658 | 20231114 | 500 | 2268114 | 722 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 16416 | 34.8581 | -120.4305 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0138509 | UG | Sus | 35511520 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890225 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 14435 | 20231113 | 1717 | 20231113 | 2335 | 2268128 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 378 | 35.2406 | -120.6073 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0138574 | OH | Sus | 31676361 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1890235 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511245073990 | 20231113 | 1835 | 20231114 | 220 | 2268253 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2325 | 35.4967 | -120.9421 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0138627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890277 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 3983 | 20231114 | 353 | 20231114 | 2130 | 2268541 | 1057 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 71876 | 35.098 | -120.603 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0138634 | UG | Sus | 46057916 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890282 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | N04 | 20231114 | 936 | 20231114 | 952 | 2268881 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 2035 | 17210 | 35.7334 | -120.8792 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0127579 | OH | Sus | 31626607 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890442 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 796386 | 20231114 | 1059 | 20231114 | 1409 | 2269025 | 190 | Distribution Circuit | Animal | Bird found | 148 | 28120 | 35.8461 | -120.3793 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0138815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890482 | 0 | EPSS Ckt | Y | 2023 | A & B
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 20095 | 20231114 | 1544 | 20231114 | 1751 | 2269221 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 508 | 34.6444 | -120.4309 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0139051 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890544 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20231114 | 1728 | 20231114 | 1926 | 2269276 | 118 | Distribution Circuit | Company Initiated | Coordination failure | 730 | 86140 | 35.7811 | -120.9891 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0139048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890543 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 85870 | 20231115 | 40 | 20231115 | 254 | 2269379 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3452 | 379669 | 35.5667 | -121.075 | No | Partly Cloudy;32-90 F |  |  | 23-0139090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890573 | 0 | EPSS Ckt | Y | 2023 | C- GRD
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | RECLOSER | 1101/2 | 20231115 | 1006 | 20231115 | 1134 | 2269708 | 88 | Distribution Circuit | Animal | Bird found | 292 | 25696 | 35.361 | -120.8117 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0139224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890748 | 0 | EPSS Ckt | Y | 2023 | B & GROUND
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512691550727 | 20231115 | 1218 | 20231115 | 1432 | 2269861 | 134 | Transformer only | 3rd Party | Kite | 7 | 938 | 34.8696 | -120.4377 | No | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0139365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890818 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 45071 | 20231115 | 1254 | 20231115 | 1645 | 2269916 | 231 | Distribution Circuit | Vegetation | Tree - fell into line | 235 | 54285 | 34.8668 | -120.427 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0139380 | OH | Sus | 31676367 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1890822 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | FUSE | 45445 | 20231115 | 1256 | 20231115 | 1843 | 2269910 | 347 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 3123 | 34.8657 | -120.3831 | No | Overcast-Strong Winds;32-90 F |  |  | 23-0139632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890907 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 15925 | 20231115 | 1449 | 20231115 | 1800 | 2270048 | 191 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 1910 | 35.2174 | -120.5957 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0139614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890896 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 796386 | 20231115 | 1547 | 20231115 | 1744 | 2270103 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 148 | 17316 | 35.8461 | -120.3793 | No | Overcast;32-90 F |  |  | 23-0139546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890868 | 0 | EPSS Ckt | Y | 2023 | B- C & INST OC
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | OTHER | WIRE DOWN 1 E/OF 1141 | 20231115 | 1558 | 20231115 | 2011 | 2270122 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 231 | 33029 | 34.5848 | -120.1067 | No | Partly Cloudy-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0139561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | Yes | Yes | 1890873 | 0 | EPSS Ckt | Y | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 925053 | 20231115 | 1611 | 20231115 | 1716 | 2270187 | 65 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3292 | 210383 | 35.5561 | -121.073 | No | Overcast-Drizzle;32-90 F |  |  | 23-0139575 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890880 | 0 | EPSS Ckt | Y | 2023 | C PHASE & SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 31709 | 20231115 | 1623 | 20231115 | 1916 | 2270206 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1557 | 35.6378 | -120.5879 | No | Overcast;32-90 F |  |  | 23-0139634 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890908 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | OTHER | 3815 | 20231115 | 1704 | 20231115 | 2349 | 2270258 | 405 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 32400 | 35.088 | -120.5641 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0139624 | OH | Sus | 31676533 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1890903 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6309 | 20231115 | 2353 | 20231116 | 758 | 2270514 | 462 | Distribution Circuit | 3rd Party | Vehicle | 88 | 12180 | 34.9591 | -120.5583 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0139716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | Yes | No | 1890958 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | M70 | 20231116 | 555 | 20231116 | 710 | 2270573 | 75 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1054 | 79050 | 35.0285 | -120.4965 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0139744 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890971 | 0 | EPSS Ckt | N | 2023 | A B
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | TRANSFORMER | 512650055405 | 20231116 | 1031 | 20231116 | 1240 | 2270795 | 129 | Transformer only | 3rd Party | Metallic Balloon | 1 | 129 | 34.9979 | -120.4577 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0139976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891078 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | JUMPER | JMPRS 1 LD SIDE CGC 513384883320 | 20231116 | 1058 | 20231116 | 1151 | 2270816 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 371 | 35.7689 | -120.2304 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0139901 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1891056 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 32403 | 20231117 | 703 | 20231117 | 940 | 2271256 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 157 | 35.6001 | -120.345 | No | Partly Cloudy;32-90 F |  |  | 23-0140332 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891299 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | RECLOSER | V102 | 20231117 | 720 | 20231117 | 808 | 2271242 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 288 | 35.3318 | -120.7386 | No | Clear;32-90 F |  |  | 23-0140267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891168 | 0 | EPSS Ckt | Y | 2023 | C PH & GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 4015 | 20231117 | 1146 | 20231117 | 1335 | 2271571 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 3161 | 35.5813 | -120.5526 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0140532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891371 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | OTHER | WIRE DOWN LOAD SIDE OF CGC# 512462056622 | 20231117 | 1405 | 20231117 | 1752 | 2271666 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 317 | 19775 | 35.0293 | -120.5191 | No | Partly Cloudy-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0140576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1891383 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6307 | 20231117 | 1455 | 20231117 | 1540 | 2271716 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 315 | 34.9561 | -120.5583 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0140631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891394 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512465856797 | 20231117 | 1522 | 20231117 | 1558 | 2271740 | 36 | Transformer only | Vegetation | Tree - bark fell into line | 5 | 180 | 35.0349 | -120.5178 | No | Overcast-Rain;32-90 F | Fuse | Failed/Faulted | 23-0140653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891400 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | TRANSFORMER | 512514352694 | 20231117 | 1554 | 20231117 | 1719 | 2271826 | 85 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 85 | 34.9224 | -120.4984 | No | Partly Cloudy-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0140679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891412 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | 597930 | 20231117 | 1720 | 20231117 | 1818 | 2271845 | 58 | Distribution Circuit | 3rd Party | Vehicle | 1239 | 71862 | 34.6603 | -120.4533 | No | Overcast-Drizzle;32-90 F | Anchor or Guy | Broken | 23-0140680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | No | No | 1891413 | 0 | EPSS Ckt | N | 2023 | A C GRD OC
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y02 | 20231117 | 1730 | 20231117 | 2229 | 2271864 | 299 | Distribution Circuit | Vegetation | Tree - branch fell on line | 549 | 40117 | 34.6503 | -120.0946 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0140686 | OH | Sus | 46059127 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1891415 | 0 | EPSS Ckt | Y | 2023 | A-C
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | FUSE | 15529 | 20231117 | 1739 | 20231117 | 1941 | 2271837 | 122 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 156 | 19032 | 35.1147 | -120.5948 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Burned/flashed | 23-0140692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1891419 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | TRANSFORMER | T0482 | 20231117 | 1802 | 20231118 | 1203 | 2271891 | 1081 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 1597 | 35.7595 | -120.9851 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0140724 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891444 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 205874 | 20231118 | 300 | 20231118 | 444 | 2272002 | 104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 204 | 21216 | 35.5111 | -120.6322 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0140742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891458 | 0 | EPSS Ckt | Y | 2023 | A GRD INST OC
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 20231118 | 511 | 20231118 | 1051 | 2272035 | 340 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 19040 | 35.4345 | -120.2869 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0140753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891467 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 400827 | 20231118 | 520 | 20231118 | 1302 | 2272275 | 462 | Distribution Circuit | Animal | Other | 1 | 462 | 35.6006 | -120.3514 | No | Partly Cloudy-Heavy Rain;32-90 F | Transformer (OH) | Normal | 23-0140842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891547 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 30609 | 20231118 | 520 | 20231118 | 1407 | 2272583 | 527 | Distribution Circuit | Animal | Other | 17 | 8959 | 35.4934 | -120.2276 | No | Partly Cloudy-Heavy Rain;32-90 F | Transformer (OH) | Normal | 23-0140924 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891601 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X24 | 20231118 | 521 | 20231118 | 1517 | 2272033 | 596 | Distribution Circuit | Animal | Other | 182 | 36844 | 35.6532 | -120.3636 | No | Overcast-Rain;32-90 F | Lightning Arrestor | Burned/flashed | 23-0140755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891469 | 0 | EPSS Ckt | N | 2023 | B GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 7419 | 20231118 | 529 | 20231118 | 1145 | 2272042 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 301 | 35530 | 35.475 | -120.6543 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0140758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891473 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 7373 | 20231118 | 605 | 20231118 | 943 | 2272051 | 218 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3706 | 35.7249 | -120.574 | No | Overcast-Rain;32-90 F |  |  | 23-0140810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891524 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 827641 | 20231118 | 815 | 20231118 | 956 | 2272274 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 101 | 35.6249 | -120.3608 | No | Partly Cloudy-Fog-Heavy Rain;32-90 F |  |  | 23-0140817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891531 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512262475750 | 20231118 | 940 | 20231118 | 1816 | 2272677 | 516 | Transformer only | 3rd Party | Vehicle | 1 | 516 | 35.5538 | -120.6021 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0140961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891632 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A32 | 20231118 | 1011 | 20231118 | 1247 | 2272384 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4391 | 311812 | 35.5007 | -120.662 | No | Overcast-Heavy Rain;32-90 F | Jumper | Burned Open | 23-0140829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1891540 | 0 | EPSS Ckt | Y | 2023 | C GRD
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | SWITCH | 14315 | 20231118 | 1033 | 20231118 | 1451 | 2272396 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3096 | 35.5642 | -121.1079 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0140830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1891542 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | V38 | 20231118 | 1035 | 20231118 | 1136 | 2272417 | 61 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1499 | 91439 | 35.1274 | -120.5689 | No | Overcast-Rain;32-90 F |  |  | 23-0140846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891552 | 0 | EPSS Ckt | N | 2023 | A-C
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6339 | 20231118 | 1118 | 20231118 | 1610 | 2272477 | 292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4672 | 35.4915 | -120.6415 | No | Overcast-Heavy Rain;32-90 F | Jumper | Arcing | 23-0140922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891599 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9403 | 20231118 | 1156 | 20231118 | 1225 | 2272547 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 2784 | 35.143 | -120.5462 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0140868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891570 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | SWITCH | 6636 | 20231118 | 1201 | 20231118 | 1209 | s1891573 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 21 | 168 | 35.4753 | -120.6572 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0140758 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1891573 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | TRANSFORMER | 512514352694 | 20231118 | 1507 | 20231118 | 2138 | 2272765 | 391 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 391 | 34.9224 | -120.4984 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891613 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512488460473 | 20231118 | 1618 | 20231118 | 2320 | 2272905 | 422 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 422 | 35.1356 | -120.5131 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0140964 | OH | Sus | 31676707 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1891634 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511565367360 | 20231118 | 1703 | 20231118 | 1800 | 2272918 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 171 | 35.3183 | -120.8288 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0140944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891619 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2287 | 20231118 | 1725 | 20231118 | 1958 | 2272937 | 153 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 306 | 35.2848 | -120.7328 | No | Clear;32-90 F |  |  | 23-0140981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891653 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | T0881 | 20231119 | 1131 | 20231119 | 2335 | 2273553 | 724 | Distribution Circuit | Equipment Failure/Involved | Underground | 99 | 15554 | 34.6056 | -120.13 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0141101 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891771 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512684354128 | 20231119 | 1233 | 20231119 | 1302 | 2273558 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 203 | 34.963 | -120.4429 | No | Clear;32-90 F | Insulator | Broken- wire on object | 23-0141098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1891768 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 12079 | 20231119 | 2033 | 20231119 | 2144 | 2273725 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 710 | 34.8792 | -120.3095 | No | Clear-Strong Winds;32-90 F |  |  | 23-0141163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891823 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 12079 | 20231119 | 2211 | 20231119 | 2336 | 2273747 | 85 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 850 | 34.8792 | -120.3095 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Arcing | 23-0141166 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891826 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | OCB | 1102/2 | 20231120 | 202 | 20231120 | 413 | 2273832 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3615 | 261292 | 35.2617 | -120.6345 | No | Clear;32-90 F |  |  | 23-0141174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | No | No | 1891834 | 0 | EPSS Ckt | N | 2023 | PH OC
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | OCB | 1104/2/NORM | 20231120 | 338 | 20231120 | 438 | 2273893 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1087 | 20940 | 35.008 | -120.4539 | No | Clear;32-90 F |  |  | 23-0141177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891838 | 0 | Non-EPSS | N | 2023 | AC INST
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | RECLOSER | 994498 | 20231120 | 403 | 20231120 | 455 | 2273845 | 52 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2446 | 127192 | 35.2794 | -120.6557 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0141179 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891840 | 0 | EPSS Ckt | N | 2023 | AC
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510812576554 | 20231120 | 622 | 20231120 | 1331 | 2273935 | 429 | Transformer only | Vegetation | Tree - fell into line | 4 | 1716 | 35.5646 | -121.0901 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0141270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891943 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 3933 | 20231120 | 1017 | 20231120 | 1157 | 2274193 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 5300 | 35.5247 | -120.6432 | No | Clear;32-90 F |  |  | 23-0141348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891963 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512053372176 | 20231120 | 1452 | 20231120 | 2010 | 2274464 | 318 | Transformer only | 3rd Party | Dig in- 3rd party | 3 | 954 | 35.4548 | -120.6708 | No | Clear;32-90 F | Service conductor | Bent or Twisted | 23-0141544 | OH | Sus | 46062948 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892012 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20231121 | 1708 | 20231121 | 1751 | 2275305 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 7955 | 34.7206 | -120.4308 | No | Partly Cloudy;32-90 F | Jumper | Burned/flashed | 23-0142012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892222 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | FUSE | 4997 | 20231122 | 431 | 20231122 | 639 | 2275468 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 281 | 36029 | 35.2576 | -120.6889 | No | Clear;32-90 F | Fuse | Broken | 23-0142139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892296 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y36 | 20231122 | 2118 | 20231122 | 2233 | 2275983 | 75 | Distribution Circuit | Animal | Bird found | 273 | 20475 | 34.6026 | -120.1931 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0142480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892422 | 0 | EPSS Ckt | Y | 2023 | C- INST OC
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y06 | 20231123 | 1124 | 20231123 | 1252 | 2276120 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 345 | 30360 | 34.6201 | -120.2103 | No | Clear;32-90 F |  |  | 23-0142515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892452 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 984519 | 20231123 | 1418 | 20231123 | 1458 | 2276166 | 40 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 2400 | 35.5028 | -120.6695 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0142537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892469 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 2641 | 20231124 | 826 | 20231124 | 1033 | 2276420 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 89 | 11303 | 35.5511 | -120.4866 | No | Fog;32-90 F |  |  | 23-0142625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892552 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | TRANSFORMER | 513184540720 | 20231124 | 1331 | 20231124 | 1452 | 2276630 | 81 | Transformer only | Animal | Bird found | 1 | 81 | 34.5977 | -120.2651 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0142670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892582 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 9129 | 20231124 | 1611 | 20231124 | 1742 | 2276686 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 121 | 35.2132 | -120.591 | No | Clear;32-90 F |  |  | 23-0142687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892594 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511507869130 | 20231125 | 1340 | 20231125 | 1416 | 2277006 | 36 | Transformer only | Equipment Failure/Involved | Electrical Overload | 17 | 612 | 35.3665 | -120.8495 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0142790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892675 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | FUSE | 7097 | 20231125 | 1453 | 20231125 | 1609 | 2277067 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 304 | 35.7741 | -120.7117 | No | Clear;32-90 F |  |  | 23-0142827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892690 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | JUMPER | BURNT OPEN JUMPER | 20231126 | 27 | 20231126 | 819 | 2277244 | 472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1162 | 12540 | 35.1187 | -120.6262 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0142877 | OH | Sus | 46065640 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1892721 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 6127 | 20231126 | 1513 | 20231126 | 1620 | 2277477 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 335 | 35.5605 | -120.6717 | No | Clear;32-90 F |  |  | 23-0142944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892776 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512192459191 | 20231126 | 1651 | 20231127 | 149 | 2277500 | 538 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 10760 | 35.0986 | -120.6114 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892778 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 6011 | 20231126 | 1720 | 20231126 | 1900 | 2277524 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 300 | 35.531 | -120.7079 | No | Clear;32-90 F |  |  | 23-0142951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892782 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 513397073050 | 20231127 | 857 | 20231127 | 2103 | 2277806 | 726 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 726 | 35.4863 | -120.2191 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0143204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893063 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | FUSE | 14809 | 20231128 | 249 | 20231128 | 459 | 2278527 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 260 | 35.1362 | -120.6382 | No | Partly Cloudy;32-90 F |  |  | 23-0143318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893133 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | RECLOSER | 320270 | 20231128 | 1102 | 20231128 | 1127 | 2278929 | 25 | Distribution Circuit | Company Initiated | Personnel- company | 199 | 4975 | 34.5995 | -120.1277 | No | Clear;32-90 F | Jumper | Normal | 23-0143436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893338 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | FUSE | 44987 | 20231129 | 910 | 20231129 | 1026 | 2279734 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 608 | 35.638 | -120.7139 | No | Partly Cloudy;32-90 F |  |  | 23-0143768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893660 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 359656 | 20231129 | 1014 | 20231129 | 1128 | 2279844 | 29 | Distribution Circuit | Animal | Bird found | 21 | 609 | 35.247 | -120.6822 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 23-0143781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893675 | 0 | EPSS Ckt | Y | 2023 | A-GRD-INST OC
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511492869894 | 20231129 | 1532 | 20231129 | 1606 | 2280045 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 408 | 35.3873 | -120.8553 | No | Partly Cloudy;32-90 F | Transformer (OH) | Arcing | 23-0143967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893754 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511566367735 | 20231129 | 1740 | 20231129 | 2241 | 2280175 | 301 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 4515 | 35.3286 | -120.8287 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0144003 | OH | Sus | 31677278 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893763 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511492869894 | 20231129 | 2337 | 20231130 | 29 | 2280314 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 624 | 35.3873 | -120.8553 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0144070 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1893802 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | 673618 | 20231130 | 752 | 20231130 | 836 | 2280416 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 616 | 34.6287 | -120.1272 | No | Overcast-Fog;32-90 F |  |  | 23-0144122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893829 | 0 | EPSS Ckt | Y | 2023 | C & INST
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | 277014 | 20231130 | 755 | 20231130 | 845 | 2280418 | 50 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 364 | 18200 | 34.5994 | -120.0979 | No | Overcast-Fog;32-90 F |  |  | 23-0144123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893831 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 7459 | 20231130 | 927 | 20231130 | 1229 | 2280646 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 182 | 34.547 | -119.8929 | No | Partly Cloudy;32-90 F |  |  | 23-0144248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1894029 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 20745 | 20231130 | 1302 | 20231130 | 1409 | 2280868 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 268 | 34.6496 | -120.5295 | No | Clear;32-90 F |  |  | 23-0144353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1894066 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY SUB | 18301 | OCB | 1102/2 | 20231201 | 653 | 20231201 | 712 | 2281203 | 19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6758 | 128402 | 35.3745 | -120.8556 | No | Clear;32-90 F | Jumper | Burned Open | 23-0144519 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1894159 | 0 | Non-EPSS | N | 2023 | ABC & TIME OC
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | JUMPER | 3035 | 20231201 | 731 | 20231201 | 906 | 2281217 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 334 | 16804 | 35.3126 | -120.8247 | No | Clear-Rain;32-90 F | Jumper | Burned Open | 23-0144569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1894217 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M52 | 20231201 | 805 | 20231201 | 933 | 2281421 | 88 | Distribution Circuit | Company Initiated | Personnel- company | 2 | 176 | 34.9254 | -120.3465 | No | Clear;32-90 F | Jumper | Normal | 23-0127364 | OH | Sus | 31634280 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894291 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | OTHER | WIRE DOWN 2P/E & 1P/S/OF 725343 | 20231201 | 1036 | 20231201 | 1507 | 2281557 | 271 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1160 | 98856 | 34.8613 | -120.4277 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0144667 | OH | Sus | 46077329 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | Yes | 1894341 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M52 | 20231201 | 1612 | 20231201 | 1654 | 2281814 | 42 | Distribution Circuit | Company Initiated | Personnel- company | 2 | 84 | 34.9254 | -120.3465 | No | Clear;32-90 F | Jumper | Normal | 23-0127364 | OH | Sus | 31634280 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894420 | 0 | EPSS Ckt | Y | 2023 | SGF
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 10048 | 20231201 | 1627 | 20231201 | 1859 | 2281825 | 152 | Distribution Circuit | Animal | Bird found | 79 | 12065 | 35.5663 | -121.0993 | No | Clear;32-90 F | Fuse | Normal | 23-0144848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894428 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | SWITCH | 9249 | 20231202 | 755 | 20231202 | 1208 | 2282010 | 253 | Distribution Circuit | 3rd Party | Vehicle | 305 | 64205 | 35.1491 | -120.5999 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0144882 | OH | Sus | 35514811 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1894484 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | RECLOSER | 1108/2 | 20231202 | 2042 | 20231202 | 2104 | 2282402 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 594 | 13068 | 35.3202 | -120.6929 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0144967 | OH | Sus | 31677963 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1894602 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | FUSE | 7097 | 20231203 | 1457 | 20231203 | 1637 | 2282777 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 400 | 35.7741 | -120.7117 | No | Partly Cloudy;32-90 F |  |  | 23-0145046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1894691 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 6213 | 20231203 | 1654 | 20231203 | 1855 | 2282809 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 484 | 35.8053 | -120.3571 | No | Clear;32-90 F |  |  | 23-0145053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894698 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512689353013 | 20231203 | 2036 | 20231203 | 2155 | 2282854 | 79 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 869 | 34.9324 | -120.4405 | No | Clear;32-90 F | Fuse | Broken | 23-0145079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894722 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9313 | 20231204 | 606 | 20231204 | 748 | 2283051 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1326 | 35.1319 | -120.5557 | No | Partly Cloudy;32-90 F |  |  | 23-0145113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1894769 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | RECLOSER | 542340 | 20231204 | 1209 | 20231204 | 1750 | 2283535 | 341 | Distribution Circuit | 3rd Party | Vehicle | 126 | 13637 | 35.0083 | -120.4889 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0145228 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1894993 | 0 | Non-EPSS | N | 2023 | A & GRD
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | RECLOSER | 858898 | 20231205 | 618 | 20231205 | 749 | 2283964 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 159 | 14469 | 34.8684 | -120.2483 | No | Clear;32-90 F |  |  | 23-0145421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895094 | 0 | EPSS Ckt | Y | 2023 | AB INST
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 95757 | 20231205 | 1200 | 20231205 | 1228 | 2284359 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 420 | 35.4952 | -120.5352 | No | Clear;32-90 F | Jumper | Arcing | 23-0145536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1895325 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | TRANSFORMER | 512898953131 | 20231205 | 1450 | 20231205 | 1742 | 2284619 | 172 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 172 | 34.9369 | -120.3706 | No | Clear;32-90 F | Fuse | Broken | 23-0145683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895391 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | OTHER | 658059 | 20231205 | 2145 | 20231206 | 447 | 2284740 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 4257 | 34.6327 | -120.5005 | No | Clear;32-90 F | Jumper | Burned Open | 23-0145732 | OH | Sus | 46079483 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1895435 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | OCB | 1106/2 | 20231206 | 1917 | 20231207 | 210 | 2285611 | 413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5702 | 385234 | 35.1017 | -120.5811 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0146039 | OH | Sus | 46080088 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1895707 | 0 | EPSS Ckt | N | 2023 | SGF- SGF & INST OC
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | TRANSFORMER | 512667553291 | 20231207 | 822 | 20231207 | 926 | 2285874 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 320 | 34.9399 | -120.448 | No | Clear;32-90 F | Fuse | Broken | 23-0146128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895882 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | FUSE | 12045 | 20231207 | 1441 | 20231208 | 117 | 2286387 | 636 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3180 | 34.9977 | -120.5365 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0146317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1896015 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | TRANSFORMER | 511998373918 | 20231208 | 1254 | 20231208 | 1433 | 2286997 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 396 | 35.5018 | -120.69 | No | Clear;32-90 F | Service conductor | Deteriorated | 23-0146534 | OH | Sus | 46083127 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896278 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | V88 | 20231208 | 1611 | 20231209 | 2337 | 2287300 | 1615 | Distribution Circuit | Equipment Failure/Involved | Underground | 739 | 215430 | 35.5597 | -121.0765 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0146585 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896307 | 0 | EPSS Ckt | Y | 2023 | A-GRD-MTT
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X16 | 20231208 | 1634 | 20231208 | 1841 | 2287331 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 283 | 27283 | 35.6868 | -120.3362 | No | Clear;32-90 F |  |  | 23-0146586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1896308 | 0 | EPSS Ckt | Y | 2023 | A-C
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRIP-SAVER | 6111 | 20231208 | 2215 | 20231209 | 820 | 2287449 | 605 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 157300 | 35.0643 | -120.4971 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0146613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896340 | 0 | EPSS Ckt | N | 2023 | NA
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46067 | 20231209 | 203 | 20231209 | 1009 | 2287516 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 12150 | 34.9682 | -120.4143 | No | Clear;32-90 F | Jumper | Burned Open | 23-0146625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1896355 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511361372059 | 20231209 | 1306 | 20231210 | 8 | 2287900 | 662 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 5958 | 35.4462 | -120.9009 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0146661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896493 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512693854034 | 20231210 | 154 | 20231210 | 212 | 2288200 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 18 | 34.9605 | -120.4397 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0146717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896555 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | T0641 | 20231210 | 651 | 20231210 | 850 | 2288235 | 119 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 1547 | 35.7218 | -120.872 | No | Clear;Below 32 F |  |  | 23-0146738 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1896588 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | RECLOSER | A28 | 20231210 | 1227 | 20231210 | 1344 | 2288367 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1795 | 110847 | 35.4622 | -120.6453 | No | Clear;32-90 F |  |  | 23-0146751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1896608 | 0 | EPSS Ckt | N | 2023 | A- B- GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 492068 | 20231210 | 1229 | 20231210 | 1618 | s1896612 | 229 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1742 | 239114 | 35.4579 | -120.6602 | No | Clear;32-90 F |  |  | 23-0146755 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896612 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A06 | 20231210 | 1607 | 20231210 | 1658 | 2288452 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 621 | 31671 | 35.4634 | -120.6701 | No | Clear;32-90 F |  |  | 23-0146761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896617 | 0 | EPSS Ckt | Y | 2023 | SGF-DCD
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 1461 | 20231211 | 146 | 20231211 | 553 | 2288553 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 10374 | 35.0209 | -120.5049 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0146811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896670 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M54 | 20231211 | 638 | 20231211 | 746 | 2288585 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 127 | 8636 | 34.8627 | -120.2773 | No | Partly Cloudy;32-90 F |  |  | 23-0146812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1896674 | 0 | EPSS Ckt | Y | 2023 | BC
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y02 | 20231211 | 917 | 20231211 | 1115 | 2288796 | 118 | Distribution Circuit | Company Initiated | Personnel- company | 517 | 39820 | 34.6503 | -120.0946 | No | Partly Cloudy;32-90 F | Jumper | Normal | 23-0146841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896799 | 0 | EPSS Ckt | Y | 2023 | C GRD
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511566067542 | 20231211 | 1137 | 20231211 | 1623 | 2289248 | 286 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 3718 | 35.3233 | -120.8288 | No | Clear;32-90 F | Secondary | Broken | 23-0146894 | OH | Sus | 46087513 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896906 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | TRANSFORMER | 513782143371 | 20231211 | 1344 | 20231211 | 1757 | 2289358 | 253 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 506 | 34.6741 | -120.0687 | No | Clear;32-90 F |  |  | 23-0146915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1896924 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A06 | 20231212 | 1643 | 20231212 | 1753 | 2290233 | 64 | Distribution Circuit | Animal | Squirrel | 621 | 43110 | 35.4634 | -120.6701 | No | Clear;32-90 F | Fuse | Normal | 23-0147117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897227 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 53029 | 20231212 | 1832 | 20231212 | 1845 | 2290309 | 13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 273 | 35.4602 | -120.6767 | No | Clear;32-90 F |  |  | 23-0147129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1897243 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | M82 | 20231213 | 608 | 20231213 | 710 | 2290489 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 791 | 49042 | 34.7368 | -120.2589 | No | Clear;32-90 F |  |  | 23-0147161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1897294 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | 483444 | 20231213 | 834 | 20231213 | 924 | 2290624 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2964 | 143484 | 35.2892 | -120.6524 | No | Clear;32-90 F |  |  | 23-0147189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897383 | 0 | EPSS Ckt | Y | 2023 | B PHASE & GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | T0235 | 20231213 | 1558 | 20231213 | 2034 | 2291230 | 276 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 552 | 34.9692 | -120.4226 | No | Clear;32-90 F | Transformer | Normal | 23-0147316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897591 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A06 | 20231213 | 1624 | 20231213 | 1823 | 2291256 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 621 | 73899 | 35.4634 | -120.6701 | No | Clear;32-90 F |  |  | 23-0147308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897584 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V10 | 20231214 | 705 | 20231214 | 1502 | 2291514 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1328 | 327472 | 35.215 | -120.6143 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147374 | OH | Sus | 46091769 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1897648 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 30225 | 20231216 | 1708 | 20231216 | 1949 | 2293337 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 3646 | 35.4909 | -120.7302 | No | Clear;32-90 F |  |  | 23-0147685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898408 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512104460757 | 20231217 | 450 | 20231217 | 935 | 2293453 | 285 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2280 | 35.141 | -120.6423 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898451 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 6313 | 20231217 | 716 | 20231217 | 828 | 2293472 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 288 | 34.958 | -120.5913 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0147735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898466 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 1437 | 20231217 | 1304 | 20231217 | 1530 | 2293627 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 3993 | 34.6012 | -120.2788 | No | Partly Cloudy;32-90 F |  |  | 23-0147745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898494 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 9433 | 20231217 | 1416 | 20231217 | 1633 | 2293734 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2385 | 35.3705 | -120.8558 | No | Partly Cloudy;32-90 F |  |  | 23-0147768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898516 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | JUMPER | JUMPERS 2P E/OF CGC# 513168450212 | 20231218 | 918 | 20231218 | 1936 | 2294382 | 618 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 618 | 34.8589 | -120.2771 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 23-0147883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898675 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | FUSE | 90081 | 20231218 | 1020 | 20231218 | 1247 | 2294406 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 6174 | 35.3914 | -120.8561 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0147886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898681 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | RECLOSER | 337126 | 20231218 | 2008 | 20231219 | 207 | 2295125 | 359 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 888 | 9392 | 35.2541 | -120.6693 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 23-0147985 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898796 | 0 | EPSS Ckt | N | 2023 | N/A
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N42 | 20231218 | 2010 | 20231219 | 1846 | 2295136 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2274 | 319892 | 35.8683 | -120.843 | No | Overcast-Fog-Drizzle;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0147986 | OH | Sus | 31679813 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1898798 | 0 | EPSS Ckt | N | 2023 | B-C-GRD
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | 104948 | 20231219 | 1137 | 20231219 | 2208 | 2295670 | 631 | Distribution Circuit | 3rd Party | Vehicle | 117 | 14190 | 34.759 | -120.4018 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0148097 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1898960 | 0 | EPSS Ckt | N | 2023 | ABC GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | JUMPER | OPEN JUMPER | 20231219 | 1455 | 20231219 | 1705 | 2295931 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1162 | 51799 | 35.1212 | -120.6277 | No | Overcast-Rain;32-90 F | Jumper | Burned Open | 23-0148136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1898999 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | RECLOSER | P26 | 20231220 | 847 | 20231220 | 1016 | 2296340 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 505 | 44371 | 35.629 | -120.6607 | No | Overcast-Drizzle;32-90 F |  |  | 23-0148223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899124 | 0 | EPSS Ckt | N | 2023 | A- GRD
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | TRIP-SAVER | 2757 | 20231220 | 1454 | 20231221 | 737 | 2296691 | 1003 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3823 | 35.8288 | -120.9578 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0148324 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899263 | 0 | EPSS Ckt | N | 2023 | A-B
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | RECLOSER | TEMP LR 1102/2 | 20231220 | 1522 | 20231220 | 1544 | 2296743 | 22 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2033 | 44726 | 34.6251 | -120.1865 | No | Overcast-Heavy Rain;32-90 F |  |  | 23-0148289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899225 | 0 | EPSS Ckt | N | 2023 | A&B
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | TEMP LR 1101/2 | 20231220 | 1522 | 20231220 | 1546 | 2296777 | 24 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2406 | 57744 | 34.7008 | -120.4358 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 23-0148290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1899226 | 0 | EPSS Ckt | N | 2023 | ABC
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | TEMP LR 1101/2 | 20231220 | 1522 | 20231220 | 1555 | 2296778 | 33 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 171 | 5643 | 34.6967 | -120.1518 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0148296 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1899232 | 0 | EPSS Ckt | N | 2023 | NO 3 PH VOLTAGE
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | TEMP LR 1103/2 | 20231220 | 1523 | 20231220 | 1557 | 2296755 | 34 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1697 | 57698 | 34.6432 | -120.4375 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0148291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899227 | 0 | EPSS Ckt | N | 2023 | A B
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | TRANSFORMER | T0602 | 20231220 | 1642 | 20231220 | 1721 | 2296845 | 39 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 39 | 34.5936 | -120.1521 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0148313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1899251 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M54 | 20231220 | 1649 | 20231220 | 1707 | 2296852 | 18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 127 | 2286 | 34.8627 | -120.2773 | No | Overcast-Heavy Rain;32-90 F |  |  | 23-0148306 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899244 | 0 | EPSS Ckt | Y | 2023 | B&C PHASE INST
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | FUSE | 49333 | 20231220 | 1743 | 20231220 | 1817 | 2296505 | 34 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 476 | 34.9551 | -120.4091 | No | Overcast-Rain;32-90 F | Secondary | Broken | 23-0148316 | OH | Sus | 46097985 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1899254 | 0 | Non-EPSS | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5655 | 20231220 | 2349 | 20231221 | 325 | 2297247 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 11880 | 35.4572 | -120.4631 | No | Overcast;32-90 F |  |  | 23-0148422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899381 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | JUMPER | V36 | 20231221 | 1041 | 20231221 | 1059 | 2297600 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 341 | 5797 | 35.1451 | -120.53 | No | Overcast-Rain;32-90 F | Jumper | Burned Open | 23-0148465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1899449 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512333062665 | 20231221 | 1655 | 20231221 | 2313 | 2297940 | 378 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 378 | 35.1941 | -120.5676 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899520 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512726253320 | 20231222 | 2055 | 20231223 | 859 | 2298628 | 724 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 724 | 34.941 | -120.4284 | No | Overcast-Fog;32-90 F | Transformer (OH) | Leaking | 23-0148636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899696 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 63641 | 20231222 | 2209 | 20231223 | 1044 | 2298635 | 755 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 16570 | 35.6113 | -121.1394 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899698 | 0 | Non-EPSS | N | 2023
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512545051729 | 20231223 | 1521 | 20231223 | 1605 | 2298883 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 572 | 34.8961 | -120.4875 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0148678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899744 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | OTHER | WIRE DOWN ON MAINLINE @ 96829 | 20231223 | 2123 | 20231224 | 1113 | 2298966 | 830 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 59902 | 35.3362 | -120.748 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0148719 | OH | Sus | 46100420 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | Yes | 1899787 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 4537 | 20231224 | 158 | 20231224 | 602 | 2299023 | 244 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 19764 | 35.5679 | -121.0997 | No | Clear;32-90 F | Insulator | Broken | 23-0148728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899796 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512075565681 | 20231224 | 2022 | 20231225 | 525 | 2299301 | 543 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1086 | 35.276 | -120.6563 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899870 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | MTR#1008531746 | 20231226 | 1057 | 20231226 | 1333 | 2299635 | 156 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 3120 | 35.1289 | -120.6261 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0148894 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900011 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | MTR#1008720021 | 20231226 | 1143 | 20231226 | 1345 | 2299860 | 122 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 244 | 35.223 | -120.6234 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0148878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1899994 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511596667060 | 20231227 | 1130 | 20231227 | 1203 | 2300404 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 132 | 35.3102 | -120.8182 | No | Overcast;32-90 F | PGs- Kearneys | Deteriorated | 23-0148999 | OH | Sus | 46101830 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900165 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | OTHER | J1106 TWD T3731 | 20231227 | 1207 | 20231227 | 1227 | 2300671 | 20 | Distribution Circuit | 3rd Party | Vehicle | 1 | 20 | 35.0276 | -120.5438 | No | Overcast;32-90 F | Transformer (UG) | Broken | 23-0148989 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900170 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | TRANSFORMER | 512685552686 | 20231227 | 1208 | 20231227 | 1505 | 2300676 | 177 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 885 | 34.9234 | -120.4415 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0149005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900173 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 2229 | 20231227 | 1721 | 20231227 | 1927 | 2300913 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2394 | 35.1568 | -120.5272 | No | Partly Cloudy;32-90 F |  |  | 23-0149047 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900221 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511532867552 | 20231228 | 1107 | 20231228 | 1549 | 2301414 | 282 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2256 | 35.3232 | -120.8398 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900369 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511533067593 | 20231228 | 1107 | 20231228 | 2018 | 2301494 | 551 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1653 | 35.3245 | -120.8398 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900385 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | FUSE | 7097 | 20231228 | 1453 | 20231228 | 1545 | 2301450 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 208 | 35.7741 | -120.7117 | No | Clear;32-90 F |  |  | 23-0149122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900380 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511502070061 | 20231228 | 1457 | 20231228 | 2130 | 2301416 | 393 | Transformer only | 3rd Party | Vehicle | 13 | 5109 | 35.3919 | -120.8523 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 23-0149128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900386 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511533167627 | 20231228 | 1514 | 20231228 | 2128 | 2301495 | 374 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3366 | 35.3255 | -120.8398 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900383 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | RECLOSER | M02 | 20231228 | 1846 | 20231228 | 2001 | 2301576 | 75 | Distribution Circuit | 3rd Party | Vehicle | 3263 | 88417 | 34.9084 | -120.4357 | No | Partly Cloudy;32-90 F | Interrupter | Broken | 23-0149139 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900396 | 0 | Non-EPSS | N | 2023 | C&GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 30481 | 20231229 | 806 | 20231229 | 851 | 2301723 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 1800 | 35.504 | -120.6817 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0149192 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900465 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | RECLOSER | 76678 | 20231229 | 2142 | 20231230 | 1105 | 2302287 | 803 | Distribution Circuit | Equipment Failure/Involved | Underground | 455 | 73173 | 35.1221 | -120.5916 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 23-0149288 | UG | Sus | 35520069 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900586 | 0 | EPSS Ckt | N | 2023 | B GRD
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20149 | 20231230 | 733 | 20231230 | 1443 | 2302468 | 430 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 10198 | 34.5309 | -120.2908 | No | Overcast-Fog-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0149343 | OH | Sus | 46118640 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1900652 | 1 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 31833 | 20231230 | 1207 | 20231230 | 1240 | 2302757 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 33 | 35.529 | -120.7917 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0149363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1900672 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y06 | 20231230 | 1343 | 20231230 | 2021 | 2302823 | 398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 345 | 15558 | 34.6201 | -120.2103 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0149379 | OH | Sus | 31680584 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1900691 | 0 | EPSS Ckt | N | 2023 | SGF
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512672653957 | 20231230 | 1644 | 20231230 | 1732 | 2302934 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 32 | 1536 | 34.9582 | -120.4467 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0149401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900713 | 0 | Non-EPSS | N | 2023
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511453070548 | 20231230 | 1813 | 20231230 | 2014 | 2302982 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 1815 | 35.4047 | -120.8687 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0149405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900720 | 0 | EPSS Ckt | N | 2023
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9415 | 20231230 | 2256 | 20231231 | 1142 | 2303047 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10724 | 35.1374 | -120.5171 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149445 | OH | Sus | 31680641 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1900760 | 0 | EPSS Ckt | N | 2023
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30643 | 20231231 | 913 | 20231231 | 953 | 2303139 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 679 | 35.5135 | -120.6856 | No | Overcast-Fog;32-90 F |  |  | 23-0149462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900780 | 1 | EPSS Ckt | N | 2023
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | RECLOSER | M02 | 20240101 | 737 | 20240101 | 1304 | 2304140 | 327 | Distribution Circuit | 3rd Party | Vehicle | 3 | 981 | 34.9084 | -120.4357 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0005762 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900868 | 0 | Non-EPSS | N | 2024 | A-C-GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 30481 | 20240101 | 920 | 20240101 | 1015 | 2304171 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 2200 | 35.504 | -120.6817 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0005774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900880 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 520924 | 20240101 | 1106 | 20240101 | 1213 | 2304199 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 5695 | 35.5345 | -120.5265 | No | Clear;32-90 F |  |  | 24-0005778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1900884 | 0 | EPSS Ckt | Y | 2024 | A-B-INST
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512447076270 | 20240101 | 1249 | 20240101 | 1655 | 2304263 | 246 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 492 | 35.5652 | -120.5406 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0005797 | OH | Sus | 31680645 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900900 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 9265 | 20240102 | 122 | 20240102 | 307 | 2304452 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 315 | 35.2393 | -120.6786 | No | Partly Cloudy;32-90 F |  |  | 24-0005845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1900944 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 513312073360 | 20240102 | 842 | 20240102 | 1655 | 2304595 | 493 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 986 | 35.4943 | -120.2473 | No | Partly Cloudy-Fog;32-90 F | Jumper | Broken- wire on object | 24-0006015 | OH | Sus | 31680629 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1901066 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 7373 | 20240102 | 2310 | 20240103 | 40 | 2305570 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1530 | 35.7249 | -120.574 | No | Overcast-Heavy Rain;32-90 F |  |  | 24-0006291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901188 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 44755 | 20240103 | 700 | 20240103 | 920 | 2305739 | 140 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 18 | 2520 | 35.5507 | -121.0812 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0006359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901249 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 14813 | 20240103 | 930 | 20240103 | 1006 | 2306180 | 36 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 1296 | 35.1412 | -120.6358 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0006383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901297 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512782053956 | 20240103 | 1146 | 20240103 | 1201 | 2306280 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 225 | 34.9588 | -120.4103 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 24-0006483 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901352 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | TRANSFORMER | 512040564633 | 20240103 | 1430 | 20240103 | 1543 | 2306421 | 73 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 146 | 35.2466 | -120.668 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0006565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901383 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 7543 | 20240105 | 26 | 20240105 | 150 | 2307512 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 160 | 13440 | 34.6651 | -120.1137 | No | Clear;32-90 F |  |  | 24-0007152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901705 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 6971 | 20240105 | 635 | 20240105 | 837 | 2307576 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 732 | 35.8149 | -120.8454 | No | Clear;32-90 F |  |  | 24-0007233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901766 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | TRANSFORMER | 512696852122 | 20240105 | 1033 | 20240105 | 1333 | 2307857 | 180 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2160 | 34.9079 | -120.4372 | No | Clear;32-90 F | Connector or Splice (OH) | Contaminated | 24-0007324 | OH | Sus | 46131693 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901848 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | OTHER | T3934 TWD T3930 | 20240105 | 1155 | 20240105 | 1312 | 2307941 | 77 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 1540 | 35.1872 | -120.7329 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0007361 | UG | Sus | 35521425 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901861 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 100000038668 | 20240105 | 2127 | 20240105 | 2154 | 2308207 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 216 | 35.1548 | -120.675 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0007536 | OH | Sus | 31681089 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901923 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512011561351 | 20240106 | 916 | 20240106 | 1137 | 2308494 | 141 | Transformer only | Equipment Failure/Involved | Overhead | 33 | 4653 | 35.1568 | -120.6736 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0007574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901969 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512241062373 | 20240106 | 1017 | 20240106 | 1048 | 2308574 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 31 | 35.1839 | -120.5979 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0007594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901987 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRIP-SAVER | 45067 | 20240107 | 522 | 20240107 | 1120 | 2309089 | 358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 34726 | 34.8636 | -120.441 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0007726 | OH | Sus | 31681163 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1902100 | 1 | EPSS Ckt | N | 2024 | NONE
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511434371159 | 20240107 | 1125 | 20240107 | 1229 | 2309202 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 64 | 35.421 | -120.8769 | No | Clear;32-90 F | Fuse | Broken | 24-0007761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902127 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 4169 | 20240107 | 1457 | 20240107 | 1651 | 2309270 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 798 | 35.7312 | -120.6242 | No | Clear;32-90 F |  |  | 24-0007772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1902134 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | OTHER | WIRE DOWN LS OF CGC 512677750411 | 20240107 | 1850 | 20240107 | 2248 | 2309365 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 19537 | 34.8606 | -120.4421 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0007781 | OH | Sus | 31681281 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1902143 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 98367 | 20240107 | 2007 | 20240107 | 2136 | 2309364 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 3204 | 34.9563 | -120.4125 | No | Clear;32-90 F |  |  | 24-0007796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1902158 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512211759478 | 20240108 | 803 | 20240109 | 859 | 2309491 | 1496 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 1496 | 35.1066 | -120.6052 | No | Clear;32-90 F | Transformer | Normal | 24-0004565 | OH | Sus | 35317857 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1902190 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512536851772 | 20240108 | 1310 | 20240108 | 1747 | 2309904 | 277 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1385 | 34.8972 | -120.4903 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0008080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902396 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 30527 | 20240109 | 648 | 20240109 | 804 | 2310279 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 127 | 35.5731 | -120.5966 | No | Clear;32-90 F |  |  | 24-0008309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902497 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | FUSE | 11473 | 20240109 | 1439 | 20240109 | 1553 | 2310961 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 113 | 8362 | 34.9292 | -120.433 | No | Clear;32-90 F |  |  | 24-0008598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1902701 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | SWITCH | 6166SW | 20240109 | 1634 | 20240109 | 1748 | 2311049 | 74 | Distribution Circuit | Equipment Failure/Involved | Underground | 34 | 2516 | 35.729 | -120.8926 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0008654 | UG | Sus | 35521958 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902712 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 30161 | 20240110 | 713 | 20240110 | 907 | 2311323 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1254 | 35.5871 | -120.6995 | No | Clear;32-90 F |  |  | 24-0008830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902839 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 136678 | 20240110 | 1603 | 20240111 | 144 | 2311960 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 188 | 56005 | 35.1945 | -120.7142 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0009233 | OH | Sus | 46141049 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1903046 | 0 | EPSS Ckt | N | 2024 | B
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | FUSE | 15817 | 20240110 | 1751 | 20240110 | 1944 | 2312068 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 349 | 39437 | 35.2782 | -120.6577 | No | Partly Cloudy;32-90 F |  |  | 24-0009298 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1903072 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512207759225 | 20240110 | 2129 | 20240110 | 2135 | 2311868 | 6 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 132 | 35.0996 | -120.6063 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0009340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903104 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | TRANSFORMER | 511986865132 | 20240111 | 240 | 20240111 | 708 | 2312544 | 268 | Transformer only | Vegetation | Tree - grew into line | 6 | 1608 | 35.2605 | -120.6851 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0009395 | OH | Sus | 46140998 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903148 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 511790564171 | 20240111 | 419 | 20240111 | 713 | 2312614 | 174 | Transformer only | Unknown Cause | Patrol - not conducted | 3 | 522 | 35.2324 | -120.7501 | No | Clear;32-90 F |  |  | 24-0009424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1903171 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512785552300 | 20240111 | 1537 | 20240112 | 35 | 2313213 | 538 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 538 | 34.9135 | -120.4076 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0009961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903463 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | FUSE | 45589 | 20240112 | 800 | 20240112 | 936 | 2313561 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 376 | 36114 | 34.8867 | -120.4356 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0010049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903579 | 1 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512118672038 | 20240112 | 1209 | 20240112 | 1403 | 2313829 | 114 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 570 | 35.451 | -120.648 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0010272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1903674 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | 705596 | 20240112 | 1341 | 20240112 | 1502 | 2314003 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 180 | 14580 | 34.5986 | -120.1926 | No | Clear;32-90 F |  |  | 24-0010245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1903669 | 0 | EPSS Ckt | N | 2024 | A B
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512457262108 | 20240113 | 1158 | 20240113 | 1855 | 2314651 | 417 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 417 | 35.1807 | -120.525 | No | Partly Cloudy;32-90 F |  |  | 24-0010552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1903843 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20635 | 20240113 | 1507 | 20240113 | 1644 | 2314826 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 679 | 34.6243 | -120.2251 | No | Clear;32-90 F |  |  | 24-0010511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1903818 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 85870 | 20240113 | 2039 | 20240114 | 159 | 2315071 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2992 | 795620 | 35.5667 | -121.075 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0010561 | OH | Sus | 46151677 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1903852 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | TRANSFORMER | 513614843780 | 20240114 | 2147 | 20240115 | 429 | 2315584 | 402 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 402 | 34.6851 | -120.1245 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 24-0010744 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904014 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 30481 | 20240115 | 1014 | 20240115 | 1059 | 2315749 | 45 | Distribution Circuit | Animal | Bird found | 40 | 1800 | 35.504 | -120.6817 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0010784 | OH | Sus | 46153430 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904050 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 30481 | 20240115 | 1316 | 20240115 | 1437 | 2315827 | 81 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 3240 | 35.504 | -120.6817 | No | Partly Cloudy;32-90 F | Other | Normal | 24-0010795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904060 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | FUSE | 7097 | 20240115 | 1529 | 20240115 | 1649 | 2315887 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 320 | 35.7741 | -120.7117 | No | Clear;32-90 F |  |  | 24-0010826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1904077 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | TRANSFORMER | 414928117666 | 20240116 | 931 | 20240116 | 1748 | 2316124 | 497 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 497 | 35.8058 | -120.7113 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0011127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904319 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 7679 | 20240116 | 952 | 20240116 | 1123 | 2316367 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 607 | 34.6559 | -120.5387 | No | Partly Cloudy;32-90 F |  |  | 24-0011034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904296 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512424361308 | 20240116 | 1105 | 20240116 | 1135 | 2316508 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 30 | 35.1583 | -120.5356 | No | Clear;32-90 F | Secondary | Broken | 24-0011045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904302 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 5935 | 20240116 | 1529 | 20240116 | 1748 | 2316696 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2363 | 35.543 | -120.7646 | No | Clear;32-90 F |  |  | 24-0011305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1904368 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | RECLOSER | P08 | 20240116 | 1616 | 20240116 | 2218 | 2316718 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1179 | 31839 | 35.6067 | -120.6929 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0011258 | OH | Sus | 46156958 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904348 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5307 | 20240117 | 304 | 20240117 | 412 | 2317217 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 136 | 35.5615 | -120.6406 | No | Clear;32-90 F |  |  | 24-0011418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904441 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512150876133 | 20240117 | 759 | 20240117 | 1403 | 2317280 | 364 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 364 | 35.5635 | -120.64 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0011558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904617 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | TRANSFORMER | 511664366150 | 20240117 | 926 | 20240117 | 1429 | 2317372 | 303 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 303 | 35.2868 | -120.7939 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0011632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904643 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | OCB | 1106/2 | 20240118 | 246 | 20240118 | 533 | 2318159 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 229 | 37447 | 35.7522 | -120.6839 | No | Overcast-Fog;32-90 F |  |  | 24-0011942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1904722 | 0 | EPSS Ckt | N | 2024 | ABC-TIME
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 6307 | 20240118 | 1012 | 20240118 | 1227 | 2318349 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 630 | 34.9561 | -120.5583 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0012178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904827 | 1 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | FUSE | 7097 | 20240118 | 1524 | 20240118 | 2346 | 2318592 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2008 | 35.7741 | -120.7117 | No | Overcast;32-90 F | Conductor- Overhead | Together | 24-0012373 | OH | Sus | 46164768 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1904859 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 969643 | 20240118 | 1912 | 20240118 | 2234 | 2318724 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 3232 | 35.1043 | -120.6068 | No | Overcast;32-90 F | Secondary | Broken | 24-0012397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904874 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512701853471 | 20240118 | 1915 | 20240119 | 143 | 2318727 | 388 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 5820 | 34.945 | -120.4368 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0012398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904875 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | OTHER | WIRE DOWN 3 SS OF 7195 | 20240119 | 1740 | 20240120 | 1406 | 2319378 | 1226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 275 | 75311 | 34.6104 | -120.3679 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0012792 | OH | Sus | 46166064 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1905131 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 75931 | 20240119 | 2011 | 20240119 | 2342 | 2319464 | 211 | Distribution Circuit | Vegetation | Tree - bark fell into line | 50 | 10550 | 35.3627 | -120.8343 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0012840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905177 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512016261296 | 20240120 | 122 | 20240120 | 847 | 2319517 | 445 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 8900 | 35.1553 | -120.672 | No | Overcast-Rain;32-90 F | Fuse | Broken | 24-0012910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905245 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | FUSE | 14491 | 20240120 | 1600 | 20240121 | 1356 | 2320029 | 1316 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 23 | 30268 | 35.4748 | -120.9134 | No | Overcast-Rain;32-90 F |  |  | 24-0013037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905310 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511557367585 | 20240121 | 1722 | 20240122 | 308 | 2320576 | 586 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1172 | 35.3244 | -120.8316 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0013169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905417 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510809975931 | 20240122 | 332 | 20240122 | 1110 | 2320895 | 453 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 4983 | 35.5476 | -121.0909 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0013192 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905441 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | FUSE | 3963 | 20240122 | 1529 | 20240123 | 1252 | 2321621 | 940 | Distribution Circuit | Animal | Other | 42 | 53886 | 35.6366 | -120.7771 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0013585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1905630 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 306275 | 20240122 | 2050 | 20240122 | 2338 | 2321861 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 23184 | 35.5721 | -121.1068 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0013645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905670 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | V88 | 20240123 | 38 | 20240123 | 904 | 2321903 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 102045 | 35.5597 | -121.0765 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0013660 | OH | Sus | 46170514 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1905674 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | RECLOSER | TEMP LR 1102/2 | 20240123 | 605 | 20240123 | 626 | 2321966 | 21 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2033 | 42693 | 34.6251 | -120.1865 | No | Partly Cloudy;32-90 F | PT/CCVT | Burned/flashed | 24-0013683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905687 | 0 | EPSS Ckt | N | 2024 | B GRD & TIME OC
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | TRANSFORMER | 512202481056 | 20240123 | 1100 | 20240123 | 1310 | 2322306 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 260 | 35.7012 | -120.6265 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0013832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905845 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRANSFORMER | 512450058343 | 20240123 | 1141 | 20240123 | 1213 | 2322361 | 32 | Transformer only | Company Initiated | Construction Activity/equip- company | 2 | 64 | 35.0766 | -120.5243 | No | Partly Cloudy;32-90 F | Secondary | Normal | 24-0013869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1905854 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511537768845 | 20240123 | 1725 | 20240123 | 2056 | 2322507 | 211 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 4009 | 35.3587 | -120.8392 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0014084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905897 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 15229 | 20240124 | 1122 | 20240124 | 1237 | 2323088 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 675 | 35.1867 | -120.7026 | No | Overcast;32-90 F |  |  | 24-0014447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1906078 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | TRANSFORMER | 512100766233 | 20240124 | 1235 | 20240125 | 357 | 2323039 | 922 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 922 | 35.2914 | -120.6483 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0014334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906050 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 14281 | 20240124 | 1333 | 20240124 | 1433 | 2323208 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 3420 | 35.4446 | -120.8966 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 24-0014504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906089 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512723554160 | 20240124 | 1930 | 20240125 | 356 | 2323444 | 506 | Distribution Circuit | Equipment Failure/Involved | Overhead | 237 | 29234 | 34.9641 | -120.4299 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 24-0014762 | OH | Sus | 35526159 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906161 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | FUSE | 45805 | 20240124 | 1932 | 20240125 | 129 | 2323428 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 119 | 12427 | 34.9647 | -120.4372 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0014697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906120 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 6621 | 20240126 | 1234 | 20240126 | 1906 | 2324942 | 392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 208 | 59438 | 34.6004 | -120.1953 | No | Clear;32-90 F | Jumper | Burned Open | 24-0015675 | OH | Sus | 31682558 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1906710 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V10 | 20240126 | 1509 | 20240127 | 1122 | 2325139 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 1347 | 52042 | 35.215 | -120.6143 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0015711 | OH | Sus | 35526414 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1906720 | 0 | EPSS Ckt | N | 2024 | A-B-C
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 2977 | 20240126 | 1559 | 20240126 | 1749 | 2325174 | 110 | Distribution Circuit | Animal | Bird found | 9 | 990 | 35.7041 | -120.7387 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0015767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1906741 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | TRANSFORMER | 510805378040 | 20240128 | 1823 | 20240129 | 244 | 2326600 | 501 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2004 | 35.6051 | -121.0955 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0016012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906953 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512149160211 | 20240129 | 1224 | 20240129 | 1321 | 2327249 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 855 | 35.1266 | -120.6265 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0016220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907213 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2963 | 20240129 | 1515 | 20240130 | 150 | 2327489 | 635 | Distribution Circuit | 3rd Party | Vehicle | 12 | 4148 | 35.4939 | -120.4553 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0016387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1907273 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511576467769 | 20240129 | 2001 | 20240130 | 147 | 2327564 | 346 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 5536 | 35.3295 | -120.8254 | No | Clear;32-90 F | Secondary | Broken | 24-0016410 | OH | Sus | 31682686 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907286 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | TRANSFORMER | 511389683447 | 20240130 | 820 | 20240130 | 1316 | 2327919 | 296 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 592 | 35.7581 | -120.9015 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0016651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907529 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 136678 | 20240130 | 1155 | 20240131 | 129 | 2328276 | 814 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 188 | 153032 | 35.1945 | -120.7142 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0016668 | OH | Sus | 31682844 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1907533 | 0 | EPSS Ckt | N | 2024 | C
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | TRANSFORMER | 512683153751 | 20240130 | 1552 | 20240130 | 2341 | 2328425 | 469 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 10787 | 34.9526 | -120.4431 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0016865 | OH | Sus | 31682881 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907577 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | TRANSFORMER | 512078265265 | 20240131 | 1500 | 20240131 | 1921 | 2329900 | 261 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 4176 | 35.2646 | -120.6551 | No | Overcast;32-90 F | Bushing | Broken | 24-0017464 | OH | Sus | 31682872 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907939 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 735055 | 20240131 | 1713 | 20240131 | 1820 | 2330081 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 4087 | 35.2821 | -120.6571 | No | Overcast;32-90 F |  |  | 24-0017579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1907995 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | Q10 | 20240131 | 1717 | 20240131 | 1808 | 2330089 | 51 | Distribution Circuit | Vegetation | Tree - fell into line | 783 | 39933 | 35.1349 | -120.5694 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0017553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1907975 | 0 | EPSS Ckt | N | 2024 | ABC OC
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30879 | 20240131 | 2159 | 20240201 | 638 | 2330546 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 519 | 35.5295 | -120.6205 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017727 | OH | Sus | 31682875 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1908123 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512774454051 | 20240131 | 2317 | 20240201 | 354 | 2330547 | 277 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2770 | 34.9613 | -120.4128 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0017715 | OH | Sus | 46176163 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1908109 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | RECLOSER | W24 | 20240131 | 2349 | 20240201 | 623 | 2330657 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 890 | 109196 | 35.3227 | -120.8356 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017723 | OH | Sus | 31682855 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1908118 | 0 | EPSS Ckt | N | 2024 | BC
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | 513629840806 | 20240201 | 123 | 20240201 | 233 | 2330729 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 140 | 34.6031 | -120.1176 | No | Overcast-Rain-Strong Winds;32-90 F | Fuse | Broken | 24-0017753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908151 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 11063 | 20240201 | 220 | 20240201 | 353 | 2330738 | 93 | Distribution Circuit | Vegetation | Tree - bark fell into line | 35 | 3255 | 35.0393 | -120.5124 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0017760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908158 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 833261 | 20240201 | 225 | 20240201 | 332 | 2330743 | 67 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 268 | 35.7342 | -120.6045 | No | Overcast-Rain;32-90 F |  |  | 24-0017757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908155 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 833261 | 20240201 | 332 | 20240201 | 1009 | 2330955 | 397 | Distribution Circuit | Animal | Other | 4 | 1589 | 35.7342 | -120.6045 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0017929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908272 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 1827 | 20240201 | 635 | 20240201 | 1117 | 2330839 | 282 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 19176 | 34.8779 | -120.4541 | No | Overcast-Fog;32-90 F | Conductor- Underground | Burned/flashed | 24-0017903 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908262 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 200598 | 20240201 | 700 | 20240201 | 906 | 2330860 | 126 | Distribution Circuit | Environmental/External | Water | 2030 | 45183 | 35.5515 | -121.0724 | No | Overcast;32-90 F | Recloser | Burned/flashed | 24-0017796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908185 | 0 | EPSS Ckt | N | 2024 | B & GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | FUSE | 2767 | 20240201 | 940 | 20240201 | 1142 | 2331130 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 187 | 22814 | 35.4673 | -120.6503 | No | Clear;32-90 F |  |  | 24-0017997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908299 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 20871 | 20240201 | 1109 | 20240201 | 1218 | 2331259 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 1932 | 34.7129 | -120.4708 | No | Partly Cloudy;32-90 F |  |  | 24-0018025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908310 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A02 | 20240201 | 1131 | 20240201 | 1856 | 2331257 | 445 | Distribution Circuit | Equipment Failure/Involved | Overhead | 504 | 55058 | 35.4838 | -120.6846 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0017994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908298 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 3837 | 20240201 | 1335 | 20240201 | 2337 | 2331405 | 602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 13244 | 35.5659 | -121.1021 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0018092 | OH | Sus | 31682879 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908328 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | RECLOSER | M58 | 20240201 | 1348 | 20240202 | 152 | 2331430 | 724 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 4715 | 34.9152 | -120.383 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0018120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908332 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | OTHER | T1194 TWD T2521 | 20240201 | 1428 | 20240201 | 1438 | 2331472 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 17 | 170 | 34.879 | -120.4624 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Underground | Normal | 24-0017903 | UG | Sus | 46176490 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1908342 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | TRANSFORMER | 512922350485 | 20240201 | 1710 | 20240202 | 130 | 2331826 | 500 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 500 | 34.8646 | -120.3605 | No | Overcast-Rain;32-90 F | Fuse | Failed/Faulted | 24-0018386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908447 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 513029454841 | 20240201 | 1755 | 20240202 | 150 | 2331874 | 475 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 475 | 34.9845 | -120.3227 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908435 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 260679 | 20240202 | 29 | 20240202 | 930 | 2332017 | 541 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 11368 | 35.0079 | -120.473 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Broken | 24-0018393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908455 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 6493 | 20240202 | 442 | 20240202 | 639 | 2332114 | 117 | Distribution Circuit | 3rd Party | Vehicle | 3 | 351 | 35.4591 | -120.6817 | No | Clear;32-90 F | Anchor or Guy | Normal | 24-0018414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908465 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | TRANSFORMER | 512435155313 | 20240202 | 708 | 20240203 | 1135 | 2332148 | 1707 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1707 | 34.9941 | -120.5267 | No | Overcast-Drizzle;32-90 F | Fuse | Burned Open | 24-0018937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908836 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 4475 | 20240202 | 811 | 20240202 | 902 | 2332203 | 51 | Distribution Circuit | Vegetation | Tree - bark fell into line | 21 | 1071 | 35.4854 | -120.6736 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0018487 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908555 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14867 | 20240202 | 1419 | 20240202 | 2059 | 2332814 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3600 | 35.5502 | -121.0732 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0018739 | OH | Sus | 46178355 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908653 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | 511875577774 | 20240203 | 916 | 20240203 | 1325 | 2333536 | 249 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 249 | 35.6071 | -120.7368 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0018459 | OH | Sus | 35352540 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1908821 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | JUMPER | 20373 | 20240203 | 1342 | 20240203 | 1705 | 2333720 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 812 | 34.6443 | -120.2209 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Burned Open | 24-0018947 | OH | Sus | 46179081 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1908852 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | SWITCH | UN-NUMBERED SBCO 2 W/OF 512711251967 | 20240203 | 1512 | 20240203 | 2119 | 2333657 | 367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 12845 | 34.9036 | -120.4336 | No | Overcast;32-90 F | Crossarm- Wood | Burned/flashed | 24-0018949 | OH | Sus | 31683342 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908855 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 8641 | 20240204 | 126 | 20240205 | 857 | 2339604 | 1891 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 160185 | 35.0383 | -120.5027 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911382 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512456057313 | 20240204 | 258 | 20240204 | 939 | 2334284 | 401 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1203 | 35.0491 | -120.5218 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Burned Open | 24-0019140 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909027 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 20139 | 20240204 | 306 | 20240204 | 738 | 2334287 | 272 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1814 | 34.73 | -120.4364 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019135 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909022 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 57849 | 20240204 | 322 | 20240204 | 1102 | 2334297 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3680 | 34.6237 | -120.2278 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909007 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | OCB | 1104/2 | 20240204 | 443 | 20240204 | 1210 | 2334372 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 290 | 37005 | 34.8788 | -120.3307 | Yes | Overcast-Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0019130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909017 | 0 | EPSS Ckt | N | 2024 | GRD OC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 378599 | 20240204 | 626 | 20240204 | 1053 | 2334622 | 267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 12903 | 35.2657 | -120.6402 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909130 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2217 | 20240204 | 643 | 20240204 | 735 | 2334689 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 1506 | 35.504 | -120.6053 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019236 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909127 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | FUSE | 10003 | 20240204 | 711 | 20240204 | 842 | 2334844 | 91 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 6734 | 35.2942 | -120.6863 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909186 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | OCB | 1102/2 | 20240204 | 740 | 20240205 | 1415 | 2336106 | 1835 | Distribution Circuit | Vegetation | Tree - fell into line | 6756 | 4444106 | 35.3745 | -120.8556 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019382 | OH | Sus | 35528639 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909266 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | OTHER | WIRE DOWN | 20240204 | 801 | 20240206 | 1102 | 2360908 | 3061 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1982 | 29327 | 35.0849 | -120.5799 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022366 | OH | Sus | 46179674 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1912017 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 10509 | 20240204 | 816 | 20240204 | 1230 | 2335293 | 254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1270 | 35.3839 | -120.8401 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909566 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRIP-SAVER | 4701 | 20240204 | 825 | 20240204 | 2313 | 2335561 | 888 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 43512 | 35.47 | -120.9762 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0019491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909365 | 0 | EPSS Ckt | N | 2024 | A/B
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 789803 | 20240204 | 831 | 20240206 | 1624 | 2357870 | 3353 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 131809 | 35.6948 | -121.2905 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0022645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1912278 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 32285 | 20240204 | 836 | 20240204 | 1806 | 2337793 | 570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 120 | 62035 | 35.5581 | -120.7626 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909542 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | OCB | 1102/2 | 20240204 | 840 | 20240205 | 1818 | 2335581 | 2018 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1442 | 318893 | 34.6967 | -120.1519 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019324 | OH | Sus | 35528784 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909208 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | RECLOSER | Y18 | 20240204 | 845 | 20240204 | 1750 | 2335611 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 536 | 159680 | 34.5941 | -120.1409 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909207 | 0 | EPSS Ckt | N | 2024 | A PH & GRD
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 7299 | 20240204 | 847 | 20240204 | 1230 | 2335708 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 7437 | 34.6579 | -120.3228 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0019461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909336 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | OTHER | WIRE DOWN 1 SOURE OF/CGC 511628466821 | 20240204 | 848 | 20240204 | 1723 | 2335666 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 215 | 5389 | 35.3041 | -120.8072 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0019396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909281 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | FUSE | 1031 | 20240204 | 849 | 20240204 | 1601 | 2335671 | 432 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 4898 | 34.6127 | -120.1785 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0020193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910018 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | 277014 | 20240204 | 851 | 20240204 | 1211 | 2335764 | 200 | Distribution Circuit | Vegetation | Tree - branch fell on line | 365 | 73000 | 34.5994 | -120.0979 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1909217 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | W52 | 20240204 | 854 | 20240205 | 1526 | 2335761 | 1788 | Distribution Circuit | Vegetation | Tree - fell into line | 3558 | 330244 | 35.5577 | -121.0774 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909218 | 0 | EPSS Ckt | N | 2024 | ABC GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | 891294 | 20240204 | 857 | 20240204 | 1829 | 2335801 | 572 | Distribution Circuit | Vegetation | Tree - fell into line | 859 | 264012 | 35.1342 | -120.5702 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1909223 | 0 | EPSS Ckt | N | 2024 | ABC GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 13065 | 20240204 | 857 | 20240204 | 1829 | 2337628 | 572 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8580 | 35.1447 | -120.5831 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909414 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | JUMPER | WIRE DOWN 1 S/S OF MTR 1008700122 | 20240204 | 857 | 20240205 | 924 | 2339365 | 1467 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1467 | 35.1545 | -120.6068 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909579 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 11007 | 20240204 | 857 | 20240205 | 1558 | 2339397 | 1861 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14888 | 35.1558 | -120.5869 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909587 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | TRANSFORMER | 512586756909 | 20240204 | 903 | 20240204 | 2044 | 2335227 | 701 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 9814 | 35.0391 | -120.478 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Arcing | 24-0019379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909264 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | M90 | 20240204 | 905 | 20240204 | 1702 | 2335948 | 477 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5884 | 148945 | 35.0247 | -120.4898 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909237 | 0 | EPSS Ckt | N | 2024 | A&GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | FUSE | 2405 | 20240204 | 906 | 20240206 | 1430 | 2335935 | 3204 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 331416 | 35.1609 | -120.6813 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020279 | OH | Sus | 35528639 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910108 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6181 | 20240204 | 906 | 20240204 | 1025 | 2336023 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 3002 | 35.4415 | -120.6163 | Yes | Clear;32-90 F |  |  | 24-0019472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909347 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | OCB | 1104/2 | 20240204 | 907 | 20240204 | 1210 | 2336010 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 285 | 52155 | 34.8788 | -120.3307 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019374 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909259 | 0 | EPSS Ckt | N | 2024 | GRD TIME OC
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | OTHER | WIRE DOWN AT 20269 | 20240204 | 909 | 20240205 | 1850 | 2353879 | 2021 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 30315 | 34.6019 | -120.1642 | Yes | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910813 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 941946 | 20240204 | 909 | 20240204 | 1717 | 2336008 | 488 | Distribution Circuit | Equipment Failure/Involved | Overhead | 656 | 320128 | 35.5719 | -120.7913 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909246 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 5583 | 20240204 | 909 | 20240205 | 1524 | 2348507 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 41745 | 35.5967 | -120.8294 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1910360 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | JUMPER | BURNED OPEN JMRP 2 LD SIDE OF Q18 | 20240204 | 914 | 20240205 | 1641 | 2337465 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 1800 | 454132 | 35.0401 | -120.525 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019654 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1909516 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 977389 | 20240204 | 914 | 20240205 | 1649 | 2339561 | 1895 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 9475 | 35.028 | -120.5392 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909617 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | JUMPER | JMPRS 1 SPAN S/S OF CGC 512378757268 | 20240204 | 914 | 20240206 | 1330 | 2355127 | 3136 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9408 | 35.0472 | -120.5477 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911021 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | FUSE | 8723 | 20240204 | 919 | 20240204 | 2346 | 2336070 | 867 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 23710 | 34.924 | -120.4372 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Fuse | Failed/Faulted | 24-0021295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911127 | 1 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | OCB | 1104/2 | 20240204 | 926 | 20240204 | 1743 | 2336242 | 497 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1471 | 619692 | 34.6432 | -120.4374 | Yes | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0020212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910038 | 0 | EPSS Ckt | N | 2024 | B-C TIME OC
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | RECLOSER | M46 | 20240204 | 928 | 20240204 | 1048 | 2336375 | 80 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1008 | 80640 | 34.8616 | -120.4506 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909283 | 0 | EPSS Ckt | N | 2024 | AC
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | FUSE | 1499 | 20240204 | 934 | 20240204 | 1833 | 2336458 | 539 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 6468 | 34.9043 | -120.4513 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0020701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910521 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | JUMPER | 6043 | 20240204 | 944 | 20240205 | 1625 | 2340351 | 1841 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1841 | 35.4715 | -120.6773 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0020353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910181 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 30297 | 20240204 | 945 | 20240205 | 1003 | 2336542 | 1458 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 75480 | 35.5022 | -120.7217 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909513 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | V38 | 20240204 | 948 | 20240204 | 1046 | 2336565 | 58 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1500 | 87000 | 35.1274 | -120.5689 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1909309 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 6553 | 20240204 | 951 | 20240206 | 1120 | 2336613 | 2969 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 20317 | 34.6354 | -120.0586 | Yes | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0020012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909846 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512244171018 | 20240204 | 955 | 20240204 | 1429 | 2336228 | 274 | Transformer only | Vegetation | Tree - fell into line | 11 | 3014 | 35.4239 | -120.6044 | Yes | Clear;32-90 F | Secondary | Bent or Twisted | 24-0019497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909371 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | TEMP LR 1101/2 | 20240204 | 957 | 20240204 | 1932 | 2336821 | 575 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2406 | 1383450 | 34.7008 | -120.4358 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909332 | 0 | EPSS Ckt | N | 2024 | A GRD
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 11071 | 20240204 | 958 | 20240204 | 1845 | 2339539 | 527 | Distribution Circuit | Vegetation | Tree - grew into line | 6 | 3162 | 35.0401 | -120.5387 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1909612 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512694454218 | 20240204 | 1003 | 20240205 | 857 | 2341842 | 1374 | Transformer only | Vegetation | Tree - fell into line | 10 | 13740 | 34.9655 | -120.4396 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909857 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | OCB | 1106/2 | 20240204 | 1004 | 20240205 | 1115 | 2336254 | 1511 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4805 | 1303599 | 34.9503 | -120.4441 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909328 | 0 | Non-EPSS | N | 2024 | ABC
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 15081 | 20240204 | 1006 | 20240204 | 1539 | 2335550 | 333 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 399 | 132867 | 35.4058 | -120.8661 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909906 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 5287 | 20240204 | 1009 | 20240204 | 1518 | 2336924 | 309 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 19467 | 35.3721 | -120.6469 | Yes | Clear;32-90 F |  |  | 24-0020128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909957 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | FUSE | 1597 | 20240204 | 1009 | 20240204 | 1940 | 2336934 | 571 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 5139 | 34.7165 | -120.1418 | Yes | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0020829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910647 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 4485 | 20240204 | 1012 | 20240204 | 1545 | 2336970 | 333 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 6075 | 35.5058 | -120.6832 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0019675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909535 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | FUSE | 45473 | 20240204 | 1014 | 20240204 | 1804 | 2336986 | 470 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 94 | 44180 | 34.968 | -120.4512 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910390 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | V82 | 20240204 | 1016 | 20240204 | 2016 | 2340345 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1300 | 565665 | 35.2151 | -120.615 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1910255 | 0 | EPSS Ckt | N | 2024 | ABC/ GRD
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | OCB | 1101/2 | 20240204 | 1017 | 20240206 | 1719 | 2337083 | 3302 | Distribution Circuit | Vegetation | Tree - fell into line | 769 | 603383 | 35.4489 | -120.8704 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909369 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | FUSE | 30073 | 20240204 | 1018 | 20240204 | 1339 | 2337066 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 14070 | 35.6155 | -120.6679 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019744 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909592 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | JUMPER | BLOWN JMPR 1 SS OF 2137 | 20240204 | 1019 | 20240204 | 1516 | 2337093 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3859 | 35.3614 | -120.812 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0019762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1909610 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | RECLOSER | 862544 | 20240204 | 1025 | 20240205 | 2059 | 2340979 | 2074 | Distribution Circuit | Vegetation | Tree - fell into line | 492 | 516762 | 35.0776 | -120.5836 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911183 | 0 | EPSS Ckt | N | 2024 | B SGF
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | TRANSFORMER | 511998478331 | 20240204 | 1028 | 20240205 | 1016 | 2337221 | 1428 | Transformer only | Environmental/External | Water | 10 | 14280 | 35.6227 | -120.6929 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 24-0020090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909919 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 30353 | 20240204 | 1030 | 20240204 | 1540 | 2338747 | 310 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 16120 | 35.6547 | -120.5784 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909510 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1101 | 182571101 | FUSE | 407489 | 20240204 | 1031 | 20240205 | 1628 | 2337270 | 1797 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 5391 | 34.8524 | -120.4187 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912421 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 79117 | 20240204 | 1035 | 20240204 | 1910 | 2338285 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 5665 | 34.6364 | -120.2949 | Yes | Partly Cloudy-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0020637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910455 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 8687 | 20240204 | 1037 | 20240205 | 1927 | 2336721 | 1970 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 31536 | 34.6384 | -120.4225 | Yes | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken | 24-0021634 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911430 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6181 | 20240204 | 1037 | 20240204 | 1509 | 2337333 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 10336 | 35.4415 | -120.6163 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 24-0019606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909473 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | FUSE | 45589 | 20240204 | 1042 | 20240204 | 1530 | 2337531 | 288 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 376 | 108342 | 34.8867 | -120.4356 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909999 | 1 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 45007 | 20240204 | 1042 | 20240205 | 1649 | 2358297 | 1807 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 43368 | 35.0205 | -120.5382 | Yes | Overcast-Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0021661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911446 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | OCB | 1102/2 | 20240204 | 1044 | 20240205 | 1342 | 2337571 | 1591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2122 | 190330 | 34.6255 | -120.1193 | Yes | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909457 | 0 | EPSS Ckt | N | 2024 | T OC/ GRD
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 45127 | 20240204 | 1047 | 20240205 | 1649 | 2339706 | 1802 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 248676 | 35.0276 | -120.5282 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909639 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | 511905076590 | 20240204 | 1050 | 20240205 | 934 | 2337595 | 1364 | Transformer only | Environmental/External | Water | 2 | 2728 | 35.5752 | -120.7245 | Yes | Clear;32-90 F | Jumper | Broken | 24-0021092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910915 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | OCB | 1105/2 | 20240204 | 1053 | 20240205 | 1745 | 2337653 | 1852 | Distribution Circuit | Vegetation | Tree - fell into line | 6419 | 2579141 | 35.1017 | -120.5809 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909563 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | OCB | 2109/2 | 20240204 | 1054 | 20240205 | 1403 | 2338730 | 1629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4262 | 1774846 | 35.555 | -120.6804 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909744 | 0 | EPSS Ckt | N | 2024 | AC T
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 951269 | 20240204 | 1055 | 20240204 | 1437 | 2337641 | 222 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 105 | 23310 | 35.3886 | -120.6123 | Yes | Clear;32-90 F |  |  | 24-0019989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909823 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 45073 | 20240204 | 1059 | 20240205 | 1158 | 2337730 | 1499 | Distribution Circuit | Vegetation | Tree - branch fell on line | 110 | 164890 | 34.8652 | -120.4232 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911405 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 3781 | 20240204 | 1111 | 20240205 | 1451 | 2339672 | 1660 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 38180 | 35.1945 | -120.5639 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911876 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20240204 | 1112 | 20240205 | 1045 | 2337955 | 1413 | Distribution Circuit | Vegetation | Tree - fell into line | 1644 | 872328 | 35.5213 | -120.7125 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909540 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 6023 | 20240204 | 1115 | 20240205 | 918 | 2344445 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 18522 | 35.5204 | -120.7115 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910068 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | JUMPER | OJ AT DDE CGC 512542456003 | 20240204 | 1116 | 20240205 | 1845 | 2337982 | 1889 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 139786 | 35.0141 | -120.4928 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0021337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1911171 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 4975 | 20240204 | 1118 | 20240204 | 1747 | 2338019 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 33843 | 35.3987 | -120.8285 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910304 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 6045 | 20240204 | 1118 | 20240204 | 1340 | 2338277 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 6816 | 35.4966 | -120.6804 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0019833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909673 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | INTERRUPTER | 826612 | 20240204 | 1123 | 20240204 | 1955 | 2338071 | 512 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 697 | 330204 | 34.8828 | -120.4184 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1910601 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | FUSE | 603183 | 20240204 | 1129 | 20240204 | 1306 | 2338147 | 97 | Distribution Circuit | 3rd Party | Metallic Balloon | 517 | 50142 | 34.9312 | -120.4404 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909603 | 1 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | OTHER | WIRE DOWN | 20240204 | 1137 | 20240205 | 1905 | 2342397 | 1888 | Distribution Circuit | Vegetation | Tree - bark fell into line | 88 | 10398 | 35.4555 | -120.6767 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1909914 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 2453 | 20240204 | 1139 | 20240204 | 1907 | 2338373 | 448 | Distribution Circuit | Vegetation | Tree - bark fell into line | 436 | 111178 | 35.3865 | -120.8534 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909731 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 2229 | 20240204 | 1154 | 20240205 | 1005 | 2338757 | 1331 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 25289 | 35.1568 | -120.5272 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021787 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911540 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 507764 | 20240204 | 1157 | 20240205 | 1630 | 2338726 | 1713 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 113 | 193569 | 35.2186 | -120.5962 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910132 | 0 | EPSS Ckt | N | 2024 | A-C
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 7149 | 20240204 | 1200 | 20240204 | 1335 | 2338776 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 4180 | 35.4608 | -120.6726 | Yes | Clear;32-90 F |  |  | 24-0019795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909641 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 635958 | 20240204 | 1211 | 20240205 | 1326 | 2338881 | 1316 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 119401 | 35.3248 | -120.5176 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909799 | 0 | EPSS Ckt | N | 2024 | A-C-GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 2687 | 20240204 | 1224 | 20240204 | 1534 | 2339094 | 190 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 9120 | 35.4921 | -120.647 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909907 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | 277014 | 20240204 | 1225 | 20240204 | 1742 | 2339098 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 329 | 104293 | 34.5994 | -120.0979 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Normal | 24-0020572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910395 | 0 | EPSS Ckt | N | 2024 | A B C
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 6887 | 20240204 | 1225 | 20240205 | 1435 | 2349448 | 1570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 56520 | 34.5871 | -120.0619 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Normal | 24-0020583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1910405 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 6017 | 20240204 | 1228 | 20240204 | 1733 | 2339156 | 305 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1830 | 35.5401 | -120.7229 | Yes | Clear;32-90 F |  |  | 24-0020545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910367 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | W20 | 20240204 | 1229 | 20240205 | 1329 | 2336963 | 1500 | Distribution Circuit | Vegetation | Tree - fell into line | 807 | 205204 | 35.3656 | -120.8403 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909754 | 0 | EPSS Ckt | N | 2024 | A GRD
LOS PADRES | PASO ROBLES | PERRY-1101 | 183071101 | FUSE | 30027 | 20240204 | 1229 | 20240206 | 1254 | 2339174 | 2905 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 40670 | 35.5641 | -120.9066 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910314 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 5181 | 20240204 | 1232 | 20240205 | 2222 | 2339225 | 2030 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 75110 | 35.3618 | -120.8075 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1911702 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 4751 | 20240204 | 1236 | 20240205 | 1405 | 2340091 | 1529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 83127 | 35.5487 | -121.0749 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909679 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14905 | 20240204 | 1237 | 20240205 | 1915 | 2339019 | 1838 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 323488 | 35.5513 | -121.0764 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0019652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909533 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 2553 | 20240204 | 1240 | 20240204 | 2137 | 2339282 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6444 | 35.4749 | -120.6731 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910438 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 99849 | 20240204 | 1250 | 20240205 | 2222 | 2339461 | 2012 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 112672 | 34.6026 | -120.1285 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Deteriorated | 24-0019761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1909609 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | OCB | 1101/2/NORM | 20240204 | 1253 | 20240205 | 1445 | 2338702 | 1530 | Distribution Circuit | Vegetation | Tree - fell into line | 2064 | 842452 | 35.0079 | -120.4539 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909580 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 986322 | 20240204 | 1301 | 20240204 | 1711 | 2340599 | 250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1590 | 397500 | 35.5505 | -121.0725 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0020496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1910320 | 0 | EPSS Ckt | N | 2024 | ABC SGF
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | RECLOSER | 489460 | 20240204 | 1310 | 20240205 | 1605 | 2358052 | 1615 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 19380 | 35.6495 | -121.1908 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912008 | 0 | Non-EPSS | N | 2024 | AB
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14047 | 20240204 | 1317 | 20240206 | 1248 | 2343517 | 2851 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 71275 | 35.553 | -121.0875 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910011 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | FUSE | 7245 | 20240204 | 1321 | 20240205 | 1732 | 2340142 | 1691 | Distribution Circuit | Equipment Failure/Involved | Overhead | 315 | 84203 | 34.9285 | -120.4404 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Cutout- fuse holder | Broken | 24-0020392 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910219 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 20615 | 20240204 | 1324 | 20240204 | 2125 | 2339994 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 10582 | 34.5989 | -120.1285 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910948 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | FUSE | 32699 | 20240204 | 1335 | 20240206 | 1130 | 2340163 | 2755 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 5289 | 35.8632 | -120.7989 | Yes | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0020779 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910597 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512017666519 | 20240204 | 1341 | 20240206 | 910 | 2361271 | 2609 | Transformer only | Vegetation | Tree - branch fell on line | 10 | 26090 | 35.2986 | -120.6764 | Yes | Strong Winds-Rain-Overcast;32-90 F | Crossarm- Wood | Broken | 24-0022472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB |  | 0 | No | No | No | 1912111 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | FUSE | 731993 | 20240204 | 1344 | 20240205 | 1238 | 2340297 | 1374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 6870 | 34.9231 | -120.3563 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909716 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512720753468 | 20240204 | 1348 | 20240205 | 858 | 2340368 | 1150 | Transformer only | Unknown Cause | Patrol - found nothing | 21 | 24150 | 34.945 | -120.4304 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0021671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911452 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 4545 | 20240204 | 1349 | 20240206 | 1941 | 2340390 | 3232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 146 | 40976 | 35.147 | -120.5306 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910212 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 45875 | 20240204 | 1419 | 20240205 | 2223 | 2360879 | 1924 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 7696 | 34.9448 | -120.4896 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0022833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912467 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 20081 | 20240204 | 1424 | 20240205 | 1915 | 2341493 | 1731 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 17310 | 34.6227 | -120.0984 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911088 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 83511 | 20240204 | 1431 | 20240206 | 1003 | 2363341 | 2612 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 7836 | 35.1349 | -120.5085 | Yes | Clear;32-90 F |  |  | 24-0023008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912592 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | 705596 | 20240204 | 1439 | 20240205 | 1850 | 2341961 | 1691 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 184082 | 34.5986 | -120.1926 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020756 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910574 | 0 | EPSS Ckt | N | 2024 | CPHASE & GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 834556 | 20240204 | 1446 | 20240205 | 2034 | 2342209 | 1788 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 98340 | 35.194 | -120.7339 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0021164 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910989 | 0 | EPSS Ckt | N | 2024 | UNKNOWN
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6095 | 20240204 | 1549 | 20240204 | 1710 | 2344389 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 3726 | 35.536 | -120.8438 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910284 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | FUSE | 1467 | 20240204 | 1551 | 20240204 | 1559 | 2344635 | 8 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 173 | 1384 | 34.883 | -120.4279 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0020262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910091 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512156459986 | 20240204 | 1607 | 20240205 | 235 | 2346011 | 628 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 10676 | 35.1202 | -120.6242 | Yes | Overcast-Strong Winds;32-90 F | Fuse | Broken | 24-0021439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911274 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 553705 | 20240204 | 1640 | 20240204 | 2217 | 2346995 | 337 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 25275 | 34.616 | -120.0854 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0021163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910988 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512732851197 | 20240204 | 1644 | 20240205 | 1811 | 2347215 | 1527 | Transformer only | Equipment Failure/Involved | Overhead | 24 | 36648 | 34.8826 | -120.4244 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0021101 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910924 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 951269 | 20240204 | 1713 | 20240204 | 2043 | 2348314 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 14707 | 35.3886 | -120.6123 | Yes | Clear;32-90 F |  |  | 24-0021029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910852 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5031 | 20240204 | 1713 | 20240205 | 1048 | 2349487 | 1055 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 157195 | 35.5561 | -121.0828 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0021788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911541 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | OTHER | 9535 | 20240204 | 1730 | 20240205 | 1936 | 2349069 | 1566 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17226 | 35.55 | -121.0778 | Yes | Partly Cloudy-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | No | 1910460 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 260679 | 20240204 | 1732 | 20240205 | 1521 | 2349169 | 1309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 51051 | 35.0079 | -120.473 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken | 24-0021410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911244 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 10793 | 20240204 | 1740 | 20240205 | 1119 | 2349429 | 1059 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 11649 | 35.2273 | -120.6491 | Yes | Overcast;32-90 F |  |  | 24-0021903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911635 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512102465474 | 20240204 | 1749 | 20240206 | 1231 | 2349677 | 2562 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 52184 | 35.2705 | -120.6471 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911520 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 10485 | 20240204 | 1820 | 20240206 | 2111 | 2349806 | 3051 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 14304 | 35.1492 | -120.5764 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1910626 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512716153905 | 20240204 | 1835 | 20240205 | 1519 | 2350983 | 1244 | Transformer only | Equipment Failure/Involved | Overhead | 26 | 32344 | 34.957 | -120.4322 | Yes | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0020892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910711 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512199862028 | 20240204 | 1858 | 20240205 | 2046 | 2361898 | 1548 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1548 | 35.1768 | -120.6115 | Yes | Overcast-Rain;32-90 F | Secondary | Broken | 24-0022638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912269 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | SWITCH | 5185BP | 20240204 | 1858 | 20240204 | 1912 | 2351560 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 509 | 7126 | 35.1808 | -120.6135 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0019340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1910600 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | FUSE | 6011 | 20240204 | 1912 | 20240205 | 1801 | 2356503 | 1369 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 16428 | 34.9988 | -120.436 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0021442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911277 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511489167111 | 20240204 | 1949 | 20240204 | 2224 | 2353233 | 155 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 155 | 35.311 | -120.854 | Yes | Strong Winds-Overcast;32-90 F | Transformer | Broken | 24-0020954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910774 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | FUSE | 7001 | 20240204 | 2112 | 20240205 | 1023 | 2354799 | 791 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 133679 | 35.0408 | -120.4739 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0021762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911516 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | TRANSFORMER | 512020879247 | 20240204 | 2113 | 20240205 | 1359 | 2354662 | 1006 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 3018 | 35.6478 | -120.6869 | Yes | Partly Cloudy;32-90 F |  |  | 24-0021095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1910918 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512201562045 | 20240204 | 2306 | 20240206 | 1216 | 2361899 | 2230 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2230 | 35.177 | -120.6108 | Yes | Overcast-Drizzle;32-90 F | Secondary | Broken | 24-0022721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912356 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | 277014 | 20240205 | 4 | 20240206 | 1936 | 2355891 | 2612 | Distribution Circuit | Equipment Failure/Involved | Overhead | 329 | 272528 | 34.5994 | -120.0979 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on object | 24-0021326 | OH | Sus | 35528639 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1911160 | 0 | EPSS Ckt | N | 2024 | AB GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 14199 | 20240205 | 655 | 20240206 | 1500 | 2357278 | 1925 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 7700 | 35.2626 | -120.6714 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912337 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9307 | 20240205 | 751 | 20240206 | 139 | 2358029 | 1068 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 8548 | 35.1452 | -120.5833 | No | Overcast-Rain;32-90 F |  |  | 24-0022864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912498 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1106 | 182061106 | FUSE | 45647 | 20240205 | 838 | 20240205 | 1733 | s1912109 | 535 | Distribution Circuit | 3rd Party | Vehicle | 1 | 535 | 34.9369 | -120.4566 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0022470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912109 | 1 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | TRANSFORMER | 512414952105 | 20240205 | 940 | 20240205 | 1538 | 2358522 | 358 | Transformer only | 3rd Party | Other | 1 | 358 | 34.9055 | -120.5312 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0022308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911961 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 15745 | 20240205 | 1023 | 20240205 | 1349 | 2337126 | 206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 334 | 68804 | 35.2673 | -120.6548 | No | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0021737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1911570 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | INTERRUPTER | 91240 | 20240205 | 1033 | 20240205 | 1731 | 2358850 | 418 | Distribution Circuit | Equipment Failure/Involved | Underground | 558 | 162649 | 35.1339 | -120.6047 | No | Overcast-Drizzle;32-90 F | Elbow | Burned/flashed | 24-0021866 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911602 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 6461 | 20240205 | 1057 | 20240205 | 1839 | 2359016 | 462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1386 | 34.9938 | -120.3446 | No | Clear;32-90 F | Insulator | Broken | 24-0021829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911574 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 20519 | 20240205 | 1109 | 20240205 | 1934 | 2359104 | 505 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1515 | 34.6357 | -120.0671 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0021851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1911590 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | JUMPER | #3 PHASE JUMPER OPEN @ CGC# 512657145908 | 20240205 | 1215 | 20240206 | 1814 | 2359537 | 1799 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 17990 | 34.7376 | -120.4462 | No | Overcast;32-90 F | Jumper | Broken | 24-0022428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1912075 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512247059915 | 20240205 | 1441 | 20240206 | 1535 | 2360380 | 1494 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 2988 | 35.1189 | -120.5936 | No | Overcast-Drizzle;32-90 F | Service conductor | Broken- wire on ground | 24-0022667 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912302 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 1139 | 20240205 | 1534 | 20240206 | 1727 | 2360647 | 1553 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7765 | 34.5892 | -120.1063 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1912106 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 8145 | 20240205 | 1544 | 20240205 | 1648 | 2360720 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 3415 | 34.6566 | -120.0884 | No | Overcast-Rain;32-90 F |  |  | 24-0022312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911966 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 10533 | 20240205 | 1545 | 20240205 | 2147 | 2360730 | 362 | Distribution Circuit | 3rd Party | Other | 1 | 362 | 35.2148 | -120.5725 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0022313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1911967 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512114676560 | 20240205 | 1642 | 20240205 | 2139 | 2361107 | 297 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 891 | 35.5749 | -120.6527 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Cutout- fuse holder | Broken | 24-0022646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912279 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512008966521 | 20240205 | 1656 | 20240205 | 1800 | 2361121 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 704 | 35.2986 | -120.6793 | No | Partly Cloudy-Drizzle;32-90 F | Secondary | Broken | 24-0022420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912068 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512693152836 | 20240205 | 1739 | 20240206 | 1338 | 2361386 | 1199 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1199 | 34.9275 | -120.4392 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Broken | 24-0022506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912143 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y62 | 20240205 | 1834 | 20240205 | 1842 | 2361746 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1363 | 10904 | 34.6442 | -120.1155 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0019324 | OH | Sus | 35528784 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912239 | 0 | EPSS Ckt | N | 2024 | NA
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512142176812 | 20240205 | 2136 | 20240206 | 633 | 2362289 | 537 | Transformer only | Environmental/External | Water | 2 | 1074 | 35.5794 | -120.6436 | No | Clear;32-90 F | Fuse | Burned Open | 24-0022868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912502 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | JUMPER | BURN OJ | 20240205 | 2328 | 20240206 | 143 | 2362623 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 291 | 22702 | 35.3543 | -120.7852 | No | Overcast-Rain;32-90 F | Jumper | Burned Open | 24-0022865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1912499 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 45875 | 20240206 | 707 | 20240206 | 930 | 2363141 | 143 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 382 | 34.9448 | -120.4896 | No | Partly Cloudy-Fog-Rain;32-90 F | Customer Equipment | Burned/flashed | 24-0023105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912658 | 1 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46059 | 20240206 | 725 | 20240206 | 917 | 2363180 | 112 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 36 | 4032 | 34.9618 | -120.4099 | No | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0023085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912644 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 3967 | 20240206 | 820 | 20240206 | 1810 | 2363443 | 590 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 5310 | 35.3387 | -120.7574 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | Yes | 1912616 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | TRANSFORMER | T1904 | 20240206 | 847 | 20240206 | 1916 | 2363481 | 629 | Transformer only | Company Initiated | Personnel- company | 44 | 27676 | 35.4569 | -120.6366 | No | Clear;32-90 F | Transformer | Normal | 24-0023127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912665 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | TRANSFORMER | 513687042521 | 20240206 | 923 | 20240206 | 1230 | 2363611 | 187 | Transformer only | Equipment Failure/Involved | Underground | 1 | 187 | 34.6503 | -120.1001 | No | Overcast-Fog-Rain;32-90 F | Fuse | Broken | 24-0023346 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912822 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9283 | 20240206 | 935 | 20240206 | 1216 | 2363674 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 161 | 35.1779 | -120.6105 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912652 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | JUMPER | FB N/OF CGC# 513738843382 | 20240206 | 1043 | 20240206 | 1312 | 2363762 | 149 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1937 | 34.6744 | -120.0832 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0023130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912668 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20240206 | 1231 | 20240206 | 1733 | 2364333 | 302 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 930 | 215343 | 35.4622 | -120.6221 | No | Clear;32-90 F |  |  | 24-0023348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912824 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | OTHER | J256 TWD T0541 | 20240206 | 1327 | 20240206 | 1410 | 2364377 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 1978 | 34.8702 | -120.4103 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0023108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1912827 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 7945 | 20240206 | 1423 | 20240206 | 1433 | 2364661 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 70 | 34.6446 | -120.5106 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0023467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912905 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 8673 | 20240206 | 1429 | 20240206 | 1717 | 2364708 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1176 | 34.5353 | -120.1804 | No | Partly Cloudy;32-90 F |  |  | 24-0023619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913025 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 2473 | 20240206 | 1604 | 20240206 | 1629 | 2365045 | 25 | Distribution Circuit | Equipment Failure/Involved | Underground | 163 | 2365 | 35.1448 | -120.6004 | No | Partly Cloudy;32-90 F | Elbow | Burned/flashed | 24-0021866 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913005 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | OTHER | J256 TWD T0541 | 20240206 | 1847 | 20240206 | 1908 | 2365601 | 21 | Distribution Circuit | Company Initiated | Return Circuit Normal | 46 | 966 | 34.8702 | -120.4103 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0023108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913129 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 7975 | 20240206 | 2056 | 20240206 | 2238 | 2364934 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 2346 | 34.6568 | -120.0898 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0023821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913198 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512458070610 | 20240206 | 2159 | 20240207 | 205 | 2365907 | 246 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 492 | 35.4135 | -120.5306 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913281 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 3939 | 20240207 | 219 | 20240207 | 354 | 2366037 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1805 | 35.5345 | -120.558 | No | Partly Cloudy;32-90 F |  |  | 24-0023935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913296 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRIP-SAVER | 4701 | 20240207 | 916 | 20240207 | 1338 | 2366326 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 12838 | 35.47 | -120.9762 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0023970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913312 | 0 | EPSS Ckt | N | 2024 | NONE
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | TRANSFORMER | 512922350485 | 20240207 | 1028 | 20240208 | 945 | 2366826 | 1397 | Transformer only | 3rd Party | Customer Equipment | 1 | 1397 | 34.8646 | -120.3605 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0024170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913420 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512293754504 | 20240207 | 1039 | 20240207 | 1716 | 2366961 | 397 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 1191 | 34.9706 | -120.5736 | No | Overcast-Rain;32-90 F |  |  | 24-0024234 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913455 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T930485 | 20240207 | 1237 | 20240207 | 2113 | 2367244 | 516 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1548 | 35.0228 | -120.516 | No | Overcast-Rain;32-90 F | Transformer (UG) | Broken | 24-0024344 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913526 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511367972001 | 20240207 | 1536 | 20240208 | 900 | 2367924 | 1044 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 19836 | 35.4446 | -120.8986 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0024645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913705 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | RECLOSER | TEMP LR 1101/2 | 20240207 | 1549 | 20240208 | 526 | 2367979 | 817 | Distribution Circuit | Equipment Failure/Involved | Overhead | 382 | 85997 | 35.2865 | -120.7064 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0024488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1913597 | 0 | EPSS Ckt | N | 2024 | ABC-GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | 42344 | 20240207 | 1558 | 20240207 | 2201 | 2368004 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 340 | 46509 | 35.2316 | -120.6362 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024499 | OH | Sus | 46182166 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913602 | 0 | EPSS Ckt | N | 2024 | C & GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | FUSE | 48923 | 20240207 | 1600 | 20240208 | 1229 | 2368018 | 1229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 449 | 236701 | 35.117 | -120.6118 | No | Overcast-Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0024701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | Yes | 1913752 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | RECLOSER | 442156 | 20240207 | 1600 | 20240208 | 1447 | 2368013 | 438 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1162 | 382740 | 35.1166 | -120.6218 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1913606 | 0 | EPSS Ckt | N | 2024 | ABC-GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V58 | 20240207 | 1604 | 20240207 | 1624 | 2368091 | 20 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5170 | 103400 | 35.247 | -120.6494 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0024512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1913607 | 0 | EPSS Ckt | N | 2024 | ABC TIME
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 13089 | 20240207 | 1608 | 20240208 | 1102 | 2368064 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 51030 | 35.1307 | -120.5736 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913765 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512729951329 | 20240207 | 1611 | 20240207 | 1827 | 2368110 | 136 | Transformer only | Vegetation | Tree - branch fell on line | 21 | 2856 | 34.8862 | -120.4255 | No | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0024620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913685 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 834556 | 20240207 | 1641 | 20240207 | 2339 | 2368214 | 418 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 22990 | 35.194 | -120.7339 | No | Overcast-Rain;32-90 F |  |  | 24-0024574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913649 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | TRANSFORMER | 512729951591 | 20240207 | 1655 | 20240207 | 2333 | 2368202 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 3980 | 34.8936 | -120.4257 | No | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913662 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | JUMPER | OJ 1 N/OF CGC 512480856380 | 20240207 | 1751 | 20240207 | 1845 | 2368399 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 162 | 35.0241 | -120.5136 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1913687 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | RECLOSER | 994498 | 20240207 | 2153 | 20240207 | 2249 | 2368945 | 56 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2455 | 137480 | 35.2794 | -120.6557 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0024926 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913956 | 0 | EPSS Ckt | N | 2024 | A-GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20240208 | 758 | 20240208 | 925 | 2369260 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1724 | 52202 | 35.5213 | -120.7125 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0025999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1914982 | 0 | EPSS Ckt | N | 2024 | C/GRD I
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | FUSE | 1967 | 20240208 | 1024 | 20240209 | 217 | 2369684 | 953 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 29268 | 34.9081 | -120.4362 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0026371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915179 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512640762954 | 20240208 | 1124 | 20240208 | 1532 | 2369909 | 248 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 248 | 35.2046 | -120.462 | No | Clear;32-90 F |  |  | 24-0026468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1915215 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | TRANSFORMER | T1287 | 20240208 | 1129 | 20240208 | 1143 | 2369919 | 14 | Transformer only | Equipment Failure/Involved | Underground | 36 | 504 | 35.2589 | -120.6911 | No | Overcast;32-90 F | Connector or Splice (UG) | Arcing | 24-0026244 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915115 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | JUMPER | OJ SS OF CGC 511618576063 | 20240208 | 1857 | 20240208 | 2240 | 2370870 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 892 | 35.5581 | -120.819 | No | Partly Cloudy;32-90 F | Jumper | Arcing | 24-0026578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1915297 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512577550935 | 20240208 | 2212 | 20240209 | 905 | 2370968 | 653 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2612 | 34.8742 | -120.4755 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0026753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915467 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512711954326 | 20240209 | 1150 | 20240209 | 1335 | 2371266 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 630 | 34.9686 | -120.4339 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0026986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915586 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 10533 | 20240209 | 1220 | 20240212 | 1645 | 2371741 | 4585 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 4585 | 35.2148 | -120.5725 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0027075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915632 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512716254161 | 20240209 | 1317 | 20240209 | 2029 | 2371833 | 432 | Transformer only | Equipment Failure/Involved | Overhead | 76 | 32832 | 34.9641 | -120.4324 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0027185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915700 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | TRANSFORMER | 512292557086 | 20240209 | 1440 | 20240209 | 2054 | 2371966 | 374 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 374 | 35.0421 | -120.5757 | No | Partly Cloudy;32-90 F | Service conductor | Normal | 24-0027117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915656 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512529556748 | 20240209 | 1509 | 20240209 | 2214 | 2371202 | 425 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2550 | 35.0346 | -120.4969 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0027099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915647 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | OTHER | T2609 TWD 6674 | 20240209 | 1614 | 20240209 | 1647 | 2372120 | 33 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 627 | 35.6117 | -120.6833 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0027103 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915666 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | MTR#1010128132 | 20240209 | 1643 | 20240210 | 1222 | 2371920 | 1179 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1179 | 34.6114 | -120.3682 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0027154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915681 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | RECLOSER | V28 | 20240209 | 1817 | 20240210 | 1626 | 2372184 | 1329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 516 | 15058 | 35.0973 | -120.6074 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0027175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915691 | 0 | EPSS Ckt | N | 2024 | NONE
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2803 | 20240209 | 1923 | 20240209 | 2240 | 2372335 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 7092 | 35.3042 | -120.805 | No | Partly Cloudy;32-90 F |  |  | 24-0027194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915708 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512114461043 | 20240210 | 1412 | 20240210 | 1555 | 2372810 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 618 | 35.1487 | -120.6386 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0027432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915874 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512652654392 | 20240210 | 2005 | 20240211 | 100 | 2373018 | 295 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 295 | 34.9701 | -120.4535 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0027553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915990 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 30161 | 20240211 | 1401 | 20240211 | 1408 | 2373316 | 7 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 77 | 35.5871 | -120.6995 | No | Clear;32-90 F |  |  | 24-0027617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916040 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511375971964 | 20240212 | 452 | 20240212 | 1135 | 2373546 | 403 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 6448 | 35.4436 | -120.8959 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0027712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916121 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | RECLOSER | 862544 | 20240212 | 613 | 20240212 | 1903 | 2373569 | 770 | Distribution Circuit | 3rd Party | Vehicle | 2065 | 89045 | 35.0776 | -120.5836 | No | Clear-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0027730 | OH | Sus | 35530981 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1916128 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | OTHER | B PHSE WIRE DOWN AT 513556541116 | 20240212 | 619 | 20240212 | 1408 | 2373641 | 469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 173 | 26940 | 34.6107 | -120.1432 | No | Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0027749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1916137 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512715853377 | 20240212 | 1106 | 20240212 | 1451 | 2373842 | 225 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1800 | 34.9425 | -120.432 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0027873 | OH | Sus | 31683966 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916244 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | T1947 | 20240212 | 1125 | 20240212 | 1916 | 2373960 | 471 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 471 | 35.3567 | -120.8483 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0028092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916323 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | 513567840680 | 20240212 | 1345 | 20240212 | 1409 | 2373977 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 32 | 768 | 34.5991 | -120.1389 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0027985 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916277 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | 513570140679 | 20240212 | 1418 | 20240212 | 1534 | 2373978 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 36 | 2736 | 34.5991 | -120.1379 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0027986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1916278 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | JUMPER | OJ SS CGC 512114461072 | 20240212 | 1640 | 20240212 | 2025 | 2373911 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 7650 | 35.1493 | -120.6388 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0028022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1916297 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 7525 | 20240212 | 1821 | 20240212 | 1906 | 2374373 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 2203 | 35.4843 | -120.6747 | No | Partly Cloudy;32-90 F |  |  | 24-0028091 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916322 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511509169095 | 20240213 | 1032 | 20240213 | 1434 | 2375035 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 3146 | 35.3655 | -120.849 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0028492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916604 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5475 | 20240213 | 1047 | 20240213 | 1214 | 2375059 | 87 | Distribution Circuit | Animal | Bird found | 7 | 637 | 35.5643 | -120.5874 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0028349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916554 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 7555 | 20240213 | 1723 | 20240213 | 1859 | 2375510 | 96 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 160 | 35.5666 | -120.788 | No | Clear;32-90 F |  |  | 24-0028594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916626 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | TRANSFORMER | T2161 | 20240214 | 1020 | 20240214 | 1041 | 2376065 | 21 | Transformer only | Equipment Failure/Involved | Underground | 3 | 63 | 35.4582 | -120.6984 | No | Clear;32-90 F | Secondary | Broken | 24-0028775 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1916826 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 3943 | 20240214 | 1132 | 20240214 | 1646 | 2376229 | 314 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 7222 | 35.4595 | -120.4926 | No | Overcast;32-90 F |  |  | 24-0029165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916919 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | TRANSFORMER | 512899846501 | 20240214 | 1234 | 20240214 | 1359 | 2376284 | 85 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 85 | 34.7547 | -120.3646 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0029011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916878 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512201559050 | 20240214 | 1428 | 20240214 | 1532 | 2376409 | 64 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 128 | 35.0951 | -120.6085 | No | Partly Cloudy;32-90 F |  |  | 24-0029038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1916883 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | P08 | 20240216 | 102 | 20240216 | 112 | 2377719 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 364 | 3605 | 35.6067 | -120.6929 | No | Clear;32-90 F | Recloser | Normal | 24-0015455 | OH | Sus | 46156958 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1917173 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 7187 | 20240216 | 1148 | 20240216 | 1158 | 2378184 | 10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 91 | 910 | 35.4468 | -120.6319 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0029921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917364 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512219959195 | 20240216 | 1257 | 20240216 | 1310 | 2378112 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 286 | 35.0989 | -120.6022 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0029978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917376 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 11543 | 20240216 | 2151 | 20240216 | 2250 | 2378603 | 59 | Distribution Circuit | Environmental/External | Water | 80 | 4722 | 34.9578 | -120.5825 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0030115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917445 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2289 | 20240217 | 843 | 20240217 | 945 | 2378731 | 62 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 62 | 35.2987 | -120.7824 | No | Clear;32-90 F |  |  | 24-0030160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1917491 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 4719 | 20240217 | 1512 | 20240218 | 213 | 2379017 | 661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 22474 | 35.6078 | -121.091 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030276 | OH | Sus | 46192118 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1917558 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14831 | 20240217 | 1601 | 20240217 | 2019 | 2379043 | 258 | Distribution Circuit | 3rd Party | Metallic Balloon | 22 | 5676 | 35.5463 | -121.0723 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0030291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917571 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | RECLOSER | 549904 | 20240218 | 349 | 20240218 | 403 | 2379375 | 14 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 215 | 2452 | 35.2965 | -120.7659 | No | Clear;32-90 F |  |  | 24-0030364 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917643 | 0 | EPSS Ckt | N | 2024 | A&C
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14865 | 20240218 | 719 | 20240218 | 810 | 2379418 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 561 | 35.5505 | -121.0726 | No | Partly Cloudy;32-90 F |  |  | 24-0030378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917654 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 10759 | 20240218 | 957 | 20240218 | 1855 | 2379494 | 538 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 538 | 35.6703 | -121.2784 | No | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Burned/flashed | 24-0030416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1917677 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14829 | 20240218 | 1819 | 20240219 | 1230 | 2379950 | 1091 | Distribution Circuit | 3rd Party | Vehicle | 16 | 17456 | 35.5465 | -121.0715 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0030530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917769 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 409691 | 20240219 | 58 | 20240219 | 710 | 2380261 | 372 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 20460 | 35.194 | -120.7339 | No | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0030612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917852 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | FUSE | 32007 | 20240219 | 116 | 20240219 | 930 | 2380251 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6422 | 35.4684 | -120.668 | No | Clear;32-90 F | Woodpin | Broken | 24-0030598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917838 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20023 | 20240219 | 408 | 20240219 | 1607 | 2380281 | 719 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 18694 | 34.6354 | -120.2811 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0030629 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1917867 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | JUMPER | OPEN CENTER PHASE JUMPER LD SIDE 10309 | 20240219 | 423 | 20240219 | 1111 | 2380411 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 17136 | 35.1016 | -120.5917 | No | Overcast-Fog-Strong Winds;32-90 F | Jumper | Broken | 24-0030633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1917870 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | SWITCH | 66471 | 20240219 | 1040 | 20240219 | 1326 | 2380814 | 166 | Distribution Circuit | Environmental/External | Water | 5 | 830 | 35.692 | -120.8005 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0030700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917953 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511397271737 | 20240219 | 1309 | 20240219 | 1347 | 2381339 | 38 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 532 | 35.4372 | -120.889 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0030854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918033 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 45131 | 20240220 | 607 | 20240220 | 1217 | 2382406 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 8372 | 35.035 | -120.5293 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0031201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1918280 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 15517 | 20240220 | 910 | 20240220 | 930 | 2382630 | 20 | Distribution Circuit | 3rd Party | Kite | 276 | 5520 | 35.1041 | -120.6125 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0031258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918333 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MESA-1103 | 182821103 | RECLOSER | 198354 | 20240220 | 1021 | 20240220 | 1028 | 2382792 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 200 | 1400 | 35.0535 | -120.5279 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 24-0031321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1918389 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SAN LUIS OBISPO | MESA-1103 | 182821103 | RECLOSER | 198354 | 20240220 | 1031 | 20240220 | 1202 | -2382792 | 91 | Distribution Circuit | Equipment Failure/Involved | Overhead | 200 | 18200 | 35.0535 | -120.5279 | No | Partly Cloudy;32-90 F | Recloser | Failed/Faulted | 24-0031321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1918391 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 511547877817 | 20240220 | 1433 | 20240220 | 1721 | 2383095 | 168 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 168 | 35.6053 | -120.8447 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0031652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918494 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | TRANSFORMER | 510761876513 | 20240221 | 1300 | 20240222 | 27 | 2384087 | 687 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 8244 | 35.5632 | -121.1075 | No | Partly Cloudy;32-90 F | Transformer (OH) | Arcing | 24-0032089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918820 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | RECLOSER | R88 | 20240222 | 924 | 20240222 | 1349 | 2385093 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 241 | 22655 | 35.7084 | -120.6137 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0032473 | OH | Sus | 31684887 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1919073 | 0 | EPSS Ckt | N | 2024 | A-B
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512910241160 | 20240222 | 1311 | 20240222 | 1540 | 2385288 | 149 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 149 | 34.6083 | -120.3556 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0032649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919192 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1101 | 182571101 | FUSE | 46315 | 20240222 | 2243 | 20240222 | 2254 | 2385757 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 671 | 34.8597 | -120.4186 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0032944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919371 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 520924 | 20240223 | 1017 | 20240223 | 1101 | 2386156 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 3696 | 35.5345 | -120.5265 | No | Partly Cloudy;32-90 F |  |  | 24-0033150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1919570 | 0 | EPSS Ckt | N | 2024 | B & C PHSE
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512980377849 | 20240223 | 1212 | 20240223 | 1607 | 2386270 | 235 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 235 | 35.616 | -120.363 | No | Partly Cloudy;32-90 F |  |  | 24-0033365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1919631 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 510965074807 | 20240224 | 643 | 20240224 | 945 | 2386657 | 182 | Transformer only | 3rd Party | Customer Equipment | 1 | 182 | 35.5178 | -121.0379 | No | Partly Cloudy;32-90 F | Other | Malfunctioning | 24-0033466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919749 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 6313 | 20240224 | 948 | 20240224 | 1734 | 2387014 | 466 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1865 | 34.958 | -120.5913 | No | Partly Cloudy;32-90 F |  |  | 24-0033540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919796 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | TRANSFORMER | 513112254060 | 20240224 | 1131 | 20240225 | 1353 | 2386825 | 1582 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 1582 | 34.964 | -120.3022 | No | Clear;32-90 F | Transformer | Normal | 24-0026412 | OH | Sus | 35493070 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1919757 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 6313 | 20240224 | 1139 | 20240224 | 1303 | 2386826 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 504 | 34.958 | -120.5913 | No | Partly Cloudy;32-90 F |  |  | 24-0033492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1919764 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X08 | 20240224 | 1403 | 20240224 | 1714 | 2386899 | 191 | Distribution Circuit | Animal | Bird found | 72 | 13752 | 35.7094 | -120.3018 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 24-0033504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1919773 | 0 | EPSS Ckt | N | 2024 | AB
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | FUSE | 45485 | 20240224 | 1924 | 20240224 | 2010 | 2387098 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 150 | 6900 | 34.9682 | -120.4441 | No | Fog;32-90 F | Connector or Splice (OH) | Arcing | 24-0033548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919804 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 10615 | 20240225 | 646 | 20240225 | 842 | 2387258 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2088 | 35.3548 | -120.7864 | No | Overcast;32-90 F |  |  | 24-0033596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1919862 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PALMER 1101 | 183031101 | JUMPER | OJ 3 N/OF HWY 135 (TWD CGC513122346292) | 20240225 | 1500 | 20240225 | 2209 | 2387471 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 7128 | 34.7483 | -120.2917 | No | Clear;32-90 F | Jumper | Burned Open | 24-0033653 | OH | Sus | 31685063 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1919912 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 6845 | 20240225 | 1639 | 20240226 | 1521 | 2387525 | 1362 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 48276 | 34.8317 | -120.2332 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0033671 | OH | Sus | 31685064 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1919919 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 472501 | 20240226 | 722 | 20240226 | 947 | 2387707 | 145 | Distribution Circuit | Animal | Bird found | 5 | 725 | 35.5427 | -120.8277 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0033765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1920116 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | RECLOSER | TEMP LR 1102/2 | 20240227 | 259 | 20240227 | 1025 | 2388607 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2033 | 281870 | 34.6251 | -120.1865 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0034152 | OH | Sus | 46200078 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1920263 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | TRANSFORMER | 512685753710 | 20240227 | 1155 | 20240227 | 1247 | 2388779 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 936 | 34.9515 | -120.4422 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0034273 | OH | Sus | 31685182 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920456 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | FUSE | 2641 | 20240227 | 1216 | 20240227 | 1330 | 2389085 | 74 | Distribution Circuit | Animal | Bird found | 89 | 6586 | 35.5511 | -120.4866 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0034443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1920514 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRIP-SAVER | 6111 | 20240227 | 1245 | 20240228 | 301 | 2389136 | 856 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 62240 | 35.0643 | -120.4971 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0034556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1920536 | 1 | EPSS Ckt | N | 2024 | NONE
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T0364 | 20240227 | 1510 | 20240227 | 1720 | 2389269 | 130 | Transformer only | 3rd Party | Customer Equipment | 16 | 2080 | 35.0365 | -120.4976 | No | Clear;32-90 F | Other | Failed/Faulted | 24-0034594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920550 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512722354387 | 20240227 | 2211 | 20240228 | 51 | 2389502 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 2240 | 34.9703 | -120.4305 | No | Clear;32-90 F | Service conductor | Deteriorated | 24-0034643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920590 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | FUSE | 2895 | 20240228 | 110 | 20240228 | 309 | 2389536 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 351 | 37290 | 35.4511 | -120.9037 | No | Clear;32-90 F |  |  | 24-0034649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920602 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 10585 | 20240228 | 716 | 20240228 | 1335 | 2389738 | 379 | Distribution Circuit | 3rd Party | Vehicle | 1 | 379 | 35.2873 | -120.6648 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0034738 | OH | Sus | 31685215 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920672 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | TRANSFORMER | 512254459679 | 20240228 | 1012 | 20240228 | 1719 | 2389946 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 5124 | 35.1122 | -120.591 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0034934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920831 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1101 | 182611101 | TRANSFORMER | 512020978371 | 20240228 | 1839 | 20240228 | 2307 | 2390337 | 268 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 4288 | 35.6239 | -120.6854 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0035130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1920883 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 2513 | 20240228 | 2023 | 20240228 | 2148 | 2390413 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 4250 | 35.5187 | -120.7008 | No | Clear;32-90 F |  |  | 24-0035181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920910 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | RECLOSER | M20 | 20240228 | 2308 | 20240229 | 203 | 2390436 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 620 | 108500 | 34.8906 | -120.431 | No | Fog;32-90 F | Crossarm- Wood | Broken | 24-0035178 | OH | Sus | 31685284 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920914 | 0 | Non-EPSS | N | 2024 | NONE
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5655 | 20240229 | 4 | 20240229 | 520 | 2390485 | 316 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 17380 | 35.4572 | -120.4631 | No | Overcast;32-90 F |  |  | 24-0035211 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1920927 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 58683 | 20240229 | 5 | 20240229 | 1125 | 2390487 | 680 | Distribution Circuit | Equipment Failure/Involved | Underground | 227 | 100256 | 35.364 | -120.8511 | No | Overcast;32-90 F | Elbow | Burned/flashed | 24-0035206 | UG | Sus | 46200699 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920920 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | TRANSFORMER | 511630066745 | 20240229 | 1021 | 20240229 | 1800 | 2391011 | 459 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 459 | 35.3019 | -120.8067 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 24-0035426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1921080 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | FUSE | 6113 | 20240229 | 1519 | 20240229 | 1700 | 2391479 | 101 | Distribution Circuit | Animal | Bird found | 102 | 10302 | 35.0529 | -120.4864 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0035717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1921196 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | FUSE | 9901 | 20240229 | 2134 | 20240301 | 305 | 2391694 | 331 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 1324 | 35.3041 | -120.8288 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0035828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1921254 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 32445 | 20240301 | 1108 | 20240301 | 1910 | 2391991 | 482 | Distribution Circuit | Equipment Failure/Involved | Underground | 188 | 27859 | 35.7417 | -120.8805 | Yes | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0036128 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921327 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | FUSE | 5707 | 20240302 | 1146 | 20240302 | 1640 | 2394867 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1470 | 35.9307 | -120.6774 | No | Clear;32-90 F |  |  | 24-0036987 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921942 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | TRANSFORMER | 513605945184 | 20240302 | 1401 | 20240302 | 1907 | 2395032 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 306 | 34.7228 | -120.1288 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0036999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921947 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 15081 | 20240302 | 2333 | 20240303 | 852 | 2395664 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 399 | 194570 | 35.4058 | -120.8661 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0037095 | OH | Sus | 31685438 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1922037 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | JUMPER | OJ 1 POLE S/S OF CGC 512026572622 | 20240303 | 1043 | 20240303 | 1248 | 2396010 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 610 | 35.4661 | -120.6794 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0037177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922106 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | SWITCH | 4874 | 20240303 | 1151 | 20240303 | 1327 | 2396073 | 96 | Distribution Circuit | Equipment Failure/Involved | Underground | 53 | 5088 | 35.1355 | -120.6231 | No | Partly Cloudy;32-90 F | Transformer (UG) | Deteriorated | 24-0037180 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922117 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46051 | 20240303 | 1634 | 20240303 | 1715 | 2396260 | 41 | Distribution Circuit | 3rd Party | Metallic Balloon | 28 | 1148 | 34.9602 | -120.4254 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0037246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922159 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T0478 | 20240303 | 2348 | 20240304 | 920 | 2396392 | 572 | Transformer only | Equipment Failure/Involved | Underground | 18 | 10296 | 35.0384 | -120.4924 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 24-0037334 | UG | Sus | 46202542 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922234 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 10491 | 20240304 | 1656 | 20240304 | 1900 | 2397060 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1364 | 35.2147 | -120.592 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0037773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922364 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 10001 | 20240305 | 1108 | 20240305 | 1300 | 2397626 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 112 | 35.2482 | -120.6171 | No | Clear;32-90 F |  |  | 24-0038193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922618 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 43839 | 20240305 | 1259 | 20240305 | 1445 | 2397761 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 106 | 34.9752 | -120.4 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0038207 | OH | Sus | 46203385 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1922623 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 10491 | 20240305 | 1826 | 20240305 | 2054 | 2398013 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1628 | 35.2147 | -120.592 | No | Clear;32-90 F |  |  | 24-0038410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922681 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512707251240 | 20240305 | 2019 | 20240305 | 2119 | 2397956 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 180 | 34.8837 | -120.433 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0038394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922669 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2371 | 20240306 | 149 | 20240306 | 533 | 2398080 | 224 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1568 | 35.5339 | -120.6639 | No | Clear;32-90 F |  |  | 24-0038522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922771 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 10421 | 20240306 | 1359 | 20240306 | 1625 | 2398605 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 292 | 35.504 | -121.019 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 24-0038887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922975 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 510965074807 | 20240306 | 1627 | 20240307 | 43 | 2398719 | 477 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1097 | 35.5178 | -121.0379 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0038942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922993 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20641 | 20240306 | 2030 | 20240307 | 1047 | 2398848 | 857 | Distribution Circuit | Environmental/External | Flood/Erosion | 5 | 4285 | 34.6541 | -120.3143 | No | Overcast-Fog;32-90 F | Pole-Wood | On Ground | 24-0039019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923055 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | SWITCH | 34423 | 20240306 | 2345 | 20240307 | 524 | 2398886 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 339 | 35.5956 | -120.6946 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0038961 | OH | Sus | 35535921 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923059 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 7359 | 20240307 | 837 | 20240307 | 1140 | 2399067 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 89 | 16287 | 34.8511 | -120.254 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0039171 | OH | Sus | 46204663 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1923232 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512560853467 | 20240307 | 1540 | 20240308 | 242 | 2399537 | 662 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1324 | 34.9437 | -120.4836 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0039478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923315 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 45345 | 20240308 | 244 | 20240308 | 530 | 2399763 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 554 | 34.9524 | -120.4471 | No | Fog;32-90 F |  |  | 24-0039602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923393 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1105 | 182581105 | TRANSFORMER | 512045466497 | 20240308 | 935 | 20240308 | 1233 | 2400045 | 178 | Transformer only | Vegetation | Tree - grew into line | 6 | 1068 | 35.2983 | -120.6669 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0039705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923534 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512694453027 | 20240308 | 1216 | 20240308 | 1224 | 2400059 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 120 | 34.9328 | -120.4388 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0039815 | OH | Sus | 46205471 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923577 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | OTHER | J470 TWD T2734 | 20240308 | 1322 | 20240308 | 1410 | 2400156 | 48 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 1248 | 35.4746 | -120.6479 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0039809 | UG | Sus | 35536219 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923585 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512163159956 | 20240308 | 1542 | 20240308 | 1554 | 2400288 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 28 | 336 | 35.1195 | -120.6216 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0039947 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923606 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 510999274116 | 20240308 | 1606 | 20240309 | 400 | 2400371 | 714 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 2142 | 35.4993 | -121.0235 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0039983 | UG | Sus | 46205656 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923621 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 6145 | 20240308 | 1652 | 20240308 | 1946 | 2400395 | 174 | Distribution Circuit | 3rd Party | Vehicle | 18 | 3132 | 34.9554 | -120.5033 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0039930 | OH | Sus | 35536231 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923618 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 512366257137 | 20240308 | 1916 | 20240308 | 1938 | 2400431 | 22 | Transformer only | Equipment Failure/Involved | Underground | 2 | 44 | 35.0435 | -120.5518 | No | Clear;32-90 F | Bus | Deteriorated | 24-0040009 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923627 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 30225 | 20240308 | 2244 | 20240309 | 1517 | 2400516 | 993 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 10820 | 35.4909 | -120.7302 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0040049 | UG | Sus | 46205658 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923665 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 3225 | 20240309 | 237 | 20240309 | 1206 | 2400537 | 569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1138 | 35.3651 | -120.824 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Broken | 24-0040053 | OH | Sus | 46205707 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923670 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512704951204 | 20240309 | 2151 | 20240309 | 2239 | 2401000 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 432 | 34.8827 | -120.4337 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0040171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923828 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 6169 | 20240310 | 1037 | 20240310 | 1216 | 2401174 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 7623 | 35.4805 | -120.6902 | No | Partly Cloudy;32-90 F |  |  | 24-0040190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923863 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T0478 | 20240310 | 1101 | 20240310 | 1851 | 2401182 | 470 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 9015 | 35.0384 | -120.4924 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0040193 | UG | Sus | 46209500 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923866 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T0478 | 20240311 | 828 | 20240311 | 1922 | 2401441 | 654 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 16287 | 35.0384 | -120.4924 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0040368 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924071 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 4719 | 20240311 | 1654 | 20240311 | 1928 | 2402068 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 5236 | 35.6078 | -121.091 | No | Overcast;32-90 F |  |  | 24-0040684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924184 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512112060644 | 20240312 | 1015 | 20240312 | 1354 | 2402632 | 219 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 3066 | 35.1378 | -120.6398 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0040968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924393 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | TRANSFORMER | 511986376780 | 20240313 | 720 | 20240314 | 120 | 2403150 | 1080 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 6480 | 35.5801 | -120.6958 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0041339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924550 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | TRANSFORMER | 511874781553 | 20240313 | 1156 | 20240313 | 1830 | 2403560 | 394 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 394 | 35.7101 | -120.7375 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0041508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924714 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 46347 | 20240313 | 1229 | 20240313 | 1840 | 2403552 | 371 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 371 | 34.759 | -120.3931 | No | Clear;32-90 F |  |  | 24-0041731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924779 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20240313 | 1350 | 20240313 | 1537 | 2403645 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 9900 | 35.3806 | -120.4438 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0041562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924727 | 0 | EPSS Ckt | N | 2024 | NONE
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 29575 | 20240313 | 1445 | 20240313 | 1925 | 2403694 | 280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 110 | 30800 | 34.9648 | -120.5746 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0041601 | OH | Sus | 31686546 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924737 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | SWITCH | 10855 | 20240313 | 1645 | 20240313 | 1821 | 2403806 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 288 | 35.3661 | -120.8402 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924759 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X08 | 20240313 | 1904 | 20240314 | 42 | 2403891 | 338 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 24336 | 35.7094 | -120.3018 | No | Clear;32-90 F |  |  | 24-0041733 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924781 | 0 | EPSS Ckt | N | 2024 | A & B PHSE
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | 705596 | 20240313 | 1908 | 20240313 | 2102 | 2403892 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 179 | 20406 | 34.5986 | -120.1926 | No | Clear;32-90 F |  |  | 24-0041734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924782 | 0 | EPSS Ckt | N | 2024 | B PHSE
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | FUSE | 7465 | 20240314 | 1202 | 20240314 | 1241 | 2405018 | 39 | Distribution Circuit | 3rd Party | Metallic Balloon | 13 | 520 | 34.9283 | -120.4371 | No | Clear;32-90 F | Jumper | Normal | 24-0042157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925138 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511378471975 | 20240314 | 1518 | 20240314 | 1942 | 2405381 | 264 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1584 | 35.4439 | -120.8951 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0042385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925215 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | TRANSFORMER | 512593844858 | 20240314 | 1527 | 20240314 | 1909 | 2404879 | 222 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 3774 | 34.707 | -120.4647 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0042321 | OH | Sus | 31686645 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925201 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X08 | 20240314 | 1553 | 20240314 | 1837 | 2405361 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 11808 | 35.7094 | -120.3018 | No | Clear;32-90 F |  |  | 24-0042354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925207 | 0 | EPSS Ckt | N | 2024 | A&B
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5475 | 20240315 | 654 | 20240315 | 823 | 2405713 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 652 | 35.5643 | -120.5874 | No | Clear;32-90 F |  |  | 24-0042605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925391 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512689053507 | 20240315 | 920 | 20240315 | 1432 | 2406031 | 312 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1248 | 34.946 | -120.441 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0042733 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925539 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | OTHER | WIRE DOWN SS OF CGC# 512269557872 | 20240315 | 1000 | 20240315 | 1458 | 2406101 | 298 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4194 | 55092 | 35.0638 | -120.5843 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0042675 | OH | Sus | 46212399 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1925506 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512606753600 | 20240315 | 1110 | 20240315 | 1347 | 2406261 | 157 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 157 | 34.948 | -120.4685 | No | Clear;32-90 F | Fuse | Burned Open | 24-0042855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925595 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20240315 | 1342 | 20240315 | 1736 | 2406607 | 234 | Distribution Circuit | 3rd Party | Customer Equipment | 184 | 43056 | 34.7206 | -120.4308 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0042839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925587 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | FUSE | 10089 | 20240318 | 53 | 20240318 | 753 | 2407910 | 420 | Distribution Circuit | 3rd Party | Vehicle | 8 | 2975 | 35.2507 | -120.6714 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0043358 | UG | Sus | 35538124 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1926038 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512513653813 | 20240318 | 1432 | 20240319 | 1120 | 2408548 | 1248 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1248 | 34.9528 | -120.4999 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926350 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 6315 | 20240318 | 1504 | 20240318 | 1605 | 2408579 | 61 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 325 | 35.5957 | -120.6949 | No | Clear;32-90 F |  |  | 24-0043698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926337 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X24 | 20240318 | 1652 | 20240319 | 252 | 2408678 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 257 | 48744 | 35.6532 | -120.3636 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0043725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1926346 | 0 | EPSS Ckt | N | 2024 | A B & C PHSE
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512238880135 | 20240318 | 2049 | 20240318 | 2148 | 2408855 | 59 | Transformer only | Animal | Other | 2 | 118 | 35.674 | -120.6138 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0043827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926410 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512620253248 | 20240319 | 908 | 20240319 | 1301 | 2409066 | 233 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 466 | 34.9385 | -120.4637 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926627 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511478370174 | 20240319 | 1001 | 20240319 | 1429 | 2409244 | 268 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 4556 | 35.3948 | -120.8602 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0044029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926622 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | 512171663346 | 20240319 | 1737 | 20240319 | 2337 | 2409648 | 360 | Transformer only | 3rd Party | Metallic Balloon | 1 | 360 | 35.213 | -120.6221 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0044343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926700 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | SWITCH | 45171 | 20240319 | 2116 | 20240320 | 740 | 2409739 | 624 | Distribution Circuit | 3rd Party | Vehicle | 1138 | 207387 | 35.0212 | -120.4741 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0044361 | OH | Sus | 35538653 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1926711 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 370989 | 20240320 | 400 | 20240320 | 633 | 2409808 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3825 | 35.4895 | -120.551 | No | Partly Cloudy;32-90 F |  |  | 24-0044414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1926745 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512140159304 | 20240320 | 1121 | 20240320 | 1211 | 2410157 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 1050 | 35.1017 | -120.629 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0044580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926939 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | OCB | 1101/2 | 20240320 | 1258 | 20240320 | 1449 | 2410373 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 279 | 30969 | 34.8788 | -120.3308 | No | Clear;32-90 F |  |  | 24-0044655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1926968 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512872552511 | 20240320 | 1304 | 20240320 | 1758 | 2410375 | 294 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 294 | 34.9199 | -120.3784 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926971 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512676153953 | 20240320 | 1433 | 20240321 | 201 | 2410442 | 688 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 688 | 34.9581 | -120.4455 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0044822 | OH | Sus | 31687134 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927017 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512282359422 | 20240320 | 1535 | 20240320 | 2155 | 2410488 | 380 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1140 | 35.1059 | -120.5816 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927021 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512372758581 | 20240320 | 1708 | 20240320 | 2345 | 2410534 | 397 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 794 | 35.0831 | -120.5498 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044880 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927036 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | RECLOSER | 289947 | 20240321 | 649 | 20240321 | 1359 | 2410691 | 430 | Distribution Circuit | 3rd Party | Vehicle | 41 | 9930 | 35.6536 | -120.698 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0045000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1927113 | 0 | EPSS Ckt | N | 2024 | AB
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | SWITCH | 6182SW | 20240321 | 1027 | 20240321 | 1315 | 2411143 | 168 | Distribution Circuit | Equipment Failure/Involved | Underground | 101 | 6828 | 35.7272 | -120.8946 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0045015 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927190 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512399680750 | 20240322 | 759 | 20240322 | 1214 | 2411598 | 255 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 255 | 35.6925 | -120.5602 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0045649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1927503 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | TRANSFORMER | 512025379325 | 20240322 | 1000 | 20240322 | 1853 | 2411846 | 533 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1066 | 35.6502 | -120.6849 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0045718 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927533 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | TRANSFORMER | T636574 | 20240322 | 1201 | 20240322 | 1430 | 2411967 | 149 | Transformer only | Equipment Failure/Involved | Underground | 2 | 298 | 34.623 | -120.2251 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0045697 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927524 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | FUSE | 1965 | 20240322 | 1957 | 20240322 | 2157 | 2412353 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 4200 | 34.9091 | -120.4402 | No | Clear;32-90 F |  |  | 24-0045841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927578 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511496469746 | 20240323 | 426 | 20240323 | 511 | 2412573 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 540 | 35.3832 | -120.8539 | No | Partly Cloudy-Rain;32-90 F | Secondary | Broken | 24-0045908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927644 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 511083782774 | 20240323 | 1400 | 20240323 | 1422 | 2412848 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 110 | 35.7372 | -121.0052 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0046013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927739 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | TRANSFORMER | 511960576484 | 20240323 | 2004 | 20240324 | 1256 | 2413130 | 1012 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 2024 | 35.5719 | -120.7041 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0046118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1927826 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SANTA MARIA-1108 | 182671108 | FUSE | 10627 | 20240324 | 457 | 20240324 | 832 | 2413243 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 4515 | 35.0902 | -120.3741 | No | Clear;32-90 F |  |  | 24-0046155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927872 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 8275 | 20240324 | 1333 | 20240324 | 1442 | 2413435 | 69 | Distribution Circuit | 3rd Party | Other | 144 | 9936 | 34.7047 | -120.4657 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0046204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927905 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | SWITCH | 658458 | 20240324 | 1400 | 20240325 | 620 | 2413450 | 980 | Distribution Circuit | 3rd Party | Vehicle | 236 | 86389 | 35.2574 | -120.6781 | No | Overcast;32-90 F | Interrupter | Broken | 24-0046195 | UG | Sus | 35539680 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927899 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 3937 | 20240324 | 1834 | 20240324 | 2043 | 2413567 | 129 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 2967 | 35.5309 | -120.5781 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0046240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927932 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512704039324 | 20240324 | 2121 | 20240325 | 430 | 2413623 | 429 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 429 | 34.5545 | -120.4236 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0046276 | OH | Sus | 31687785 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927968 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 14393 | 20240325 | 741 | 20240325 | 947 | 2413791 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 756 | 35.195 | -120.566 | No | Clear;32-90 F |  |  | 24-0046408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1928148 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 10441 | 20240325 | 814 | 20240325 | 1635 | 2413850 | 501 | Distribution Circuit | 3rd Party | Customer Equipment | 4 | 2004 | 35.5178 | -121.038 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0046403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1928142 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | FUSE | 1813 | 20240325 | 2239 | 20240326 | 359 | 2414545 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 166 | 53120 | 34.957 | -120.4403 | No | Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0046731 | OH | Sus | 46216288 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | Yes | 1928261 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | 632102 | 20240326 | 306 | 20240326 | 352 | 2414576 | 46 | Distribution Circuit | Animal | Bird found | 121 | 5566 | 34.6335 | -120.188 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0046737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1928268 | 0 | EPSS Ckt | N | 2024 | A/C
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511469071143 | 20240326 | 907 | 20240326 | 1227 | 2415198 | 200 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 200 | 35.4211 | -120.8644 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0046950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928504 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | TRANSFORMER | 512731351668 | 20240326 | 1243 | 20240326 | 1910 | 2415656 | 387 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2709 | 34.8956 | -120.4253 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0046993 | OH | Sus | 31687772 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928521 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 136678 | 20240326 | 1933 | 20240326 | 2255 | 2415974 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 189 | 38178 | 35.1945 | -120.7142 | No | Partly Cloudy;32-90 F |  |  | 24-0047151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1928565 | 0 | EPSS Ckt | N | 2024 | A & C
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | OTHER | WIRE DOWN 3 S/S/O 32697 | 20240326 | 1953 | 20240327 | 448 | 2416046 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 21434 | 35.8283 | -120.7598 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0047162 | OH | Sus | 31688014 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1928580 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 3423 | 20240327 | 1055 | 20240327 | 1155 | 2416491 | 60 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 60 | 35.1124 | -120.6253 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0047406 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1928812 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | FUSE | 45493 | 20240327 | 1735 | 20240327 | 1905 | 2416786 | 90 | Distribution Circuit | 3rd Party | Metallic Balloon | 39 | 3510 | 34.9678 | -120.4339 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0047682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1928894 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 5025 | 20240328 | 655 | 20240328 | 928 | 2417033 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 3060 | 35.6001 | -121.1172 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0047812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1929009 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511516167407 | 20240329 | 1438 | 20240329 | 2205 | 2418251 | 447 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 447 | 35.3193 | -120.8453 | No | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929448 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 9547 | 20240329 | 1835 | 20240330 | 256 | 2418471 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 305 | 8166 | 35.5433 | -121.0727 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048594 | OH | Sus | 46218239 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1929478 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | OTHER | J39658 TWD T2369 | 20240330 | 947 | 20240330 | 1251 | 2418960 | 184 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 368 | 35.6178 | -120.6589 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0048333 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1929588 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 8797 | 20240330 | 1001 | 20240330 | 1234 | 2418913 | 153 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 3213 | 35.0618 | -120.5937 | No | Overcast;32-90 F | Insulator | Broken | 24-0048710 | OH | Sus | 46218387 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1929590 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512714751260 | 20240330 | 1344 | 20240330 | 1827 | 2419020 | 283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3396 | 34.8843 | -120.4305 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0048799 | OH | Sus | 31689067 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929619 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 468301 | 20240330 | 1408 | 20240330 | 1640 | 2419102 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3800 | 35.663 | -120.3949 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0048826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1929640 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 1439 | 20240330 | 2156 | 20240401 | 11 | 2419312 | 1575 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11025 | 34.5974 | -120.2761 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0048878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1929692 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | TRANSFORMER | 512084866052 | 20240331 | 1200 | 20240331 | 2323 | 2419518 | 680 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 6800 | 35.2863 | -120.6534 | No | Partly Cloudy;32-90 F | Transformer (OH) | Contaminated | 24-0048921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929731 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | FUSE | 6011 | 20240331 | 1706 | 20240331 | 1915 | 2419690 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1548 | 34.9988 | -120.436 | No | Clear;32-90 F |  |  | 24-0048935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1929750 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9421 | 20240401 | 702 | 20240401 | 922 | 2419834 | 140 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 420 | 35.1295 | -120.5089 | No | Clear;32-90 F |  |  | 24-0049019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1929835 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9649 | 20240401 | 854 | 20240401 | 958 | 2419971 | 64 | Distribution Circuit | Animal | Bird found | 4 | 256 | 35.1294 | -120.5075 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0049034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1929859 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 3739 | 20240401 | 929 | 20240401 | 1229 | 2419973 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1800 | 35.2961 | -120.6299 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0049035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1929861 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | FUSE | 997669 | 20240401 | 1031 | 20240401 | 1207 | 2420135 | 96 | Distribution Circuit | Animal | Other | 1 | 96 | 34.8845 | -120.2615 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0049172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1929977 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | JUMPER | FB 1 LD SIDE OF CGC 512005372397 | 20240401 | 1718 | 20240401 | 1907 | 2420438 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 3379 | 35.4598 | -120.6865 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0049352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930021 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9403 | 20240402 | 213 | 20240402 | 458 | 2420613 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 96 | 15840 | 35.143 | -120.5462 | No | Clear;32-90 F |  |  | 24-0049459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1930093 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 45511 | 20240402 | 730 | 20240402 | 1108 | 2420679 | 218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 158 | 34444 | 34.9485 | -120.4404 | No | Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0049523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1930150 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 827641 | 20240402 | 1039 | 20240402 | 1209 | 2420964 | 90 | Distribution Circuit | Animal | Other | 1 | 90 | 35.6249 | -120.3608 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0049705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930312 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | 998752 | 20240403 | 1032 | 20240403 | 1246 | 2421735 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1576 | 63577 | 35.6432 | -120.6939 | No | Partly Cloudy;32-90 F |  |  | 24-0050120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | No | No | 1930597 | 0 | EPSS Ckt | N | 2024 | A C DCD
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | SWITCH | 1243 | 20240403 | 2258 | 20240404 | 351 | 2422148 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 5567 | 34.8794 | -120.3337 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0050353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930720 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512705875701 | 20240404 | 521 | 20240404 | 715 | 2422196 | 114 | Transformer only | Animal | Other | 2 | 228 | 35.5588 | -120.4566 | No | Overcast-Rain;32-90 F | Fuse | Normal | 24-0050504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930747 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 30161 | 20240404 | 646 | 20240404 | 847 | 2422207 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1331 | 35.5871 | -120.6995 | No | Clear;32-90 F |  |  | 24-0050554 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930783 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 9383 | 20240404 | 1124 | 20240404 | 1827 | 2422504 | 423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 846 | 35.3028 | -120.7985 | No | Partly Cloudy-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0050828 | OH | Sus | 46220560 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1930878 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | OTHER | Y24 | 20240405 | 43 | 20240405 | 1639 | 2423329 | 956 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 68688 | 34.6331 | -120.4541 | No | Overcast-Fog-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0051105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1931031 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A02 | 20240405 | 54 | 20240405 | 810 | 2423332 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 504 | 117030 | 35.4838 | -120.6846 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 24-0051096 | OH | Sus | 31689825 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931021 | 0 | EPSS Ckt | N | 2024 | A-GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 13055 | 20240405 | 947 | 20240405 | 1631 | 2423902 | 404 | Distribution Circuit | Environmental/External | Lightning | 21 | 4328 | 35.1348 | -120.4848 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0051354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | No | No | 1931243 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | TRANSFORMER | T1099 | 20240405 | 1038 | 20240405 | 1103 | 2423992 | 25 | Transformer only | Equipment Failure/Involved | Underground | 28 | 700 | 35.1093 | -120.5954 | No | Overcast-Drizzle;32-90 F | Secondary | Deteriorated | 24-0051311 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931224 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | INTERRUPTER | 48102 | 20240405 | 1225 | 20240405 | 1300 | 2423600 | 35 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 2660 | 34.9539 | -120.5691 | No | Overcast-Rain;32-90 F | Transformer (UG) | Deteriorated | 24-0051267 | UG | Sus | 35542135 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931201 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 84926 | 20240405 | 1425 | 20240405 | 1548 | 2424245 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 14110 | 35.3873 | -120.8517 | No | Partly Cloudy-Strong Winds;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0051488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931300 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 8497 | 20240405 | 1511 | 20240406 | 442 | 2424227 | 811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 26763 | 35.0675 | -120.4028 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0051540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931330 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | JUMPER | OJS @ LINE & BUCK S/OF CGC-512241557590 | 20240405 | 1602 | 20240405 | 1840 | 2424114 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 790 | 35.0556 | -120.5928 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Deteriorated | 24-0051476 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931292 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46087 | 20240405 | 1610 | 20240405 | 1659 | 2424607 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 539 | 35.0586 | -120.3875 | No | Clear;32-90 F |  |  | 24-0051577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931350 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512608260265 | 20240405 | 1748 | 20240406 | 1115 | 2424771 | 1047 | Transformer only | Environmental/External | Lightning | 1 | 1047 | 35.1321 | -120.4756 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931392 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512021266218 | 20240406 | 130 | 20240406 | 253 | 2425003 | 83 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 664 | 35.2903 | -120.6747 | No | Clear;32-90 F |  |  | 24-0051677 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1931444 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512661153661 | 20240406 | 916 | 20240406 | 1309 | 2425106 | 233 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 5359 | 34.95 | -120.4504 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0051714 | OH | Sus | 46221233 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931490 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | OTHER | T3771 TWD T3772 | 20240406 | 923 | 20240406 | 1119 | 2425164 | 116 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 348 | 35.5927 | -120.6795 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0051706 | UG | Sus | 35541373 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931498 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512163674403 | 20240407 | 621 | 20240407 | 1830 | 2425635 | 729 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 729 | 35.5161 | -120.6349 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051880 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931633 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2939 | 20240407 | 627 | 20240407 | 759 | 2425563 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 276 | 35.513 | -120.639 | No | Partly Cloudy;32-90 F |  |  | 24-0051865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931607 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | FUSE | 11539 | 20240407 | 724 | 20240407 | 1710 | 2425609 | 586 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 15610 | 34.9539 | -120.4535 | No | Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0051876 | UG | Sus | 35542428 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931626 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 46143 | 20240408 | 1057 | 20240408 | 1803 | 2426147 | 426 | Distribution Circuit | 3rd Party | Vehicle | 10 | 1028 | 34.9245 | -120.3477 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0052071 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931867 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511497967384 | 20240408 | 1706 | 20240408 | 1732 | 2426388 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 234 | 35.3184 | -120.8515 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0052284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931926 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N34 | 20240409 | 338 | 20240409 | 344 | 2427018 | 6 | Distribution Circuit | Company Initiated | Operating error | 601 | 3606 | 35.8138 | -120.755 | No | Clear;32-90 F | Recloser | Normal | 24-0052577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932220 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | TRANSFORMER | 512342355235 | 20240409 | 1000 | 20240409 | 1537 | 2426818 | 337 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 337 | 34.9913 | -120.558 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0052550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932206 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 20553 | 20240409 | 1249 | 20240409 | 1607 | 2427108 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2178 | 34.6351 | -120.1134 | No | Clear;32-90 F |  |  | 24-0052780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932273 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512506142959 | 20240409 | 1441 | 20240410 | 212 | 2427139 | 691 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 691 | 34.6551 | -120.4929 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0052743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932264 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512506142960 | 20240409 | 1441 | 20240410 | 212 | 2427138 | 691 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 691 | 34.655 | -120.4929 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0052747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932265 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | OTHER | J6665 TWD T62303 | 20240409 | 1641 | 20240409 | 1734 | 2427313 | 53 | Distribution Circuit | 3rd Party | Vehicle | 2 | 106 | 35.2694 | -120.656 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0052598 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1932274 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | RECLOSER | V86 | 20240410 | 301 | 20240410 | 313 | 2427484 | 12 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 888 | 10656 | 35.33 | -120.8246 | No | Clear;32-90 F |  |  | 24-0052895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932322 | 0 | EPSS Ckt | N | 2024 | BC
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRANSFORMER | 512512758538 | 20240410 | 1246 | 20240411 | 136 | 2427998 | 770 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 770 | 35.0834 | -120.5035 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0053304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932567 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | TRANSFORMER | T1689 | 20240410 | 1650 | 20240411 | 151 | 2428057 | 541 | Distribution Circuit | Equipment Failure/Involved | Underground | 25 | 5725 | 34.6663 | -120.1162 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 24-0053302 | UG | Sus | 35543556 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1932566 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 15159 | 20240411 | 940 | 20240411 | 1149 | 2428451 | 129 | Distribution Circuit | 3rd Party | Other | 6 | 774 | 35.5988 | -121.1219 | No | Clear;32-90 F | Other | Normal | 24-0053513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932797 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 5697 | 20240411 | 1942 | 20240412 | 453 | 2428957 | 551 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 5488 | 35.696 | -120.6801 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0053801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1932881 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 11021 | 20240412 | 27 | 20240412 | 326 | 2429058 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 14310 | 34.8547 | -120.4504 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0053845 | OH | Sus | 31690352 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932926 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | TRANSFORMER | T142584 | 20240412 | 1344 | 20240412 | 1403 | 2429549 | 19 | Transformer only | 3rd Party | Customer Equipment | 1 | 19 | 34.632 | -120.0107 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 24-0054156 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933145 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20637 | 20240413 | 246 | 20240413 | 405 | 2430101 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 553 | 34.6277 | -120.2842 | No | Overcast-Drizzle;32-90 F |  |  | 24-0054321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1933251 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | OTHER | J420 TWD T1580 | 20240413 | 725 | 20240413 | 853 | 2430160 | 88 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 88 | 35.4881 | -120.6646 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 24-0054333 | UG | Sus | 35544101 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933265 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | FUSE | 1965 | 20240413 | 735 | 20240413 | 1354 | 2430166 | 379 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 8848 | 34.9091 | -120.4402 | No | Overcast-Fog-Rain;32-90 F | Cutout- fuse holder | Broken | 24-0054368 | OH | Sus | 46228576 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1933282 | 1 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | TRANSFORMER | 513433541140 | 20240413 | 1057 | 20240413 | 1707 | 2430238 | 370 | Transformer only | Vegetation | Tree - grew into line | 7 | 2590 | 34.6109 | -120.1836 | No | Overcast-Rain;32-90 F | Service conductor | Contaminated | 24-0054414 | OH | Sus | 31690513 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933307 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | FUSE | 7537 | 20240413 | 1224 | 20240413 | 1517 | 2430313 | 173 | Distribution Circuit | Vegetation | Tree - bark fell into line | 14 | 2422 | 34.8836 | -120.4549 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0054490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933365 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512708975675 | 20240413 | 1257 | 20240413 | 1416 | 2430362 | 79 | Transformer only | Animal | Other | 1 | 79 | 35.559 | -120.4547 | No | Overcast-Rain;32-90 F | Transformer (OH) |  | 24-0054477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933355 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | JUMPER | 45449 | 20240413 | 1802 | 20240413 | 2137 | 2430841 | 215 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3655 | 34.8828 | -120.4478 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0054542 | OH | Sus | 31690586 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1933409 | 1 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512943877568 | 20240414 | 823 | 20240414 | 1627 | 2431147 | 484 | Transformer only | Animal | Other | 1 | 484 | 35.6084 | -120.375 | No | Overcast-Rain;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0054719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933580 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512940566568 | 20240414 | 957 | 20240415 | 1317 | 2431204 | 1640 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 4718 | 35.3051 | -120.3673 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0054696 | OH | Sus | 46228745 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933562 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512645151498 | 20240414 | 1222 | 20240415 | 1424 | 2431291 | 1562 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3706 | 34.8903 | -120.4537 | No | Partly Cloudy-Drizzle;32-90 F | Cutout- fuse holder | Broken | 24-0054843 | OH | Sus | 31690667 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933743 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512500153854 | 20240415 | 1341 | 20240415 | 1933 | 2432019 | 352 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 352 | 34.954 | -120.5044 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 24-0055157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933867 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 9191 | 20240415 | 1500 | 20240415 | 1737 | 2432084 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 10519 | 35.5471 | -121.0943 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0055086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933854 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 5025 | 20240416 | 611 | 20240416 | 835 | 2432362 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2880 | 35.6001 | -121.1172 | No | Clear;32-90 F |  |  | 24-0055300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1934001 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | JUMPER | OJ 3 P SS OF CGC# 512012283295 | 20240416 | 904 | 20240416 | 1144 | 2432500 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 160 | 35.7587 | -120.6942 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0055323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934038 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 1459 | 20240416 | 2250 | 20240417 | 110 | 2433073 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 23100 | 34.8964 | -120.4185 | No | Fog;32-90 F |  |  | 24-0055712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1934312 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 11013 | 20240417 | 1039 | 20240418 | 232 | 2433422 | 953 | Distribution Circuit | Equipment Failure/Involved | Underground | 160 | 57905 | 35.0261 | -120.4978 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0055923 | UG | Sus | 35546159 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934514 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512875079828 | 20240417 | 1310 | 20240417 | 1823 | 2433541 | 313 | Transformer only | Equipment Failure/Involved | Underground | 1 | 313 | 35.6699 | -120.3992 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0056035 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934552 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 513766574125 | 20240417 | 1425 | 20240417 | 1924 | 2433607 | 299 | Transformer only | Animal | Bird found | 2 | 598 | 35.5189 | -120.0961 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0056104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934574 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511507969393 | 20240417 | 1615 | 20240417 | 1723 | 2433673 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 952 | 35.3736 | -120.8498 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 24-0056075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934566 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512095874884 | 20240417 | 1635 | 20240417 | 2250 | 2433689 | 375 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 750 | 35.5296 | -120.658 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0056125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934586 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512726354349 | 20240417 | 1812 | 20240417 | 2125 | 2433767 | 193 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 3088 | 34.9693 | -120.429 | No | Clear;32-90 F | Fuse | Broken | 24-0056139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934601 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | 705596 | 20240418 | 612 | 20240418 | 712 | 2433923 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 179 | 10740 | 34.5986 | -120.1926 | No | Overcast-Fog;32-90 F |  |  | 24-0056204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1934665 | 0 | EPSS Ckt | N | 2024 | B/C
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 513151541198 | 20240418 | 1358 | 20240418 | 1410 | 2434138 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 36 | 34.61 | -120.2769 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 24-0056467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934770 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PALMER-1101 | 183031101 | JUMPER | JUMPERS 4P SS OF CGC# 513328045426 | 20240418 | 1405 | 20240418 | 1516 | 2434215 | 71 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 142 | 34.7265 | -120.2242 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0056414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934762 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | FUSE | 92731 | 20240418 | 1619 | 20240419 | 301 | 2434333 | 642 | Distribution Circuit | 3rd Party | Vehicle | 18 | 11556 | 35.1472 | -120.6464 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0056601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | Yes | No | 1934794 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | 420128 | 20240419 | 804 | 20240419 | 1740 | 2434667 | 576 | Distribution Circuit | 3rd Party | Vehicle | 141 | 17988 | 34.6658 | -120.4028 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0056730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1934891 | 0 | EPSS Ckt | N | 2024 | C
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512579250899 | 20240419 | 1541 | 20240419 | 2252 | 2435157 | 431 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 431 | 34.8732 | -120.475 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0057055 | OH | Sus | 31691307 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935062 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46045 | 20240420 | 111 | 20240420 | 234 | 2435333 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 6225 | 34.9571 | -120.4249 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0057106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935113 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512197859659 | 20240420 | 811 | 20240420 | 907 | 2435413 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 952 | 35.1115 | -120.6099 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935190 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | JUMPER | 1 SP LD SIDE OF CGC 512912078907 | 20240420 | 902 | 20240420 | 1312 | 2435434 | 250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 250 | 35.6448 | -120.3859 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0057129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935171 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510833575854 | 20240420 | 1039 | 20240420 | 1105 | 2435484 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 156 | 35.5455 | -121.0828 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0057142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935197 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | FUSE | 9793 | 20240422 | 1100 | 20240422 | 1230 | 2436531 | 90 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 145 | 13050 | 35.2918 | -120.6781 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0057514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935527 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9421 | 20240422 | 1126 | 20240423 | 254 | 2436589 | 928 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2784 | 35.1295 | -120.5089 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0057602 | OH | Sus | 31691855 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | Yes | No | 1935564 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | FUSE | 3369 | 20240422 | 1229 | 20240422 | 1317 | 2436642 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 140 | 6720 | 35.6099 | -120.6587 | No | Clear;32-90 F |  |  | 24-0057606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1935565 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 5967 | 20240422 | 1514 | 20240422 | 1547 | 2436756 | 33 | Distribution Circuit | Animal | Bird found | 57 | 1890 | 35.5048 | -120.7014 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0057711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935598 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | T3000 | 20240422 | 1608 | 20240423 | 15 | 2436817 | 487 | Transformer only | Equipment Failure/Involved | Underground | 1 | 487 | 34.9481 | -120.434 | No | Overcast;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0057740 | UG | Sus | 46232376 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935604 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 15517 | 20240422 | 1938 | 20240422 | 2057 | 2436954 | 79 | Distribution Circuit | 3rd Party | Metallic Balloon | 184 | 14543 | 35.1041 | -120.6125 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0057770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935625 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512542453743 | 20240422 | 2118 | 20240423 | 301 | 2436965 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 343 | 34.9514 | -120.4898 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 24-0057802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935654 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | JUMPER | WIRE BROKEN 1 SS OF 45959 | 20240423 | 353 | 20240423 | 933 | 2437082 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 29606 | 34.909 | -120.3829 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0057807 | OH | Sus | 46232608 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1935660 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 166273 | 20240424 | 1036 | 20240424 | 1233 | 2438218 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 624 | 35.1692 | -120.6433 | No | Overcast;32-90 F |  |  | 24-0058518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936147 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | SWITCH | 85827 | 20240424 | 1058 | 20240424 | 1342 | 2438131 | 164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 284 | 46576 | 35.2933 | -120.678 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0057488 | OH | Sus | 46232182 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936126 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | OTHER | WIRE DOWN HOT 1 SS OF 10335 | 20240424 | 1128 | 20240424 | 1415 | 2438173 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 167 | 35.1033 | -120.5815 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0058490 | OH | Sus | 31692080 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1936133 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512308554081 | 20240424 | 1309 | 20240424 | 1844 | 2438144 | 335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 6562 | 34.9591 | -120.5683 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0058561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936164 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512680578955 | 20240425 | 948 | 20240425 | 1220 | 2438835 | 152 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 152 | 35.6448 | -120.462 | No | Overcast;32-90 F | Metering Equipment | Malfunctioning | 24-0058934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936444 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 53297 | 20240426 | 58 | 20240426 | 158 | 2439436 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 900 | 34.6775 | -120.118 | No | Partly Cloudy;32-90 F |  |  | 24-0059158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1936557 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 738593 | 20240426 | 1226 | 20240426 | 1304 | 2439830 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 38 | 35.2865 | -120.7991 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0059340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936741 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5483 | 20240426 | 1355 | 20240426 | 1544 | 2439904 | 109 | Distribution Circuit | Animal | Bird found | 52 | 5668 | 35.5724 | -120.5886 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0059427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1936770 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512591853817 | 20240426 | 1632 | 20240426 | 2009 | 2440046 | 217 | Transformer only | 3rd Party | Customer Equipment | 1 | 217 | 34.9539 | -120.4735 | No | Partly Cloudy-Strong Winds;32-90 F | Fuse | Broken | 24-0059523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936833 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | FUSE | 45953 | 20240426 | 1645 | 20240427 | 130 | 2440062 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 9414 | 35.0421 | -120.5725 | No | Partly Cloudy-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059491 | OH | Sus | 31692169 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936807 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | RECLOSER | A26 | 20240427 | 1740 | 20240427 | 1927 | 2440762 | 107 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2831 | 302917 | 35.4647 | -120.6506 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0059686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | No | No | 1937005 | 0 | EPSS Ckt | N | 2024 | A B C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 3007 | 20240427 | 2341 | 20240428 | 1808 | 2440875 | 748 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 37209 | 35.2664 | -120.6364 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0059731 | UG | Sus | 35549040 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1937053 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | JUMPER | BURNED OJ 1 SS OF CGC 512299954529 | 20240428 | 1458 | 20240428 | 1949 | 2441103 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4656 | 34.9712 | -120.5713 | No | Clear;32-90 F | Jumper | Burned Open | 24-0059785 | OH | Sus | 46235903 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1937109 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511542767050 | 20240428 | 2247 | 20240429 | 555 | 2441231 | 428 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3604 | 35.3095 | -120.8361 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0059824 | OH | Sus | 31692483 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1937140 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6053 | 20240429 | 813 | 20240429 | 1035 | 2441375 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3550 | 35.5084 | -120.4863 | No | Clear;32-90 F |  |  | 24-0059952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1937312 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 7433 | 20240429 | 1433 | 20240429 | 2317 | 2441881 | 524 | Distribution Circuit | 3rd Party | Vehicle | 96 | 50304 | 35.4689 | -120.6972 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0060115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1937382 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | 511904574423 | 20240430 | 211 | 20240430 | 323 | 2442133 | 72 | Transformer only | Animal | Other | 1 | 72 | 35.5148 | -120.722 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0060220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1937470 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 10299 | 20240430 | 1413 | 20240430 | 1640 | 2442818 | 147 | Distribution Circuit | Animal | Bird found | 54 | 7938 | 35.0726 | -120.5574 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Normal | 24-0060612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1937772 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 513064180190 | 20240430 | 2226 | 20240501 | 18 | 2443026 | 112 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 112 | 35.682 | -120.3367 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0060668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1937809 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512229875729 | 20240501 | 757 | 20240501 | 822 | 2443077 | 25 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 25 | 35.5531 | -120.6133 | No | Clear;32-90 F |  |  | 24-0060754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1937881 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 6741 | 20240501 | 1021 | 20240501 | 1301 | 2443337 | 160 | Distribution Circuit | 3rd Party | Vehicle | 24 | 3840 | 34.6149 | -120.375 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0060918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1938034 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 63397 | 20240502 | 1058 | 20240502 | 1219 | 2444214 | 81 | Distribution Circuit | 3rd Party | Metallic Balloon | 5 | 378 | 34.6476 | -120.3078 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0061286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938357 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511435071275 | 20240502 | 1459 | 20240502 | 1607 | 2444413 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 612 | 35.4244 | -120.8765 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0061425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938411 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 2111 | 20240502 | 1646 | 20240502 | 1756 | 2444482 | 70 | Distribution Circuit | Animal | Bird found | 92 | 6440 | 35.5109 | -120.7079 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0061479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938422 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 6285 | 20240503 | 1234 | 20240503 | 1836 | 2445076 | 362 | Distribution Circuit | 3rd Party | Vehicle | 8 | 844 | 34.66 | -120.5017 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0061748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938695 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 1459 | 20240503 | 2248 | 20240504 | 5 | 2445420 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 12705 | 34.8964 | -120.4185 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0061955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938813 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512864843546 | 20240504 | 844 | 20240504 | 1102 | 2445603 | 138 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 276 | 34.673 | -120.3739 | No | Overcast-Fog;32-90 F |  |  | 24-0062045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1938881 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | OTHER | J6595 TWD T0163 | 20240504 | 848 | 20240504 | 1218 | 2445595 | 210 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 3780 | 35.5208 | -120.7013 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0062001 | UG | Sus | 35549619 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938856 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X10 | 20240504 | 1745 | 20240504 | 2035 | 2446050 | 109 | Distribution Circuit | Animal | Other | 105 | 17640 | 35.5847 | -120.3364 | No | Overcast-Rain;32-90 F | Pothead(Riser Termination) | Normal | 24-0062177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | No | No | 1938956 | 0 | EPSS Ckt | N | 2024 | A- B- C- & GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | FUSE | 8947 | 20240504 | 1903 | 20240505 | 1501 | 2446142 | 1198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 19361 | 34.9871 | -120.4759 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0062232 | OH | Sus | 35550860 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939008 | 1 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 6201 | 20240504 | 1910 | 20240504 | 2202 | 2446149 | 172 | Distribution Circuit | Animal | Other | 3 | 516 | 35.6261 | -120.3576 | No | Partly Cloudy-Drizzle;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0062265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939038 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | FUSE | 14811 | 20240505 | 544 | 20240505 | 720 | 2446280 | 96 | Distribution Circuit | Animal | Bird found | 71 | 6851 | 35.1376 | -120.6395 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0062312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939077 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | SWITCH | 6431 | 20240506 | 115 | 20240506 | 1219 | 2446636 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4648 | 34.6914 | -120.4403 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0062441 | OH | Sus | 35550825 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939192 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | TRANSFORMER | 513660742018 | 20240506 | 531 | 20240506 | 1011 | 2446655 | 280 | Transformer only | Animal | Bird found | 1 | 280 | 34.6362 | -120.1087 | No | Fog;32-90 F | Conductor- Overhead | Broken | 24-0062446 | OH | Sus | 31693219 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939201 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 3007 | 20240506 | 1055 | 20240506 | 1453 | 2447100 | 238 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 9282 | 35.2664 | -120.6364 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0062567 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1939364 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6053 | 20240506 | 2035 | 20240506 | 2157 | 2447493 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2050 | 35.5084 | -120.4863 | No | Clear;32-90 F |  |  | 24-0062821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1939461 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | RECLOSER | 512313 | 20240507 | 500 | 20240507 | 815 | 2447548 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 127 | 24765 | 35.2791 | -120.6501 | No | Clear;32-90 F |  |  | 24-0062844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1939486 | 0 | EPSS Ckt | N | 2024 | A-B
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512745753908 | 20240507 | 1109 | 20240507 | 1247 | 2447901 | 98 | Transformer only | Vegetation | Tree - grew into line | 14 | 1372 | 34.9573 | -120.4223 | No | Clear;32-90 F | Secondary | Arcing | 24-0063124 | OH | Sus | 46239456 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939696 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | JUMPER | OJS 1 SP SS OF CGC 512011079864 | 20240507 | 1642 | 20240507 | 1851 | 2448144 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 516 | 35.665 | -120.6908 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0063251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939739 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512745753908 | 20240507 | 1643 | 20240507 | 1909 | 2448138 | 146 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 14 | 2044 | 34.9573 | -120.4223 | No | Clear;32-90 F | Secondary | Normal | 24-0063239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939734 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510788476675 | 20240507 | 2320 | 20240508 | 135 | 2448301 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 405 | 35.5679 | -121.0985 | No | Clear;32-90 F | Secondary | Broken | 24-0063365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939842 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9649 | 20240508 | 939 | 20240508 | 1752 | 2448608 | 493 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1972 | 35.1294 | -120.5075 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0063765 | OH | Sus | 31693196 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940092 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 6425 | 20240508 | 1132 | 20240508 | 1425 | 2448822 | 173 | Distribution Circuit | Equipment Failure/Involved | Underground | 131 | 6717 | 35.7267 | -120.8717 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0063565 | UG | Sus | 35551382 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940049 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 1463 | 20240508 | 1632 | 20240508 | 1707 | 2449178 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 105 | 34.6381 | -120.2031 | No | Clear;32-90 F |  |  | 24-0063896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940131 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | FUSE | 15785 | 20240508 | 2009 | 20240508 | 2203 | 2449240 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 736 | 83904 | 35.2956 | -120.6721 | No | Clear;32-90 F |  |  | 24-0063929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940153 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512023766377 | 20240508 | 2223 | 20240509 | 215 | 2449279 | 232 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 3944 | 35.2948 | -120.6742 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0063961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940178 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512752139600 | 20240509 | 1044 | 20240509 | 1431 | 2449567 | 227 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 227 | 34.5644 | -120.4091 | No | Clear-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0064184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940402 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511365772024 | 20240509 | 1544 | 20240509 | 2330 | 2450006 | 466 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3728 | 35.4453 | -120.8994 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0064435 | OH | Sus | 31693742 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940469 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 6839 | 20240509 | 1759 | 20240509 | 1841 | 2450116 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 1722 | 35.6414 | -120.5612 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0064446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940475 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | FUSE | 6417 | 20240510 | 855 | 20240510 | 1224 | 2450436 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 2943 | 34.9204 | -120.5224 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0064623 | OH | Sus | 46245260 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1940689 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512311560088 | 20240510 | 1210 | 20240510 | 1549 | 2450869 | 219 | Transformer only | Equipment Failure/Involved | Overhead | 30 | 6570 | 35.1238 | -120.5723 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0064790 | OH | Sus | 31693606 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940747 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 2111 | 20240510 | 1430 | 20240510 | 1550 | 2450991 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 7360 | 35.5109 | -120.7079 | No | Clear;32-90 F |  |  | 24-0064836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940765 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 7433 | 20240510 | 1834 | 20240510 | 2146 | 2451154 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 512 | 34.9533 | -120.4684 | No | Overcast;32-90 F | Fuse | Burned Open | 24-0064873 | OH | Sus | 46245318 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940781 | 1 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | SWITCH | 6126 | 20240511 | 1050 | 20240511 | 1101 | 2451437 | 11 | Distribution Circuit | Equipment Failure/Involved | Underground | 313 | 3443 | 35.5546 | -120.7053 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0064952 | UG | Sus | 35552301 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940890 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 4045 | 20240512 | 1802 | 20240512 | 2004 | 2452177 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 854 | 35.5645 | -120.5406 | No | Partly Cloudy;32-90 F |  |  | 24-0065209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1941060 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 469333 | 20240513 | 1034 | 20240513 | 1422 | 2452602 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 912 | 34.8731 | -120.3046 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0065464 | OH | Sus | 46246418 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1941337 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512694454193 | 20240513 | 1951 | 20240513 | 2120 | 2453086 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 890 | 34.9648 | -120.4396 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0065607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941399 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | T0781 | 20240514 | 700 | 20240514 | 1541 | 2453192 | 521 | Transformer only | Equipment Failure/Involved | Underground | 27 | 14067 | 35.1794 | -120.7321 | No | Overcast;32-90 F | Secondary | Broken | 24-0065752 | UG | Sus | 46246860 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941588 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | TRANSFORMER | 513590541194 | 20240514 | 749 | 20240514 | 1236 | 2453230 | 287 | Transformer only | Animal | Bird found | 2 | 574 | 34.6123 | -120.1317 | No | Overcast-Fog;32-90 F | Transformer | On Ground | 24-0065814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941609 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 30703 | 20240514 | 852 | 20240514 | 1201 | 2453314 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 378 | 35.5139 | -120.2333 | No | Overcast;32-90 F |  |  | 24-0065866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1941628 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | OTHER | T3429 TWD T3430 | 20240515 | 1945 | 20240515 | 2350 | 2454685 | 245 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 7105 | 34.9121 | -120.4198 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0066578 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1941986 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 1889 | 20240515 | 2045 | 20240516 | 253 | s1941994 | 368 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 49680 | 34.8592 | -120.4011 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0066586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1941994 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PALMER-1101 | 183031101 | SWITCH | 1781 | 20240515 | 2155 | 20240516 | 2130 | 2460447 | 1415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 33960 | 34.7938 | -120.2625 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0066513 | OH | Sus | 35553356 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942023 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | SWITCH | 679447 | 20240516 | 1628 | 20240516 | 1735 | 2460847 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 456 | 34.6121 | -120.2799 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0066960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942142 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512698442492 | 20240516 | 1722 | 20240517 | 128 | 2460893 | 486 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 972 | 34.6427 | -120.4292 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0067012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942182 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | RECLOSER | M12 | 20240516 | 2218 | 20240517 | 710 | 2461132 | 532 | Distribution Circuit | 3rd Party | Vehicle | 132 | 29835 | 34.9206 | -120.4648 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0067035 | OH | Sus | 35553430 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1942204 | 0 | Non-EPSS | N | 2024 | C-GRD
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRIP-SAVER | 6111 | 20240517 | 139 | 20240517 | 323 | 2461165 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 175 | 18244 | 35.0643 | -120.4971 | No | Overcast;32-90 F |  |  | 24-0067049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942218 | 1 | EPSS Ckt | N | 2024 | A
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | JUMPER | WIRE DWN JEO 46253 | 20240517 | 740 | 20240517 | 1140 | 2461307 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 12579 | 34.9206 | -120.4974 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0067169 | OH | Sus | 46248280 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1942369 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 9999 | 20240517 | 1455 | 20240517 | 2334 | 2461765 | 519 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 14532 | 35.1876 | -120.5569 | No | Partly Cloudy;32-90 F |  |  | 24-0067408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942455 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 30459 | 20240517 | 1624 | 20240517 | 1711 | 2461816 | 47 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 642 | 35.4756 | -120.6805 | No | Clear;32-90 F | Fuse | Broken | 24-0067403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942450 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 1459 | 20240517 | 2248 | 20240518 | 130 | 2461970 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 26730 | 34.8964 | -120.4185 | No | Overcast;32-90 F |  |  | 24-0067440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942486 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | TRANSFORMER | 512281259380 | 20240518 | 822 | 20240518 | 1340 | 2462094 | 318 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 4452 | 35.1044 | -120.582 | No | Overcast-Rain;32-90 F | Secondary | Broken- wire on ground | 24-0067492 | OH | Sus | 46248882 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942562 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512274658385 | 20240518 | 848 | 20240518 | 938 | 2462112 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 50 | 35.0773 | -120.5827 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0067473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942538 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | JUMPER | OJS 1 1/2 SPANS SS OF CGC 512094572394 | 20240518 | 1231 | 20240518 | 1532 | 2462206 | 181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2172 | 35.4612 | -120.6558 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0067500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942568 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRIP-SAVER | 4701 | 20240518 | 1353 | 20240518 | 1728 | 2462247 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 10535 | 35.47 | -120.9762 | No | Partly Cloudy;32-90 F |  |  | 24-0067549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942590 | 0 | EPSS Ckt | N | 2024 | AB
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511472670353 | 20240518 | 1353 | 20240518 | 1708 | 2462258 | 195 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 4095 | 35.3997 | -120.8623 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0067540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942582 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | FUSE | 45345 | 20240519 | 50 | 20240519 | 1045 | 2462445 | 595 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 2133 | 34.9524 | -120.4471 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0067592 | UG | Sus | 35554161 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942621 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511537768845 | 20240519 | 808 | 20240519 | 1536 | 2462697 | 442 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 8398 | 35.3587 | -120.8392 | No | Overcast;32-90 F | Secondary | Broken | 24-0067646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942681 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 76531 | 20240520 | 1146 | 20240520 | 1629 | 2463287 | 283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2830 | 34.9669 | -120.5738 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0067893 | OH | Sus | 46249308 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942914 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511537768845 | 20240520 | 1231 | 20240520 | 1706 | 2463316 | 275 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 5225 | 35.3587 | -120.8392 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0067987 | OH | Sus | 46249390 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942943 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | JUMPER | 512243958022 | 20240520 | 1448 | 20240520 | 1825 | 2463418 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 868 | 35.0671 | -120.5926 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0067994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942945 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | TRANSFORMER | 414608620973 | 20240520 | 1509 | 20240520 | 1809 | 2463431 | 180 | Transformer only | Equipment Failure/Involved | Underground | 1 | 180 | 35.8955 | -120.821 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0068070 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942973 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 20489 | 20240520 | 1730 | 20240520 | 1825 | 2463599 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 1925 | 34.6363 | -120.1134 | No | Clear;32-90 F |  |  | 24-0068067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942971 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | TRANSFORMER | 513646542070 | 20240520 | 1906 | 20240521 | 717 | 2463643 | 731 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 16625 | 34.6376 | -120.1133 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0068080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942982 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | R26 | 20240521 | 358 | 20240521 | 550 | 2463905 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 638 | 43820 | 35.5898 | -120.6934 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0068121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | No | No | 1943020 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14537 | 20240521 | 1903 | 20240521 | 2313 | 2464725 | 250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 8250 | 35.554 | -120.9289 | No | Clear;32-90 F |  |  | 24-0068552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943303 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 6321 | 20240522 | 1320 | 20240522 | 1757 | 2465221 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 831 | 34.9613 | -120.6136 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0068841 | OH | Sus | 31694579 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1943538 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 20240522 | 1737 | 20240522 | 2004 | 2465360 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 8232 | 35.4345 | -120.2869 | No | Clear;32-90 F |  |  | 24-0068960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943559 | 0 | EPSS Ckt | Y | 2024 | B & C PHSE
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | RECLOSER | M80 | 20240522 | 2102 | 20240523 | 1634 | 2465480 | 1172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 384 | 160160 | 35.0146 | -120.3607 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0068997 | OH | Sus | 46250613 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1943585 | 0 | EPSS Ckt | N | 2024 | B GRD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 510808575792 | 20240522 | 2237 | 20240523 | 259 | 2465485 | 258 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 3354 | 35.5437 | -121.0912 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0069030 | OH | Sus | 31694981 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943614 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511564367301 | 20240522 | 2348 | 20240523 | 515 | 2465531 | 327 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2289 | 35.3167 | -120.829 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0069041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943627 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | FUSE | 8119 | 20240523 | 1013 | 20240524 | 518 | 2465804 | 1145 | Distribution Circuit | Equipment Failure/Involved | Underground | 134 | 33102 | 34.8743 | -120.4458 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0069200 | UG | Sus | 35555397 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1943799 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 2137 | 20240524 | 1410 | 20240524 | 1634 | 2466722 | 144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1728 | 35.3613 | -120.812 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0069843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944079 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | TRANSFORMER | 512082073083 | 20240524 | 1534 | 20240524 | 1830 | 2466775 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 704 | 35.4794 | -120.6612 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0069894 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944101 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | FUSE | 235269 | 20240524 | 2308 | 20240525 | 37 | 2466957 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 801 | 34.9162 | -120.4008 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0069932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944136 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512006566297 | 20240525 | 441 | 20240525 | 906 | 2467268 | 265 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 1325 | 35.2924 | -120.6799 | No | Overcast;32-90 F | Secondary | Broken- wire on ground | 24-0069950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944161 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512835652381 | 20240525 | 1408 | 20240525 | 1517 | 2467434 | 69 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 207 | 34.9162 | -120.3919 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0069988 | OH | Sus | 31695280 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944199 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL 1107 | 182661107 | TRANSFORMER | 512042882766 | 20240525 | 1600 | 20240525 | 2025 | 2467580 | 265 | Transformer only | 3rd Party | Fire- house or bldg. | 8 | 2120 | 35.7451 | -120.682 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944226 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2677 | 20240526 | 834 | 20240526 | 1830 | 2467751 | 596 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 6024 | 35.543 | -120.66 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0070084 | OH | Sus | 46251961 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1944278 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 32399 | 20240526 | 1412 | 20240526 | 1500 | 2467868 | 48 | Distribution Circuit | Animal | Bird found | 2 | 96 | 35.6501 | -120.3638 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944299 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 4015 | 20240526 | 1829 | 20240526 | 2052 | 2467992 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 4004 | 35.5813 | -120.5526 | No | Clear;32-90 F |  |  | 24-0070141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944318 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 8403 | 20240527 | 406 | 20240527 | 659 | 2468058 | 173 | Distribution Circuit | Equipment Failure/Involved | Underground | 167 | 28891 | 34.8652 | -120.4094 | No | Overcast-Fog;32-90 F | Elbow | Failed/Faulted | 24-0070169 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944344 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511546969071 | 20240527 | 2203 | 20240528 | 425 | 2468433 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 3820 | 35.365 | -120.8361 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944445 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 32239 | 20240528 | 517 | 20240528 | 700 | 2468502 | 103 | Distribution Circuit | Animal | Bird found | 2 | 206 | 35.5116 | -120.6356 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Normal | 24-0070302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944461 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | TRANSFORMER | 512104873416 | 20240528 | 616 | 20240528 | 754 | 2468475 | 98 | Transformer only | Animal | Bird found | 3 | 294 | 35.4888 | -120.6538 | No | Partly Cloudy-Fog;32-90 F | Fuse | Failed/Faulted | 24-0070351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944495 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 20237 | 20240528 | 1100 | 20240528 | 1223 | 2468829 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 249 | 34.6277 | -120.1147 | No | Partly Cloudy;32-90 F |  |  | 24-0070511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944640 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512238859436 | 20240528 | 1227 | 20240528 | 1753 | 2468958 | 326 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 326 | 35.1056 | -120.5961 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944680 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 307832 | 20240528 | 1444 | 20240528 | 1502 | 2469135 | 18 | Distribution Circuit | Company Initiated | Personnel- company | 1282 | 23076 | 35.5578 | -120.7747 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944674 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 8047 | 20240528 | 1446 | 20240528 | 1555 | 2469145 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 3036 | 35.0715 | -120.591 | No | Clear;32-90 F |  |  | 24-0070646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944683 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 492068 | 20240529 | 953 | 20240529 | 1434 | 2469737 | 281 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1744 | 439412 | 35.4579 | -120.6602 | No | Clear;32-90 F |  |  | 24-0070863 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944917 | 0 | EPSS Ckt | Y | 2024 | SFG DCD
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X12 | 20240529 | 1833 | 20240529 | 2202 | 2470274 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 10659 | 35.6437 | -120.3772 | No | Clear;32-90 F |  |  | 24-0071120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945017 | 0 | EPSS Ckt | Y | 2024 | A&C
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | SWITCH | 45015 | 20240529 | 2006 | 20240530 | 1601 | 2470404 | 1195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 4845 | 35.6179 | -120.6802 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0071094 | OH | Sus | 31695545 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1945031 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | OTHER | WIRE DOWN @ CGC 512866051389 | 20240530 | 715 | 20240530 | 1252 | 2470537 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 337 | 34.8892 | -120.3802 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0071260 | OH | Sus | 31695761 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1945149 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 2285 | 20240530 | 1134 | 20240530 | 1316 | 2470895 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 510 | 35.2843 | -120.7326 | No | Clear;32-90 F |  |  | 24-0071428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945292 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 317796 | 20240530 | 1912 | 20240530 | 2010 | 2471249 | 58 | Distribution Circuit | Animal | Bird found | 1393 | 78376 | 35.5433 | -120.7453 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | No | No | 1945352 | 0 | EPSS Ckt | Y | 2024 | ABC&GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 511640077578 | 20240531 | 718 | 20240531 | 1523 | 2471475 | 485 | Transformer only | Vegetation | Tree - fell into line | 2 | 970 | 35.599 | -120.813 | No | Clear;32-90 F | Service conductor | Broken | 24-0071886 | OH | Sus | 31695884 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945581 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 245596 | 20240531 | 1429 | 20240531 | 1439 | 2471962 | 10 | Distribution Circuit | Company Initiated | Personnel- company | 67 | 670 | 35.4907 | -120.5433 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0072013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945623 | 0 | EPSS Ckt | Y | 2024 | C PHASE
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | RECLOSER | 773358 | 20240531 | 1538 | 20240531 | 1552 | 2472022 | 14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1754 | 24556 | 34.9325 | -120.445 | No | Clear;32-90 F | Recloser | Burned/flashed | 24-0072037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1945632 | 0 | Non-EPSS | N | 2024 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | R92 | 20240531 | 2016 | 20240531 | 2142 | 2472194 | 86 | Distribution Circuit | Company Initiated | Coordination failure | 2685 | 213558 | 35.5705 | -120.6481 | No | Clear;32-90 F | Recloser | Normal | 24-0072091 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945657 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | PASO ROBLES | PASO ROBLES-1101 | 182611101 | TRANSFORMER | 512004378860 | 20240601 | 808 | 20240601 | 1238 | 2472378 | 270 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 6210 | 35.6374 | -120.6916 | No | Overcast;32-90 F | Transformer (OH) | Broken | 24-0072139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1945711 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | V66 | 20240601 | 1932 | 20240601 | 2256 | 2472837 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 333 | 67932 | 35.3759 | -120.8526 | No | Overcast;32-90 F |  |  | 24-0072237 | OH | Sus | 46254120 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | No | No | 1945796 | 0 | EPSS Ckt | N | 2024 | A- B- C- & TIME OC
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512696554036 | 20240602 | 1814 | 20240602 | 2350 | 2473316 | 336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 10920 | 34.9605 | -120.4388 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0072353 | OH | Sus | 31696120 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1945916 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | JUMPER | OJS 1 SP SOURCE SIDE CGC 513770841952 | 20240603 | 115 | 20240603 | 333 | 2473549 | 138 | Distribution Circuit | 3rd Party | Vehicle | 1 | 138 | 34.6354 | -120.0712 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0072377 | OH | Sus | 35557645 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1945937 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | 104948 | 20240603 | 606 | 20240603 | 1311 | 2473616 | 425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 17985 | 34.759 | -120.4018 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0072424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1945984 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511614467826 | 20240603 | 711 | 20240603 | 1213 | 2473663 | 302 | Transformer only | Animal | Bird found | 1 | 302 | 35.3313 | -120.8124 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0072468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946062 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | RECLOSER | N34 | 20240603 | 1533 | 20240603 | 1837 | 2474320 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 94 | 17296 | 35.8138 | -120.755 | No | Partly Cloudy;32-90 F |  |  | 24-0072707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946195 | 0 | EPSS Ckt | Y | 2024 | AB
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 307832 | 20240604 | 6 | 20240604 | 858 | 2474542 | 532 | Distribution Circuit | Company Initiated | Coordination failure | 1327 | 372658 | 35.5578 | -120.7747 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0072792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946249 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20240604 | 847 | 20240604 | 1126 | 2474746 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 929 | 147711 | 35.4622 | -120.6221 | No | Clear;32-90 F |  |  | 24-0072884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946359 | 0 | EPSS Ckt | Y | 2024 | AC
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | TRANSFORMER | 510773076555 | 20240604 | 1031 | 20240605 | 538 | 2474969 | 1147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 27519 | 35.5645 | -121.1037 | No | Clear-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946620 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | RECLOSER | 1101/2 | 20240604 | 1124 | 20240604 | 1614 | 2475036 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 291 | 77150 | 35.361 | -120.8117 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0073005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946459 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V58 | 20240604 | 1248 | 20240604 | 1345 | 2475134 | 57 | Distribution Circuit | Company Initiated | Coordination failure | 2884 | 164388 | 35.247 | -120.6494 | No | Clear;32-90 F | Recloser | Normal | 24-0073077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946480 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | V82 | 20240604 | 1249 | 20240604 | 1925 | 2475125 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1298 | 111885 | 35.2151 | -120.615 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Multi-Fault | 0 | No | No | No | 1946482 | 0 | EPSS Ckt | Y | 2024 | AC&GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | 934355 | 20240604 | 1253 | 20240604 | 1306 | 2475144 | 13 | Distribution Circuit | Company Initiated | Personnel- company | 36 | 468 | 35.2542 | -120.6279 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946484 | 0 | EPSS Ckt | Y | 2024 | A&C
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | RECLOSER | 514987 | 20240604 | 1627 | 20240605 | 121 | 2475354 | 534 | Distribution Circuit | Vegetation | Tree - bark fell into line | 41 | 21894 | 35.7947 | -120.5837 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0073248 | OH | Sus | 31696264 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1946532 | 0 | EPSS Ckt | Y | 2024 | B
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | JUMPER | OJ CGC 512191871060 | 20240604 | 1707 | 20240604 | 1808 | 2475333 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 305 | 35.4247 | -120.6229 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0073229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1946527 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | FUSE | 45755 | 20240604 | 2130 | 20240605 | 430 | 2475683 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 420 | 34.9386 | -120.4462 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0073338 | OH | Sus | 46255364 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946608 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | RECLOSER | 320270 | 20240605 | 828 | 20240605 | 932 | 2475913 | 64 | Distribution Circuit | 3rd Party | Customer Equipment | 230 | 14720 | 34.5995 | -120.1277 | No | Clear;32-90 F | Generator | Malfunctioning | 24-0073436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | No | No | 1946712 | 0 | EPSS Ckt | Y | 2024 | ABC
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512179075464 | 20240605 | 1118 | 20240605 | 1727 | 2476163 | 369 | Transformer only | 3rd Party | Other | 1 | 369 | 35.5456 | -120.6299 | No | Clear;32-90 F | Service conductor | Broken | 24-0073590 | OH | Sus | 31696054 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946831 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | V64 | 20240605 | 1211 | 20240605 | 1238 | 2476234 | 27 | Distribution Circuit | 3rd Party | Metallic Balloon | 1191 | 32157 | 35.3784 | -120.8554 | No | Clear-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0073599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946836 | 0 | EPSS Ckt | N | 2024 | BC
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | 512696042533 | 20240605 | 1232 | 20240605 | 1329 | 2476247 | 57 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 114 | 34.6419 | -120.4283 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0073653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946861 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | FUSE | 11205 | 20240605 | 1858 | 20240606 | 1420 | 2477024 | 546 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 40810 | 34.6025 | -120.1282 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0073845 | UG | Sus | 46255828 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946967 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | SWITCH | 272452 | 20240605 | 2225 | 20240606 | 206 | 2477148 | 221 | Distribution Circuit | 3rd Party | Vehicle | 29 | 6409 | 35.2521 | -120.6875 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Broken | 24-0073739 | UG | Sus | 35558514 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947010 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | OTHER | J944 TWD T3410 | 20240605 | 2345 | 20240606 | 336 | 2476233 | 231 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 231 | 34.9128 | -120.4483 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0073775 | UG | Sus | 35558373 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947022 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | RECLOSER | W18 | 20240606 | 611 | 20240606 | 1035 | 2477332 | 264 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2386 | 120805 | 35.4245 | -120.8785 | No | Overcast;32-90 F | Insulator | Failed/Faulted | 24-0073951 | OH | Sus | 46256116 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947057 | 0 | EPSS Ckt | N | 2024 | B & DCD & TIME OC
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 46343 | 20240606 | 1320 | 20240606 | 2122 | 2477962 | 482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 668 | 34.7584 | -120.3878 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074281 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947274 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | OTHER | T0213 | 20240606 | 1607 | 20240606 | 1729 | 2478148 | 82 | Transformer only | Company Initiated | Personnel- company | 13 | 1066 | 34.6029 | -120.1264 | No | Clear;32-90 F | Generator | Normal | 24-0074378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947310 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 3583 | 20240606 | 1700 | 20240606 | 1755 | 2478228 | 55 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 55 | 35.1076 | -120.5783 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0074355 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947291 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | OTHER | J432 TWD T2835 | 20240606 | 1748 | 20240606 | 1853 | 2478351 | 65 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 65 | 35.5053 | -120.5267 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0074329 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947307 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | T0213 | 20240606 | 1839 | 20240606 | 1932 | 2478434 | 53 | Transformer only | Company Initiated | Personnel- company | 13 | 689 | 34.6029 | -120.1264 | No | Clear;32-90 F | Generator | Normal | 24-0074396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947323 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 307832 | 20240607 | 517 | 20240607 | 1332 | 2478829 | 495 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1326 | 252708 | 35.5578 | -120.7747 | No | Clear;32-90 F |  |  | 24-0074490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947401 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 46343 | 20240607 | 749 | 20240607 | 816 | 2478914 | 27 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 72 | 34.7584 | -120.3878 | No | Overcast-Fog;32-90 F | Customer Equipment | Failed/Faulted | 24-0074547 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947448 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 2831 | 20240607 | 1054 | 20240607 | 1512 | 2479205 | 258 | Distribution Circuit | Animal | Bird found | 2 | 516 | 35.449 | -120.6342 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0074808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947579 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | TRANSFORMER | 512088680023 | 20240607 | 1532 | 20240607 | 1711 | 2479512 | 99 | Transformer only | Vegetation | Tree - grew into line | 2 | 198 | 35.6695 | -120.6649 | No | Clear;32-90 F | Service conductor | Together | 24-0074856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947607 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20240608 | 559 | 20240609 | 1750 | 2479875 | 2151 | Distribution Circuit | Equipment Failure/Involved | Underground | 732 | 214451 | 35.7811 | -120.9891 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0074921 | UG | Sus | 35559247 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947672 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V58 | 20240608 | 841 | 20240608 | 1044 | 2479960 | 123 | Distribution Circuit | Animal | Bird found | 2883 | 354609 | 35.247 | -120.6494 | No | Overcast;32-90 F | Switch (OH) | Normal | 24-0074933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947696 | 0 | EPSS Ckt | N | 2024 | B GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20240608 | 1646 | 20240608 | 1925 | 2480243 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 34662 | 35.1757 | -120.5255 | No | Partly Cloudy;32-90 F |  |  | 24-0075001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947748 | 0 | EPSS Ckt | Y | 2024 | B&C PHASE
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 3941 | 20240609 | 559 | 20240609 | 801 | 2480413 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 6344 | 35.571 | -120.5607 | No | Partly Cloudy;32-90 F |  |  | 24-0075073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947827 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X12 | 20240610 | 941 | 20240610 | 1112 | 2481214 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 4641 | 35.6437 | -120.3772 | No | Clear;32-90 F |  |  | 24-0075249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948060 | 0 | EPSS Ckt | Y | 2024 | A&B
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | TRANSFORMER | 511990678997 | 20240610 | 1433 | 20240610 | 1626 | 2481527 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 226 | 35.641 | -120.6963 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0075379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1948130 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511144773797 | 20240610 | 1741 | 20240610 | 1840 | 2481713 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 59 | 35.4923 | -120.9756 | No | Clear;32-90 F | Insulator | Broken | 24-0075480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1948165 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6527 | 20240611 | 929 | 20240611 | 1111 | 2482164 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 204 | 35.5497 | -120.7755 | No | Clear;32-90 F |  |  | 24-0075724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948426 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2391 | 20240611 | 1639 | 20240611 | 1745 | 2482598 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 594 | 35.5022 | -120.6636 | No | Clear;32-90 F |  |  | 24-0075978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948515 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | RECLOSER | W58 | 20240612 | 322 | 20240612 | 813 | 2482991 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5033 | 1356678 | 35.4511 | -120.9069 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0076048 | OH | Sus | 46262525 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1948576 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6309 | 20240612 | 717 | 20240612 | 818 | 2483072 | 61 | Distribution Circuit | 3rd Party | Vehicle | 88 | 5368 | 34.9591 | -120.5583 | No | Overcast-Fog;32-90 F | Anchor or Guy | Broken | 24-0076115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948633 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 45183 | 20240612 | 2056 | 20240612 | 2218 | 2484055 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 3198 | 35.0275 | -120.4904 | No | Overcast;32-90 F |  |  | 24-0076485 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948875 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | RECLOSER | Y70 | 20240612 | 2327 | 20240613 | 110 | 2484099 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 5548 | 34.7348 | -120.126 | No | Partly Cloudy;32-90 F |  |  | 24-0076495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948885 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | RECLOSER | 858898 | 20240613 | 719 | 20240613 | 1800 | 2484195 | 641 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 20235 | 34.8684 | -120.2483 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0076529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948919 | 0 | EPSS Ckt | Y | 2024 | B C INST OC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 15921 | 20240613 | 837 | 20240613 | 1120 | 2484296 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 652 | 35.1977 | -120.6076 | No | Overcast;32-90 F |  |  | 24-0076683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949091 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 8683 | 20240613 | 1033 | 20240614 | 241 | 2484511 | 968 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4840 | 34.9113 | -120.4903 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0076637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949065 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | JUMPER | OPEN CHANCE @ SS OF CGC# 511600570343 | 20240613 | 1618 | 20240613 | 1715 | 2484894 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 114 | 35.4006 | -120.8202 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0076869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949139 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511587366756 | 20240613 | 1853 | 20240613 | 2107 | 2484982 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 134 | 35.302 | -120.8208 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0076917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949164 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512325178563 | 20240614 | 724 | 20240614 | 1120 | 2485198 | 236 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 472 | 35.6322 | -120.5833 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0076990 | OH | Sus | 31696879 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949243 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | FUSE | 32015 | 20240614 | 725 | 20240614 | 922 | 2485230 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3978 | 35.4643 | -120.6536 | No | Clear;32-90 F |  |  | 24-0077017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949305 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20240614 | 737 | 20240614 | 1127 | 2485236 | 230 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 932 | 128385 | 35.4622 | -120.6221 | No | Clear;32-90 F |  |  | 24-0076987 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949240 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | FUSE | 46295 | 20240614 | 1135 | 20240614 | 1841 | 2485930 | 426 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 426 | 35.0053 | -120.5106 | No | Clear;32-90 F |  |  | 24-0077276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949443 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | RECLOSER | 1101/2 | 20240614 | 2036 | 20240614 | 2249 | 2486034 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 292 | 33594 | 35.361 | -120.8117 | No | Clear;32-90 F |  |  | 24-0077287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949454 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | FUSE | 5693 | 20240614 | 2048 | 20240614 | 2306 | 2486161 | 138 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 4830 | 35.6724 | -120.6677 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949479 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | RECLOSER | 1101/2 | 20240615 | 352 | 20240615 | 1108 | 2486221 | 436 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 292 | 78166 | 35.361 | -120.8117 | No | Clear;32-90 F |  |  | 24-0077323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949491 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512375852223 | 20240615 | 949 | 20240615 | 1053 | 2486385 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 64 | 34.9092 | -120.5444 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0077360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949531 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | TRANSFORMER | 100000054453 | 20240615 | 1320 | 20240615 | 1413 | 2486509 | 53 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 159 | 35.3539 | -120.7879 | No | Clear;32-90 F |  |  | 24-0077385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949553 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | 2577 | 20240615 | 1353 | 20240615 | 1527 | 2486529 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 668 | 35.5521 | -120.7276 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0077384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949552 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20240615 | 1507 | 20240615 | 1826 | 2486563 | 199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 433 | 86167 | 35.2197 | -120.5967 | No | Clear;32-90 F | Customer Equipment | Broken | 24-0077390 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949555 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | 597930 | 20240615 | 1908 | 20240615 | 2027 | 2486744 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1239 | 97881 | 34.6603 | -120.4533 | No | Clear-Strong Winds;32-90 F |  |  | 24-0077416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949578 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | RECLOSER | 1101/2 | 20240615 | 2008 | 20240615 | 2039 | 2486755 | 31 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 292 | 9052 | 35.361 | -120.8117 | No | Clear-Strong Winds;32-90 F |  |  | 24-0077420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949583 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | 766140 | 20240616 | 712 | 20240616 | 1008 | 2486875 | 176 | Distribution Circuit | Vegetation | Tree - bark fell into line | 139 | 24464 | 35.1494 | -120.5877 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949607 | 0 | EPSS Ckt | Y | 2024 | A
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20240616 | 824 | 20240616 | 1006 | 2486904 | 102 | Distribution Circuit | Animal | Bird found | 1724 | 160764 | 35.5213 | -120.7125 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0077453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949613 | 0 | EPSS Ckt | Y | 2024 | B & GRD
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511422071496 | 20240616 | 1359 | 20240616 | 1747 | 2487000 | 228 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2508 | 35.4305 | -120.8808 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0077502 | OH | Sus | 46264222 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949656 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | 511995773761 | 20240616 | 1400 | 20240616 | 1510 | 2487043 | 70 | Transformer only | Animal | Bird found | 1 | 70 | 35.4974 | -120.6907 | No | Clear;32-90 F | Fuse | Normal | 24-0077497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949651 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 11051 | 20240617 | 147 | 20240617 | 312 | 2487341 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 382 | 32486 | 35.0269 | -120.4913 | No | Clear;32-90 F |  |  | 24-0077557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949702 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | RECLOSER | TEMP LR 1102/2 | 20240617 | 1431 | 20240617 | 1947 | 2487992 | 316 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2035 | 463364 | 34.6251 | -120.1865 | No | Clear-Strong Winds;32-90 F |  |  | 24-0077752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949909 | 0 | EPSS Ckt | Y | 2024 | C-SGF DCD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 79696 | 20240617 | 2146 | 20240618 | 200 | 2488660 | 254 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 131 | 33274 | 35.5731 | -121.0414 | No | Clear;32-90 F |  |  | 24-0077893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949999 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N44 | 20240617 | 2311 | 20240618 | 310 | 2488731 | 239 | Distribution Circuit | Animal | Bird found | 2277 | 495113 | 35.7755 | -120.8971 | No | Clear;32-90 F | Recloser | Normal | 24-0077917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950023 | 0 | EPSS Ckt | Y | 2024 | GRD 50 INST OC
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | TRANSFORMER | 513511840483 | 20240618 | 1430 | 20240618 | 1716 | 2489438 | 166 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 166 | 34.5939 | -120.1569 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0078293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950290 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M26 | 20240618 | 1445 | 20240618 | 2100 | 2489445 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 250 | 31542 | 34.9083 | -120.3283 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0078245 | OH | Sus | 31697760 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1950271 | 0 | EPSS Ckt | Y | 2024 | B-GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 698881 | 20240618 | 1742 | 20240618 | 2004 | 2489521 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 11589 | 35.2688 | -120.6693 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0078279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950283 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20240619 | 33 | 20240619 | 228 | 2489729 | 115 | Distribution Circuit | Animal | Bird found | 932 | 107180 | 35.4622 | -120.6221 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950340 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | OTHER | T2175 TWD J630 | 20240619 | 700 | 20240619 | 1340 | 2489781 | 11 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 429 | 34.6015 | -120.1277 | No | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Burned/flashed | 24-0073845 | UG | Sus | 46255828 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950353 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y10 | 20240619 | 1154 | 20240619 | 1320 | 2490037 | 86 | Distribution Circuit | 3rd Party | Metallic Balloon | 1083 | 93138 | 34.665 | -120.4225 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950455 | 0 | EPSS Ckt | Y | 2024 | C-GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | R94 | 20240619 | 1252 | 20240619 | 1300 | 2489916 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 128 | 1024 | 35.5605 | -120.7743 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950464 | 0 | EPSS Ckt | Y | 2024 | A-B
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 30845 | 20240620 | 1148 | 20240620 | 1236 | 2490814 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 48 | 35.7069 | -120.6094 | No | Clear;32-90 F |  |  | 24-0078710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950619 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512796976860 | 20240620 | 1342 | 20240621 | 223 | 2490899 | 761 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 761 | 35.5877 | -120.4243 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0078821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950658 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | FUSE | 270853 | 20240620 | 1440 | 20240620 | 1708 | 2491025 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 195 | 28825 | 35.1226 | -120.6172 | No | Clear;32-90 F |  |  | 24-0078813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950652 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | FUSE | 14811 | 20240620 | 2141 | 20240620 | 2309 | 2491163 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 9416 | 35.1376 | -120.6395 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0078876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950713 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511565666820 | 20240621 | 1320 | 20240621 | 1354 | 2491741 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 68 | 35.3037 | -120.8281 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0079086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950899 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X08 | 20240622 | 817 | 20240622 | 1124 | 2492361 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 13464 | 35.7094 | -120.3018 | No | Clear;32-90 F |  |  | 24-0079366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951019 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | R82 | 20240624 | 1024 | 20240625 | 137 | 2493669 | 913 | Distribution Circuit | Environmental/External | Lightning | 905 | 75017 | 35.5299 | -120.523 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Multi-Fault | 0 | No | No | No | 1951373 | 0 | EPSS Ckt | Y | 2024 | B-C-GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512709274482 | 20240624 | 1359 | 20240625 | 137 | 2494297 | 698 | Transformer only | Environmental/External | Lightning | 1 | 698 | 35.5224 | -120.4512 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951478 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512702174485 | 20240624 | 1404 | 20240625 | 137 | 2494295 | 693 | Transformer only | Environmental/External | Lightning | 1 | 693 | 35.5226 | -120.4534 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951498 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512698074465 | 20240624 | 1410 | 20240625 | 137 | 2494294 | 687 | Transformer only | Environmental/External | Lightning | 1 | 687 | 35.5222 | -120.4548 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951495 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512709074510 | 20240624 | 1438 | 20240625 | 137 | 2494296 | 659 | Transformer only | Environmental/External | Lightning | 1 | 659 | 35.523 | -120.4515 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951489 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | JUMPER | OJ 2 SS OF CGC 511986678559 | 20240624 | 1517 | 20240624 | 1832 | 2494032 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2145 | 35.6296 | -120.6971 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0079879 | OH | Sus | 35562459 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951479 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y30 | 20240624 | 1602 | 20240624 | 1655 | 2494437 | 53 | Distribution Circuit | Animal | Bird found | 1073 | 37432 | 34.6352 | -120.0891 | No | Clear;32-90 F | Capacitor | Normal | 24-0079911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951501 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | N54 | 20240625 | 604 | 20240625 | 646 | 2494936 | 42 | Distribution Circuit | Company Initiated | Personnel- company | 1316 | 54005 | 35.6543 | -120.7258 | No | Overcast;32-90 F | Transformer (OH) | Broken | 24-0080120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951673 | 0 | EPSS Ckt | Y | 2024 | C & GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | N58 | 20240625 | 901 | 20240625 | 927 | 2495140 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 2197 | 57122 | 35.6286 | -120.6955 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0080203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951780 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | TRANSFORMER | TRANSFORMER MTR#1008268084 | 20240625 | 1007 | 20240625 | 1355 | 2495290 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 228 | 35.6432 | -120.7364 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0080315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951884 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512658963415 | 20240625 | 1222 | 20240625 | 1825 | 2495449 | 363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 2861 | 35.2175 | -120.4576 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0080415 | OH | Sus | 46268512 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951922 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | JUMPER | CENTER PHASE BURNED OJ @ 8921 | 20240625 | 1520 | 20240625 | 1806 | 2495646 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 289 | 36994 | 34.9161 | -120.3742 | No | Clear;32-90 F | Jumper | Burned Open | 24-0080452 | OH | Sus | 46268602 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1951933 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 440856 | 20240625 | 2124 | 20240626 | 444 | 2495934 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 561 | 246840 | 35.4611 | -120.6732 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0080559 | OH | Sus | 46268702 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951983 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | T1196 | 20240626 | 259 | 20240626 | 1136 | 2496062 | 517 | Distribution Circuit | Equipment Failure/Involved | Underground | 199 | 14317 | 35.1717 | -120.6963 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0080645 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952031 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | TRANSFORMER | 512100972185 | 20240626 | 337 | 20240626 | 1121 | 2496074 | 464 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 464 | 35.455 | -120.6538 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0080652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952034 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512338881458 | 20240626 | 346 | 20240626 | 848 | 2496112 | 302 | Transformer only | Animal | Other | 1 | 302 | 35.7138 | -120.5816 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0080735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952142 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 14957 | 20240626 | 800 | 20240626 | 1156 | 2496321 | 236 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 6 | 1416 | 35.2244 | -120.5983 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0080703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952062 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | OCB | 1106/2 | 20240626 | 958 | 20240626 | 1052 | 2496563 | 54 | Distribution Circuit | 3rd Party | Vehicle | 5708 | 308232 | 35.1017 | -120.5811 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0080783 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952189 | 0 | EPSS Ckt | N | 2024 | NONE
LOS PADRES | PASO ROBLES | TEMPLETON SUB | 18305 | OCB | 2200/2 | 20240626 | 1152 | 20240627 | 358 | 2496720 | 966 | Distribution Circuit | 3rd Party | Vehicle | 4318 | 379791 | 35.555 | -120.6805 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0080861 | OH | Sus | 35563222 | SOUTH BAY AND CENTRAL COAST | JUN | Multi-Fault | 0 | No | Yes | No | 1952214 | 0 | Non-EPSS | N | 2024 | ABC GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | RECLOSER | P26 | 20240626 | 1215 | 20240626 | 1432 | 2496808 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 511 | 70007 | 35.629 | -120.6607 | No | Clear;Above 90 |  |  | 24-0080879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952222 | 0 | EPSS Ckt | N | 2024 | C AND GRD
LOS PADRES | PASO ROBLES | PASO ROBLES 1102 | 182611102 | RECLOSER | R64 | 20240626 | 1438 | 20240626 | 1504 | 2496964 | 26 | Distribution Circuit | Equipment Failure/Involved | Underground | 850 | 20405 | 35.6381 | -120.6628 | No | Clear;Above 90 | Recloser | Malfunctioning | 24-0080879 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952248 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 6679 | 20240626 | 2105 | 20240626 | 2243 | 2497196 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1470 | 35.5726 | -120.6016 | No | Clear;32-90 F |  |  | 24-0081091 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952306 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M52 | 20240627 | 825 | 20240627 | 905 | 2497443 | 40 | Distribution Circuit | Company Initiated | Personnel- company | 2 | 80 | 34.9254 | -120.3465 | No | Clear;32-90 F | Recloser | Normal | 24-0081183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952398 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512514551187 | 20240627 | 1028 | 20240627 | 1857 | 2497620 | 509 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 509 | 34.8808 | -120.4979 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0081415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952530 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | RECLOSER | 28088 | 20240627 | 1032 | 20240627 | 1202 | 2497626 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 299 | 26910 | 35.4646 | -120.6762 | No | Clear;32-90 F |  |  | 24-0081252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952486 | 0 | EPSS Ckt | Y | 2024 | A
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 9771 | 20240627 | 1455 | 20240628 | 1700 | 2497825 | 1565 | Distribution Circuit | Equipment Failure/Involved | Underground | 58 | 34416 | 35.369 | -120.8536 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0081457 | UG | Sus | 35563338 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952537 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512687153126 | 20240627 | 1525 | 20240627 | 1745 | 2497845 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 980 | 34.9355 | -120.4413 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0081472 | OH | Sus | 31698619 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1952541 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30645 | 20240628 | 930 | 20240628 | 1305 | 2498281 | 215 | Distribution Circuit | 3rd Party | Vehicle | 31 | 6665 | 35.5122 | -120.6794 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0081650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952686 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | JUMPER | UN-NUMBERED FUSES | 20240628 | 1223 | 20240628 | 1305 | 2498641 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 83 | 3486 | 34.6005 | -120.1284 | No | Clear;32-90 F |  |  | 24-0081819 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952848 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y02 | 20240628 | 1251 | 20240628 | 1508 | 2498700 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 549 | 53133 | 34.6503 | -120.0946 | No | Clear;32-90 F |  |  | 24-0081820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952849 | 0 | EPSS Ckt | Y | 2024 | A & B
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | FUSE | 7623 | 20240628 | 1419 | 20240628 | 1615 | 2498779 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 812 | 35.7471 | -120.6139 | No | Clear;32-90 F |  |  | 24-0081928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952891 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 20783 | 20240628 | 2000 | 20240628 | 2114 | 2499005 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 518 | 34.6573 | -120.1176 | No | Clear;32-90 F |  |  | 24-0081972 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952908 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | JUMPER | OJ SS OF 7403 | 20240629 | 320 | 20240629 | 927 | 2499077 | 367 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 11 | 4028 | 35.6851 | -120.695 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0082005 | OH | Sus | 46270360 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952944 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | OCB | 1102/2 | 20240630 | 506 | 20240630 | 746 | 2499589 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6757 | 1081120 | 35.3745 | -120.8556 | No | Overcast;32-90 F | PT/CCVT | Burned/flashed | 24-0082151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1953073 | 0 | EPSS Ckt | Y | 2024 | BC
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | JUMPER | OJ #2 @ 7643 | 20240630 | 1131 | 20240630 | 1501 | 2499741 | 210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 182 | 38220 | 34.8748 | -120.4458 | No | Clear;32-90 F | Jumper | Burned Open | 24-0082196 | OH | Sus | 31698883 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1953109 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | OTHER | WIRE DOWN 1 W/OF CGC#512072579510 | 20240630 | 1416 | 20240630 | 2333 | 2499793 | 524 | Distribution Circuit | Vegetation | Tree - branch fell on line | 348 | 29812 | 35.6557 | -120.6699 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0082217 | OH | Sus | 31698963 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1953131 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | TRANSFORMER | 512089673353 | 20240630 | 1924 | 20240701 | 326 | 2500149 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 964 | 35.487 | -120.6587 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0082248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1953161 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | TEMP LR 1103/2 | 20240630 | 2017 | 20240630 | 2205 | 2500192 | 108 | Distribution Circuit | Animal | Other | 1698 | 48294 | 34.6432 | -120.4375 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0082244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1953157 | 0 | EPSS Ckt | Y | 2024 | AC
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 848137 | 20240701 | 825 | 20240701 | 905 | 2500544 | 40 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 40 | 35.4629 | -120.6373 | No | Clear;32-90 F | Other | Normal | 24-0082333 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953246 | 0 | EPSS Ckt | Y | 2024 | C
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | TRANSFORMER | 514050239841 | 20240701 | 1355 | 20240701 | 1446 | 2500858 | 51 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 51 | 34.5781 | -119.9793 | No | Clear;32-90 F |  |  | 24-0082596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1953361 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | FUSE | 10735 | 20240701 | 1403 | 20240701 | 1515 | 2500976 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 72 | 35.2504 | -120.6702 | No | Clear;32-90 F |  |  | 24-0082592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953360 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 511009276918 | 20240701 | 2249 | 20240702 | 7 | 2501189 | 78 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 156 | 35.5768 | -121.0241 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0082710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953396 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | JUMPER | JMPRS 1 E/O CGC 413760018157 | 20240702 | 1208 | 20240702 | 1620 | 2501902 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3276 | 35.8159 | -121.1014 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0082988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953599 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X12 | 20240702 | 2009 | 20240702 | 2118 | 2503082 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 3519 | 35.6437 | -120.3772 | No | Clear;32-90 F |  |  | 24-0083291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953727 | 0 | EPSS Ckt | Y | 2024 | C
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | FUSE | 32015 | 20240702 | 2302 | 20240703 | 426 | 2503272 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 11016 | 35.4643 | -120.6536 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0083358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953778 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 45083 | 20240703 | 1404 | 20240703 | 1518 | 2503869 | 74 | Distribution Circuit | Animal | Bird found | 17 | 1258 | 34.86 | -120.401 | No | Clear-Heat Wave;32-90 F | Pothead(Riser Termination) | Normal | 24-0083669 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953937 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | FUSE | 45445 | 20240703 | 1625 | 20240704 | 9 | 2504038 | 464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1692 | 34.8657 | -120.3831 | No | Partly Cloudy-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 24-0083759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953968 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | OTHER | J905 TWD T3292 | 20240703 | 1637 | 20240703 | 1732 | 2504066 | 55 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 935 | 34.9778 | -120.4263 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0083706 | UG | Sus | 35564573 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953960 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | R82 | 20240703 | 2134 | 20240703 | 2324 | 2504510 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1719 | 186645 | 35.5299 | -120.523 | No | Clear;32-90 F | Jumper | Burned Open | 24-0083877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954056 | 1 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | RECLOSER | N38 | 20240704 | 931 | 20240704 | 1104 | 2504826 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 9114 | 35.7985 | -120.7392 | No | Clear-Heat Wave;32-90 F |  |  | 24-0083961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954118 | 0 | EPSS Ckt | Y | 2024 | B PHASE AND GRD
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | JUMPER | OJ 2 LD SIDE OF CGC 512691144014 | 20240704 | 1038 | 20240704 | 1333 | 2504999 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 6793 | 34.685 | -120.4312 | No | Clear-Heat Wave;32-90 F | Jumper | Burned Open | 24-0083991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1954133 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | 313404 | 20240704 | 1557 | 20240704 | 1711 | 2505194 | 74 | Distribution Circuit | Animal | Bird found | 1512 | 89848 | 35.63 | -120.6132 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Normal | 24-0084058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954162 | 0 | EPSS Ckt | Y | 2024 | B PHASE AND GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | R86 | 20240704 | 1630 | 20240704 | 2357 | 2505226 | 447 | Distribution Circuit | 3rd Party | Vehicle | 283 | 38400 | 35.5357 | -120.7224 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0084069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1954169 | 0 | EPSS Ckt | Y | 2024 | C- GRD
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512528267132 | 20240704 | 1632 | 20240705 | 330 | 2505250 | 658 | Transformer only | Vegetation | Tree - fell into line | 1 | 658 | 35.3186 | -120.5061 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0084105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1954189 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | OTHER | WIRE DOWN 2/LD SIDE OF 45869 | 20240704 | 1834 | 20240705 | 45 | 2505438 | 371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 34254 | 34.9564 | -120.4511 | No | Clear-Heat Wave;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0084109 | OH | Sus | 46272850 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1954193 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | 42344 | 20240704 | 1929 | 20240704 | 2128 | 2505437 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 341 | 40579 | 35.2316 | -120.6362 | No | Clear-Heat Wave;32-90 F |  |  | 24-0084108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954192 | 0 | EPSS Ckt | Y | 2024 | A&C
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | R76 | 20240704 | 1935 | 20240705 | 352 | 2505440 | 497 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1067 | 60795 | 35.5454 | -120.7081 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954195 | 0 | EPSS Ckt | Y | 2024 | C&GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512659053895 | 20240705 | 722 | 20240705 | 847 | 2505737 | 85 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 425 | 34.9564 | -120.4513 | No | Overcast-Fog;32-90 F |  |  | 24-0084243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954301 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512393354203 | 20240705 | 1006 | 20240705 | 1023 | 2505856 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 17 | 34.963 | -120.5399 | No | Clear-Heat Wave;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0084297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954331 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | FUSE | 45445 | 20240705 | 1020 | 20240705 | 1143 | 2505903 | 83 | Distribution Circuit | Vegetation | Tree - grew into line | 9 | 747 | 34.8657 | -120.3831 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Normal | 24-0084274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954317 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512366858462 | 20240705 | 1055 | 20240705 | 1120 | 2505933 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 75 | 35.0797 | -120.5516 | No | Clear-Heat Wave;32-90 F | Secondary | Deteriorated | 24-0084283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954323 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 507764 | 20240705 | 1545 | 20240705 | 1801 | 2506226 | 136 | Distribution Circuit | Vegetation | Tree - branch fell on line | 113 | 15368 | 35.2186 | -120.5962 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Normal | 24-0084370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954373 | 0 | EPSS Ckt | Y | 2024 | A&C PHASE
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 635958 | 20240705 | 1809 | 20240705 | 2037 | 2506463 | 148 | Distribution Circuit | Company Initiated | Personnel- company | 133 | 19684 | 35.3248 | -120.5176 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Annealed | 24-0084415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954393 | 0 | EPSS Ckt | N | 2024 | NA
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 30089 | 20240705 | 1809 | 20240705 | 2212 | 2506658 | 243 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2751 | 35.5433 | -120.731 | No | Clear;32-90 F |  |  | 24-0084465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954436 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20240705 | 1812 | 20240706 | 945 | 2506466 | 933 | Distribution Circuit | Equipment Failure/Involved | Overhead | 433 | 28407 | 35.2197 | -120.5967 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954394 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | FUSE | 6259 | 20240705 | 1935 | 20240705 | 2135 | 2506545 | 120 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1 | 120 | 34.7444 | -120.0922 | No | Clear-Heat Wave;Above 90 | Customer Equipment | Contaminated | 24-0084425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954403 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | TRANSFORMER | T2460 | 20240705 | 2242 | 20240706 | 741 | 2507194 | 539 | Transformer only | Equipment Failure/Involved | Underground | 12 | 6468 | 35.5566 | -120.7215 | No | Clear;32-90 F | Secondary | Broken | 24-0084530 | UG | Sus | 31699342 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954500 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | TRANSFORMER | 512043473587 | 20240706 | 217 | 20240706 | 820 | 2507261 | 363 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 7260 | 35.493 | -120.6745 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954484 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | SWITCH | 85870 | 20240706 | 2032 | 20240706 | 2228 | 2508393 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3389 | 292558 | 35.5667 | -121.075 | No | Clear;32-90 F |  |  | 24-0084725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954626 | 0 | EPSS Ckt | Y | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | W12 | 20240706 | 2245 | 20240706 | 2326 | s1959545 | 41 | Distribution Circuit | Company Initiated | Operating error | 783 | 32103 | 35.5487 | -121.0892 | No | Clear;32-90 F | Recloser | Normal | 24-0084725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1959545 | 0 | EPSS Ckt | Y | 2024 | C PHASE
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y54 | 20240707 | 127 | 20240716 | 2017 | 2508616 | 14090 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 319 | 315506 | 34.6532 | -120.0715 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 24-0084796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954694 | 0 | EPSS Ckt | Y | 2024 | NONE
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 942274 | 20240707 | 1059 | 20240707 | 1229 | 2508869 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2880 | 35.5192 | -120.6406 | No | Clear-Heat Wave;32-90 F |  |  | 24-0084847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954735 | 0 | EPSS Ckt | Y | 2024 | A C
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | RECLOSER | 531590 | 20240707 | 1535 | 20240707 | 1824 | 2509054 | 168 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 383 | 15607 | 35.6 | -121.1156 | No | Clear-Heat Wave;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0084887 | OH | Sus | 46273186 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954761 | 0 | Non-EPSS | N | 2024 | FORCE OUT
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 6679 | 20240708 | 311 | 20240708 | 502 | 2509674 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 964 | 47217 | 35.5726 | -120.6016 | No | Clear;32-90 F |  |  | 24-0085045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954900 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y66 | 20240708 | 1024 | 20240708 | 1238 | 2510154 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 144 | 6570 | 34.6109 | -120.0203 | No | Clear-Heat Wave;32-90 F |  |  | 24-0085158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955025 | 0 | EPSS Ckt | Y | 2024 | A & C PHSE
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512169559795 | 20240708 | 1407 | 20240708 | 2003 | 2510361 | 356 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2848 | 35.1158 | -120.6194 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 24-0085259 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955074 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | TRANSFORMER | 511968479363 | 20240708 | 1509 | 20240709 | 622 | 2511029 | 913 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1826 | 35.651 | -120.7042 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0085432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955156 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | R74 | 20240708 | 1809 | 20240708 | 2322 | 2510709 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3118 | 695419 | 35.5922 | -120.6471 | No | Clear;32-90 F | Jumper | Burned Open | 24-0085348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | No | No | 1955099 | 1 | EPSS Ckt | Y | 2024 | BC&GRD
LOS PADRES | PASO ROBLES | SAN MIGUEL-1107 | 182661107 | FUSE | 679381 | 20240708 | 2045 | 20240709 | 416 | 2510897 | 451 | Distribution Circuit | Vegetation | Tree - branch fell on line | 122 | 6946 | 35.7428 | -120.6852 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0085391 | OH | Sus | 31698899 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1955123 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A20 | 20240709 | 342 | 20240709 | 1054 | 2511107 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 3147 | 236348 | 35.5005 | -120.6607 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0085447 | OH | Sus | 31700319 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1955174 | 0 | EPSS Ckt | Y | 2024 | GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 848137 | 20240709 | 702 | 20240709 | 1638 | s1955638 | 129 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 174 | 35.4629 | -120.6373 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0086206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955638 | 0 | EPSS Ckt | N | 2024 | PHSE TO PHSE
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | RECLOSER | 320270 | 20240709 | 1032 | 20240709 | 1039 | 2511463 | 7 | Distribution Circuit | Company Initiated | Personnel- company | 205 | 1435 | 34.5995 | -120.1277 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Normal | 24-0085583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955305 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | FUSE | 30531 | 20240709 | 1227 | 20240709 | 1403 | 2511556 | 96 | Distribution Circuit | Animal | Bird found | 2 | 192 | 35.6739 | -120.6587 | No | Clear-Heat Wave;Above 90 | Fuse | Burned Open | 24-0085699 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955342 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 96971 | 20240709 | 1608 | 20240709 | 2003 | 2511733 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 705 | 34.6192 | -120.2095 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Deteriorated | 24-0085768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955363 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | Y24 | 20240709 | 1937 | 20240709 | 2228 | 2511875 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 12312 | 34.6331 | -120.4541 | No | Partly Cloudy-Heat Wave;32-90 F |  |  | 24-0085829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955382 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | T2779 | 20240709 | 2103 | 20240710 | 332 | 2511943 | 389 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 1167 | 35.5886 | -120.6604 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0085882 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955437 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | RECLOSER | 605393 | 20240710 | 553 | 20240710 | 709 | 2512076 | 76 | Distribution Circuit | Animal | Bird found | 90 | 6840 | 35.8451 | -120.7004 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0085902 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955466 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | RECLOSER | 531590 | 20240710 | 612 | 20240710 | 852 | 2512086 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 383 | 61280 | 35.6 | -121.1156 | No | Clear;32-90 F |  |  | 24-0085905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955474 | 0 | Non-EPSS | Y | 2024 | A PHSE & SGF
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | RECLOSER | M80 | 20240710 | 747 | 20240710 | 1900 | 2512120 | 673 | Distribution Circuit | 3rd Party | Vehicle | 384 | 93188 | 35.0146 | -120.3607 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0085935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1955485 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | TRANSFORMER | 510657278472 | 20240710 | 938 | 20240710 | 1541 | 2512324 | 363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 582 | 35.6162 | -121.1444 | No | Clear;32-90 F | Transformer (OH) | Arcing | 24-0086020 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955601 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512102465598 | 20240710 | 1119 | 20240710 | 1708 | 2512428 | 349 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2792 | 35.2738 | -120.6473 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0086105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955620 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | 705596 | 20240710 | 1427 | 20240710 | 1433 | 2512605 | 6 | Distribution Circuit | Company Initiated | Personnel- company | 83 | 498 | 34.5986 | -120.1926 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0086262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955643 | 0 | EPSS Ckt | Y | 2024 | B
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | TRANSFORMER | 513338849581 | 20240711 | 736 | 20240711 | 954 | 2513368 | 138 | Transformer only | 3rd Party | Customer Equipment | 1 | 138 | 34.8419 | -120.2208 | No | Clear-Heat Wave;32-90 F | Fuse | Burned Open | 24-0086624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955916 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 30521 | 20240711 | 1228 | 20240711 | 1302 | 2513754 | 34 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 2 | 68 | 35.6594 | -120.5337 | No | Clear-Heat Wave;Above 90 | Fuse | Normal | 24-0086716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955956 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N44 | 20240712 | 248 | 20240712 | 643 | 2514659 | 235 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1191 | 151249 | 35.7755 | -120.8971 | No | Clear;32-90 F |  |  | 24-0087057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956125 | 0 | EPSS Ckt | Y | 2024 | B-GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | R82 | 20240712 | 503 | 20240712 | 827 | 2514675 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 904 | 75540 | 35.5299 | -120.523 | No | Partly Cloudy;32-90 F |  |  | 24-0087062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956130 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | OTHER | J-352 TWD T2456 | 20240712 | 923 | 20240712 | 1041 | 2514906 | 78 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 936 | 35.4965 | -120.6838 | No | Partly Cloudy-Heat Wave;32-90 F | Transformer (UG) | Failed/Faulted | 24-0087094 | UG | Sus | 35565950 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956222 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | R22 | 20240712 | 1405 | 20240712 | 2127 | 2515227 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 53742 | 35.685 | -120.5587 | No | Partly Cloudy-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0087304 | OH | Sus | 31700828 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1956304 | 0 | EPSS Ckt | N | 2024 | A GRD
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20240713 | 551 | 20240713 | 836 | 2515768 | 84 | Distribution Circuit | Animal | Bird found | 191 | 7803 | 34.5979 | -120.0297 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0087467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956408 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | R76 | 20240713 | 1149 | 20240713 | 1815 | 2515976 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 1067 | 37370 | 35.5454 | -120.7081 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0087539 | OH | Sus | 35566114 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956471 | 0 | EPSS Ckt | Y | 2024 | NONE
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20240713 | 1235 | 20240713 | 1522 | 2516011 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 9901 | 35.1757 | -120.5255 | No | Partly Cloudy;32-90 F |  |  | 24-0087552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956478 | 0 | EPSS Ckt | Y | 2024 | B- C- & INST OC
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | RECLOSER | R28 | 20240714 | 335 | 20240714 | 532 | 2516423 | 117 | Distribution Circuit | Animal | Bird found | 329 | 34608 | 35.5899 | -120.6934 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0087660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956571 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | TRANSFORMER | T0348 | 20240714 | 1256 | 20240714 | 1906 | 2516624 | 370 | Distribution Circuit | Equipment Failure/Involved | Underground | 58 | 8965 | 35.631 | -120.6621 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0087724 | UG | Sus | 35566202 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956633 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | OCB | 1104/2 | 20240714 | 2105 | 20240715 | 1435 | 2516844 | 1050 | Distribution Circuit | Animal | Bird found | 1291 | 108130 | 35.7522 | -120.6838 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0087767 | OH | Sus | 31701101 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | Yes | No | 1956678 | 0 | EPSS Ckt | N | 2024 | B-C-GRD
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 1379 | 20240715 | 1059 | 20240715 | 1232 | 2517313 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 310 | 34.6793 | -120.1166 | No | Clear;32-90 F |  |  | 24-0088014 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956900 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511318073175 | 20240715 | 1119 | 20240715 | 1715 | 2517341 | 356 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 356 | 35.4752 | -120.9159 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0088025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956905 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | FUSE | 270853 | 20240715 | 1341 | 20240715 | 1507 | 2517479 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 292 | 25112 | 35.1226 | -120.6172 | No | Clear;32-90 F |  |  | 24-0088115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956934 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512377557975 | 20240715 | 2105 | 20240716 | 20 | 2517749 | 195 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 585 | 35.0665 | -120.5476 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0088219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956970 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | V82 | 20240716 | 100 | 20240716 | 1205 | 2517794 | 665 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1303 | 220589 | 35.2151 | -120.615 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0088250 | OH | Sus | 31701222 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | No | No | 1957004 | 0 | EPSS Ckt | N | 2024 | A-B-C-GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | TRANSFORMER | 511957179211 | 20240716 | 759 | 20240716 | 1855 | 2517937 | 656 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2589 | 35.6471 | -120.7088 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0088418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957193 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | FUSE | 270853 | 20240716 | 1146 | 20240716 | 1255 | 2518228 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 292 | 20148 | 35.1226 | -120.6172 | No | Overcast;32-90 F |  |  | 24-0088495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957219 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | FUSE | 10311 | 20240716 | 1403 | 20240716 | 1647 | 2518377 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 9184 | 35.1064 | -120.5957 | No | Partly Cloudy;32-90 F |  |  | 24-0088627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957258 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | INTERRUPTER | 21262 | 20240716 | 1413 | 20240716 | 2311 | 2518392 | 332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2584 | 212033 | 34.6158 | -120.1993 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0088584 | OH | Sus | 31701105 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1957248 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | TRANSFORMER | 512600244868 | 20240717 | 756 | 20240717 | 934 | 2519314 | 98 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 490 | 34.7073 | -120.4625 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0088789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957457 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512169359794 | 20240717 | 1253 | 20240717 | 1537 | 2519582 | 164 | Transformer only | Unknown Cause | Patrol - found nothing | 21 | 3444 | 35.1152 | -120.6194 | No | Clear;32-90 F |  |  | 24-0089040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1957539 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X10 | 20240717 | 1442 | 20240717 | 1655 | 2519666 | 133 | Distribution Circuit | Animal | Bird found | 105 | 13965 | 35.5847 | -120.3364 | No | Clear;Above 90 | Transformer (OH) | Normal | 24-0088983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957527 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | RECLOSER | P26 | 20240717 | 2127 | 20240718 | 26 | 2519936 | 179 | Distribution Circuit | Company Initiated | Coordination failure | 511 | 78617 | 35.629 | -120.6607 | No | Clear;32-90 F | Recloser | Normal | 24-0089101 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | No | No | 1957575 | 0 | EPSS Ckt | N | 2024 | B C GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | FUSE | 12089 | 20240717 | 2128 | 20240718 | 237 | 2519930 | 309 | Distribution Circuit | Equipment Failure/Involved | Underground | 293 | 82737 | 35.6157 | -120.6666 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0089126 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957599 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M54 | 20240718 | 810 | 20240718 | 900 | 2520041 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 127 | 6350 | 34.8627 | -120.2773 | No | Partly Cloudy;32-90 F |  |  | 24-0089178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957628 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N40 | 20240718 | 1209 | 20240719 | 143 | 2520238 | 719 | Distribution Circuit | Equipment Failure/Involved | Underground | 1004 | 47863 | 35.7571 | -120.8803 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0089302 | UG | Sus | 46281680 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957686 | 0 | EPSS Ckt | Y | 2024 | A GRD
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512853052382 | 20240718 | 1704 | 20240719 | 552 | 2520436 | 768 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1536 | 34.9162 | -120.3854 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0089500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957741 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL SUB | 18266 | OCB | 1106/2 | 20240718 | 1920 | 20240719 | 546 | 2520505 | 626 | Distribution Circuit | 3rd Party | Vehicle | 327 | 142908 | 35.7522 | -120.6839 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0089506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1957746 | 0 | Non-EPSS | Y | 2024 | B GRD
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | OCB | 1105/2 | 20240718 | 1920 | 20240718 | 2256 | s1957783 | 216 | Distribution Circuit | 3rd Party | Vehicle | 1109 | 239544 | 35.7522 | -120.6839 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0089506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | Yes | No | 1957783 | 0 | EPSS Ckt | Y | 2024 | A B C
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | RECLOSER | P26 | 20240719 | 631 | 20240719 | 703 | 2520772 | 32 | Distribution Circuit | Company Initiated | Coordination failure | 511 | 10801 | 35.629 | -120.6607 | No | Clear;32-90 F | Fuse | Normal | 24-0089579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957802 | 0 | EPSS Ckt | N | 2024 | AB GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | FUSE | 31511 | 20240719 | 631 | 20240719 | 1911 | 2520774 | 760 | Distribution Circuit | Equipment Failure/Involved | Underground | 58 | 32020 | 35.6267 | -120.6618 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0089589 | UG | Sus | 46281537 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957810 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20240719 | 637 | 20240719 | 650 | 2520777 | 13 | Distribution Circuit | Company Initiated | Personnel- company | 732 | 9516 | 35.7811 | -120.9891 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0089584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957805 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 5975 | 20240719 | 2120 | 20240719 | 2308 | 2521496 | 108 | Distribution Circuit | Animal | Bird found | 6 | 648 | 35.7109 | -120.3822 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0089950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958039 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y48 | 20240720 | 1807 | 20240721 | 400 | 2522012 | 593 | Distribution Circuit | 3rd Party | Vehicle | 828 | 161169 | 34.6653 | -120.1182 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0090079 | OH | Sus | 35567563 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1958156 | 0 | EPSS Ckt | Y | 2024 | ABC
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 2993 | 20240720 | 2013 | 20240720 | 2133 | 2522086 | 80 | Distribution Circuit | Animal | Bird found | 8 | 640 | 35.5434 | -120.7008 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0090095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958172 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20240721 | 705 | 20240721 | 831 | 2522287 | 86 | Distribution Circuit | Animal | Bird found | 1724 | 43405 | 35.5213 | -120.7125 | No | Fog;32-90 F | Conductor- Overhead | Normal | 24-0090134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958209 | 0 | EPSS Ckt | Y | 2024 | B GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | RECLOSER | 238418 | 20240721 | 1208 | 20240721 | 1330 | 2522443 | 82 | Distribution Circuit | Animal | Bird found | 12 | 984 | 35.5905 | -120.7299 | No | Clear;32-90 F | Bushing | Broken | 24-0090169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958240 | 0 | EPSS Ckt | Y | 2024 | B C
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | V38 | 20240721 | 1242 | 20240721 | 1416 | 2522455 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1500 | 101680 | 35.1274 | -120.5689 | No | Partly Cloudy;32-90 F |  |  | 24-0090176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958245 | 0 | EPSS Ckt | Y | 2024 | B C INST
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | OTHER | 2763 | 20240721 | 1514 | 20240721 | 2254 | 2522505 | 460 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 30664 | 35.4746 | -120.6629 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0090195 | OH | Sus | 31701576 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1958263 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6527 | 20240721 | 1515 | 20240721 | 1728 | 2522506 | 133 | Distribution Circuit | Animal | Squirrel | 2 | 266 | 35.5497 | -120.7755 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0090204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958272 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1102 | 182821102 | FUSE | 6531 | 20240721 | 1627 | 20240722 | 208 | 2522539 | 581 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2324 | 35.0103 | -120.5661 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0090198 | OH | Sus | 31701525 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958268 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | RECLOSER | M86 | 20240722 | 618 | 20240722 | 1307 | 2522787 | 409 | Distribution Circuit | Equipment Failure/Involved | Overhead | 760 | 195056 | 35.0492 | -120.4827 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Broken | 24-0090257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958318 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | R92 | 20240722 | 734 | 20240722 | 1620 | 2522844 | 526 | Distribution Circuit | 3rd Party | Vehicle | 965 | 188858 | 35.5705 | -120.6481 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0090285 | OH | Sus | 35567673 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1958332 | 0 | EPSS Ckt | Y | 2024 | B C
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | FUSE | 8649 | 20240722 | 1532 | 20240722 | 2020 | 2523457 | 288 | Distribution Circuit | Vegetation | Tree - grew into line | 29 | 8352 | 35.0549 | -120.5895 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0090577 | OH | Sus | 46282938 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958527 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 3371 | 20240722 | 1607 | 20240722 | 1934 | 2523502 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 207 | 35.5586 | -120.335 | No | Clear;Above 90 |  |  | 24-0090644 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958539 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | FUSE | 45073 | 20240722 | 2234 | 20240722 | 2300 | 2523736 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 110 | 2860 | 34.8652 | -120.4232 | No | Partly Cloudy-Fog;32-90 F | Jumper | Burned/flashed | 24-0090694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958583 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 20603 | 20240723 | 908 | 20240723 | 1252 | 2524151 | 224 | Distribution Circuit | Animal | Squirrel | 5 | 1066 | 34.6275 | -120.1161 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0090865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1958786 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | OCB | 1104/2 | 20240723 | 1453 | 20240723 | 2030 | 2524511 | 337 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 3442 | 223378 | 34.6255 | -120.1193 | No | Clear-Heat Wave;Above 90 | Circuit Breaker | Normal | 24-0091059 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1958842 | 0 | EPSS Ckt | Y | 2024 | INST OC
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | JUMPER | OJ @ 1515 ELM AVE | 20240724 | 745 | 20240724 | 1102 | 2525251 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1576 | 34.5974 | -120.1444 | No | Clear;32-90 F | Bushing | Broken | 24-0091298 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958968 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | TRANSFORMER | T0684 | 20240724 | 1723 | 20240725 | 1005 | 2526024 | 987 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 14256 | 34.6095 | -120.0972 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0091690 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959228 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | RECLOSER | N38 | 20240724 | 1814 | 20240724 | 1932 | 2526056 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 97 | 7566 | 35.7985 | -120.7392 | No | Clear-Heat Wave;Above 90 |  |  | 24-0091668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959217 | 0 | EPSS Ckt | Y | 2024 | A-GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 641367 | 20240724 | 1947 | 20240724 | 2144 | 2526101 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 298 | 34866 | 35.4544 | -120.4862 | No | Clear-Heat Wave;32-90 F |  |  | 24-0091699 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1959237 | 0 | EPSS Ckt | Y | 2024 | A-B
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | OCB | 1101/2 | 20240725 | 216 | 20240725 | 746 | 2526272 | 330 | Distribution Circuit | 3rd Party | Customer Equipment | 279 | 19234 | 34.8788 | -120.3308 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0091759 | OH | Sus | 31702014 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959306 | 0 | EPSS Ckt | N | 2024 | TRIP TGT
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512657853821 | 20240725 | 226 | 20240725 | 236 | 2526253 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 50 | 34.9545 | -120.4516 | No | Fog;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0091760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959307 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512081973387 | 20240725 | 740 | 20240725 | 1607 | 2526349 | 507 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1014 | 35.4879 | -120.6615 | No | Clear;32-90 F | Secondary | Broken | 24-0091830 | OH | Sus | 31702372 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959428 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | T0544 | 20240725 | 758 | 20240726 | 200 | 2526368 | 1082 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 1194 | 34.9263 | -120.4074 | No | Clear-Heat Wave;32-90 F | Transformer (UG) | Deteriorated | 24-0091891 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959472 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1104 | 182661104 | RECLOSER | R88 | 20240725 | 1936 | 20240726 | 5 | 2526990 | 269 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 244 | 63231 | 35.7084 | -120.6137 | No | Clear;Above 90 |  |  | 24-0092188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1959565 | 0 | EPSS Ckt | Y | 2024 | ABC
LOS PADRES | SANTA MARIA | PALMER-1101 | 183031101 | RECLOSER | M84 | 20240725 | 2121 | 20240726 | 56 | 2527038 | 215 | Distribution Circuit | 3rd Party | Vehicle | 912 | 195869 | 34.8208 | -120.2887 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0092193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1959577 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y04 | 20240725 | 2305 | 20240726 | 1035 | 2527086 | 690 | Distribution Circuit | Animal | Bird found | 451 | 273406 | 34.6354 | -120.0656 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0092220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959605 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | PASO ROBLES | SAN LUIS OBISPO-1101 | 182631101 | TRANSFORMER | 512097369334 | 20240726 | 800 | 20240726 | 923 | 2527221 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 83 | 35.3768 | -120.6523 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0092280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959650 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | JUMPER | OJ 3 S/OF CGC 511155082620 | 20240726 | 838 | 20240726 | 1151 | 2527168 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2509 | 35.7318 | -120.9813 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0092239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959630 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PALMER-1101 | 183031101 | OCB | 1101/2 | 20240726 | 1150 | 20240726 | 1156 | 2527542 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 955 | 5730 | 34.8252 | -120.2993 | No | Clear;32-90 F | Recloser | Normal | 24-0092432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959780 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | FUSE | 270853 | 20240726 | 1527 | 20240726 | 1808 | 2527737 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 292 | 47012 | 35.1226 | -120.6172 | No | Clear-Rain;32-90 F |  |  | 24-0092609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1959833 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | R34 | 20240727 | 429 | 20240727 | 633 | 2528110 | 124 | Distribution Circuit | Animal | Bird found | 321 | 39804 | 35.5716 | -120.5425 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0092702 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1959911 | 0 | EPSS Ckt | Y | 2024 | AC
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512517073965 | 20240727 | 1109 | 20240727 | 1331 | 2528262 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 142 | 35.5064 | -120.5156 | No | Clear;32-90 F | Jumper | Broken | 24-0092756 | OH | Sus | 46285197 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959987 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | FUSE | 270853 | 20240727 | 1401 | 20240727 | 1547 | 2528352 | 106 | Distribution Circuit | Animal | Bird found | 292 | 30952 | 35.1226 | -120.6172 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092790 | OH | Sus | 31702563 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960010 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | OTHER | T3332 TWD T3334 | 20240727 | 1454 | 20240727 | 1529 | 2528371 | 35 | Distribution Circuit | Equipment Failure/Involved | Underground | 84 | 2940 | 35.6479 | -120.6821 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0092775 | UG | Sus | 35569114 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1960002 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 4975 | 20240727 | 1700 | 20240727 | 1907 | 2528415 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 7370 | 35.3987 | -120.8285 | No | Partly Cloudy;32-90 F |  |  | 24-0092798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960014 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20240728 | 128 | 20240728 | 1738 | 2528504 | 368 | Distribution Circuit | Equipment Failure/Involved | Underground | 732 | 208837 | 35.7811 | -120.9891 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0092836 | UG | Sus | 31702581 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960059 | 0 | EPSS Ckt | Y | 2024 | B GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 4015 | 20240728 | 439 | 20240728 | 1915 | 2528569 | 876 | Distribution Circuit | Animal | Bird found | 28 | 24528 | 35.5813 | -120.5526 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Normal | 24-0092920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960119 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X24 | 20240728 | 511 | 20240728 | 706 | 2528541 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 259 | 29785 | 35.6532 | -120.3636 | No | Partly Cloudy;32-90 F |  |  | 24-0092840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960064 | 0 | EPSS Ckt | Y | 2024 | A/ GRD
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X06 | 20240728 | 1416 | 20240729 | 1135 | 2528719 | 1279 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 172 | 189532 | 35.7373 | -120.2884 | No | Clear;32-90 F |  |  | 24-0092896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960104 | 0 | EPSS Ckt | Y | 2024 | B & C INST OC
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 29575 | 20240728 | 2126 | 20240729 | 259 | 2528815 | 333 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 36297 | 34.9648 | -120.5746 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0092960 | OH | Sus | 46285627 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960157 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 236895 | 20240728 | 2302 | 20240729 | 32 | 2528836 | 90 | Distribution Circuit | Animal | Bird found | 4 | 360 | 35.1761 | -120.535 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0092957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960154 | 0 | EPSS Ckt | Y | 2024 | B & C
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | 511926673254 | 20240729 | 211 | 20240729 | 354 | 2528851 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 503 | 26226 | 35.4826 | -120.7134 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 24-0092959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1960156 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 901690 | 20240729 | 1824 | 20240730 | 1848 | 2529734 | 1464 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 95974 | 35.5595 | -120.7826 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0093418 | OH | Sus | 31702672 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1960410 | 0 | EPSS Ckt | Y | 2024 | B PHASE & GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | 42344 | 20240729 | 2330 | 20240730 | 631 | 2529865 | 421 | Distribution Circuit | Animal | Bird found | 343 | 116661 | 35.2316 | -120.6362 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0093465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1960446 | 0 | EPSS Ckt | N | 2024 | A & GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20240729 | 2330 | 20240730 | 1250 | 2529866 | 800 | Distribution Circuit | Equipment Failure/Involved | Overhead | 435 | 189373 | 35.2197 | -120.5967 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0093463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1960444 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 721823 | 20240729 | 2330 | 20240730 | 45 | 2529864 | 75 | Distribution Circuit | Company Initiated | Coordination failure | 1227 | 92025 | 35.1986 | -120.607 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0093464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960445 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | TRANSFORMER | T0435 | 20240730 | 603 | 20240730 | 825 | 2529949 | 142 | Transformer only | Equipment Failure/Involved | Underground | 4 | 568 | 35.7497 | -120.9882 | No | Clear;32-90 F | Splice box | Failed/Faulted | 24-0093495 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960473 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | 514592 | 20240730 | 959 | 20240730 | 1214 | 2530222 | 135 | Distribution Circuit | Animal | Bird found | 2044 | 167525 | 35.5368 | -120.7146 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960652 | 0 | EPSS Ckt | Y | 2024 | B&C
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | FUSE | 270853 | 20240730 | 1438 | 20240730 | 1538 | 2530453 | 60 | Distribution Circuit | Animal | Bird found | 292 | 17520 | 35.1226 | -120.6172 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960730 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 7421 | 20240731 | 1147 | 20240731 | 1313 | 2531334 | 86 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 86 | 34.9415 | -120.5746 | No | Partly Cloudy;32-90 F | Metering Equipment | Failed/Faulted | 24-0094295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1961062 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | OTHER | J49154 TWD T730466 | 20240731 | 1937 | 20240731 | 2039 | 2531561 | 62 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 186 | 35.646 | -120.6747 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0094433 | UG | Sus | 35570044 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1961109 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | 998752 | 20240801 | 725 | 20240801 | 751 | 2531656 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 828 | 21528 | 35.6432 | -120.6939 | No | Clear;32-90 F | Recloser | Normal | 24-0094521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961150 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X20 | 20240801 | 811 | 20240801 | 1659 | 2531739 | 528 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 11451 | 35.5238 | -120.2128 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0094540 | OH | Sus | 31702678 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1961180 | 0 | EPSS Ckt | N | 2024 | B & GRD
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y06 | 20240801 | 1029 | 20240801 | 1035 | 2531921 | 6 | Distribution Circuit | Company Initiated | Personnel- company | 321 | 1926 | 34.6201 | -120.2103 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0094637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961284 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | R12 | 20240801 | 1549 | 20240801 | 1955 | 2532168 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2517 | 276941 | 35.6607 | -120.7652 | No | Clear;32-90 F |  |  | 24-0094824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961343 | 0 | EPSS Ckt | Y | 2024 | C&INST
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 4637 | 20240801 | 1727 | 20240802 | 52 | 2532312 | 445 | Distribution Circuit | Animal | Bird found | 111 | 45631 | 35.6551 | -120.506 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0094897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961380 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | OTHER | T3505 TWD T3506 | 20240802 | 123 | 20240802 | 248 | 2532411 | 85 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 1275 | 34.9107 | -120.4263 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0094891 | UG | Sus | 35570281 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961377 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 641367 | 20240802 | 800 | 20240802 | 1035 | 2532720 | 155 | Distribution Circuit | 3rd Party | Aircraft | 298 | 46190 | 35.4544 | -120.4862 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0095003 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961515 | 0 | EPSS Ckt | Y | 2024 | B&C
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M52 | 20240802 | 822 | 20240802 | 1151 | 2532768 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 14630 | 34.9254 | -120.3465 | No | Clear;32-90 F |  |  | 24-0094997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961509 | 0 | EPSS Ckt | Y | 2024 | A&B
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | 873068 | 20240802 | 1201 | 20240802 | 1316 | 2533043 | 75 | Distribution Circuit | Company Initiated | Personnel- company | 302 | 22650 | 35.138 | -120.5669 | No | Overcast;32-90 F | Recloser | Normal | 24-0095147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961596 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | RECLOSER | V32 | 20240802 | 1203 | 20240802 | 2325 | 2533026 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 2062 | 180980 | 35.1042 | -120.6199 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0095145 | OH | Sus | 46288317 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | Yes | No | 1961593 | 0 | EPSS Ckt | N | 2024 | ABC
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A18 | 20240802 | 1853 | 20240802 | 2127 | 2533275 | 154 | Distribution Circuit | Animal | Bird found | 1676 | 258104 | 35.449 | -120.6492 | No | Clear;32-90 F | Other | Normal | 24-0095311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961656 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | OCB | 1102/2 | 20240803 | 538 | 20240803 | 553 | 2533435 | 15 | Distribution Circuit | 3rd Party | Vehicle | 529 | 7935 | 34.8788 | -120.3308 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0095352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961695 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 3971 | 20240803 | 724 | 20240803 | 938 | 2533455 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 536 | 35.3609 | -120.8063 | No | Overcast-Fog;32-90 F |  |  | 24-0095385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961729 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | JUMPER | OJ 1 SPAN S/S/OF CGC 511976278501 | 20240803 | 918 | 20240803 | 1135 | 2533542 | 137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 548 | 35.6267 | -120.7004 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0095375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961723 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | TRANSFORMER | 512780052372 | 20240803 | 1236 | 20240803 | 1900 | 2533656 | 384 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1048 | 34.9155 | -120.4096 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0095430 | OH | Sus | 46288299 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961755 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20240803 | 1307 | 20240803 | 1725 | 2533699 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 132 | 34056 | 35.3806 | -120.4438 | No | Clear;32-90 F |  |  | 24-0095422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961749 | 0 | EPSS Ckt | Y | 2024 | A B INST OC
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | TRANSFORMER | 512245357573 | 20240803 | 1504 | 20240803 | 1603 | 2533625 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 413 | 35.0554 | -120.5916 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0095436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961758 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | RECLOSER | M86 | 20240803 | 1914 | 20240803 | 2131 | 2533881 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 760 | 58488 | 35.0492 | -120.4827 | No | Clear;32-90 F |  |  | 24-0095457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961771 | 0 | EPSS Ckt | Y | 2024 | A B INST OC
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y10 | 20240803 | 2219 | 20240804 | 1112 | 2533955 | 773 | Distribution Circuit | 3rd Party | Vehicle | 1083 | 120909 | 34.665 | -120.4225 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0095487 | OH | Sus | 35570641 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1961810 | 0 | EPSS Ckt | Y | 2024 | A C
LOS PADRES | SAN LUIS OBISPO | CMC 1101 | 183111101 | OCB | 166 | 20240804 | 645 | 20240804 | 928 | s1961842 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 163 | 35.3208 | -120.6932 | No | Clear;32-90 F |  |  | 24-0095519 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961842 | 0 | EPSS Ckt | Y | 2024 | NONE RECORDED BY DO
LOS PADRES | SAN LUIS OBISPO | CMC-1101 | 183111101 | OCB | 1102/2 | 20240804 | 958 | 20240804 | 1205 | s1961857 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 127 | 35.3207 | -120.6932 | No | Clear;32-90 F |  |  | 24-0095534 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961857 | 0 | EPSS Ckt | Y | 2024 | SET A RLY- TRIP- INST OC
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | OCB | 1102/2 | 20240804 | 1102 | 20240804 | 1201 | 2534156 | 59 | Distribution Circuit | 3rd Party | Metallic Balloon | 3847 | 84029 | 35.2865 | -120.7064 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | No | No | 1961861 | 0 | EPSS Ckt | Y | 2024 | BC& GRD INST OC
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | SWITCH | 8258 | 20240804 | 1140 | 20240804 | 1148 | 2534169 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 195 | 1560 | 34.6846 | -120.443 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0095487 | OH | Sus | 35570641 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1961864 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | FUSE | 31673 | 20240804 | 2113 | 20240805 | 238 | 2534375 | 325 | Distribution Circuit | Equipment Failure/Involved | Underground | 843 | 260466 | 35.6082 | -120.6586 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0095625 | UG | Sus | 31703445 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961917 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | OCB | 1106/2 | 20240805 | 616 | 20240805 | 829 | 2534601 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 327 | 43491 | 35.7522 | -120.6839 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0095643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961937 | 0 | EPSS Ckt | Y | 2024 | A-B
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y04 | 20240805 | 652 | 20240805 | 1009 | 2534611 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 451 | 66992 | 34.6354 | -120.0656 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0095652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961943 | 0 | EPSS Ckt | Y | 2024 | SGF/ DCD
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | RECLOSER | TEMP LR 1102/2 | 20240805 | 831 | 20240805 | 1136 | 2534706 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2038 | 275838 | 34.6251 | -120.1865 | No | Partly Cloudy;32-90 F |  |  | 24-0095700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961993 | 0 | EPSS Ckt | Y | 2024 | A GRD
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20240805 | 842 | 20240805 | 1328 | 2534724 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 280 | 80080 | 35.7984 | -120.9741 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0095710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1962003 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | RECLOSER | Y04 | 20240805 | 1012 | 20240805 | 1104 | 2534851 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 451 | 13628 | 34.6354 | -120.0656 | No | Clear;32-90 F |  |  | 24-0095780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962065 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512151254075 | 20240805 | 1226 | 20240805 | 1513 | 2534753 | 167 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 167 | 34.9574 | -120.6206 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0095938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962113 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V58 | 20240806 | 807 | 20240806 | 815 | 2535560 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 1616 | 12928 | 35.247 | -120.6494 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0096202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962262 | 0 | EPSS Ckt | N | 2024 | SGF DCD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 14167 | 20240806 | 807 | 20240806 | 1357 | 2535580 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 13307 | 35.244 | -120.6729 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0096412 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962442 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | TRANSFORMER | 511555367556 | 20240806 | 819 | 20240806 | 1446 | 2535590 | 387 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 7353 | 35.3237 | -120.8323 | No | Rain-Partly Cloudy;32-90 F | Service conductor | Broken | 24-0096274 | OH | Sus | 31703411 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962375 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | V82 | 20240806 | 901 | 20240806 | 1203 | 2535661 | 182 | Distribution Circuit | Company Initiated | Personnel- company | 1226 | 223132 | 35.2151 | -120.615 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0096247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962324 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512353652443 | 20240806 | 1241 | 20240806 | 1721 | 2535888 | 280 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 280 | 34.9145 | -120.5518 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0096385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962432 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | V82 | 20240806 | 1522 | 20240806 | 1531 | 2535963 | 9 | Distribution Circuit | Company Initiated | Personnel- company | 1307 | 11763 | 35.2151 | -120.615 | No | Clear;32-90 F | Recloser | Normal | 24-0096473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962464 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | JUMPER | OJ @ RISER 14163 | 20240806 | 1548 | 20240806 | 1652 | 2536044 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1191 | 75972 | 35.3844 | -120.8573 | No | Clear;32-90 F | Jumper | Burned Open | 24-0096489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1962470 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | W12 | 20240807 | 304 | 20240807 | 503 | 2536338 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 783 | 93177 | 35.5487 | -121.0892 | No | Clear;32-90 F |  |  | 24-0096593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962543 | 0 | EPSS Ckt | Y | 2024 | B GRD
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y06 | 20240808 | 856 | 20240808 | 920 | 2537457 | 24 | Distribution Circuit | Vegetation | Tree - branch fell on line | 345 | 8280 | 34.6201 | -120.2103 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0097135 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1962927 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | RECLOSER | M86 | 20240808 | 954 | 20240808 | 1020 | 2537584 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 688 | 17888 | 35.0492 | -120.4827 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0097178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962996 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | TEMP LR 1101/2 | 20240808 | 1820 | 20240808 | 2038 | 2538255 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2407 | 60960 | 34.7008 | -120.4358 | No | Clear;32-90 F |  |  | 24-0097444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963080 | 0 | EPSS Ckt | Y | 2024 | A & GRD
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | TEMP LR 1103/2 | 20240808 | 2018 | 20240808 | 2225 | 2538318 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1698 | 165831 | 34.6432 | -120.4375 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0097466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963099 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y10 | 20240808 | 2228 | 20240808 | 2250 | 2538370 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1083 | 23826 | 34.665 | -120.4225 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0097478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963124 | 0 | EPSS Ckt | Y | 2024 | A & GRD
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | TRANSFORMER | T1541 | 20240809 | 324 | 20240809 | 1512 | 2538421 | 708 | Distribution Circuit | Equipment Failure/Involved | Underground | 178 | 17153 | 34.6877 | -120.443 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0097491 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1963140 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | SWITCH | 536076 | 20240809 | 903 | 20240809 | 1242 | 2538608 | 219 | Distribution Circuit | Animal | Bird found | 17 | 3723 | 35.7473 | -120.716 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0097596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963254 | 0 | EPSS Ckt | Y | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 513658466545 | 20240809 | 1249 | 20240810 | 1040 | 2538793 | 1311 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 1311 | 35.3098 | -120.1234 | No | Clear;Above 90 |  |  | 24-0097864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963344 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | TRANSFORMER | 511932682671 | 20240809 | 1353 | 20240809 | 1422 | 2538830 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 29 | 35.7416 | -120.7195 | No | Clear;Above 90 | Cutout- fuse holder | Broken | 24-0097789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963325 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | TEMP LR 1103/2 | 20240809 | 1441 | 20240809 | 1507 | 2538875 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 1592 | 41392 | 34.6432 | -120.4375 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0097821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963329 | 0 | EPSS Ckt | Y | 2024 | SGF-DCD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 4745 | 20240809 | 1550 | 20240809 | 2056 | 2538926 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 191 | 58446 | 35.5468 | -121.0907 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0097858 | OH | Sus | 46293376 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963342 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | TRANSFORMER | 413810817980 | 20240809 | 1732 | 20240810 | 41 | 2539122 | 429 | Transformer only | Animal | Bird found | 3 | 1287 | 35.8083 | -121.0888 | No | Clear;Above 90 | Fuse | Failed/Faulted | 24-0097935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963386 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14047 | 20240809 | 2127 | 20240810 | 302 | 2539086 | 335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 8375 | 35.553 | -121.0875 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0097916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963371 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | OTHER | J-556 TWD T0431 | 20240810 | 1418 | 20240810 | 1434 | 2539452 | 16 | Distribution Circuit | Company Initiated | Return Circuit Normal | 27 | 432 | 35.7503 | -120.9913 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0092836 | UG | Sus | 31702581 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1963464 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | SWITCH | 45009 | 20240811 | 244 | 20240811 | 1718 | 2539680 | 874 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 874 | 34.9462 | -120.4547 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0098061 | OH | Sus | 46297561 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963528 | 1 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 31071 | 20240811 | 610 | 20240811 | 749 | 2539689 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 99 | 35.528 | -120.5738 | No | Clear;32-90 F |  |  | 24-0098059 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963524 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512340574703 | 20240811 | 801 | 20240811 | 817 | 2539708 | 16 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 48 | 35.5257 | -120.5753 | No | Partly Cloudy;32-90 F |  |  | 24-0098060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1963525 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20240811 | 1657 | 20240811 | 2118 | 2539852 | 261 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 434 | 113274 | 35.2197 | -120.5967 | No | Clear;32-90 F |  |  | 24-0098097 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963565 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | SWITCH | 45009 | 20240811 | 1834 | 20240811 | 2020 | 2539884 | 106 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 106 | 34.9462 | -120.4547 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0098105 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963571 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 45403 | 20240812 | 712 | 20240812 | 1033 | 2540282 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 201 | 34.9581 | -120.5088 | No | Partly Cloudy;32-90 F |  |  | 24-0098255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963753 | 1 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1107 | 182661107 | TRANSFORMER | 511990581939 | 20240812 | 840 | 20240812 | 1058 | 2540145 | 138 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 138 | 35.7217 | -120.699 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0098175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963648 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511394171818 | 20240812 | 932 | 20240812 | 958 | 2540283 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 338 | 35.4394 | -120.8899 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0098219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963722 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512557251771 | 20240812 | 2243 | 20240812 | 2330 | 2540825 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 705 | 34.8973 | -120.4834 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood |  | 24-0098577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963859 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | RECLOSER | 798137 | 20240813 | 1008 | 20240813 | 1104 | 2541171 | 56 | Distribution Circuit | Company Initiated | Personnel- company | 21 | 1176 | 35.3054 | -120.8082 | No | Clear;32-90 F | Recloser | Normal | 24-0098775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964062 | 0 | EPSS Ckt | Y | 2024 | B
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V58 | 20240814 | 340 | 20240814 | 559 | 2541685 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2899 | 402961 | 35.247 | -120.6494 | No | Clear;32-90 F |  |  | 24-0099123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964177 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | RECLOSER | 1101/2 | 20240814 | 408 | 20240814 | 1104 | 2541691 | 416 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 292 | 88874 | 35.361 | -120.8117 | No | Overcast;32-90 F |  |  | 24-0099125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964179 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | V66 | 20240814 | 1201 | 20240814 | 1749 | 2542115 | 348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 332 | 84550 | 35.3759 | -120.8526 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0099305 | OH | Sus | 46299221 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1964391 | 0 | EPSS Ckt | N | 2024 | C GRD
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511345572276 | 20240814 | 1917 | 20240814 | 2037 | 2542488 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 320 | 35.4522 | -120.906 | No | Clear;32-90 F | Fuse | Burned Open | 24-0099515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964460 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | RECLOSER | 1101/2 | 20240815 | 153 | 20240815 | 900 | 2542667 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 46987 | 35.361 | -120.8117 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0099535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964472 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | INTERRUPTER | 22113 | 20240815 | 2049 | 20240816 | 1638 | 2543330 | 1189 | Distribution Circuit | 3rd Party | Vehicle | 1275 | 16477 | 34.6161 | -120.2001 | No | Clear;32-90 F | Fuse | Broken | 24-0099847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964622 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | 55374 | 20240816 | 13 | 20240816 | 154 | 2543346 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 520 | 52035 | 35.6203 | -120.6963 | No | Clear;32-90 F |  |  | 24-0099858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964631 | 0 | EPSS Ckt | Y | 2024 | C PHASE AND GRD
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y06 | 20240816 | 407 | 20240816 | 719 | 2543357 | 192 | Distribution Circuit | Animal | Bird found | 345 | 51930 | 34.6201 | -120.2103 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0099862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1964636 | 0 | EPSS Ckt | Y | 2024 | B AND C PHASE
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512729854348 | 20240816 | 1523 | 20240816 | 1649 | 2543723 | 86 | Transformer only | Vegetation | Tree - grew into line | 14 | 1204 | 34.9693 | -120.4279 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964867 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | SWITCH | 21264 | 20240816 | 2342 | 20240817 | 1958 | 2544034 | 1216 | Distribution Circuit | Equipment Failure/Involved | Underground | 1274 | 25403 | 34.6154 | -120.1981 | No | Clear;32-90 F | Bushing | Burned/flashed | 24-0100187 | UG | Sus | 35575011 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964898 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | R56 | 20240817 | 455 | 20240817 | 725 | 2544119 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 426 | 63706 | 35.6443 | -120.7067 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0100212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964905 | 0 | EPSS Ckt | Y | 2024 | A PHASE AND GRD INST
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V02 | 20240817 | 1002 | 20240817 | 1607 | 2544260 | 365 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2017 | 568453 | 35.2377 | -120.6796 | No | Partly Cloudy;32-90 F |  |  | 24-0100248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964957 | 0 | EPSS Ckt | Y | 2024 | DCD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 79696 | 20240817 | 1403 | 20240819 | 1730 | 2544394 | 3087 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 131 | 73751 | 35.5731 | -121.0414 | No | Clear;32-90 F | Pole-Wood | On Ground | 24-0100281 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1964989 | 0 | EPSS Ckt | Y | 2024 | B C
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | TRANSFORMER | T159934 | 20240818 | 1959 | 20240819 | 309 | 2544994 | 430 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 860 | 34.8615 | -120.3713 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0100445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965136 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | V70 | 20240818 | 2010 | 20240819 | 816 | 2544928 | 726 | Distribution Circuit | Animal | Bird found | 1866 | 481774 | 35.3701 | -120.8475 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0100433 | OH | Sus | 46300912 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1965123 | 0 | EPSS Ckt | Y | 2024 | AB & GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | JUMPER | OJ @ CGC512697653598 | 20240819 | 303 | 20240819 | 404 | 2544966 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 976 | 34.9487 | -120.4381 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0100442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965132 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | Y08 | 20240819 | 1028 | 20240819 | 1355 | 2545404 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 89 | 7113 | 34.6667 | -120.4928 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0100543 | OH | Sus | 46300898 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965290 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512089665842 | 20240819 | 1345 | 20240819 | 2313 | 2545637 | 568 | Transformer only | 3rd Party | Vehicle | 13 | 7384 | 35.2805 | -120.6518 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0100737 | OH | Sus | 31705608 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1965354 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512277359544 | 20240819 | 1403 | 20240819 | 1451 | 2545649 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 48 | 35.109 | -120.5833 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0100679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965339 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | JUMPER | JMPRS 2 N/O CGC 512886552590 | 20240819 | 1547 | 20240819 | 1739 | 2545684 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 336 | 34.9233 | -120.3739 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0100701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965344 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | RECLOSER | 300858 | 20240819 | 1610 | 20240819 | 1849 | 2545758 | 159 | Distribution Circuit | Animal | Bird found | 577 | 41883 | 35.2631 | -120.699 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0100746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965357 | 0 | EPSS Ckt | Y | 2024 | B-G
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | W12 | 20240819 | 1658 | 20240819 | 1738 | 2545786 | 40 | Distribution Circuit | Company Initiated | Personnel- company | 783 | 31320 | 35.5487 | -121.0892 | No | Clear-Rain;32-90 F | Recloser | Malfunctioning | 24-0100763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | No | No | 1965360 | 0 | EPSS Ckt | Y | 2024 | AB&GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | OCB | 1101/2 | 20240820 | 426 | 20240820 | 909 | 2546025 | 283 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3609 | 1016304 | 35.2617 | -120.6345 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965420 | 0 | EPSS Ckt | Y | 2024 | SET A TRIP
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | FUSE | 6375 | 20240820 | 1458 | 20240821 | 247 | 2546620 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 28048 | 35.4843 | -120.6515 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0101196 | OH | Sus | 31705649 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1965672 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | OTHER | WIRE DOWN 1/N/1/W OF CGC 512663054412 | 20240820 | 1536 | 20240821 | 155 | 2546700 | 619 | Distribution Circuit | Equipment Failure/Involved | Overhead | 470 | 44025 | 34.9714 | -120.4506 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0101192 | OH | Sus | 31705652 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1965668 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512704853284 | 20240820 | 1538 | 20240820 | 1935 | 2546621 | 237 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 2133 | 34.9399 | -120.4356 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0101176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965663 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 10615 | 20240820 | 2148 | 20240821 | 15 | 2546813 | 147 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 2646 | 35.3548 | -120.7864 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0101243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965703 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N40 | 20240820 | 2220 | 20240821 | 1534 | 2546818 | 799 | Distribution Circuit | Equipment Failure/Involved | Underground | 1005 | 130614 | 35.7571 | -120.8803 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0101239 | UG | Sus | 46302959 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965700 | 0 | EPSS Ckt | Y | 2024 | GRD INST DCD
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20240821 | 41 | 20240821 | 117 | 2546857 | 36 | Distribution Circuit | Company Initiated | Coordination failure | 732 | 26352 | 35.7811 | -120.9891 | No | Clear;32-90 F | Recloser | Normal | 24-0101250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965713 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 43833 | 20240821 | 703 | 20240821 | 1837 | 2546922 | 694 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2776 | 35.1276 | -120.5663 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0101555 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1965956 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | SWITCH | 629924 | 20240821 | 706 | 20240821 | 713 | 2546921 | 7 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 28 | 34.9536 | -120.4362 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 24-0092421 | UG | Sus | 35352170 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965740 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20240821 | 813 | 20240821 | 1135 | 2547008 | 202 | Distribution Circuit | Animal | Bird found | 280 | 56560 | 35.7984 | -120.9741 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0101309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965801 | 0 | EPSS Ckt | Y | 2024 | A & C PHASE
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | 277014 | 20240821 | 1024 | 20240821 | 1041 | 2547209 | 17 | Distribution Circuit | Company Initiated | Personnel- company | 353 | 6001 | 34.5994 | -120.0979 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0101387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965911 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | PASO ROBLES | SAN MIGUEL-1107 | 182661107 | TRANSFORMER | 511930081084 | 20240821 | 1206 | 20240821 | 1256 | 2547350 | 50 | Transformer only | Company Initiated | Improper Construction | 1 | 50 | 35.6979 | -120.7191 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0101497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965942 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512192772105 | 20240821 | 1929 | 20240821 | 2045 | 2547604 | 76 | Transformer only | Vegetation | Tree - fell into line | 1 | 76 | 35.4534 | -120.6224 | No | Clear;32-90 F | Fuse | Normal | 24-0101694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965991 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | M72 | 20240822 | 51 | 20240822 | 345 | 2547712 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2965 | 378631 | 35.0397 | -120.5225 | No | Overcast;32-90 F |  |  | 24-0101715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966015 | 0 | EPSS Ckt | Y | 2024 | B & C
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | V70 | 20240822 | 557 | 20240822 | 838 | 2547779 | 161 | Distribution Circuit | Animal | Bird found | 1866 | 207320 | 35.3701 | -120.8475 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0101730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966035 | 0 | EPSS Ckt | Y | 2024 | B/C
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X16 | 20240822 | 852 | 20240822 | 1300 | 2547940 | 248 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 283 | 25241 | 35.6868 | -120.3362 | No | Clear;32-90 F |  |  | 24-0101815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966129 | 0 | EPSS Ckt | Y | 2024 | C PHASE
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | R18 | 20240822 | 1544 | 20240822 | 2009 | 2548431 | 265 | Distribution Circuit | Vegetation | Tree - grew into line | 530 | 9258 | 35.6287 | -120.6931 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102056 | OH | Sus | 46303734 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966262 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | TEMP LR 1103/2 | 20240822 | 1545 | 20240822 | 1715 | 2548452 | 90 | Distribution Circuit | Animal | Bird found | 1698 | 47736 | 34.6432 | -120.4375 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0102094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966263 | 0 | EPSS Ckt | Y | 2024 | A & B PHSE
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20240823 | 1021 | 20240823 | 1343 | 2549107 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 44036 | 35.1757 | -120.5255 | No | Partly Cloudy;32-90 F |  |  | 24-0102384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966505 | 0 | EPSS Ckt | Y | 2024 | B C INST OC
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512408360725 | 20240823 | 1114 | 20240823 | 1510 | 2549160 | 236 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 236 | 35.1431 | -120.5397 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0102587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966578 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 20743 | 20240824 | 826 | 20240824 | 1518 | 2550286 | 412 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 412 | 34.6506 | -120.531 | No | Clear;32-90 F |  |  | 24-0102804 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966738 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 85870 | 20240824 | 844 | 20240824 | 1132 | 2549986 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3389 | 167676 | 35.5667 | -121.075 | No | Partly Cloudy;32-90 F |  |  | 24-0102723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966669 | 0 | EPSS Ckt | Y | 2024 | BC
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | SWITCH | 5858 | 20240824 | 1108 | 20240824 | 1150 | 2550136 | 42 | Distribution Circuit | Company Initiated | Return Circuit Normal | 565 | 12039 | 35.6091 | -120.6445 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0102709 | UG | Sus | 35570668 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966710 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 9973 | 20240824 | 1632 | 20240825 | 503 | 2550424 | 751 | Distribution Circuit | 3rd Party | Vehicle | 35 | 26285 | 35.2865 | -120.7201 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0102850 | OH | Sus | 35576628 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1966775 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | 891294 | 20240824 | 1635 | 20240824 | 1746 | 2550444 | 71 | Distribution Circuit | Vegetation | Tree - branch fell on line | 883 | 42373 | 35.1342 | -120.5702 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0102824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966753 | 0 | EPSS Ckt | Y | 2024 | BC
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 307832 | 20240824 | 1838 | 20240824 | 2259 | 2550526 | 261 | Distribution Circuit | Animal | Bird found | 1327 | 166823 | 35.5578 | -120.7747 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966768 | 0 | EPSS Ckt | Y | 2024 | AB
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X08 | 20240825 | 802 | 20240825 | 1126 | 2550766 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 14688 | 35.7094 | -120.3018 | No | Clear;32-90 F |  |  | 24-0102887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966835 | 0 | EPSS Ckt | Y | 2024 | AB
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | TRANSFORMER | T1142 | 20240825 | 2026 | 20240825 | 2221 | 2551017 | 115 | Transformer only | Equipment Failure/Involved | Underground | 30 | 3450 | 34.9074 | -120.4277 | No | Clear;32-90 F | Other | Burned/flashed | 24-0102956 | UG | Sus | 46304849 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966901 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T2653 | 20240826 | 650 | 20240826 | 1335 | 2551114 | 405 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 6190 | 35.0281 | -120.4766 | No | Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0103069 | UG | Sus | 35576897 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967096 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | TRANSFORMER | 512228759931 | 20240826 | 909 | 20240826 | 1311 | 2551328 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2420 | 35.1193 | -120.5997 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0103079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967110 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512201858888 | 20240826 | 1526 | 20240827 | 209 | 2551675 | 643 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 643 | 35.0909 | -120.6075 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0103302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967198 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20240826 | 1653 | 20240826 | 1855 | 2551869 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 26596 | 35.1757 | -120.5255 | No | Clear;32-90 F |  |  | 24-0103319 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967204 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | TRANSFORMER | 512077779563 | 20240826 | 2019 | 20240827 | 204 | 2552006 | 345 | Transformer only | Animal | Bird found | 3 | 1035 | 35.6572 | -120.6675 | No | Clear;32-90 F | Bushing | Broken | 24-0103377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967239 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | TEMP LR 1103/2 | 20240827 | 937 | 20240827 | 950 | 2552487 | 13 | Distribution Circuit | Company Initiated | Personnel- company | 1692 | 21996 | 34.6432 | -120.4375 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0103496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967459 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | FUSE | 14727 | 20240827 | 1314 | 20240828 | 248 | 2552726 | 814 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 17094 | 35.1105 | -120.5942 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0103778 | OH | Sus | 31706645 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1967571 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | 998752 | 20240827 | 1843 | 20240828 | 232 | 2552988 | 469 | Distribution Circuit | 3rd Party | Vehicle | 1579 | 166927 | 35.6432 | -120.6939 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0103779 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967572 | 0 | EPSS Ckt | Y | 2024 | ABC
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | TRANSFORMER | 512082379160 | 20240827 | 1916 | 20240828 | 538 | 2553061 | 622 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 622 | 35.6463 | -120.6653 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0103827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967615 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 30527 | 20240828 | 606 | 20240828 | 805 | 2553325 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 198 | 35.5731 | -120.5966 | No | Clear;32-90 F |  |  | 24-0103902 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967703 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46055 | 20240828 | 1249 | 20240828 | 2056 | 2553863 | 487 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 32286 | 34.9604 | -120.4232 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0104219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967905 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | FUSE | 603183 | 20240828 | 1659 | 20240829 | 26 | 2554202 | 447 | Distribution Circuit | Equipment Failure/Involved | Underground | 829 | 149955 | 34.9312 | -120.4405 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0104382 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967940 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X16 | 20240828 | 1850 | 20240828 | 2119 | 2554274 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 283 | 28625 | 35.6868 | -120.3362 | No | Clear;32-90 F |  |  | 24-0104409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967950 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | SANTA MARIA | DIVIDE-1103 | 182571103 | JUMPER | 48160 | 20240829 | 538 | 20240829 | 1537 | 2554446 | 599 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 64260 | 34.8293 | -120.4499 | No | Overcast-Fog;32-90 F | Jumper | Burned Open | 24-0104470 | OH | Sus | 46306275 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1967993 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M26 | 20240829 | 1107 | 20240829 | 1405 | 2554948 | 178 | Distribution Circuit | 3rd Party | Vehicle | 250 | 44500 | 34.9083 | -120.3283 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0104696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968230 | 1 | EPSS Ckt | Y | 2024 | A
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | 873068 | 20240829 | 1130 | 20240829 | 1141 | 2554968 | 11 | Distribution Circuit | Company Initiated | Personnel- company | 277 | 3047 | 35.138 | -120.5669 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0104712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1968235 | 0 | EPSS Ckt | Y | 2024 | A C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20240829 | 1637 | 20240829 | 1821 | 2555286 | 104 | Distribution Circuit | Animal | Bird found | 434 | 28072 | 35.2197 | -120.5967 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0104977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1968284 | 0 | EPSS Ckt | Y | 2024 | B C
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A20 | 20240830 | 706 | 20240830 | 1153 | 2555614 | 287 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3146 | 217292 | 35.5005 | -120.6607 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0105106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1968373 | 0 | EPSS Ckt | Y | 2024 | A C
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 4001 | 20240830 | 827 | 20240830 | 1109 | 2555694 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 648 | 35.4228 | -120.6062 | No | Clear;32-90 F |  |  | 24-0105254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1968515 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 14859 | 20240831 | 752 | 20240831 | 941 | 2556365 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 9047 | 35.1938 | -120.4327 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0105539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1968612 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20240831 | 808 | 20240831 | 830 | 2556379 | 22 | Distribution Circuit | Company Initiated | Personnel- company | 351 | 7722 | 35.2197 | -120.5967 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0105541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968623 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 641367 | 20240831 | 856 | 20240831 | 1202 | 2556401 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 298 | 55428 | 35.4544 | -120.4862 | No | Partly Cloudy;32-90 F |  |  | 24-0105549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1968632 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 30601 | 20240831 | 1111 | 20240831 | 1705 | 2556591 | 354 | Distribution Circuit | Animal | Bird found | 2 | 708 | 35.5035 | -120.243 | No | Clear;Above 90 | Fuse | Burned Open | 24-0105608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1968663 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512549773028 | 20240901 | 1059 | 20240901 | 1125 | 2557111 | 26 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 26 | 35.483 | -120.5041 | No | Partly Cloudy;32-90 F |  |  | 24-0105701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1968737 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MESA-1103 | 182821103 | TRANSFORMER | 512401458167 | 20240901 | 1745 | 20240901 | 2119 | 2557248 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 428 | 35.0715 | -120.5406 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0105730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1968760 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | RECLOSER | W50 | 20240901 | 1750 | 20240901 | 1853 | 2557251 | 63 | Distribution Circuit | 3rd Party | Metallic Balloon | 615 | 38745 | 35.567 | -121.1052 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0105728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1968758 | 0 | Non-EPSS | Y | 2024 | B C
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | X08 | 20240902 | 435 | 20240902 | 1032 | 2557443 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 283 | 33722 | 35.7094 | -120.3018 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0105765 | OH | Sus | 46307590 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1968794 | 0 | EPSS Ckt | Y | 2024 | B C
LOS PADRES | PASO ROBLES | SAN MIGUEL-1107 | 182661107 | FUSE | 7459 | 20240902 | 549 | 20240902 | 958 | 2557453 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1494 | 35.7156 | -120.6139 | No | Clear;32-90 F |  |  | 24-0105799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1968814 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 14035 | 20240902 | 900 | 20240902 | 1010 | 2557477 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 770 | 35.0715 | -120.5956 | No | Overcast-Rain;32-90 F | Transformer (OH) | Deteriorated | 24-0105782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1968807 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 440856 | 20240902 | 957 | 20240902 | 1315 | 2557526 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 627 | 113593 | 35.4611 | -120.6732 | No | Clear;32-90 F |  |  | 24-0105802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1968815 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | SWITCH | 6172SW | 20240902 | 959 | 20240902 | 1535 | 2557531 | 336 | Distribution Circuit | Equipment Failure/Involved | Underground | 43 | 1968 | 35.7307 | -120.89 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0101239 | UG | Sus | 46302959 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1968817 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | FUSE | 6417 | 20240902 | 1121 | 20240902 | 1926 | 2557577 | 485 | Distribution Circuit | 3rd Party | Vehicle | 18 | 8730 | 34.9204 | -120.5224 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | Yes | No | 1968830 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | SWITCH | 10855 | 20240903 | 1003 | 20240903 | 1450 | 2558183 | 287 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 861 | 35.3661 | -120.8402 | No | Clear-Drizzle;32-90 F | Pole-Wood | Broken | 24-0105944 | OH | Sus | 35578429 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969051 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | OCB | 1104/2 | 20240903 | 1135 | 20240903 | 2009 | 2558317 | 514 | Distribution Circuit | 3rd Party | Vehicle | 3376 | 230060 | 34.9106 | -120.4461 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0106088 | OH | Sus | 35578570 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1969090 | 0 | Non-EPSS | N | 2024 | C GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 3313 | 20240903 | 1207 | 20240903 | 1748 | 2558396 | 341 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 4092 | 35.5012 | -120.6493 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0106171 | UG | Sus | 31707351 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969120 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | TRANSFORMER | 512118679795 | 20240903 | 1400 | 20240903 | 2011 | 2558521 | 371 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 371 | 35.6642 | -120.6538 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0106275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969148 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | RECLOSER | A28 | 20240904 | 1028 | 20240904 | 1111 | 2559271 | 43 | Distribution Circuit | Animal | Squirrel | 1832 | 77208 | 35.4622 | -120.6453 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0106629 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969407 | 0 | EPSS Ckt | Y | 2024 | B-GRD
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y06 | 20240904 | 1039 | 20240904 | 1046 | 2559285 | 7 | Distribution Circuit | Company Initiated | Personnel- company | 199 | 1393 | 34.6201 | -120.2103 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969411 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 702241 | 20240904 | 1126 | 20240904 | 1250 | 2559319 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 336 | 35.5613 | -120.334 | No | Clear;32-90 F |  |  | 24-0106770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969452 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 79696 | 20240904 | 1407 | 20240904 | 1935 | 2559477 | 193 | Distribution Circuit | Animal | Bird found | 131 | 25283 | 35.5731 | -121.0414 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969474 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | RECLOSER | W22 | 20240905 | 1004 | 20240905 | 1023 | 2560182 | 19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4164 | 79116 | 35.3291 | -120.8245 | No | Partly Cloudy-Heavy Rain;32-90 F | Switch (OH) | Broken | 24-0107060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969731 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | FUSE | 45747 | 20240905 | 1018 | 20240905 | 1534 | 2560193 | 316 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 948 | 34.935 | -120.4897 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0107194 | OH | Sus | 31707585 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969732 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | 745714 | 20240905 | 1303 | 20240905 | 2141 | 2560340 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 5376 | 34.7556 | -120.35 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0107354 | OH | Sus | 35579383 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969767 | 0 | EPSS Ckt | Y | 2024 | C INST OC
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | FUSE | 11595 | 20240905 | 1427 | 20240906 | 121 | 2560419 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 137 | 9902 | 34.9659 | -120.4351 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0107481 | OH | Sus | 46309406 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969796 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V14 | 20240905 | 1508 | 20240905 | 1523 | 2560449 | 15 | Distribution Circuit | Company Initiated | Coordination failure | 1221 | 18315 | 35.1791 | -120.6181 | No | Clear;Above 90 | Recloser | Normal | 24-0101346 | OH | Sus | 35561857 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969789 | 0 | EPSS Ckt | Y | 2024 | SGF/ DCD/VOLTAGE TARGET
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20240905 | 1538 | 20240905 | 1549 | 2560483 | 11 | Distribution Circuit | Company Initiated | Coordination failure | 435 | 4785 | 35.2197 | -120.5967 | No | Clear;Above 90 | Recloser | Normal | 24-0101346 | OH | Sus | 35561857 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969797 | 0 | EPSS Ckt | Y | 2024 | SGF/ DCD/VOLTAGE TARGET
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y36 | 20240905 | 1542 | 20240905 | 1621 | 2560485 | 39 | Distribution Circuit | 3rd Party | Vehicle | 274 | 10686 | 34.6026 | -120.1931 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0107498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1969798 | 0 | EPSS Ckt | Y | 2024 | ABC
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | 512533055197 | 20240905 | 1755 | 20240906 | 245 | 2560351 | 530 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 530 | 34.9922 | -120.4922 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0107583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969817 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | Y24 | 20240905 | 1842 | 20240905 | 2007 | 2560617 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 6120 | 34.6331 | -120.4541 | No | Clear;32-90 F |  |  | 24-0107587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969820 | 0 | EPSS Ckt | Y | 2024 | AC
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | TRANSFORMER | 513632241626 | 20240905 | 1945 | 20240905 | 2051 | 2560648 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 66 | 34.6255 | -120.1182 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0107594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969825 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | TRANSFORMER | 513457640564 | 20240906 | 13 | 20240906 | 134 | 2560716 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 81 | 34.5949 | -120.1738 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0107633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969854 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 511995566560 | 20240906 | 954 | 20240906 | 1426 | 2561030 | 272 | Transformer only | Vegetation | Tree - grew into line | 6 | 1632 | 35.2995 | -120.6839 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0107911 | OH | Sus | 46310325 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970065 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20240906 | 1003 | 20240906 | 1151 | 2561043 | 108 | Distribution Circuit | Animal | Bird found | 732 | 79056 | 35.7811 | -120.9891 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0107821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970029 | 0 | EPSS Ckt | Y | 2024 | SGF/ DCD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | 42344 | 20240906 | 1409 | 20240906 | 1753 | 2561330 | 224 | Distribution Circuit | Vegetation | Tree - fell into line | 342 | 15042 | 35.2316 | -120.6362 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0108016 | OH | Sus | 35579477 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1970095 | 0 | EPSS Ckt | Y | 2024 | GRD INST OC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20240906 | 1410 | 20240906 | 1508 | 2561342 | 58 | Distribution Circuit | Company Initiated | Personnel- company | 435 | 25230 | 35.2197 | -120.5967 | No | Clear;Above 90 | Recloser | Normal | 24-0108017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970096 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | 460184 | 20240906 | 1628 | 20240906 | 1927 | 2561494 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 130 | 9630 | 34.6643 | -120.3829 | No | Clear;32-90 F |  |  | 24-0108097 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970134 | 0 | EPSS Ckt | Y | 2024 | B & C INST OC
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | TRANSFORMER | 512113573686 | 20240906 | 2317 | 20240907 | 943 | 2561794 | 626 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 626 | 35.4963 | -120.6512 | No | Partly Cloudy-Drizzle;32-90 F | Service conductor | Broken- wire on ground | 24-0108210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970253 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 3345 | 20240907 | 3 | 20240907 | 800 | 2561720 | 477 | Distribution Circuit | Animal | Other | 1 | 477 | 35.5748 | -120.6984 | No | Clear;32-90 F | Jumper | Burned Open | 24-0108154 | OH | Sus | 46310594 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970175 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 10331 | 20240907 | 1043 | 20240907 | 1131 | 2561954 | 48 | Distribution Circuit | Animal | Bird found | 155 | 7440 | 35.3633 | -120.8348 | No | Partly Cloudy-Drizzle;32-90 F | Cutout- fuse holder | Broken | 24-0108220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970262 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | RECLOSER | A28 | 20240908 | 924 | 20240908 | 951 | 2562477 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 1832 | 49464 | 35.4622 | -120.6453 | No | Clear;32-90 F | Fuse | Normal | 24-0108349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970365 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | V66 | 20240908 | 935 | 20240908 | 1414 | 2562479 | 279 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 331 | 92349 | 35.3759 | -120.8526 | No | Overcast-Fog;32-90 F |  |  | 24-0108352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970366 | 0 | EPSS Ckt | Y | 2024 | GRD & INST OC
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | SWITCH | 6901 | 20240908 | 1007 | 20240908 | 1224 | 2562495 | 137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 149 | 20413 | 35.4581 | -120.6411 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 24-0107537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970369 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | TRANSFORMER | 513573940963 | 20240909 | 928 | 20240909 | 1020 | 2563196 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 312 | 34.6068 | -120.1369 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0108530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970600 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | 745714 | 20240909 | 1138 | 20240909 | 1238 | 2563347 | 60 | Distribution Circuit | Company Initiated | Personnel- company | 57 | 3420 | 34.7556 | -120.35 | No | Clear;32-90 F | Recloser | Normal | 24-0108650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970646 | 0 | EPSS Ckt | Y | 2024 | C INST OC
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 702241 | 20240909 | 1434 | 20240909 | 1558 | 2563593 | 84 | Distribution Circuit | Animal | Bird found | 4 | 336 | 35.5613 | -120.334 | No | Clear;Above 90 | Pothead(Riser Termination) | Normal | 24-0108881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970702 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | T0265 | 20240909 | 1746 | 20240909 | 1940 | 2563769 | 114 | Transformer only | Equipment Failure/Involved | Underground | 12 | 1368 | 35.5005 | -120.6507 | No | Clear;32-90 F |  | Malfunctioning | 24-0108934 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970728 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511701371180 | 20240909 | 1900 | 20240909 | 2256 | 2563838 | 236 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 236 | 35.4238 | -120.7864 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0108957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970745 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512304077045 | 20240909 | 1912 | 20240909 | 2039 | 2563850 | 87 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 174 | 35.5898 | -120.5889 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0108947 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970735 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 7583 | 20240909 | 2207 | 20240910 | 556 | 2563975 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5159 | 35.4991 | -120.7026 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0108960 | OH | Sus | 31708227 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1970749 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 1459 | 20240909 | 2249 | 20240910 | 127 | 2563994 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 26070 | 34.8964 | -120.4185 | No | Clear;32-90 F |  |  | 24-0108961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970750 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1107 | 182661107 | TRANSFORMER | 512024781648 | 20240910 | 1038 | 20240910 | 1048 | 2564446 | 10 | Transformer only | Animal | Other | 1 | 10 | 35.7138 | -120.6863 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0109107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970970 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | 745714 | 20240910 | 1126 | 20240910 | 1247 | 2564507 | 81 | Distribution Circuit | Company Initiated | Personnel- company | 57 | 4617 | 34.7556 | -120.35 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0109143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970989 | 0 | EPSS Ckt | Y | 2024 | C INST OC
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A30 | 20240910 | 1227 | 20240910 | 1343 | 2564588 | 76 | Distribution Circuit | 3rd Party | Other | 430 | 32680 | 35.4889 | -120.6644 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0109214 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971019 | 0 | EPSS Ckt | Y | 2024 | A & GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 2641 | 20240910 | 1338 | 20240910 | 1537 | 2564650 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 10710 | 35.5511 | -120.4866 | No | Clear;32-90 F |  |  | 24-0109309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971048 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1102 | 183041102 | RECLOSER | Y50 | 20240910 | 1642 | 20240911 | 300 | 2564755 | 618 | Distribution Circuit | Equipment Failure/Involved | Underground | 598 | 36946 | 34.6126 | -120.1756 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0109352 | UG | Sus | 46319516 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971050 | 0 | EPSS Ckt | Y | 2024 | B & GRD
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | JUMPER | FB JWO 7263 | 20240910 | 2037 | 20240911 | 108 | 2564861 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 5149 | 34.5995 | -120.13 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0108763 | OH | Sus | 31708067 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971069 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512045065625 | 20240910 | 2322 | 20240911 | 137 | 2564955 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 270 | 35.2742 | -120.6664 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0109428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971094 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20240911 | 1055 | 20240911 | 1333 | 2565414 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 34444 | 35.1757 | -120.5255 | No | Clear;32-90 F |  |  | 24-0109655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971312 | 0 | EPSS Ckt | Y | 2024 | B C INST
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 3983 | 20240911 | 1516 | 20240912 | 1700 | 2565715 | 733 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 86714 | 35.098 | -120.603 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0109930 | UG | Sus | 35580558 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971408 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 618168 | 20240911 | 2223 | 20240912 | 20 | 2566037 | 117 | Distribution Circuit | Animal | Bird found | 152 | 17784 | 35.5454 | -121.076 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109982 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971448 | 0 | EPSS Ckt | Y | 2024 | A/C INST
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | JUMPER | VERT JUMPERS 1P NE/OF CGC# 5957 | 20240911 | 2328 | 20240912 | 210 | 2566045 | 162 | Distribution Circuit | 3rd Party | Vehicle | 7 | 1134 | 35.0129 | -120.4748 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0109988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1971453 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | V38 | 20240912 | 545 | 20240912 | 905 | 2566158 | 200 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1390 | 278000 | 35.1274 | -120.5689 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0110016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971474 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | RECLOSER | M20 | 20240912 | 640 | 20240912 | 723 | 2566182 | 43 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 623 | 26789 | 34.8906 | -120.431 | No | Overcast-Fog;32-90 F | Transformer (UG) | Normal | 24-0110040 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971484 | 0 | Non-EPSS | N | 2024 | NONE
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 91545 | 20240912 | 654 | 20240912 | 1639 | 2566234 | 585 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 5 | 2925 | 34.8899 | -120.3152 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0110094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1971538 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20240912 | 1029 | 20240912 | 1223 | 2566525 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 24852 | 35.1757 | -120.5255 | No | Clear;32-90 F |  |  | 24-0110190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971670 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20240912 | 1302 | 20240912 | 1637 | 2566653 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 46870 | 35.1757 | -120.5255 | No | Clear;32-90 F |  |  | 24-0110304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971696 | 0 | EPSS Ckt | Y | 2024 | B&C PHASE
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 5181 | 20240912 | 1519 | 20240912 | 1803 | 2566785 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 6068 | 35.3618 | -120.8075 | No | Clear;32-90 F |  |  | 24-0110493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971722 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | FUSE | 674127 | 20240912 | 1601 | 20240912 | 1923 | 2566795 | 202 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 381 | 76962 | 34.8902 | -120.4275 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0110040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971714 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | RECLOSER | 560634 | 20240912 | 1653 | 20240912 | 2321 | 2566837 | 388 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2708 | 162604 | 34.9679 | -120.4529 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0110488 | OH | Sus | 31708672 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1971721 | 0 | Non-EPSS | N | 2024 | A AND C PHASE AND GRD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | FUSE | 3983 | 20240912 | 2049 | 20240912 | 2057 | 2566972 | 8 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 304 | 35.098 | -120.603 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0109930 | UG | Sus | 35580558 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971744 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512685353953 | 20240913 | 135 | 20240913 | 239 | 2567048 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 960 | 34.9583 | -120.4425 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken | 24-0110546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971773 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1105 | 182581105 | OCB | 1105/2 | 20240913 | 736 | 20240913 | 853 | 2567140 | 77 | Distribution Circuit | 3rd Party | Vehicle | 1782 | 137214 | 35.3202 | -120.693 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0110595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971806 | 0 | EPSS Ckt | Y | 2024 | A GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20240913 | 1150 | 20240913 | 1634 | 2567461 | 284 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 43504 | 35.1757 | -120.5255 | No | Clear;32-90 F |  |  | 24-0110791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971956 | 0 | EPSS Ckt | Y | 2024 | B & C
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | OCB | 1101/2/NORM | 20240913 | 1848 | 20240913 | 2012 | 2567806 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2092 | 118495 | 35.0079 | -120.4539 | No | Overcast;32-90 F |  |  | 24-0110935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972015 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | RECLOSER | M86 | 20240914 | 137 | 20240914 | 752 | 2567929 | 375 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 761 | 149536 | 35.0492 | -120.4827 | No | Overcast;32-90 F |  |  | 24-0110964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972044 | 0 | EPSS Ckt | Y | 2024 | A-B
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A10 | 20240914 | 631 | 20240914 | 902 | 2567971 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 411 | 27465 | 35.4109 | -120.5655 | No | Clear;32-90 F |  |  | 24-0110975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972058 | 0 | EPSS Ckt | Y | 2024 | B C
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | V66 | 20240914 | 1031 | 20240914 | 1228 | 2568152 | 117 | Distribution Circuit | Animal | Bird found | 310 | 36270 | 35.3759 | -120.8526 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0111031 | OH | Sus | 46321731 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972133 | 0 | EPSS Ckt | Y | 2024 | GRD INST OC
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | TRANSFORMER | 511972065081 | 20240914 | 1043 | 20240914 | 2006 | 2568164 | 563 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3941 | 35.259 | -120.69 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0111085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972175 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 1189 | 20240914 | 2111 | 20240914 | 2319 | 2568456 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1446 | 64172 | 34.677 | -120.1231 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 24-0111119 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972197 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512702153619 | 20240915 | 820 | 20240915 | 1603 | 2568585 | 463 | Transformer only | Equipment Failure/Involved | Overhead | 35 | 16205 | 34.9491 | -120.4367 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Broken | 24-0111161 | OH | Sus | 31708882 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972245 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | N04 | 20240915 | 843 | 20240915 | 925 | 2568613 | 42 | Distribution Circuit | Company Initiated | Operating error | 2080 | 87360 | 35.7334 | -120.8792 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0054002 | OH | Sus | 46062284 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972233 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6307 | 20240916 | 133 | 20240916 | 954 | 2569193 | 501 | Distribution Circuit | 3rd Party | Vehicle | 7 | 3507 | 34.9561 | -120.5583 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0111276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1972348 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | FUSE | 15257 | 20240916 | 1018 | 20240916 | 1521 | 2569371 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 30906 | 35.2953 | -120.6776 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0111295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972446 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | Y46 | 20240916 | 1100 | 20240916 | 1957 | 2569648 | 537 | Distribution Circuit | Equipment Failure/Involved | Overhead | 276 | 29892 | 34.6448 | -120.429 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0111489 | OH | Sus | 46322217 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1972556 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | TRANSFORMER | 513338849578 | 20240916 | 1328 | 20240916 | 1655 | 2569704 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 207 | 34.8419 | -120.2208 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0111597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972607 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | SWITCH | 827587 | 20240916 | 1717 | 20240916 | 1909 | 2569982 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 6720 | 35.0971 | -120.5074 | No | Partly Cloudy;32-90 F | Crossarm- Steel | Broken | 24-0111724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972639 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | SWITCH | 827587 | 20240916 | 1717 | 20240916 | 1909 | 2569982 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 6720 | 35.0971 | -120.5074 | No | Partly Cloudy;32-90 F | Crossarm- Steel | Broken | 24-0111724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972639 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M54 | 20240916 | 1840 | 20240916 | 2100 | 2570045 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 127 | 13911 | 34.8627 | -120.2773 | No | Partly Cloudy;32-90 F |  |  | 24-0111753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972655 | 0 | EPSS Ckt | Y | 2024 | A&B INST OC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512861262800 | 20240916 | 2230 | 20240916 | 2341 | 2570181 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 142 | 35.2015 | -120.3909 | No | Fog;32-90 F | Transformer (OH) | Leaking | 24-0111785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972679 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512168959382 | 20240917 | 150 | 20240917 | 221 | 2570215 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 248 | 35.1039 | -120.6195 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0111797 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972694 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | FUSE | 6909 | 20240917 | 749 | 20240917 | 1442 | 2570287 | 413 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 47 | 7865 | 34.6349 | -120.0803 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0111895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1972855 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 45657 | 20240917 | 916 | 20240917 | 1930 | 2570921 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1228 | 34.9588 | -120.5268 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0112150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972977 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 2669 | 20240917 | 941 | 20240917 | 1152 | 2570590 | 131 | Distribution Circuit | Animal | Bird found | 5 | 655 | 35.574 | -120.7934 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0111986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972913 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1101 | 182681101 | FUSE | TEMP LR 1101/2 | 20240917 | 1020 | 20240917 | 1355 | 2570642 | 215 | Distribution Circuit | Company Initiated | Personnel- company | 1028 | 221020 | 34.6967 | -120.1518 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102840 | OH | Sus | 31658094 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972897 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511460170475 | 20240917 | 1117 | 20240917 | 1733 | 2570681 | 376 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2632 | 35.4031 | -120.8668 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0111996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972922 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | R56 | 20240917 | 1339 | 20240917 | 1626 | 2570802 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 427 | 43619 | 35.6443 | -120.7067 | No | Clear;32-90 F |  |  | 24-0112055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972953 | 0 | EPSS Ckt | Y | 2024 | A GRD
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512043765547 | 20240917 | 1950 | 20240917 | 2129 | 2571051 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 495 | 35.2721 | -120.6668 | No | Clear;32-90 F | Fuse | Broken | 24-0112201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973001 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512043765532 | 20240917 | 2013 | 20240917 | 2128 | 2571060 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 33 | 2475 | 35.2717 | -120.6668 | No | Clear;32-90 F | Fuse | Broken | 24-0112202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973004 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511399571734 | 20240918 | 154 | 20240918 | 424 | 2571142 | 150 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1800 | 35.4371 | -120.8882 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0112218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973024 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | FUSE | 6141 | 20240919 | 642 | 20240919 | 1137 | 2572219 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 17895 | 35.0468 | -120.5771 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0112862 | OH | Sus | 31709196 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1973426 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 14027 | 20240919 | 642 | 20240919 | 855 | 2572221 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1596 | 35.088 | -120.578 | No | Overcast;32-90 F | Lightning Arrestor | Broken | 24-0112865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973432 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 317796 | 20240919 | 918 | 20240919 | 1218 | 2572386 | 180 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1546 | 268934 | 35.5433 | -120.7453 | No | Clear;32-90 F |  |  | 24-0112905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973506 | 0 | EPSS Ckt | Y | 2024 | A B PHASE AND GRD
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1102 | 182951102 | FUSE | 2297 | 20240919 | 1611 | 20240920 | 235 | 2572765 | 624 | Distribution Circuit | Equipment Failure/Involved | Underground | 95 | 26358 | 35.26 | -120.6945 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0113259 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973617 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30643 | 20240919 | 1619 | 20240919 | 1659 | 2572769 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 679 | 35.5135 | -120.6856 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0113252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973615 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | R82 | 20240919 | 1717 | 20240919 | 1937 | 2572821 | 140 | Distribution Circuit | Environmental/External | Lightning | 906 | 69080 | 35.5299 | -120.523 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0113269 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973621 | 0 | EPSS Ckt | Y | 2024 | B GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A20 | 20240919 | 1803 | 20240919 | 1932 | 2572850 | 89 | Distribution Circuit | Environmental/External | Lightning | 2849 | 253561 | 35.5005 | -120.6607 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0113285 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1973623 | 0 | EPSS Ckt | Y | 2024 | A-B-C
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6367 | 20240919 | 1948 | 20240919 | 2030 | 2572908 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 504 | 35.4868 | -120.6331 | No | Partly Cloudy;32-90 F |  |  | 24-0113321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973647 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | FUSE | 45767 | 20240919 | 1953 | 20240920 | 1020 | 2572910 | 867 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 11789 | 34.943 | -120.4427 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0113356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973658 | 1 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 848137 | 20240919 | 2005 | 20240919 | 2016 | 2572920 | 11 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 11 | 35.4629 | -120.6373 | No | Clear;32-90 F | Generator | Normal | 24-0113318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973640 | 0 | EPSS Ckt | Y | 2024 | C
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | RECLOSER | M58 | 20240919 | 2006 | 20240920 | 635 | 2572917 | 629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 9565 | 34.9152 | -120.383 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 24-0113317 | OH | Sus | 31709426 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973639 | 0 | EPSS Ckt | N | 2024 | B & GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | JUMPER | OJ 3 N/OF 6385 | 20240920 | 59 | 20240920 | 341 | 2572940 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 2916 | 34.9458 | -120.4351 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Burned/flashed | 24-0113398 | OH | Sus | 31709427 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973669 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 513397073055 | 20240920 | 124 | 20240920 | 736 | 2573009 | 372 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 744 | 35.4864 | -120.2191 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0113409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973673 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A20 | 20240920 | 526 | 20240920 | 720 | 2573043 | 114 | Distribution Circuit | Environmental/External | Lightning | 3142 | 358188 | 35.5005 | -120.6607 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0113415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973681 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A20 | 20240920 | 722 | 20240920 | 1401 | 2573091 | 399 | Distribution Circuit | Environmental/External | Lightning | 3141 | 195188 | 35.5005 | -120.6607 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0113415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973700 | 0 | EPSS Ckt | Y | 2024 | A B C
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 1955 | 20240920 | 840 | 20240920 | 922 | 2573223 | 42 | Distribution Circuit | Animal | Squirrel | 3 | 126 | 34.6502 | -120.1037 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0113528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973845 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | FUSE | 5919 | 20240920 | 1737 | 20240920 | 1905 | 2573722 | 88 | Distribution Circuit | Animal | Bird found | 33 | 2904 | 35.611 | -120.6931 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0113885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973952 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 13085 | 20240920 | 2146 | 20240921 | 1427 | 2573793 | 1001 | Distribution Circuit | 3rd Party | Vehicle | 7 | 6833 | 35.135 | -120.571 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0113895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1973965 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | RECLOSER | P26 | 20240921 | 1135 | 20240921 | 1153 | 2574039 | 18 | Distribution Circuit | Animal | Bird found | 465 | 8370 | 35.629 | -120.6607 | No | Clear;32-90 F | Fuse | Normal | 24-0113971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974075 | 0 | EPSS Ckt | N | 2024 | C GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | FUSE | 6355 | 20240921 | 1139 | 20240921 | 1238 | 2574040 | 59 | Distribution Circuit | Animal | Bird found | 120 | 7080 | 35.6258 | -120.6689 | No | Clear;32-90 F | Fuse | Normal | 24-0114000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974090 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | FUSE | 6141 | 20240922 | 15 | 20240922 | 214 | 2574313 | 119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 13209 | 35.0468 | -120.5771 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0114087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974150 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511501267093 | 20240922 | 1556 | 20240922 | 1615 | 2574557 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 152 | 35.3103 | -120.8501 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0114141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974256 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20240923 | 815 | 20240923 | 823 | 2575029 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 383 | 3064 | 35.2197 | -120.5967 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0114227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974380 | 0 | EPSS Ckt | Y | 2024 | SGF/ DCD
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | TRANSFORMER | 512672153344 | 20240923 | 1113 | 20240923 | 1618 | 2575306 | 305 | Transformer only | Vegetation | Tree - branch fell on line | 12 | 3660 | 34.9414 | -120.4465 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0114349 | OH | Sus | 46325644 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1974523 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511563167245 | 20240923 | 1856 | 20240924 | 205 | 2575730 | 429 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1716 | 35.3151 | -120.8294 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0114594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974605 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | OTHER | J571 TWD T2965 | 20240923 | 1942 | 20240923 | 2154 | 2575741 | 132 | Distribution Circuit | Equipment Failure/Involved | Underground | 32 | 4224 | 35.6568 | -120.3687 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0114561 | UG | Sus | 35583128 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974600 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 30609 | 20240924 | 38 | 20240924 | 232 | 2575860 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1938 | 35.4934 | -120.2276 | No | Clear;32-90 F |  |  | 24-0114640 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974642 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | RECLOSER | 1108/2 | 20240924 | 757 | 20240924 | 1246 | 2576003 | 181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5855 | 324499 | 35.3202 | -120.6929 | No | Clear;32-90 F | Switch (OH) | Arcing | 24-0091807 | OH | Sus | 35238137 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1974686 | 0 | EPSS Ckt | N | 2024 | NONE
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | JUMPER | JUMPERS 2P SS OF CGC# 512668553345 | 20240924 | 1040 | 20240924 | 1329 | 2576227 | 169 | Distribution Circuit | Vegetation | Tree - grew into line | 28 | 4732 | 34.9414 | -120.4485 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0114843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974862 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1108 | 182611108 | RECLOSER | P26 | 20240924 | 1140 | 20240924 | 1151 | 2576389 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 466 | 5126 | 35.629 | -120.6607 | No | Clear;32-90 F |  |  | 24-0114886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974893 | 0 | EPSS Ckt | N | 2024 | A/GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512721053591 | 20240924 | 1437 | 20240924 | 2128 | 2576568 | 411 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 7809 | 34.9484 | -120.4303 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0115096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974966 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | TRANSFORMER | 511553571504 | 20240924 | 1755 | 20240924 | 1831 | 2576745 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 72 | 35.4323 | -120.8357 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0115119 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1974978 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | 597930 | 20240925 | 606 | 20240925 | 721 | 2576969 | 75 | Distribution Circuit | 3rd Party | Vehicle | 1239 | 92925 | 34.6603 | -120.4533 | No | Overcast-Fog;32-90 F | Anchor or Guy | Broken | 24-0115181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1975034 | 0 | EPSS Ckt | Y | 2024 | A&GRD INST
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | FUSE | 89499 | 20240925 | 852 | 20240925 | 1435 | 2577152 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 343 | 35.0751 | -120.5238 | No | Overcast-Fog;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0115361 | OH | Sus | 46326934 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975255 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 7195 | 20240925 | 1513 | 20240925 | 1612 | 2577627 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 236 | 34.6084 | -120.3652 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0115603 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975331 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20240925 | 1627 | 20240925 | 1854 | 2577695 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 931 | 81217 | 35.4622 | -120.6221 | No | Clear;32-90 F |  |  | 24-0115664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1975344 | 0 | EPSS Ckt | Y | 2024 | A&C
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | R92 | 20240925 | 1924 | 20240926 | 350 | 2577811 | 506 | Distribution Circuit | Animal | Bird found | 969 | 52204 | 35.5705 | -120.6481 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0115693 | OH | Sus | 31710090 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1975366 | 0 | EPSS Ckt | N | 2024 | B GRD
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 159459 | 20240926 | 859 | 20240926 | 1647 | 2578127 | 468 | Distribution Circuit | Animal | Bird found | 1 | 468 | 35.4802 | -120.2377 | No | Clear;32-90 F | Fuse | Burned Open | 24-0116240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975683 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | R82 | 20240926 | 935 | 20240926 | 1305 | 2578210 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 907 | 78886 | 35.5299 | -120.523 | No | Partly Cloudy;32-90 F |  |  | 24-0115852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975554 | 0 | EPSS Ckt | Y | 2024 | C PHASE AND GRD
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512941379081 | 20240926 | 1500 | 20240927 | 235 | 2578503 | 695 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 695 | 35.6489 | -120.3773 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0116204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1975665 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1107 | 182661107 | RECLOSER | R88 | 20240927 | 50 | 20240927 | 1315 | s1975746 | 741 | Distribution Circuit | 3rd Party | Vehicle | 244 | 156942 | 35.7084 | -120.6137 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 24-0116301 | OH | Sus | 35583976 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1975746 | 0 | EPSS Ckt | N | 2024 | AB
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 901690 | 20240927 | 645 | 20240927 | 1136 | 2579070 | 291 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 284 | 82644 | 35.5595 | -120.7826 | No | Clear;32-90 F |  |  | 24-0116321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975761 | 0 | EPSS Ckt | Y | 2024 | A C
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20240927 | 647 | 20240927 | 1051 | 2579073 | 244 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 132 | 32208 | 35.3806 | -120.4438 | No | Clear;32-90 F |  |  | 24-0116322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975762 | 0 | EPSS Ckt | Y | 2024 | A B INST
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512700351280 | 20240927 | 1441 | 20240927 | 1457 | 2579565 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 272 | 34.8847 | -120.4353 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0116754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975994 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | TRANSFORMER | 513815241948 | 20240927 | 1756 | 20240927 | 2111 | 2579653 | 195 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 390 | 34.6354 | -120.057 | No | Clear;32-90 F | Fuse | Broken | 24-0116824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976024 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20240927 | 2300 | 20240928 | 1234 | 2579757 | 814 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 190 | 154660 | 34.5979 | -120.0297 | No | Clear;32-90 F |  |  | 24-0116844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976050 | 0 | EPSS Ckt | Y | 2024 | B C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | 483444 | 20240928 | 1537 | 20240929 | 1103 | 2580219 | 1166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2993 | 404500 | 35.2892 | -120.6524 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0116938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976221 | 0 | EPSS Ckt | Y | 2024 | GRD
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 5087 | 20240929 | 710 | 20240929 | 1914 | 2580486 | 724 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1636 | 35.2948 | -120.7619 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0117049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976331 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512147059855 | 20240929 | 756 | 20240929 | 1631 | 2580539 | 515 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1545 | 35.1169 | -120.6269 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0117040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976322 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | JUMPER | OJ 1 SPAN N/OF CGC # 512669771808 | 20240929 | 1100 | 20240929 | 1353 | 2580613 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 173 | 35.4524 | -120.4641 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0117037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976320 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | Q12 | 20240930 | 647 | 20240930 | 1010 | 2580989 | 203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 172 | 34916 | 35.1396 | -120.5208 | No | Clear-Rain;32-90 F |  |  | 24-0117173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976434 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | RECLOSER | M06 | 20240930 | 914 | 20240930 | 1729 | 2581219 | 495 | Distribution Circuit | 3rd Party | Vehicle | 828 | 88651 | 34.9493 | -120.4202 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 24-0117242 | OH | Sus | 31710328 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976561 | 0 | Non-EPSS | N | 2024 | A PHASE & GRD
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512282154102 | 20240930 | 1456 | 20240930 | 2131 | 2581116 | 395 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3555 | 34.9594 | -120.5771 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0117434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976633 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 9421 | 20240930 | 1655 | 20240930 | 1943 | 2581740 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 504 | 35.1295 | -120.5089 | No | Clear;32-90 F |  |  | 24-0117533 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976670 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | 440856 | 20241001 | 639 | 20241001 | 913 | 2581922 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 566 | 87164 | 35.4611 | -120.6732 | No | Clear;32-90 F |  |  | 24-0117594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1976716 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | SWITCH | 6077 | 20241001 | 839 | 20241001 | 1600 | 2582071 | 441 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 21849 | 34.5116 | -120.2371 | No | Overcast-Fog;32-90 F | Jumper | Burned Open | 24-0117959 | OH | Sus | 46329496 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1977018 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | JUMPER | 45481 | 20241001 | 1111 | 20241001 | 1455 | 2582299 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 9408 | 34.9685 | -120.4462 | No | Clear;32-90 F | Jumper | Burned Open | 24-0117898 | OH | Sus | 46329929 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1976999 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 3873 | 20241001 | 1312 | 20241001 | 1425 | 2582443 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 3577 | 35.5499 | -120.6264 | No | Clear;32-90 F |  |  | 24-0117935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977015 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 512166659277 | 20241001 | 1352 | 20241001 | 1633 | 2582275 | 161 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1288 | 35.101 | -120.6201 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0117907 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977002 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | 87034 | 20241001 | 1529 | 20241001 | 1651 | 2582551 | 82 | Distribution Circuit | Equipment Failure/Involved | Underground | 732 | 60024 | 35.7811 | -120.9891 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0117979 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977020 | 0 | EPSS Ckt | Y | 2024 | A PHASE & INST OC
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | RECLOSER | 317156 | 20241001 | 1635 | 20241002 | 1251 | 2582703 | 1216 | Distribution Circuit | Animal | Bird found | 52 | 6735 | 35.4156 | -120.8725 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0118017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977033 | 0 | EPSS Ckt | Y | 2024 | B&C PHASE
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | RECLOSER | 553934 | 20241001 | 1640 | 20241002 | 130 | 2582707 | 530 | Distribution Circuit | Company Initiated | Coordination failure | 97 | 50922 | 35.5338 | -120.6932 | No | Clear;32-90 F | Recloser | Normal | 24-0118063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977059 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | TRANSFORMER | 512093366273 | 20241001 | 1833 | 20241001 | 1947 | 2582780 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 1258 | 35.2924 | -120.6501 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0118041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977043 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | TRANSFORMER | T325 | 20241001 | 1843 | 20241002 | 1517 | 2582967 | 1234 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 4412 | 35.7557 | -120.982 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0118104 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977095 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | V38 | 20241002 | 915 | 20241002 | 937 | 2583268 | 22 | Distribution Circuit | Company Initiated | Personnel- company | 1470 | 32340 | 35.1274 | -120.5689 | No | Clear;32-90 F | Fuse | Normal | 24-0118215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977247 | 0 | EPSS Ckt | Y | 2024 | SFG & DCD
LOS PADRES | PASO ROBLES | SAN MIGUEL-1107 | 182661107 | RECLOSER | R54 | 20241002 | 1104 | 20241002 | 1212 | 2583431 | 68 | Distribution Circuit | Animal | Bird found | 450 | 30600 | 35.7105 | -120.641 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0118296 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977300 | 0 | EPSS Ckt | Y | 2024 | A PHASE & GRD
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M54 | 20241002 | 1124 | 20241002 | 1331 | 2583475 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 127 | 16129 | 34.8627 | -120.2773 | No | Clear;32-90 F | Regulator | Burned/flashed | 24-0118311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977307 | 0 | EPSS Ckt | Y | 2024 | C PHASE- GRD- INST OC
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512784653972 | 20241002 | 1128 | 20241002 | 1142 | 2583335 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 140 | 34.9592 | -120.4094 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0118329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977312 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | TRANSFORMER | 512174760236 | 20241002 | 1247 | 20241002 | 1401 | 2583563 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 814 | 35.1273 | -120.618 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0118356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977330 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | W12 | 20241002 | 1445 | 20241002 | 2201 | 2583694 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 783 | 80975 | 35.5487 | -121.0892 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0118492 | OH | Sus | 35585038 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977359 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512441378266 | 20241002 | 1943 | 20241003 | 118 | 2584127 | 335 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 335 | 35.6244 | -120.5442 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0118654 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977418 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512557451831 | 20241002 | 2008 | 20241002 | 2135 | 2584142 | 87 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 435 | 34.8989 | -120.4834 | No | Clear;32-90 F |  |  | 24-0118658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977422 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 512000664189 | 20241003 | 6 | 20241003 | 327 | 2584217 | 201 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 402 | 35.2347 | -120.6801 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0118694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977445 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | 838078 | 20241003 | 622 | 20241003 | 1230 | 2584325 | 368 | Distribution Circuit | 3rd Party | Vehicle | 160 | 12520 | 34.6455 | -120.4608 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0118713 | OH | Sus | 31710829 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977453 | 0 | EPSS Ckt | Y | 2024 | BC
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | TRANSFORMER | 511019275167 | 20241003 | 945 | 20241003 | 1006 | 2584611 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 21 | 35.5283 | -121.0195 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0118853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977593 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | 483444 | 20241003 | 1439 | 20241003 | 1624 | 2584915 | 105 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2993 | 243655 | 35.2892 | -120.6524 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0119074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977639 | 0 | EPSS Ckt | Y | 2024 | A GRD
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | RECLOSER | N42 | 20241003 | 1625 | 20241003 | 1639 | 2585055 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 2279 | 31906 | 35.8683 | -120.843 | No | Clear;Above 90 | Recloser | Normal | 24-0119150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977658 | 0 | EPSS Ckt | N | 2024 | DCD
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | OTHER | T3158 TWD T3157 | 20241003 | 1847 | 20241003 | 1948 | 2585159 | 61 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 1464 | 35.6059 | -120.6449 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0119198 | UG | Sus | 35585359 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977681 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 511940762376 | 20241003 | 2320 | 20241004 | 31 | 2585274 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 355 | 35.1846 | -120.6984 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0119255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977717 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | RECLOSER | A64 | 20241004 | 526 | 20241004 | 801 | 2585380 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2919 | 419097 | 35.5233 | -120.6936 | No | Clear;32-90 F |  |  | 24-0119283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977745 | 0 | EPSS Ckt | Y | 2024 | B & GRD
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | OCB | 1101/2 | 20241004 | 629 | 20241004 | 831 | 2585418 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3558 | 138133 | 35.5712 | -121.0559 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0119289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977748 | 0 | EPSS Ckt | Y | 2024 | INST OC TGT
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 2513 | 20241004 | 951 | 20241004 | 1105 | 2585660 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 3700 | 35.5187 | -120.7008 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0119471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977903 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 307832 | 20241004 | 1106 | 20241004 | 1147 | 2585743 | 41 | Distribution Circuit | Company Initiated | Personnel- company | 1327 | 54407 | 35.5578 | -120.7747 | No | Clear;32-90 F | Recloser | Normal | 24-0119479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977906 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | 263406 | 20241005 | 903 | 20241005 | 1039 | 2586652 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 4128 | 34.6578 | -120.091 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0119776 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978055 | 0 | EPSS Ckt | Y | 2024 | A
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | RECLOSER | 597930 | 20241006 | 12 | 20241006 | 757 | 2587101 | 465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1239 | 208222 | 34.6603 | -120.4533 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0119896 | OH | Sus | 46332340 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1978133 | 0 | EPSS Ckt | Y | 2024 | A- SGF- & DCD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | RECLOSER | 891294 | 20241006 | 655 | 20241006 | 919 | 2587156 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 881 | 65638 | 35.1342 | -120.5702 | No | Overcast;32-90 F |  |  | 24-0119906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978147 | 0 | EPSS Ckt | Y | 2024 | AB
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | TRANSFORMER | 512119573420 | 20241006 | 1607 | 20241006 | 1954 | 2587449 | 227 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1362 | 35.489 | -120.6488 | No | Clear;Above 90 | Cutout- fuse holder | Broken | 24-0119970 | OH | Sus | 31711246 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978219 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | RECLOSER | 560634 | 20241006 | 2201 | 20241007 | 757 | 2587804 | 595 | Distribution Circuit | Equipment Failure/Involved | Overhead | 341 | 202895 | 34.9679 | -120.4529 | No | Clear;32-90 F | Cutout- fuse holder | Arcing | 24-0120016 | OH | Sus | 31711224 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978267 | 0 | Non-EPSS | N | 2024 | NONE
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512701853471 | 20241007 | 1532 | 20241007 | 2007 | 2588554 | 275 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 3850 | 34.945 | -120.4368 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0120392 | OH | Sus | 31711211 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978605 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A70 | 20241007 | 1929 | 20241007 | 2239 | 2588913 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1721 | 257102 | 35.5023 | -120.649 | No | Clear;32-90 F |  |  | 24-0120428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978630 | 0 | EPSS Ckt | Y | 2024 | A & B
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 31153 | 20241007 | 2042 | 20241008 | 1207 | 2588948 | 218 | Distribution Circuit | Equipment Failure/Involved | Underground | 269 | 57754 | 35.5507 | -120.728 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0120470 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978654 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | FUSE | 3465 | 20241007 | 2231 | 20241008 | 308 | 2588994 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 7166 | 35.1071 | -120.5958 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0120465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978652 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5475 | 20241008 | 1331 | 20241008 | 1501 | 2589652 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2070 | 35.5643 | -120.5874 | No | Clear;32-90 F |  |  | 24-0120834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978943 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1104 | 182721104 | SWITCH | 228367 | 20241008 | 1803 | 20241008 | 1833 | 2589853 | 30 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 330 | 34.6368 | -120.1147 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0120911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978965 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 159459 | 20241009 | 843 | 20241009 | 1103 | 2590362 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 140 | 35.4802 | -120.2377 | No | Clear;32-90 F |  |  | 24-0121233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1979225 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 9023 | 20241009 | 854 | 20241009 | 1023 | 2590386 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 89 | 35.2686 | -120.6469 | No | Partly Cloudy;32-90 F |  |  | 24-0121170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979204 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | N30 | 20241009 | 1231 | 20241009 | 1315 | 2590686 | 44 | Distribution Circuit | Company Initiated | Personnel- company | 1683 | 74052 | 35.626 | -120.8965 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0121283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979249 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512747453951 | 20241009 | 1406 | 20241009 | 1705 | 2590762 | 179 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2148 | 34.9585 | -120.4218 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0121346 | OH | Sus | 31711217 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979275 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512680754456 | 20241009 | 1558 | 20241009 | 1855 | 2590810 | 177 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 708 | 34.972 | -120.4444 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0121447 | OH | Sus | 46333649 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979295 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 14405 | 20241009 | 1650 | 20241009 | 1730 | 2591035 | 40 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 40 | 35.2609 | -120.6722 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0121537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979313 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | TRANSFORMER | 512731451723 | 20241010 | 1206 | 20241010 | 1513 | 2591325 | 187 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 935 | 34.8971 | -120.4253 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 24-0121801 | OH | Sus | 31712349 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979539 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | 483444 | 20241010 | 1540 | 20241010 | 1754 | 2591739 | 134 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 2993 | 292549 | 35.2892 | -120.6524 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0121934 | OH | Sus | 31712373 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979570 | 0 | EPSS Ckt | Y | 2024 | B&GRD INST OC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 136678 | 20241010 | 1625 | 20241011 | 28 | 2591724 | 483 | Distribution Circuit | Vegetation | Tree - branch fell on line | 189 | 19467 | 35.1945 | -120.7142 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0121959 | OH | Sus | 46337374 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979574 | 0 | EPSS Ckt | N | 2024 | NA
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20241010 | 1740 | 20241010 | 1907 | 2591811 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 189 | 16443 | 34.5979 | -120.0297 | No | Clear;32-90 F |  |  | 24-0121984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1979579 | 0 | EPSS Ckt | Y | 2024 | AB & C PHSE
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 30313 | 20241010 | 1910 | 20241010 | 2001 | 2591843 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 1989 | 35.6716 | -120.6055 | No | Partly Cloudy;32-90 F | Anchor or Guy | Normal | 24-0122000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979586 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | RECLOSER | A64 | 20241011 | 623 | 20241011 | 913 | 2591988 | 170 | Distribution Circuit | Animal | Bird found | 2919 | 205930 | 35.5233 | -120.6936 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0122053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1979643 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | FUSE | 45189 | 20241012 | 1431 | 20241012 | 1547 | 2593155 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 203 | 34.8649 | -120.3697 | No | Partly Cloudy;32-90 F |  |  | 24-0122612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980043 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PALMER-1101 | 183031101 | TRANSFORMER | 513154246026 | 20241012 | 1543 | 20241012 | 1941 | 2593222 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 797 | 28182 | 34.7434 | -120.28 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0122615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980046 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | RECLOSER | M98 | 20241013 | 1652 | 20241013 | 1738 | 2593650 | 46 | Distribution Circuit | Animal | Bird found | 36 | 1656 | 34.8946 | -120.3018 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0122717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980147 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE INST OC
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | TRANSFORMER | 513131753045 | 20241013 | 1805 | 20241013 | 2240 | 2593665 | 275 | Transformer only | Animal | Other | 1 | 275 | 34.937 | -120.2934 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0122723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980153 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 20909 | 20241013 | 2029 | 20241014 | 135 | 2593750 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2448 | 34.6647 | -120.4166 | No | Overcast-Fog-Rain;32-90 F | Connector or Splice (OH) | Broken | 24-0122727 | OH | Sus | 31712740 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980158 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | TRANSFORMER | 512302260173 | 20241014 | 153 | 20241014 | 326 | 2593744 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 465 | 35.1263 | -120.5754 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0122732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980164 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 43125 | 20241014 | 304 | 20241014 | 610 | 2593818 | 186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 6510 | 35.3924 | -120.8574 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0122742 | OH | Sus | 31712741 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980172 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | OCB | 1111/2 | 20241014 | 357 | 20241014 | 1307 | 2593824 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1994 | 366677 | 34.9503 | -120.4442 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0122748 | OH | Sus | 31712742 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1980178 | 0 | Non-EPSS | N | 2024 | A- B- & C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20241014 | 720 | 20241014 | 1232 | 2593896 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 218 | 65676 | 35.1757 | -120.5255 | No | Overcast-Fog;32-90 F | Jumper | Normal | 24-0122766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980196 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 7421 | 20241014 | 1205 | 20241014 | 1423 | 2594367 | 138 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 138 | 34.9415 | -120.5746 | No | Partly Cloudy;32-90 F | Metering Equipment | Failed/Faulted | 24-0123009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980460 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | JUMPER | OPEN JUMPER | 20241014 | 1328 | 20241014 | 1805 | 2594486 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 4354 | 34.9432 | -120.4376 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0123022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1980464 | 1 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511587569806 | 20241014 | 1425 | 20241014 | 1820 | 2594407 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 235 | 35.3859 | -120.8235 | No | Overcast;32-90 F | Transformer (OH) | Contaminated | 24-0123019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980462 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511564867443 | 20241015 | 15 | 20241015 | 144 | 2594747 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1157 | 35.3205 | -120.829 | No | Overcast;32-90 F | Fuse | Broken | 24-0123151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980514 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 6675 | 20241015 | 851 | 20241015 | 1006 | 2595074 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 300 | 35.5935 | -120.5945 | No | Clear;32-90 F |  |  | 24-0123288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980707 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20241015 | 854 | 20241015 | 1102 | 2595039 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 190 | 24320 | 34.5979 | -120.0297 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0123254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980647 | 0 | EPSS Ckt | Y | 2024 | A & C
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T3231 | 20241015 | 1324 | 20241015 | 1852 | 2595379 | 328 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 1968 | 35.0259 | -120.4976 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0123418 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980785 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | SWITCH | 9113 | 20241015 | 2230 | 20241016 | 136 | 2595709 | 186 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 3534 | 35.1219 | -120.6042 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0123619 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980865 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 31713 | 20241016 | 114 | 20241016 | 336 | 2595735 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1278 | 35.6088 | -120.6077 | No | Clear;32-90 F |  |  | 24-0123638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980881 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 777686 | 20241016 | 845 | 20241016 | 1023 | 2595905 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1246 | 121224 | 35.1989 | -120.6058 | No | Overcast;32-90 F | Capacitor | Failed/Faulted | 24-0123790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980977 | 0 | EPSS Ckt | Y | 2024 | A & B
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | J742 TWD T1201 | 20241016 | 1035 | 20241017 | 151 | 2596595 | 916 | Distribution Circuit | Equipment Failure/Involved | Underground | 203 | 185948 | 35.1399 | -120.6287 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0124219 | UG | Sus | 35589612 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981172 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 513064180190 | 20241016 | 1237 | 20241016 | 1426 | 2596093 | 109 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 109 | 35.682 | -120.3367 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0124036 | OH | Sus | 46340066 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981108 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 468301 | 20241016 | 1757 | 20241016 | 1919 | 2596541 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 2050 | 35.663 | -120.3949 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0124208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981163 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | 511752564955 | 20241016 | 2052 | 20241016 | 2306 | 2596650 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 268 | 35.2541 | -120.7624 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0124283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981198 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 64223 | 20241016 | 2209 | 20241017 | 245 | 2596677 | 276 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 8100 | 35.1231 | -120.5669 | No | Partly Cloudy;32-90 F |  |  | 24-0124285 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981200 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 10615 | 20241017 | 706 | 20241017 | 831 | 2596824 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1530 | 35.3548 | -120.7864 | Yes | Partly Cloudy;32-90 F |  |  | 24-0124377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981238 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | TRANSFORMER | 510933579180 | 20241018 | 420 | 20241018 | 726 | 2598148 | 186 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 186 | 35.637 | -121.0516 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0124889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981649 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | RECLOSER | 858898 | 20241018 | 825 | 20241019 | 1100 | 2598343 | 1595 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 159 | 253605 | 34.8684 | -120.2483 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981691 | 0 | EPSS Ckt | N | 2024 | NONE
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | RECLOSER | W04 | 20241018 | 1549 | 20241018 | 1726 | 2598857 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 466 | 45202 | 35.3613 | -120.8365 | No | Clear;32-90 F |  |  | 24-0125207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981834 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 984519 | 20241019 | 913 | 20241019 | 1010 | 2599229 | 57 | Distribution Circuit | Animal | Squirrel | 60 | 3420 | 35.5028 | -120.6695 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0125347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981971 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | FUSE | 8947 | 20241019 | 1135 | 20241020 | 11 | 2599318 | 756 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 7776 | 34.9871 | -120.4759 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0125410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982001 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | PALMER-1101 | 183031101 | RECLOSER | M84 | 20241020 | 55 | 20241020 | 1235 | 2599607 | 700 | Distribution Circuit | Animal | Bird found | 912 | 401896 | 34.8208 | -120.2887 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0125488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982052 | 0 | EPSS Ckt | Y | 2024 | SGF/ DCD
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | FUSE | 14739 | 20241021 | 346 | 20241021 | 500 | 2599978 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 8440 | 35.1229 | -120.5951 | No | Overcast-Fog;32-90 F |  |  | 24-0125589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982154 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20241021 | 722 | 20241021 | 1226 | 2600017 | 304 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 63368 | 35.1757 | -120.5255 | No | Clear;32-90 F |  |  | 24-0125605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982170 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | RECLOSER | 961060 | 20241021 | 805 | 20241021 | 937 | 2600049 | 92 | Distribution Circuit | Animal | Squirrel | 3479 | 194350 | 35.3001 | -120.6751 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0125630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982186 | 0 | EPSS Ckt | Y | 2024 | A PAHSE
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 46347 | 20241021 | 926 | 20241021 | 1001 | 2600245 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 35 | 34.759 | -120.3931 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0125725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982331 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 100000026687 | 20241021 | 939 | 20241021 | 945 | 2600062 | 6 | Transformer only | 3rd Party | Customer Equipment | 1 | 6 | 34.6553 | -120.4887 | No | Overcast;32-90 F | Customer Equipment | Normal | 24-0125701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1982319 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 11045 | 20241021 | 943 | 20241021 | 1825 | 2600445 | 522 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 522 | 34.9432 | -120.5254 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0125861 | UG | Sus | 31713226 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982375 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | 514592 | 20241021 | 956 | 20241021 | 1153 | 2600297 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2623 | 208261 | 35.5368 | -120.7146 | No | Clear;32-90 F |  |  | 24-0125714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982325 | 0 | EPSS Ckt | Y | 2024 | B & GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | SWITCH | 6546 | 20241021 | 1516 | 20241021 | 1613 | s1982396 | 57 | Distribution Circuit | Equipment Failure/Involved | Underground | 118 | 731 | 35.5469 | -120.7075 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0125917 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982396 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 31005 | 20241021 | 2035 | 20241021 | 2327 | 2600758 | 172 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 2752 | 35.534 | -120.733 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0126034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1982418 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | SWITCH | 14103 | 20241022 | 14 | 20241022 | 354 | 2600809 | 220 | Distribution Circuit | Vegetation | Tree - grew into line | 1133 | 36515 | 35.5716 | -121.1105 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0126036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982435 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20241022 | 420 | 20241022 | 807 | 2600833 | 227 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 189 | 42903 | 34.5979 | -120.0297 | No | Clear;32-90 F |  |  | 24-0126056 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982443 | 0 | EPSS Ckt | Y | 2024 | B/C
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 7337 | 20241022 | 644 | 20241022 | 845 | 2600848 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 847 | 35.5819 | -120.5424 | No | Partly Cloudy;32-90 F |  |  | 24-0126127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982527 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 721823 | 20241022 | 834 | 20241022 | 921 | 2600967 | 47 | Distribution Circuit | Company Initiated | Personnel- company | 1214 | 56815 | 35.1986 | -120.607 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0126132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982545 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | T2939 | 20241022 | 910 | 20241022 | 1342 | 2601057 | 272 | Transformer only | Animal | Other | 26 | 7072 | 35.0523 | -120.5341 | No | Clear;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0126153 | UG | Sus | 46343158 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982593 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | RECLOSER | 941946 | 20241022 | 1000 | 20241022 | 1242 | 2601171 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 679 | 88719 | 35.5719 | -120.7913 | No | Clear;32-90 F |  |  | 24-0126181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982641 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A70 | 20241022 | 1128 | 20241022 | 1408 | 2601273 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1721 | 249947 | 35.5023 | -120.649 | No | Clear;32-90 F |  |  | 24-0126283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982664 | 0 | EPSS Ckt | Y | 2024 | A & B PHSE
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 4045 | 20241022 | 1344 | 20241022 | 1500 | 2601429 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 177 | 35.5647 | -120.5405 | No | Clear;32-90 F |  |  | 24-0126447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982707 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | TRANSFORMER | 1637 | 20241022 | 1419 | 20241023 | 356 | 2601691 | 817 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 15653 | 35.0249 | -120.4986 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0126537 | UG | Sus | 35592203 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982753 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V14 | 20241022 | 1443 | 20241022 | 1449 | 2601474 | 6 | Distribution Circuit | Company Initiated | Personnel- company | 1205 | 7230 | 35.1791 | -120.6181 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0126448 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982708 | 0 | EPSS Ckt | N | 2024 | SGD
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | JUMPER | OJS 1 SP/N/OF CGC-512699953968 @ LINE & BUCK | 20241023 | 1713 | 20241023 | 1814 | 2602438 | 61 | Distribution Circuit | Vegetation | Tree - grew into line | 11 | 671 | 34.9587 | -120.4376 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983054 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V58 | 20241023 | 2210 | 20241024 | 2 | 2602596 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2911 | 260843 | 35.247 | -120.6494 | No | Partly Cloudy;32-90 F |  |  | 24-0127105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983082 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE INST OC
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | FUSE | 6123 | 20241024 | 1035 | 20241024 | 1238 | 2603009 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 6765 | 35.038 | -120.4832 | No | Partly Cloudy;32-90 F |  |  | 24-0127357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983306 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | FUSE | 6141 | 20241024 | 1618 | 20241024 | 2354 | 2603229 | 456 | Distribution Circuit | Vegetation | Tree - branch fell on line | 110 | 20772 | 35.0468 | -120.5771 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0127621 | OH | Sus | 31713743 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983360 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | RECLOSER | Y06 | 20241024 | 1629 | 20241025 | 1453 | 2603248 | 1344 | Distribution Circuit | 3rd Party | Other | 345 | 52936 | 34.6201 | -120.2103 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0127584 | OH | Sus | 35592656 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983348 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20241024 | 1704 | 20241024 | 1859 | 2603279 | 115 | Distribution Circuit | Animal | Bird found | 931 | 75717 | 35.4622 | -120.6221 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983352 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | TRANSFORMER | 512830646378 | 20241024 | 1755 | 20241025 | 240 | 2603310 | 525 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1050 | 34.7512 | -120.3874 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0127658 | OH | Sus | 31713648 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983389 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y46 | 20241026 | 34 | 20241026 | 420 | 2604417 | 226 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 276 | 62376 | 34.6448 | -120.429 | No | Overcast;32-90 F |  |  | 24-0128100 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983648 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE- INST O C
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M52 | 20241026 | 823 | 20241026 | 842 | 2604626 | 19 | Distribution Circuit | Company Initiated | Personnel- company | 2 | 38 | 34.9254 | -120.3465 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983717 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | RECLOSER | A22 | 20241026 | 1003 | 20241026 | 1200 | 2604749 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1418 | 165906 | 35.4741 | -120.6661 | No | Clear;32-90 F |  |  | 24-0128149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983754 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | SWITCH | 8387 | 20241026 | 1436 | 20241026 | 1453 | 2604940 | 17 | Distribution Circuit | Company Initiated | Return Circuit Normal | 9 | 153 | 34.6112 | -120.2446 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0127584 | OH | Sus | 35592656 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983809 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V40 | 20241026 | 1826 | 20241027 | 1035 | 2605096 | 969 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 435 | 103809 | 35.2197 | -120.5967 | No | Partly Cloudy;32-90 F |  |  | 24-0128228 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983836 | 0 | EPSS Ckt | Y | 2024 | C PHASE- SGF- DCD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512274080368 | 20241026 | 1846 | 20241026 | 2334 | 2604994 | 288 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 1152 | 35.6804 | -120.6024 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0128229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983838 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | JUMPER | OPEN JUMPER | 20241027 | 712 | 20241027 | 1411 | 2605355 | 419 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 17797 | 34.9585 | -120.4364 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned Open | 24-0128280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1983908 | 1 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | OCB | 1101/2/NORM | 20241027 | 1754 | 20241027 | 2117 | 2605527 | 203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2092 | 423345 | 35.0079 | -120.4539 | No | Overcast;32-90 F |  |  | 24-0128328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983949 | 0 | EPSS Ckt | Y | 2024 | B & C INST OC
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | FUSE | 5087 | 20241028 | 710 | 20241028 | 838 | 2605668 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 352 | 35.2948 | -120.7619 | No | Clear;32-90 F |  |  | 24-0128404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1984044 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | 846970 | 20241028 | 844 | 20241028 | 1037 | 2605909 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 127 | 8511 | 34.8317 | -120.2332 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0128424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1984071 | 0 | EPSS Ckt | Y | 2024 | A-B
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | TRANSFORMER | 512106377978 | 20241028 | 1320 | 20241028 | 1452 | 2606295 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1196 | 35.6138 | -120.6565 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0128597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984197 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y54 | 20241029 | 807 | 20241029 | 834 | 2606913 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 116 | 3132 | 34.6532 | -120.0715 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0128861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1984334 | 0 | EPSS Ckt | Y | 2024 | SGF
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | FUSE | 12077 | 20241030 | 341 | 20241030 | 601 | 2607882 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 560 | 34.8794 | -120.3327 | No | Partly Cloudy-Fog-Rain;32-90 F |  |  | 24-0129319 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1984661 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | INTERRUPTER | 108014 | 20241030 | 843 | 20241030 | 1310 | 2608062 | 267 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 267 | 34.9529 | -120.4387 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0129364 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984749 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | 513581340583 | 20241030 | 1150 | 20241030 | 1227 | 2608356 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 370 | 34.5965 | -120.1341 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0129563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984886 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 3345 | 20241030 | 1400 | 20241030 | 1442 | 2608492 | 42 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 42 | 35.5748 | -120.6984 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0129639 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984925 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 4151 | 20241030 | 1521 | 20241030 | 1650 | 2608580 | 89 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 89 | 35.1809 | -120.7264 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 24-0129694 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984950 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | TRANSFORMER | 512023072628 | 20241031 | 900 | 20241101 | 648 | 2609301 | 1308 | Transformer only | Company Initiated | Construction Activity/equip- company | 3 | 3924 | 35.4666 | -120.6806 | No | Clear;32-90 F | Transformer | Normal | 24-0125376 | OH | Sus | 35546147 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1985164 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | OCEANO-1102 | 182601102 | FUSE | 45953 | 20241031 | 2240 | 20241101 | 107 | 2609936 | 147 | Distribution Circuit | Company Initiated | Improper Construction | 18 | 2646 | 35.0421 | -120.5725 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0130340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1985350 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | Y48 | 20241101 | 621 | 20241101 | 629 | 2609996 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 2956 | 23648 | 34.6653 | -120.1182 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0100511 | OH | Sus | 35507051 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985361 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | FUSE | 32303 | 20241101 | 658 | 20241101 | 930 | 2610014 | 152 | Distribution Circuit | 3rd Party | Customer Equipment | 277 | 18644 | 35.5722 | -120.6966 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0130389 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985378 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 31993 | 20241101 | 1252 | 20241101 | 1354 | 2610458 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 310 | 35.5696 | -120.4696 | No | Clear;32-90 F |  |  | 24-0130628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985580 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1105 | 182671105 | TRANSFORMER | 512685754343 | 20241101 | 1445 | 20241101 | 2239 | 2610572 | 473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 150 | 23865 | 34.9689 | -120.4426 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0130729 | OH | Sus | 31714712 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985610 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | RECLOSER | 117616 | 20241101 | 1445 | 20241101 | 1615 | 2610582 | 90 | Distribution Circuit | Company Initiated | Coordination failure | 2116 | 190440 | 34.6407 | -120.1154 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0130680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985594 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | SAN LUIS OBISPO | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512846159096 | 20241101 | 1658 | 20241101 | 2052 | 2610702 | 234 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 234 | 35.1014 | -120.393 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0130760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985634 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 3417 | 20241101 | 1822 | 20241101 | 2321 | 2610756 | 299 | Distribution Circuit | Animal | Bird found | 8 | 2392 | 35.3861 | -120.7747 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0130781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985653 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | RECLOSER | 351084 | 20241102 | 314 | 20241102 | 459 | 2611155 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 352 | 36960 | 35.6223 | -120.7024 | No | Overcast;32-90 F |  |  | 24-0130817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985678 | 0 | EPSS Ckt | Y | 2024 | B & GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | OCB | 2112/2 | 20241102 | 449 | 20241102 | 1323 | 2611193 | 514 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1154 | 185155 | 35.555 | -120.6804 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0130828 | OH | Sus | 46368670 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | Yes | No | 1985690 | 0 | EPSS Ckt | N | 2024 | A B C GRD TIME
LOS PADRES | PASO ROBLES | PASO ROBLES-1103 | 182611103 | FUSE | 7671 | 20241102 | 500 | 20241102 | 1500 | 2611201 | 600 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 1200 | 35.6229 | -120.7267 | No | Clear;32-90 F |  |  | 24-0130996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985883 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | RECLOSER | 428314 | 20241102 | 520 | 20241102 | 859 | 2611220 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 12921 | 35.7754 | -120.6943 | No | Overcast;32-90 F |  |  | 24-0130832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985694 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 30609 | 20241102 | 546 | 20241102 | 1259 | 2611237 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 7361 | 35.4934 | -120.2276 | No | Overcast-Heavy Rain;32-90 F | Fuse | Burned Open | 24-0130972 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985871 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | R92 | 20241102 | 843 | 20241102 | 2008 | 2611482 | 685 | Distribution Circuit | Equipment Failure/Involved | Overhead | 971 | 130277 | 35.5705 | -120.6481 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0130877 | OH | Sus | 35595604 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985780 | 0 | EPSS Ckt | N | 2024 | A & B
LOS PADRES | PASO ROBLES | PASO ROBLES-1106 | 182611106 | TRANSFORMER | 512106977903 | 20241102 | 908 | 20241102 | 1051 | 2611512 | 101 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 505 | 35.6117 | -120.6563 | No | Overcast-Drizzle;32-90 F | Secondary | Deteriorated | 24-0130883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1985789 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X06 | 20241102 | 1735 | 20241102 | 1937 | 2611843 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 172 | 20984 | 35.7373 | -120.2884 | No | Clear;32-90 F |  |  | 24-0131023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985898 | 0 | EPSS Ckt | Y | 2024 | AB
LOS PADRES | SAN LUIS OBISPO | BAYWOOD-1101 | 182801101 | FUSE | 10615 | 20241103 | 619 | 20241103 | 839 | 2612174 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2520 | 35.3548 | -120.7864 | No | Clear;32-90 F |  |  | 24-0131096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985962 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | FOOTHILL-1101 | 182951101 | TRANSFORMER | 511565767491 | 20241103 | 827 | 20241103 | 1018 | 2612254 | 111 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 1443 | 35.3219 | -120.8288 | No | Clear;32-90 F |  |  | 24-0131113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1985984 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1107 | 182661107 | FUSE | 5697 | 20241103 | 906 | 20241103 | 1202 | 2612291 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 6336 | 35.696 | -120.6801 | No | Clear;32-90 F |  |  | 24-0131131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1985999 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M54 | 20241104 | 559 | 20241104 | 837 | 2612833 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 127 | 9539 | 34.8627 | -120.2773 | No | Clear;32-90 F |  |  | 24-0131228 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986063 | 0 | EPSS Ckt | Y | 2024 | A-B
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512721151650 | 20241104 | 851 | 20241104 | 924 | 2613060 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 231 | 34.895 | -120.4286 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0131295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986158 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512751653942 | 20241104 | 1415 | 20241104 | 1614 | 2613529 | 119 | Transformer only | Vegetation | Tree - grew into line | 13 | 1547 | 34.9582 | -120.4203 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986339 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | RECLOSER | R56 | 20241104 | 1423 | 20241104 | 1701 | 2613506 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 427 | 42506 | 35.6443 | -120.7067 | No | Clear;32-90 F |  |  | 24-0131551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986335 | 0 | EPSS Ckt | Y | 2024 | B-GRD
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | SWITCH | 2075 | 20241104 | 1440 | 20241105 | 245 | 2613738 | 725 | Distribution Circuit | 3rd Party | Vehicle | 67 | 48575 | 35.3118 | -120.8362 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0131594 | OH | Sus | 35595884 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986388 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | RECLOSER | 18370 | 20241105 | 1050 | 20241105 | 1214 | 2614259 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 273 | 22932 | 35.5256 | -120.5217 | Yes | Clear;32-90 F |  |  | 24-0132026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986616 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | TRANSFORMER | 512927080716 | 20241105 | 1630 | 20241105 | 1838 | 2614479 | 128 | Transformer only | Animal | Bird found | 2 | 256 | 35.6963 | -120.3831 | Yes | Clear;32-90 F | Transformer | Normal | 24-0132266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986686 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | RECLOSER | R82 | 20241105 | 1838 | 20241105 | 2131 | 2614698 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 906 | 78756 | 35.5299 | -120.523 | Yes | Partly Cloudy;32-90 F |  |  | 24-0132277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986692 | 0 | EPSS Ckt | Y | 2024 | A-B
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 6053 | 20241105 | 2141 | 20241105 | 2357 | 2615007 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 273 | 13320 | 35.5084 | -120.4863 | Yes | Clear;32-90 F |  |  | 24-0132305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986847 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | RECLOSER | 337126 | 20241106 | 106 | 20241106 | 340 | 2615340 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 928 | 104364 | 35.2541 | -120.6693 | No | Partly Cloudy;32-90 F |  |  | 24-0132321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986893 | 0 | EPSS Ckt | Y | 2024 | B-GRD
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 7143 | 20241106 | 607 | 20241106 | 908 | 2615624 | 181 | Distribution Circuit | Animal | Bird found | 3 | 543 | 35.795 | -120.8753 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987104 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | RECLOSER | R82 | 20241106 | 1912 | 20241106 | 2041 | 2617264 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 906 | 74294 | 35.5299 | -120.523 | No | Clear;32-90 F |  |  | 24-0132892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987332 | 0 | EPSS Ckt | Y | 2024 | B
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | FUSE | 6053 | 20241106 | 2056 | 20241107 | 924 | 2617310 | 748 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4290 | 35.5084 | -120.4863 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0132917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987350 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | RECLOSER | 707662 | 20241107 | 709 | 20241108 | 28 | 2617420 | 1039 | Distribution Circuit | 3rd Party | Vehicle | 9 | 5949 | 34.9526 | -120.3852 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0132968 | OH | Sus | 35596517 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987381 | 0 | Non-EPSS | N | 2024 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | RECLOSER | A70 | 20241107 | 747 | 20241107 | 944 | 2617494 | 117 | Distribution Circuit | Animal | Bird found | 1717 | 152401 | 35.5023 | -120.649 | No | Clear-Rain;32-90 F | Conductor- Overhead | Normal | 24-0132986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987397 | 0 | EPSS Ckt | Y | 2024 | A-C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V58 | 20241107 | 803 | 20241107 | 815 | 2617544 | 12 | Distribution Circuit | Company Initiated | Personnel- company | 2912 | 34944 | 35.247 | -120.6494 | No | Clear;32-90 F | Jumper | Normal | 24-0132990 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987413 | 0 | EPSS Ckt | Y | 2024 | SGF-DCD
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | TRANSFORMER | 513048649514 | 20241107 | 921 | 20241107 | 1145 | 2617682 | 144 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 144 | 34.8384 | -120.3177 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0133016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1987482 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 30705 | 20241107 | 938 | 20241107 | 1414 | 2617740 | 276 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1380 | 35.5226 | -120.2311 | No | Clear;32-90 F |  |  | 24-0133181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1987591 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A80 | 20241107 | 940 | 20241107 | 1303 | 2617752 | 203 | Distribution Circuit | Animal | Bird found | 512 | 37636 | 35.4259 | -120.6312 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0133029 | OH | Sus | 31716962 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987517 | 0 | EPSS Ckt | Y | 2024 | A/B
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | FUSE | 3213 | 20241108 | 2300 | 20241109 | 129 | 2619387 | 149 | Distribution Circuit | Animal | Other | 60 | 8944 | 35.256 | -120.6647 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0133751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987971 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | R86 | 20241109 | 538 | 20241109 | 726 | 2619415 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 282 | 19096 | 35.5357 | -120.7224 | No | Clear;32-90 F |  |  | 24-0133757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987981 | 0 | EPSS Ckt | Y | 2024 | B-C
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 4695 | 20241109 | 1203 | 20241109 | 1524 | 2619724 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 6432 | 35.6446 | -120.3782 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0133807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1988072 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20241109 | 1542 | 20241109 | 1833 | 2619878 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 37278 | 35.1757 | -120.5255 | No | Clear;32-90 F |  |  | 24-0133846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988110 | 0 | EPSS Ckt | Y | 2024 | B-C- INST
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | FUSE | 7095 | 20241109 | 1750 | 20241109 | 1918 | 2619946 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 3784 | 35.7463 | -120.6997 | No | Clear;32-90 F |  |  | 24-0133867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988128 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 14295 | 20241110 | 853 | 20241110 | 1042 | 2620134 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2725 | 35.23 | -120.6722 | No | Clear-Drizzle;32-90 F |  |  | 24-0133914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988189 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y46 | 20241110 | 1320 | 20241110 | 1949 | 2620228 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 276 | 46492 | 34.6448 | -120.429 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0133939 | OH | Sus | 31717141 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988209 | 0 | EPSS Ckt | Y | 2024 | A&B INST OC
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | RECLOSER | 277242 | 20241110 | 1704 | 20241110 | 2006 | 2620304 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1200 | 218400 | 35.5999 | -121.1157 | No | Clear;32-90 F |  |  | 24-0133971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988237 | 0 | Non-EPSS | Y | 2024 | A-B
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | SWITCH | 251466 | 20241110 | 2022 | 20241110 | 2034 | 2620353 | 12 | Distribution Circuit | Company Initiated | Return Circuit Normal | 88 | 1056 | 34.5948 | -120.2681 | No | Partly Cloudy-Fog-Rain;32-90 F | Crossarm- Wood | Broken | 24-0133939 | OH | Sus | 31717141 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1988255 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | JUMPER | OJ 1 SPAN N/O CGC 512363877306 | 20241111 | 937 | 20241111 | 1249 | 2620656 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 384 | 35.5975 | -120.5704 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0134063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1988362 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | N42 | 20241111 | 1441 | 20241111 | 1623 | 2621452 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2283 | 217638 | 35.8683 | -120.843 | No | Overcast-Drizzle;32-90 F |  |  | 24-0134199 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988513 | 1 | EPSS Ckt | Y | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | FUSE | 291773 | 20241111 | 1655 | 20241112 | 102 | 2621648 | 487 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2435 | 34.9029 | -120.3021 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0134268 | OH | Sus | 46387526 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1988569 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 848137 | 20241112 | 318 | 20241112 | 341 | 2622323 | 23 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 23 | 35.4629 | -120.6373 | No | Clear;32-90 F |  |  | 24-0134423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1988731 | 0 | EPSS Ckt | Y | 2024 | ABC
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y46 | 20241112 | 637 | 20241112 | 814 | 2622402 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 276 | 26772 | 34.6448 | -120.429 | No | Fog;32-90 F |  |  | 24-0134445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988770 | 0 | EPSS Ckt | Y | 2024 | A-B
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20241112 | 810 | 20241112 | 903 | 2622503 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 9607 | 34.7206 | -120.4308 | No | Clear;32-90 F |  |  | 24-0134477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988813 | 0 | EPSS Ckt | Y | 2024 | C PHASE AND GRD
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | RECLOSER | Y46 | 20241112 | 1458 | 20241112 | 1635 | 2623183 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 276 | 26772 | 34.6448 | -120.429 | No | Clear;32-90 F |  |  | 24-0134758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1989065 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | SANTA MARIA | PALMER-1101 | 183031101 | TRANSFORMER | 513129948582 | 20241112 | 1612 | 20241112 | 2113 | 2623072 | 301 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 301 | 34.8135 | -120.2903 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0134809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989084 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | OTHER | J896 TWD T96166 | 20241112 | 1731 | 20241112 | 1847 | 2623368 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 608 | 35.5758 | -120.6907 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0134818 | UG | Sus | 35597193 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1989094 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | TRANSFORMER | 512588552005 | 20241113 | 1229 | 20241113 | 1910 | 2624058 | 401 | Transformer only | Equipment Failure/Involved | Underground | 1 | 401 | 34.9039 | -120.4732 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0135105 | UG | Sus | 31717440 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989391 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512305354535 | 20241114 | 1103 | 20241114 | 1141 | 2624869 | 38 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 532 | 34.9714 | -120.5698 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0135479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989725 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | FUSE | 45681 | 20241114 | 1606 | 20241114 | 1952 | 2625298 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 3512 | 34.8925 | -120.4345 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0135687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1989808 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512708954230 | 20241114 | 2045 | 20241115 | 135 | 2625457 | 290 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 580 | 34.9659 | -120.4348 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Deteriorated | 24-0135735 | OH | Sus | 31717527 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989828 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512079365714 | 20241115 | 1203 | 20241115 | 1735 | 2626115 | 332 | Transformer only | Equipment Failure/Involved | Overhead | 36 | 11952 | 35.2769 | -120.655 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0135947 | OH | Sus | 31717584 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990083 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | JUMPER | OJ 2 N/OF CGC#512334058230 | 20241116 | 822 | 20241116 | 1055 | 2626796 | 153 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 306 | 35.0742 | -120.5625 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0136170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1990202 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20651 | 20241116 | 1412 | 20241116 | 1547 | 2627111 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 285 | 34.6212 | -120.2472 | No | Clear;32-90 F |  |  | 24-0136266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1990295 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20241117 | 1233 | 20241117 | 1409 | 2627445 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 17760 | 34.7206 | -120.4308 | No | Clear;32-90 F |  |  | 24-0136322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990388 | 0 | EPSS Ckt | Y | 2024 | GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1102 | 182611102 | FUSE | 31843 | 20241117 | 1502 | 20241118 | 31 | 2627545 | 569 | Distribution Circuit | 3rd Party | Vehicle | 28 | 15932 | 35.6258 | -120.6715 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0136345 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1990406 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10295 | 20241118 | 1413 | 20241119 | 945 | 2628449 | 1172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1172 | 35.2506 | -120.761 | No | Clear;32-90 F |  |  | 24-0137001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990982 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20651 | 20241118 | 1557 | 20241118 | 1741 | 2628531 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 312 | 34.6212 | -120.2472 | No | Clear;32-90 F | Insulator | Broken | 24-0136739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1990721 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | JUMPER | OJS 1 SP SS OF CGC 512260258454 | 20241118 | 1629 | 20241118 | 1650 | 2628559 | 21 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 105 | 35.079 | -120.5877 | No | Clear;32-90 F | Insulator | Broken | 24-0136759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1990726 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 12079 | 20241118 | 2137 | 20241119 | 224 | 2628718 | 287 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1914 | 34.8792 | -120.3095 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0136817 | OH | Sus | 31717902 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990765 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5049 | 20241119 | 708 | 20241119 | 1015 | 2628842 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 9911 | 35.5335 | -121.0503 | No | Partly Cloudy;Below 32 F |  |  | 24-0136986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1990969 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20241119 | 915 | 20241119 | 1053 | 2629066 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2978 | 169387 | 35.5213 | -120.7125 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0136958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990939 | 0 | EPSS Ckt | N | 2024 | A & GRD
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | T3331 | 20241119 | 1259 | 20241119 | 1854 | 2629365 | 355 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 7455 | 34.8606 | -120.4028 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0137177 | UG | Sus | 35598871 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991047 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20241119 | 2247 | 20241120 | 116 | 2629922 | 149 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 174 | 25926 | 34.7206 | -120.4308 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0137403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991141 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 7881 | 20241119 | 2247 | 20241120 | 259 | 2629998 | 252 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2772 | 34.7559 | -120.3352 | No | Partly Cloudy;32-90 F |  |  | 24-0137411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1991152 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512673453608 | 20241120 | 1629 | 20241120 | 1703 | 2631596 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 27 | 918 | 34.9486 | -120.4463 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0137986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991565 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511535567568 | 20241120 | 2243 | 20241121 | 120 | 2632027 | 157 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 2669 | 35.3238 | -120.8389 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0138116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991661 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | RECLOSER | M58 | 20241121 | 1142 | 20241121 | 1905 | 2632481 | 443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2658 | 34.9152 | -120.383 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0138380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991826 | 0 | EPSS Ckt | N | 2024 | NA
LOS PADRES | SANTA MARIA | SANTA MARIA-1107 | 182671107 | TRANSFORMER | T2708 | 20241121 | 2127 | 20241121 | 2147 | 2633255 | 20 | Transformer only | Equipment Failure/Involved | Underground | 13 | 260 | 34.9246 | -120.4433 | No | Partly Cloudy;32-90 F | Bus | Deteriorated | 24-0138700 | UG | Sus | 46398106 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991955 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | RECLOSER | W16 | 20241121 | 2227 | 20241122 | 27 | 2633392 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1358 | 162960 | 35.4296 | -120.8819 | No | Overcast;32-90 F | Capacitor | Failed/Faulted | 24-0138712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991964 | 0 | EPSS Ckt | N | 2024 | B- GRD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | RECLOSER | 18370 | 20241122 | 957 | 20241122 | 1131 | 2634250 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 272 | 13465 | 35.5256 | -120.5217 | No | Partly Cloudy;32-90 F |  |  | 24-0138899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992120 | 0 | EPSS Ckt | Y | 2024 | B & C PHSE
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | RECLOSER | M64 | 20241122 | 1837 | 20241122 | 2221 | 2635228 | 224 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 5600 | 35.04 | -120.5498 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0139167 | OH | Sus | 46398959 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992269 | 0 | EPSS Ckt | N | 2024 | NA
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 31709 | 20241123 | 136 | 20241123 | 306 | 2635754 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 810 | 35.6378 | -120.5879 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0139388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992394 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | TRANSFORMER | 511971772836 | 20241123 | 1027 | 20241123 | 1442 | 2636217 | 255 | Distribution Circuit | Animal | Bird found | 1 | 255 | 35.4718 | -120.6981 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 24-0139540 | OH | Sus | 31718190 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992527 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 6353 | 20241124 | 1352 | 20241124 | 2017 | 2637063 | 385 | Distribution Circuit | 3rd Party | Vehicle | 5 | 1925 | 34.6618 | -120.5105 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0139750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1992678 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X24 | 20241125 | 752 | 20241125 | 1132 | 2637364 | 220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 26330 | 35.6532 | -120.3636 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0139845 | OH | Sus | 31718584 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992716 | 0 | EPSS Ckt | N | 2024 | N/A
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 6053 | 20241125 | 824 | 20241125 | 1535 | 2637397 | 431 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4895 | 35.5084 | -120.4863 | No | Overcast-Fog-Heavy Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992766 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6343 | 20241125 | 1125 | 20241125 | 1919 | 2637639 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 8532 | 35.3953 | -120.5192 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0140032 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992793 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 32071 | 20241125 | 1446 | 20241125 | 2355 | 2637865 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4392 | 35.528 | -120.7337 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0140178 | OH | Sus | 31718612 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1992843 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | FUSE | 4545 | 20241126 | 2132 | 20241126 | 2305 | 2639019 | 93 | Distribution Circuit | Vegetation | Tree - branch fell on line | 146 | 13578 | 35.147 | -120.5306 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0140703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993074 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | JUMPER | OPEN JUMPERS 1/P SS OF CGC# 512860352157 | 20241127 | 804 | 20241127 | 1110 | 2639141 | 186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 558 | 34.91 | -120.3828 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Deteriorated | 24-0140762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993103 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | FUSE | 45603 | 20241127 | 941 | 20241127 | 1004 | 2639269 | 23 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 79 | 1810 | 35.0432 | -120.4759 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0140872 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993149 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | MTR#1008543976 | 20241127 | 1105 | 20241127 | 1124 | 2639165 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 95 | 34.5906 | -120.1443 | No | Overcast-Fog;32-90 F | Transformer (OH) | Leaking | 24-0140917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993159 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511506368991 | 20241127 | 1202 | 20241127 | 1250 | 2639388 | 48 | Transformer only | 3rd Party | Metallic Balloon | 22 | 1056 | 35.3626 | -120.8499 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0140997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993175 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | JUMPER | BURN'T OJ POS#2 2P/SS/OF 79917 | 20241127 | 1212 | 20241128 | 1253 | 2639409 | 1481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 276 | 77904 | 34.6208 | -120.3977 | No | Clear;32-90 F | Jumper | Burned Open | 24-0140976 | OH | Sus | 46401450 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1993171 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1104 | 182061104 | TRANSFORMER | 512719351435 | 20241127 | 1419 | 20241127 | 1511 | 2639490 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 676 | 34.889 | -120.4286 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0141099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993195 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512536951878 | 20241127 | 1741 | 20241128 | 1011 | 2639638 | 990 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 4950 | 34.9001 | -120.4903 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0141164 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993213 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | FUSE | 14983 | 20241128 | 2227 | 20241129 | 614 | 2639991 | 467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 18066 | 35.4315 | -120.8837 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0141238 | OH | Sus | 31718849 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993284 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | 512216263284 | 20241129 | 551 | 20241129 | 2148 | 2640011 | 957 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1914 | 35.2114 | -120.6072 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993291 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 4595 | 20241129 | 641 | 20241129 | 2145 | 2640033 | 904 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 12548 | 35.5334 | -121.0161 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1993298 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1111 | 182671111 | TRANSFORMER | 512697053019 | 20241129 | 741 | 20241129 | 835 | 2640055 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 648 | 34.9323 | -120.4379 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0141248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993296 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | TRANSFORMER | 512710253436 | 20241129 | 922 | 20241129 | 953 | 2640112 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 527 | 34.9441 | -120.4339 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0141264 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993309 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PALMER-1101 | 183031101 | RECLOSER | M84 | 20241129 | 1036 | 20241129 | 1646 | 2640158 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 912 | 89010 | 34.8208 | -120.2887 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0141276 | OH | Sus | 31718850 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1993318 | 0 | EPSS Ckt | N | 2024 | B PHASE & GRD TIME OC
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 415954 | 20241129 | 1630 | 20241129 | 2043 | 2640320 | 253 | Distribution Circuit | 3rd Party | Vehicle | 76 | 19228 | 35.1988 | -120.4304 | No | Overcast;32-90 F | Pole-Wood | Normal | 24-0141308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1993339 | 0 | EPSS Ckt | N | 2024 | A&B PHASE
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | FUSE | 14789 | 20241130 | 2137 | 20241130 | 2326 | 2640909 | 109 | Distribution Circuit | Animal | Bird found | 33 | 3597 | 35.2733 | -120.6562 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0141468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1993446 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 63043 | 20241201 | 1738 | 20241201 | 1946 | 2641211 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1024 | 35.6332 | -120.6144 | No | Clear;32-90 F |  |  | 24-0141570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1993513 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | TRANSFORMER | 512133563641 | 20241201 | 1800 | 20241201 | 1917 | 2641220 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 385 | 35.2207 | -120.6351 | No | Clear;32-90 F | Fuse | Broken | 24-0141564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993511 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | TRANSFORMER | 512525052745 | 20241202 | 643 | 20241202 | 1320 | 2641297 | 397 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 397 | 34.9237 | -120.4948 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0141593 | OH | Sus | 46402655 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993537 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 6307 | 20241202 | 850 | 20241202 | 1046 | 2641509 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 542 | 34.9561 | -120.5583 | No | Partly Cloudy;32-90 F |  |  | 24-0141709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993719 | 1 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | OTHER | 11211 | 20241202 | 1249 | 20241202 | 2102 | 2641925 | 493 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 493 | 34.668 | -120.0675 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Broken | 24-0141826 | UG | Sus | 46402989 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1993780 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512519042515 | 20241202 | 1803 | 20241203 | 235 | 2642065 | 512 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1536 | 34.6429 | -120.487 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141926 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993813 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PASO ROBLES-1107 | 182611107 | FUSE | 5695 | 20241203 | 124 | 20241203 | 341 | 2642410 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 5209 | 35.6745 | -120.6499 | No | Partly Cloudy;32-90 F |  |  | 24-0141980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993839 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | OTHER | T28046 TWD T44795 | 20241203 | 1729 | 20241203 | 1940 | 2643243 | 131 | Distribution Circuit | 3rd Party | Other | 8 | 1048 | 35.4717 | -120.7287 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0142269 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1994148 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511508067061 | 20241204 | 1654 | 20241204 | 1723 | 2644193 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 58 | 35.3095 | -120.8478 | No | Clear;32-90 F | Service conductor | Deteriorated | 24-0142694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1994528 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1101 | 182811101 | JUMPER | OJ 1 W/OF CGC # 512870650558 | 20241204 | 1744 | 20241205 | 57 | 2644186 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 9959 | 34.8661 | -120.3783 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0142688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1994527 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 986322 | 20241205 | 1310 | 20241206 | 140 | 2645052 | 750 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1575 | 541053 | 35.5505 | -121.0725 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0142957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994842 | 0 | EPSS Ckt | N | 2024 | SGF INST OC
LOS PADRES | SANTA MARIA | SANTA MARIA-1109 | 182671109 | TRANSFORMER | 512624354333 | 20241205 | 1320 | 20241205 | 1328 | 2645020 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 8 | 34.9682 | -120.463 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0142971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994847 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1103 | 182631103 | RECLOSER | V82 | 20241205 | 1435 | 20241205 | 1706 | 2645238 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1310 | 196841 | 35.2151 | -120.615 | No | Clear;32-90 F |  |  | 24-0143027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994864 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 5463 | 20241205 | 1502 | 20241205 | 1631 | 2645268 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 445 | 35.5507 | -120.6004 | No | Clear;32-90 F |  |  | 24-0143104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1994888 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | FUSE | 6593 | 20241205 | 1828 | 20241205 | 1929 | 2645392 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 854 | 34.8794 | -120.3478 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0143137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1994906 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | RECLOSER | 277014 | 20241207 | 932 | 20241207 | 942 | s1995324 | 10 | Distribution Circuit | Company Initiated | Personnel- company | 222 | 2220 | 34.5994 | -120.0979 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0130354 | OH | Sus | 35572347 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1995324 | 0 | EPSS Ckt | N | 2024 | SGF & DCD
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 8333 | 20241207 | 1007 | 20241207 | 1150 | 2646479 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 8931 | 34.7064 | -120.4575 | No | Clear;32-90 F |  |  | 24-0143590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995348 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | SWITCH | 5680 | 20241207 | 1056 | 20241207 | 1340 | 2646505 | 164 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 1804 | 35.7531 | -120.9905 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0143523 | UG | Sus | 35603984 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995340 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1107 | 182061107 | OCB | 1107/2 | 20241207 | 1646 | 20241208 | 342 | 2646684 | 656 | Distribution Circuit | 3rd Party | Vehicle | 975 | 80174 | 34.9106 | -120.4462 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0143635 | OH | Sus | 35604041 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1995388 | 0 | Non-EPSS | N | 2024 | A- B-& C
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | FUSE | 4719 | 20241207 | 1721 | 20241208 | 931 | 2646703 | 970 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 32980 | 35.6078 | -121.091 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0143652 | OH | Sus | 31719480 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1995402 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1105 | 182631105 | TRANSFORMER | 512079365714 | 20241207 | 1901 | 20241207 | 2000 | 2646679 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 36 | 2124 | 35.2769 | -120.655 | No | Partly Cloudy;32-90 F | Insulator | Failed/Faulted | 24-0143648 | OH | Sus | 31719419 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995397 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512710373614 | 20241208 | 1118 | 20241208 | 1610 | 2646931 | 292 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 292 | 35.5008 | -120.4537 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0143714 | OH | Sus | 31719503 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995491 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | TRANSFORMER | 512346558205 | 20241208 | 1601 | 20241208 | 1707 | 2647032 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 66 | 35.0729 | -120.5585 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0143742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995504 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 4989 | 20241208 | 1646 | 20241208 | 2332 | 2647048 | 406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 331 | 19256 | 35.3787 | -120.8517 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0143754 | OH | Sus | 31719504 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995512 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PALMER-1101 | 183031101 | FUSE | 7885 | 20241209 | 1650 | 20241209 | 1953 | 2647974 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 549 | 34.7691 | -120.3095 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0144006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995839 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 9845 | 20241209 | 1745 | 20241209 | 1835 | 2648021 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 2300 | 35.3184 | -120.8488 | No | Clear;32-90 F |  |  | 24-0144029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995852 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1112 | 182671112 | FUSE | 40257 | 20241210 | 16 | 20241210 | 1551 | 2648206 | 911 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 305 | 10574 | 34.9511 | -120.4092 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0144062 | UG | Sus | 35604432 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995890 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1104 | 182601104 | JUMPER | OJ 1 SPAN S/E OF R491 | 20241210 | 207 | 20241210 | 417 | 2648270 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 25802 | 35.2044 | -120.5782 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0143884 | OH | Sus | 35604263 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995895 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | RECLOSER | 986322 | 20241210 | 712 | 20241210 | 932 | 2648338 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1575 | 135756 | 35.5505 | -121.0725 | No | Clear;32-90 F |  |  | 24-0144084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995912 | 0 | EPSS Ckt | Y | 2024 | A&C PHASE
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 6161 | 20241210 | 837 | 20241210 | 1235 | 2648407 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3332 | 35.5891 | -120.6412 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0144106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995951 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | TRANSFORMER | 512479142837 | 20241210 | 1228 | 20241210 | 1530 | 2648786 | 182 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 182 | 34.6513 | -120.5018 | No | Clear;32-90 F | Transformer (OH) | Arcing | 24-0144206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996201 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | RECLOSER | 320270 | 20241210 | 2222 | 20241211 | 952 | 2649252 | 690 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 230 | 31395 | 34.5995 | -120.1277 | No | Partly Cloudy;32-90 F |  |  | 24-0144311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996280 | 0 | EPSS Ckt | Y | 2024 | A B
LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | RECLOSER | A46 | 20241211 | 1022 | 20241211 | 1236 | s1996557 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 815 | 109210 | 35.4018 | -120.6222 | No | Clear;32-90 F |  |  | 24-0144413 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996557 | 0 | EPSS Ckt | N | 2024 | A AND GRD
LOS PADRES | SANTA MARIA | CABRILLO-1104 | 183101104 | FUSE | 7521 | 20241211 | 1322 | 20241211 | 1517 | 2649892 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1150 | 34.5793 | -120.5127 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0144435 | OH | Sus | 46415779 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996584 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2112 | 183052112 | TRANSFORMER | 511988176903 | 20241211 | 1700 | 20241211 | 1739 | 2650088 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 78 | 35.5834 | -120.6953 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0144478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996619 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 175566 | 20241211 | 1727 | 20241211 | 1904 | 2650155 | 97 | Distribution Circuit | Company Initiated | Coordination failure | 1302 | 126294 | 35.489 | -120.6385 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0144481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996621 | 0 | EPSS Ckt | Y | 2024 | DCD
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 31623 | 20241211 | 1728 | 20241211 | 1756 | 2650113 | 28 | Distribution Circuit | Animal | Bird found | 269 | 7532 | 35.5124 | -120.6703 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0144489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996627 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 848137 | 20241211 | 2032 | 20241211 | 2138 | 2650280 | 66 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 66 | 35.4629 | -120.6373 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0144506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996647 | 0 | EPSS Ckt | Y | 2024 | B & INST OC
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 81595 | 20241212 | 637 | 20241212 | 1236 | 2650449 | 359 | Distribution Circuit | Animal | Bird found | 11 | 1235 | 35.4824 | -120.6922 | No | Overcast-Rain;32-90 F | Cutout- fuse holder | Broken | 24-0144552 | OH | Sus | 31719557 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996699 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | 587564 | 20241212 | 1501 | 20241212 | 1543 | 2651086 | 42 | Distribution Circuit | Animal | Bird found | 21 | 882 | 35.495 | -120.644 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 24-0144681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996923 | 0 | EPSS Ckt | Y | 2024 | A GRD
LOS PADRES | PASO ROBLES | PASO ROBLES-1101 | 182611101 | FUSE | 30165 | 20241213 | 1020 | 20241213 | 1340 | 2651740 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 3000 | 35.6218 | -120.6851 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0144819 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1997126 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1102 | 182541102 | RECLOSER | 276036 | 20241213 | 1153 | 20241213 | 1159 | 2651851 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2869 | 17214 | 35.4645 | -120.651 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0144850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1997152 | 0 | EPSS Ckt | N | 2024 | BC GRD
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | FUSE | 3449 | 20241213 | 1440 | 20241214 | 310 | 2652223 | 750 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 9702 | 35.3061 | -120.8583 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0144939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997230 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | GOLDTREE-1108 | 182581108 | TRANSFORMER | 512042566177 | 20241213 | 1537 | 20241213 | 2018 | 2652116 | 281 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2810 | 35.2894 | -120.6677 | No | Overcast;32-90 F | Fuse | Normal | 24-0144960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997259 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | OTHER | 3451 | 20241214 | 149 | 20241214 | 1156 | 2652822 | 607 | Distribution Circuit | 3rd Party | Vehicle | 21 | 12747 | 35.2745 | -120.6561 | Yes | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 24-0145062 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997366 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 4015 | 20241214 | 752 | 20241214 | 908 | 2654693 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 709 | 35.5813 | -120.5526 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0145361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997676 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511365372165 | 20241214 | 849 | 20241214 | 1012 | 2655954 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 332 | 35.4491 | -120.8994 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0145438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997760 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511364772173 | 20241214 | 858 | 20241214 | 1355 | 2657446 | 297 | Transformer only | Environmental/External | Water | 7 | 2079 | 35.4494 | -120.8996 | Yes | Strong Winds-Rain-Overcast;32-90 F | Transformer | Broken | 24-0145461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997783 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512249763490 | 20241214 | 909 | 20241214 | 1317 | 2656210 | 248 | Transformer only | Environmental/External | Water | 4 | 992 | 35.2171 | -120.596 | Yes | Rain-Overcast;32-90 F | Transformer | Broken | 24-0145520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997845 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 5935 | 20241214 | 924 | 20241214 | 1440 | 2656522 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5372 | 35.543 | -120.7646 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 1997786 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 2911 | 20241214 | 927 | 20241214 | 1420 | 2656434 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 6895 | 35.5342 | -120.7274 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997849 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | PERRY-1101 | 183071101 | FUSE | 30027 | 20241214 | 933 | 20241215 | 1055 | 2656517 | 1522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 21308 | 35.5641 | -120.9066 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0145806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998139 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511506468971 | 20241214 | 934 | 20241214 | 1647 | 2656514 | 433 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 7361 | 35.3621 | -120.8499 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0145633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997958 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 6027 | 20241214 | 939 | 20241214 | 1704 | 2656579 | 445 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 4895 | 35.5122 | -120.7071 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998021 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 81595 | 20241214 | 940 | 20241214 | 1438 | 2656811 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3278 | 35.4824 | -120.6922 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997915 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 7359 | 20241214 | 958 | 20241215 | 1225 | 2657105 | 1587 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 20631 | 35.6228 | -120.8555 | Yes | Overcast-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 1998180 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2108 | 183052108 | TRANSFORMER | 512033273841 | 20241214 | 1017 | 20241214 | 1830 | 2656703 | 493 | Transformer only | Vegetation | Tree - fell into line | 10 | 4930 | 35.5 | -120.6784 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0145511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997835 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511365372165 | 20241214 | 1023 | 20241214 | 1354 | 2657445 | 211 | Transformer only | Environmental/External | Water | 4 | 844 | 35.4491 | -120.8994 | Yes | Strong Winds-Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0145499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997822 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | FUSE | 8609 | 20241214 | 1026 | 20241214 | 1152 | 2657677 | 86 | Distribution Circuit | Vegetation | Tree - bark fell into line | 29 | 2494 | 35.0824 | -120.5852 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0145579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997902 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511531469077 | 20241214 | 1027 | 20241214 | 1450 | 2658039 | 263 | Transformer only | Vegetation | Tree - branch fell on line | 13 | 3419 | 35.365 | -120.8424 | Yes | Overcast-Rain-Strong Winds;32-90 F | Service conductor | Broken | 24-0145566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997888 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 30125 | 20241214 | 1029 | 20241214 | 1447 | 2657551 | 258 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 774 | 35.533 | -120.7376 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 24-0145860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998194 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | TRANSFORMER | 512290262037 | 20241214 | 1050 | 20241214 | 1513 | 2657893 | 263 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 526 | 35.1773 | -120.5798 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0145708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998036 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 6047 | 20241214 | 1130 | 20241214 | 1549 | 2658359 | 259 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 777 | 35.5127 | -120.3956 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Together | 24-0145800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998133 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | RECLOSER | X12 | 20241214 | 1130 | 20241214 | 1657 | 2658360 | 327 | Distribution Circuit | Animal | Other | 49 | 16023 | 35.6437 | -120.3772 | Yes | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Contaminated | 24-0145889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998222 | 0 | EPSS Ckt | N | 2024 | A B
LOS PADRES | SANTA MARIA | SISQUOC-1103 | 182811103 | FUSE | 45823 | 20241214 | 1958 | 20241215 | 1032 | 2660560 | 874 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1748 | 34.8939 | -120.3198 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998453 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | OILFIELDS-1103 | 182391103 | FUSE | 568013 | 20241214 | 2125 | 20241215 | 2 | 2660654 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 9420 | 35.8088 | -120.982 | Yes | Clear;32-90 F |  |  | 24-0146130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998479 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2111 | 183052111 | FUSE | 30563 | 20241215 | 733 | 20241215 | 1153 | 2660956 | 260 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 7800 | 35.513 | -120.7111 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146186 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998535 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | JUMPER | BLOWN JMPR AT 14993 | 20241215 | 1231 | 20241215 | 1403 | 2661616 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2389 | 186536 | 35.4027 | -120.8611 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0146307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1998678 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRANSFORMER | 512551358613 | 20241215 | 1307 | 20241215 | 1710 | 2661530 | 243 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 243 | 35.0854 | -120.4903 | No | Clear;32-90 F | Jumper | Broken | 24-0146342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998713 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | FUSE | 1557 | 20241216 | 739 | 20241216 | 1005 | 2662741 | 146 | Distribution Circuit | Animal | Bird found | 1 | 146 | 34.7555 | -120.3452 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0146533 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998919 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512302854560 | 20241216 | 1045 | 20241216 | 1307 | 2662640 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 142 | 34.9722 | -120.5706 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0146559 | OH | Sus | 46419305 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998944 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | TRANSFORMER | 512738751083 | 20241216 | 1251 | 20241216 | 1324 | 2663058 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 198 | 34.8796 | -120.4224 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0146607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998989 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1102 | 182551102 | OTHER | WIRE DOWN SOURCE SIDE OF 14281 | 20241216 | 1636 | 20241216 | 2232 | 2663465 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1358 | 53146 | 35.4447 | -120.8966 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0146685 | OH | Sus | 46419239 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1999064 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512519051200 | 20241217 | 1306 | 20241217 | 1406 | 2664284 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 60 | 34.8833 | -120.4958 | No | Clear;32-90 F | Fuse | Broken | 24-0146818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999318 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRANSFORMER | 512547058266 | 20241217 | 1350 | 20241217 | 1646 | 2664332 | 176 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 176 | 35.0759 | -120.4919 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0146835 | OH | Sus | 46419827 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999333 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | TRANSFORMER | 512710454036 | 20241217 | 1449 | 20241217 | 1634 | 2664346 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 105 | 34.9606 | -120.4342 | No | Clear;32-90 F | Jumper | Broken | 24-0146832 | OH | Sus | 31720392 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999331 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | MESA-1101 | 182821101 | FUSE | 7001 | 20241217 | 1724 | 20241217 | 1843 | 2664537 | 79 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 169 | 13351 | 35.0408 | -120.4739 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999357 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | CABRILLO-1103 | 183101103 | FUSE | 6741 | 20241217 | 1852 | 20241218 | 208 | 2664597 | 436 | Distribution Circuit | Animal | Bird found | 24 | 10464 | 34.6149 | -120.375 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146884 | OH | Sus | 46419942 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1999381 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 14127 | 20241218 | 245 | 20241218 | 1518 | 2664690 | 753 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 23343 | 35.5578 | -121.0812 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146902 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1999406 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1104 | 182811104 | FUSE | 11483 | 20241218 | 355 | 20241218 | 601 | 2664706 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 630 | 34.8959 | -120.3475 | No | Clear;32-90 F |  |  | 24-0146904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999408 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1101 | 183011101 | TRANSFORMER | 511543669061 | 20241218 | 435 | 20241218 | 1227 | 2664692 | 472 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 10856 | 35.3647 | -120.8374 | No | Clear;32-90 F | Secondary | Together | 24-0146900 | OH | Sus | 46419974 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999404 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5037 | 20241218 | 901 | 20241218 | 1309 | 2664897 | 248 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 10416 | 35.5506 | -121.084 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146950 | OH | Sus | 46420482 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999572 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | TRANSFORMER | T3542 | 20241218 | 1129 | 20241218 | 1455 | 2665148 | 206 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 206 | 34.9623 | -120.5712 | No | Clear;32-90 F |  |  | 24-0147021 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1999654 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | TRANSFORMER | 511014874533 | 20241218 | 1152 | 20241218 | 1415 | 2665020 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 286 | 35.5114 | -121.0207 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0146971 | OH | Sus | 31720522 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999591 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20241218 | 1348 | 20241218 | 1356 | 2665299 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 185 | 1480 | 34.7206 | -120.4308 | No | Clear;32-90 F |  |  | 24-0147005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999646 | 0 | EPSS Ckt | N | 2024 | A-GRD
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | TRANSFORMER | 512557451831 | 20241218 | 1401 | 20241218 | 1822 | 2665320 | 261 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1305 | 34.8989 | -120.4834 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999664 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1108 | 182631108 | TRANSFORMER | 512066364877 | 20241218 | 1455 | 20241218 | 1823 | 2665350 | 208 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 416 | 35.254 | -120.6593 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999660 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | TRANSFORMER | 510656178528 | 20241218 | 2238 | 20241219 | 507 | 2665608 | 389 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 778 | 35.6182 | -121.1456 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0147065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999716 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | TRANSFORMER | 512290454316 | 20241219 | 1441 | 20241219 | 2301 | 2666028 | 500 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 7500 | 34.9653 | -120.5745 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 24-0147135 | OH | Sus | 31720529 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999867 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1110 | 182671110 | FUSE | 6313 | 20241219 | 1616 | 20241219 | 1726 | 2666173 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 420 | 34.958 | -120.5913 | No | Partly Cloudy;32-90 F |  |  | 24-0147153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999882 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1102 | 182631102 | TRANSFORMER | 512036665511 | 20241220 | 944 | 20241220 | 1033 | 2666632 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 245 | 35.2711 | -120.6692 | No | Clear;32-90 F | Fuse | Broken | 24-0147221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000097 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1106 | 182601106 | TRANSFORMER | 100000004004 | 20241220 | 1613 | 20241220 | 1629 | 2666985 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 16 | 35.0947 | -120.5884 | No | Overcast;32-90 F | Fuse | Broken | 24-0147254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000162 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1104 | 182821104 | FUSE | 58236 | 20241220 | 1721 | 20241221 | 354 | 2667042 | 633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 21522 | 34.9591 | -120.5705 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147264 | OH | Sus | 31720662 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 2000175 | 0 | Non-EPSS | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512420676726 | 20241221 | 933 | 20241221 | 1026 | 2667312 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 53 | 35.5818 | -120.5501 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0147326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000281 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | TRANSFORMER | 512939338031 | 20241221 | 1306 | 20241221 | 1502 | 2667420 | 116 | Transformer only | Animal | Bird found | 1 | 116 | 34.522 | -120.3441 | No | Partly Cloudy;32-90 F | Bushing | Arcing | 24-0147337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000293 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1104 | 183071104 | OCB | 1104/2 | 20241222 | 1308 | 20241222 | 1901 | 2667777 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1638 | 195414 | 35.5712 | -121.056 | No | Partly Cloudy;32-90 F | Regulator | Failed/Faulted | 24-0147387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000371 | 0 | Non-EPSS | N | 2024 | A AND GRD
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | RECLOSER | 54728 | 20241223 | 1634 | 20241223 | 2133 | 2668523 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 1775 | 34.7596 | -120.4087 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0147501 | OH | Sus | 46438428 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000549 | 0 | EPSS Ckt | N | 2024 | SGF
LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | FUSE | 30609 | 20241223 | 1727 | 20241223 | 2005 | 2668553 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2686 | 35.4934 | -120.2276 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0147515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000564 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2110 | 183052110 | FUSE | 6489 | 20241224 | 713 | 20241224 | 855 | 2668860 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1224 | 35.5612 | -120.774 | No | Clear;32-90 F |  |  | 24-0147578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000630 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20635 | 20241224 | 743 | 20241224 | 938 | 2668888 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 805 | 34.6243 | -120.2251 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0147597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000651 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MESA-1101 | 182821101 | TRIP-SAVER | 6111 | 20241224 | 817 | 20241224 | 1209 | 2668923 | 232 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 264 | 51264 | 35.0643 | -120.4971 | No | Overcast-Rain;32-90 F |  |  | 24-0147623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000681 | 0 | EPSS Ckt | N | 2024 | A & B
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | 459340 | 20241224 | 819 | 20241224 | 948 | 2668908 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 418 | 37202 | 35.1471 | -120.6355 | No | Overcast-Rain;32-90 F |  |  | 24-0147581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000634 | 0 | EPSS Ckt | N | 2024 | A-C
LOS PADRES | SANTA MARIA | FAIRWAY-1108 | 182061108 | RECLOSER | M02 | 20241224 | 828 | 20241224 | 1227 | 2668932 | 239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3246 | 137711 | 34.9084 | -120.4357 | No | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0147585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 2000638 | 0 | Non-EPSS | N | 2024 | B-GRD
LOS PADRES | SANTA MARIA | DIVIDE-1103 | 182571103 | RECLOSER | 48160 | 20241224 | 835 | 20241224 | 1348 | 2668944 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 22575 | 34.8293 | -120.4499 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Together | 24-0147587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000641 | 0 | EPSS Ckt | N | 2024 | B C
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | 834556 | 20241224 | 836 | 20241224 | 1307 | 2669014 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 14905 | 35.194 | -120.7339 | No | Overcast-Rain;32-90 F |  |  | 24-0147650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000709 | 0 | EPSS Ckt | N | 2024 | B-C
LOS PADRES | SANTA MARIA | PURISIMA-1101 | 182971101 | JUMPER | OJ A PH @ 6425 | 20241224 | 841 | 20241224 | 1049 | 2668947 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 23678 | 34.7029 | -120.4345 | No | Overcast-Fog-Rain;32-90 F | Jumper | Burned Open | 24-0147588 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000644 | 1 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20149 | 20241224 | 901 | 20241224 | 1520 | 2669002 | 379 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 14023 | 34.5309 | -120.2908 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 2000699 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 457099 | 20241224 | 911 | 20241224 | 1025 | 2669021 | 74 | Distribution Circuit | Vegetation | Tree - bark fell into line | 9 | 666 | 35.0349 | -120.5357 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0147622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000680 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | BUELLTON-1101 | 183041101 | FUSE | 20651 | 20241224 | 1048 | 20241224 | 1335 | 2669159 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 501 | 34.6212 | -120.2472 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Together | 24-0147657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000716 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1107 | 182661107 | FUSE | 7375 | 20241224 | 1213 | 20241224 | 1428 | 2669220 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 9995 | 35.7224 | -120.5692 | No | Overcast-Drizzle;32-90 F |  |  | 24-0147652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000711 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | SWITCH | 5627 | 20241224 | 1221 | 20241224 | 1616 | 2669251 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1645 | 35.6132 | -120.3631 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0147639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2000708 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1108 | 182601108 | FUSE | 2881 | 20241224 | 1445 | 20241224 | 1454 | 2669004 | 9 | Distribution Circuit | 3rd Party | Vehicle | 133 | 1197 | 35.1289 | -120.6156 | No | Overcast-Fog-Heavy Rain;32-90 F | Anchor or Guy | Broken | 24-0147673 | OH | Sus | 35607481 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2000733 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | DIVIDE-1102 | 182571102 | RECLOSER | M144 | 20241224 | 1625 | 20241224 | 1648 | 2669398 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1468 | 33372 | 34.8651 | -120.4227 | No | Clear;32-90 F | Switch (OH) | Arcing | 24-0147680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2000740 | 0 | EPSS Ckt | N | 2024 | NONE
LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 1167 | 20241224 | 1627 | 20241224 | 1730 | 2669397 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 1953 | 34.5994 | -120.0923 | No | Clear;32-90 F |  |  | 24-0147683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000743 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1103 | 182601103 | TRANSFORMER | 512253059591 | 20241224 | 1654 | 20241224 | 2331 | 2669409 | 397 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3176 | 35.1099 | -120.5915 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000749 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | FUSE | 3935 | 20241225 | 929 | 20241225 | 1049 | 2669586 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1600 | 35.5518 | -120.5871 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000781 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA YNEZ-1102 | 182721102 | TRANSFORMER | 513725337952 | 20241225 | 1636 | 20241225 | 2007 | 2669724 | 211 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 211 | 34.5232 | -120.0842 | No | Partly Cloudy;32-90 F |  |  | 24-0147752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 2000812 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | 846970 | 20241225 | 1709 | 20241225 | 1904 | 2669731 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 6210 | 34.8317 | -120.2332 | No | Partly Cloudy;32-90 F |  |  | 24-0147747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000807 | 0 | EPSS Ckt | N | 2024 | A- B
LOS PADRES | SAN LUIS OBISPO | OCEANO-1102 | 182601102 | SWITCH | 10036 | 20241226 | 1026 | 20241226 | 1249 | 2670028 | 143 | Distribution Circuit | Equipment Failure/Involved | Underground | 173 | 24739 | 35.072 | -120.5834 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0147736 | UG | Sus | 35607451 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2000886 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | SAN MIGUEL-1105 | 182661105 | FUSE | 7097 | 20241226 | 2018 | 20241226 | 2131 | 2670346 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 292 | 35.7741 | -120.7117 | No | Partly Cloudy;32-90 F |  |  | 24-0147849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000943 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2109 | 183052109 | TRANSFORMER | 512163275802 | 20241227 | 832 | 20241227 | 929 | 2670524 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 57 | 35.5541 | -120.6355 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0147890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2000985 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | SAN LUIS OBISPO-1107 | 182631107 | TRANSFORMER | MTR#1006229692 | 20241227 | 1048 | 20241227 | 1105 | 2670740 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 51 | 35.1912 | -120.6942 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 24-0147926 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2001052 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 4695 | 20241228 | 845 | 20241228 | 1034 | 2671219 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2326 | 35.6446 | -120.3782 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0148027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001164 | 1 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 2785 | 20241228 | 1731 | 20241228 | 1827 | 2671478 | 56 | Distribution Circuit | Animal | Bird found | 6 | 336 | 35.5269 | -120.5071 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0148065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001206 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | FAIRWAY-1103 | 182061103 | FUSE | 878209 | 20241230 | 1515 | 20241230 | 1654 | 2672672 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 891 | 34.9249 | -120.4185 | No | Clear;32-90 F |  |  | 24-0148233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001481 | 0 | Non-EPSS | N | 2024
LOS PADRES | SAN LUIS OBISPO | PERRY-1101 | 183071101 | FUSE | 5049 | 20241230 | 1722 | 20241230 | 2100 | 2672770 | 218 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 11554 | 35.5335 | -121.0503 | No | Partly Cloudy;32-90 F |  |  | 24-0148246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001496 | 0 | EPSS Ckt | N | 2024
LOS PADRES | PASO ROBLES | ATASCADERO-1101 | 182541101 | JUMPER | DDE AT CGC 511989572476 | 20241230 | 2320 | 20241231 | 530 | 2672858 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2220 | 35.462 | -120.692 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0148256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2001510 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | CAYUCOS-1101 | 182551101 | FUSE | 14489 | 20241231 | 719 | 20241231 | 1102 | 2672965 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 7136 | 35.4765 | -120.9158 | No | Partly Cloudy;32-90 F |  |  | 24-0148289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001581 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1106 | 182671106 | FUSE | 46071 | 20241231 | 1026 | 20241231 | 1109 | 2673127 | 43 | Distribution Circuit | 3rd Party | Metallic Balloon | 141 | 6063 | 34.9674 | -120.4176 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0148293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001585 | 0 | Non-EPSS | N | 2024
LOS PADRES | SANTA MARIA | SANTA MARIA-1108 | 182671108 | FUSE | 46099 | 20241231 | 1319 | 20241231 | 1440 | 2673265 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 162 | 35.0375 | -120.3059 | No | Clear;32-90 F |  |  | 24-0148313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001610 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | RECLOSER | M26 | 20241231 | 1636 | 20241231 | 1851 | 2673412 | 135 | Distribution Circuit | Company Initiated | Coordination failure | 240 | 32400 | 34.9083 | -120.3283 | No | Clear;32-90 F | Recloser | Normal | 24-0148321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001618 | 0 | EPSS Ckt | Y | 2024 | A & C PHASE
LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | FUSE | 46143 | 20241231 | 1636 | 20241231 | 1931 | 2673486 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1750 | 34.9245 | -120.3477 | No | Clear;32-90 F |  |  | 24-0148335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001632 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SANTA MARIA | MESA-1103 | 182821103 | FUSE | 52281 | 20241231 | 1646 | 20241231 | 2126 | 2673419 | 280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 840 | 35.0108 | -120.4606 | No | Clear;32-90 F |  |  | 24-0148345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001642 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | OCEANO-1105 | 182601105 | FUSE | 5269 | 20241231 | 1858 | 20250101 | 36 | 2673488 | 296 | Distribution Circuit | 3rd Party | Metallic Balloon | 458 | 150682 | 35.1275 | -120.6237 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0148333 | OH | Sus | 46443270 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001630 | 0 | EPSS Ckt | N | 2024
LOS PADRES | SAN LUIS OBISPO | MORRO BAY-1102 | 183011102 | TRANSFORMER | 511566367735 | 20241231 | 2020 | 20250101 | 1003 | 2673497 | 823 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 12345 | 35.3286 | -120.8287 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 25-0004785 | OH | Sus | 35607931 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001666 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | OCB | 1104/2 | 20230101 | 15 | 20230101 | 1349 | 1907593 | 814 | Distribution Circuit | 3rd Party | Vehicle | 1340 | 238190 | 37.7107 | -122.1487 | No | Heavy Rain; | Pole-Wood | Broken- wire on ground | 23-0004220 | OH | Sus | 45612824 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1794812 | 0 | Non-EPSS | N | 2023 | PHASE & GRD
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 50214 | 20230101 | 710 | 20230101 | 1935 | 1907895 | 443 | Distribution Circuit | Equipment Failure/Involved | Underground | 757 | 399930 | 37.6923 | -122.1302 | No | Heavy Rain; | Conductor- Underground | Burned/flashed | 23-0004332 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1794928 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO 1102 | 13751102 | FUSE | 73719 | 20230101 | 739 | 20230101 | 1845 | 1909068 | 666 | Distribution Circuit | Animal | Squirrel | 2 | 1332 | 37.666 | -121.6777 | No | Heavy Rain; | Conductor- Overhead | Normal | 23-0004548 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1795148 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 61175 | 20230101 | 1254 | 20230101 | 2308 | -1908519 | 502 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 3060 | 37.5361 | -122.0606 | No | Heavy Rain; | Conductor- Underground | Deteriorated | 23-0004601 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1795224 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1111 | 14351111 | TRANSFORMER | T6083 | 20230101 | 1448 | 20230102 | 2034 | 1907841 | 1786 | Distribution Circuit | Equipment Failure/Involved | Underground | 140 | 92836 | 37.5532 | -121.9891 | No | Heavy Rain; | Transformer (UG) | Failed/Faulted | 23-0004461 | UG | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1795060 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS 1101 | 13501101 | TRANSFORMER | MTR#1010492102 | 20230101 | 1849 | 20230102 | 930 | 1909078 | 881 | Transformer only | Vegetation | Tree - fell into line | 14 | 12334 | 37.6166 | -122.0388 | No | Heavy Rain; | Conductor- Overhead | Arcing | 23-0004572 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1795174 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 6151 | 20230101 | 2021 | 20230102 | 1536 | 1909181 | 1155 | Distribution Circuit | Equipment Failure/Involved | Underground | 61 | 19740 | 37.7259 | -121.9349 | No | Heavy Rain; | Transformer (UG) | Failed/Faulted | 23-0004617 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1795221 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD 2110 | 14502110 | SWITCH | 73669 | 20230101 | 2246 | 20230102 | 1339 | s1795231 | 893 | Distribution Circuit | Equipment Failure/Involved | Underground | 86 | 30622 | 37.7086 | -121.8671 | No | Heavy Rain; | Transformer (UG) | Leaking | 23-0004576 | UG | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1795231 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT 1104 | 14351104 | FUSE | 14128 | 20230102 | 22 | 20230102 | 1545 | 1909389 | 923 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 49842 | 37.5417 | -121.9264 | No | Heavy Rain; | Conductor- Overhead | Normal | 23-0004629 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1795242 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1103 | 14471103 | FUSE | 9669 | 20230102 | 221 | 20230102 | 834 | 1909452 | 373 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 200 | 74637 | 37.5836 | -122.0577 | No | Heavy Rain; |  |  | 23-0004664 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1795275 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1109 | 13761109 | TRANSFORMER | 315409842098 | 20230102 | 1606 | 20230102 | 1813 | 1910351 | 127 | Transformer only | Equipment Failure/Involved | Electrical Overload | 11 | 1397 | 37.6454 | -122.0866 | No | Heavy Rain; | Crossarm- Wood | Broken | 23-0004836 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1795439 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 50214 | 20230102 | 1826 | 20230103 | 104 | s1795465 | 398 | Distribution Circuit | Equipment Failure/Involved | Underground | 900 | 174891 | 37.6923 | -122.1302 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0004860 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1795465 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1105 | 14381105 | FUSE | 14711 | 20230102 | 1835 | 20230103 | 815 | 1911084 | 820 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 4 | 3282 | 37.6674 | -122.1539 | No | Clear;32-90 F | Fuse | Burned Open | 23-0004994 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1795583 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1106 | 13761106 | FUSE | 14815 | 20230103 | 915 | 20230103 | 1945 | 1911186 | 630 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1261 | 37.6332 | -122.1275 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0005028 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1795603 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1109 | 13111109 | SWITCH | 1709 | 20230103 | 1017 | 20230103 | 1042 | 1911392 | 25 | Distribution Circuit | Company Initiated | Personnel- company | 67 | 1409 | 37.724 | -122.1559 | No | Clear;32-90 F | Other | Broken | 22-0140779 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1795641 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | SWITCH | 50220 | 20230103 | 1110 | 20230103 | 1130 | 1911370 | 20 | Distribution Circuit | Equipment Failure/Involved | Underground | 1665 | 33300 | 37.6922 | -122.1301 | No | Clear;32-90 F | Fuse | Broken | 23-0004991 | UG | Sus | 45612824 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1795638 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | TRANSFORMER | T24861 | 20230103 | 1126 | 20230104 | 129 | 1911135 | 843 | Distribution Circuit | Equipment Failure/Involved | Underground | 138 | 9004 | 37.6977 | -122.1174 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0005089 | UG | Sus | 45612824 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1795650 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | SWITCH | 983 | 20230103 | 1143 | 20230103 | 1200 | 1911434 | 17 | Distribution Circuit | Equipment Failure/Involved | Underground | 84 | 1428 | 37.6937 | -122.1331 | No | Clear;32-90 F | Fuse | Broken | 23-0004991 | UG | Sus | 45612824 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1795660 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1110 | 13761110 | RECLOSER | MR200 | 20230103 | 1416 | 20230103 | 1609 | 1911698 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 5763 | 37.6279 | -122.1228 | No | Clear;32-90 F |  |  | 23-0005213 | OH | Sus | 0 | BAY AREA | JAN | Open Circuit | 0 | No | No | No | 1795722 | 0 | Non-EPSS | N | 2023 | NONE
MISSION | MISSION | GRANT-1104 | 14381104 | SWITCH | 50220 | 20230103 | 1423 | 20230103 | 1438 | 1911691 | 15 | Distribution Circuit | Equipment Failure/Involved | Underground | 1665 | 24975 | 37.6922 | -122.1301 | No | Clear;32-90 F | Fuse | Broken | 23-0004991 | UG | Sus | 45612824 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1795718 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | SWITCH | 983 | 20230103 | 1447 | 20230103 | 1507 | 1911729 | 20 | Distribution Circuit | Equipment Failure/Involved | Underground | 84 | 1680 | 37.6937 | -122.1331 | No | Clear;32-90 F | Fuse | Broken | 23-0004991 | UG | Sus | 45612824 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1795726 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | RECLOSER | MR643 | 20230103 | 1531 | 20230103 | 1640 | 1911804 | 69 | Distribution Circuit | 3rd Party | Vehicle | 2210 | 125370 | 37.6564 | -122.0987 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0005243 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1795741 | 1 | Non-EPSS | N | 2023 | A PH & GRD
MISSION | MISSION | MT EDEN-1110 | 13761110 | RECLOSER | MR200 | 20230103 | 1655 | 20230103 | 1727 | 1911922 | 32 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 1632 | 37.6279 | -122.1228 | No | Clear;32-90 F | Recloser | Failed/Faulted | 23-0005213 | OH | Sus | 0 | BAY AREA | JAN | Open Circuit | 0 | No | No | No | 1795758 | 0 | Non-EPSS | N | 2023 | NONE
MISSION | MISSION | VINEYARD-2105 | 14502105 | RECLOSER | 855920 | 20230104 | 843 | 20230104 | 854 | 1912767 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1907 | 20977 | 37.6749 | -121.8952 | Yes | Clear;32-90F |  |  | 23-0005628 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1796064 | 0 | Non-EPSS | N | 2023 | NONE
MISSION | MISSION | VINEYARD-2105 | 14502105 | RECLOSER | 855920 | 20230104 | 856 | 20230104 | 1029 | 1912829 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1907 | 177351 | 37.6749 | -121.8952 | Yes | Clear;32-90F | Recloser | Malfunctioning | 23-0005640 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1796073 | 0 | Non-EPSS | N | 2023 | NONE
MISSION | MISSION | FREMONT-1107 | 14351107 | INTERRUPTER | 906230 | 20230104 | 859 | 20230104 | 936 | 1912913 | 37 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 215 | 7955 | 37.5311 | -121.9587 | Yes | Clear;32-90F |  |  | 23-0005680 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1796101 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2106 | 14402106 | JUMPER | OJ CORNER OF 8TH ST & SOUTH I ST | 20230104 | 946 | 20230104 | 1116 | 1912768 | 90 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 10080 | 37.6764 | -121.765 | Yes | Strong Winds-Heavy Rain-Clear;32-90F | Jumper | Burned Open | 23-0005696 | OH | Sus | 0 | BAY AREA | JAN | Open Circuit | 0 | No | No | No | 1796112 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY 1111 | 14091111 | FUSE | 9393 | 20230104 | 1002 | 20230104 | 1658 | 1913120 | 416 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 20533 | 37.6647 | -122.0519 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005766 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1796168 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1107 | 14471107 | FUSE | 62476 | 20230104 | 1038 | 20230104 | 1325 | 1913286 | 167 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 288 | 48096 | 37.5553 | -122.0046 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005973 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1796321 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS 2110 | 14402110 | FUSE | 68029 | 20230104 | 1217 | 20230104 | 1309 | 1913737 | 52 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 51 | 2652 | 37.712 | -121.7386 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005919 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1796282 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 7913 | 20230104 | 1246 | 20230105 | 358 | 1918142 | 912 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 912 | 37.7464 | -122.0316 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006504 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1796850 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 15203 | 20230104 | 1526 | 20230104 | 1555 | 1914793 | 29 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 81 | 2349 | 37.5244 | -122.0425 | Yes | Clear;32-90F | Cutout- fuse holder | Normal | 23-0006152 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1796470 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON 2108 | 14232108 | FUSE | 13115 | 20230104 | 1631 | 20230105 | 1500 | 1916032 | 1349 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 28734 | 37.7709 | -122.003 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006504 | OH | Sus | 0 | BAY AREA | JAN | Open Circuit | 0 | No | Yes | No | 1796803 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS 2107 | 14402107 | OCB | 2107/2 | 20230104 | 1725 | 20230105 | 15 | 1916052 | 410 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 4239 | 314909 | 37.7009 | -121.7335 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006330 | OH | Sus | 35419842 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1796628 | 0 | EPSS Ckt | N | 2023 | GRD TIME OC & PH GRD OC TGT
MISSION | MISSION | CASTRO VALLEY 1110 | 14091110 | TRIP-SAVER | 10315 | 20230104 | 1832 | 20230104 | 2114 | 1917051 | 153 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 11169 | 37.6519 | -121.9824 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006683 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1796985 | 0 | EPSS Ckt | N | 2023 | A & B
MISSION | MISSION | SAN LEANDRO-1112 | 13111112 | TRANSFORMER | 315201844637 | 20230104 | 1845 | 20230104 | 2037 | 1917278 | 112 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 1456 | 37.7142 | -122.1599 | Yes | Clear;32-90F |  |  | 23-0006620 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1796921 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | BANCROFT 0402 | 13030402 | FUSE | 10403 | 20230104 | 1848 | 20230105 | 444 | 1917199 | 596 | Distribution Circuit | Equipment Failure/Involved | Overhead | 160 | 21767 | 37.7345 | -122.1457 | Yes | Clear;32-90F | Transformer (OH) | Broken | 23-0006500 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1796799 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY 1108 | 14091108 | TRIP-SAVER | 8971 | 20230104 | 1906 | 20230106 | 137 | 1917425 | 1831 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 77106 | 37.7112 | -122.0551 | Yes | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0006749 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1797051 | 0 | EPSS Ckt | N | 2023 | 1 & 3
MISSION | MISSION | SUNOL 1101 | 14241101 | RECLOSER | MR297 | 20230104 | 1914 | 20230104 | 2230 | 1917546 | 196 | Distribution Circuit | Vegetation | Tree - fell into line | 163 | 26250 | 37.5946 | -121.8882 | Yes | Strong Winds-Heavy Rain-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006469 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1796766 | 0 | EPSS Ckt | N | 2023 | B & GRD
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 11704 | 20230104 | 2017 | 20230104 | 2329 | 1918119 | 192 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 162 | 31104 | 37.7175 | -121.9347 | Yes | Clear;32-90F |  |  | 23-0006802 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1797103 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11230 | 20230104 | 2044 | 20230105 | 905 | 1918598 | 741 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 20748 | 37.6454 | -121.6472 | Yes | Clear;32-90F |  |  | 23-0007134 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1797420 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO U 1114 | 13111114 | SWITCH | 7848 | 20230104 | 2113 | 20230105 | 145 | 1918918 | 272 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 38352 | 37.7268 | -122.1278 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006570 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1797005 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1103 | 14471103 | FUSE | 9669 | 20230105 | 46 | 20230105 | 836 | 1920090 | 470 | Distribution Circuit | Equipment Failure/Involved | Underground | 300 | 81999 | 37.5836 | -122.0577 | Yes | Clear;32-90F | Conductor- Underground | Broken | 23-0006978 | UG | Sus | 35419841 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1797281 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2104 | 14502104 | FUSE | 75033 | 20230105 | 308 | 20230105 | 744 | 1920467 | 276 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 22 | 5974 | 37.6819 | -121.8654 | Yes | Clear;32-90F |  |  | 23-0007039 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1797338 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1107 | 14471107 | TRANSFORMER | 315645838747 | 20230105 | 618 | 20230105 | 1509 | 1920712 | 531 | Transformer only | Vegetation | Tree - branch fell on line | 74 | 39294 | 37.5544 | -122.0032 | Yes | Clear;32-90F | Secondary | Normal | 23-0007389 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1797637 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | TRANSFORMER | T24861 | 20230105 | 741 | 20230105 | 1130 | 1920973 | 229 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 687 | 37.6977 | -122.1174 | Yes | Clear;32-90 F | Transformer | Normal | 23-0007106 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1797400 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | TASSAJARA 2109 | 14662109 | FUSE | 15801 | 20230105 | 826 | 20230105 | 1045 | 1921225 | 139 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 695 | 37.7507 | -121.8716 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007243 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1797514 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | FUSE | 751135 | 20230105 | 945 | 20230105 | 1745 | 1921583 | 480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 17760 | 37.5281 | -121.9554 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0007211 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1797486 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO 1103 | 13751103 | FUSE | 12265 | 20230105 | 1533 | 20230106 | 148 | 1923092 | 615 | Distribution Circuit | 3rd Party | Vehicle | 20 | 12300 | 37.6941 | -121.6757 | Yes | Clear;32-90F | Anchor or Guy | Broken- wire on ground | 23-0007721 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1797903 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1111 | 14351111 | FUSE | 60883 | 20230105 | 2202 | 20230106 | 1744 | 1923945 | 1182 | Distribution Circuit | Equipment Failure/Involved | Underground | 138 | 67288 | 37.5525 | -121.9909 | Yes | Clear;32-90F | Transformer (UG) | Broken | 23-0008023 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798155 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | FUSE | 73363 | 20230105 | 2336 | 20230106 | 910 | 1924009 | 574 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 20060 | 37.7056 | -121.9204 | Yes | Clear;32-90F |  |  | 23-0008103 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798207 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316539843600 | 20230106 | 756 | 20230107 | 150 | 1924225 | 1074 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1074 | 37.6914 | -121.6969 | No | Clear;32-90F | Cutout- fuse holder | Burned/flashed | 23-0008432 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798384 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1107 | 13761107 | FUSE | 51075 | 20230106 | 1111 | 20230106 | 1712 | 1924643 | 361 | Distribution Circuit | Equipment Failure/Involved | Underground | 265 | 35283 | 37.6188 | -122.0699 | No | Clear;32-90F | Elbow | Broken | 23-0008254 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798299 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | EDES-1110 | 13681110 | TRANSFORMER | 315111744965 | 20230106 | 1154 | 20230108 | 643 | 1925131 | 2569 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 7707 | 37.7228 | -122.1913 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0008426 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798382 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1111 | 14351111 | SWITCH | 1148 | 20230107 | 1 | 20230107 | 920 | 1925824 | 559 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 29068 | 37.5525 | -121.9891 | Yes | Clear;32-90F | Transformer (UG) | Broken | 23-0008618 | UG | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1798533 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | T95351 | 20230107 | 744 | 20230108 | 101 | 1926083 | 1037 | Distribution Circuit | Equipment Failure/Involved | Underground | 139 | 24786 | 37.5191 | -122.0499 | Yes | Clear;32-90F | Transformer (UG) | Leaking | 23-0008694 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798576 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | INTERRUPTER | 14215 | 20230107 | 913 | 20230108 | 1434 | 1926216 | 1559 | Distribution Circuit | Equipment Failure/Involved | Underground | 6466 | 180756 | 37.6895 | -122.1389 | Yes | Clear;32-90F | Elbow | Failed/Faulted | 23-0008709 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798592 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRANSFORMER | 315353642485 | 20230107 | 1422 | 20230108 | 1732 | 1926707 | 1630 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 9780 | 37.6558 | -122.1062 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0008844 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798702 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1110 | 14471110 | OCB | 1110/2 | 20230107 | 1545 | 20230108 | 1532 | 1927026 | 1414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2356 | 79229 | 37.5571 | -122.0582 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008889 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | Yes | 1798741 | 0 | Non-EPSS | N | 2023 | A C PHASE TIME
MISSION | MISSION | FREMONT-1111 | 14351111 | TRANSFORMER | T6083 | 20230107 | 1547 | 20230107 | 1912 | 1927027 | 205 | Transformer only | Equipment Failure/Involved | Underground | 51 | 10455 | 37.5532 | -121.9891 | Yes | Clear;32-90F | Other | Failed/Faulted | 23-0009037 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798864 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 10711 | 20230107 | 1557 | 20230109 | 250 | 1927074 | 2093 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 77636 | 37.7065 | -122.0673 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0008905 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1798755 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | FUSE | 11670 | 20230107 | 1602 | 20230107 | 1850 | 1927088 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 200 | 33600 | 37.698 | -122.0781 | Yes | Clear;32-90F |  |  | 23-0008983 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1798813 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1104 | 14471104 | FUSE | 7514 | 20230107 | 1730 | 20230107 | 2020 | 1927132 | 170 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 10710 | 37.5317 | -122.0309 | Yes | Clear;32-90F | Secondary | Normal | 23-0008961 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1798794 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315294043046 | 20230107 | 1731 | 20230109 | 2 | 1927351 | 1831 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 21972 | 37.6709 | -122.127 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0009165 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798992 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 14128 | 20230107 | 1805 | 20230108 | 1738 | 1927451 | 1413 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 76302 | 37.5417 | -121.9264 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009023 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1798850 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | FUSE | 11701 | 20230107 | 1805 | 20230109 | 1231 | 1927482 | 2546 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 16704 | 37.5332 | -121.9191 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009070 | OH | Sus | 0 | BAY AREA | JAN | Multi-Fault | 0 | No | Yes | No | 1798899 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11230 | 20230107 | 1825 | 20230108 | 1045 | 1927554 | 980 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 27440 | 37.6454 | -121.6472 | Yes | Clear;32-90F |  |  | 23-0009043 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1798872 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1106 | 14381106 | RECLOSER | MR664 | 20230107 | 1903 | 20230107 | 2023 | 1927768 | 80 | Distribution Circuit | 3rd Party | Vehicle | 3658 | 252548 | 37.6711 | -122.126 | Yes | Clear;32-90F | Pothead(Riser Termination) | Burned/flashed | 23-0009029 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1798856 | 0 | Non-EPSS | N | 2023 | B PHASE & GRD
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 10295 | 20230107 | 2309 | 20230108 | 228 | 1928850 | 199 | Distribution Circuit | Vegetation | Tree - branch fell on line | 244 | 48556 | 37.6836 | -122.1159 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009427 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1799260 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS 2108 | 14402108 | FUSE | 71291 | 20230107 | 2339 | 20230108 | 845 | 1932143 | 546 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1455 | 37.6316 | -121.7866 | Yes | Clear;32-90F |  |  | 23-0009900 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1799750 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 11004 | 20230107 | 2340 | 20230108 | 313 | 1929427 | 213 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 5112 | 37.7227 | -121.9368 | Yes | Clear;32-90F |  |  | 23-0009684 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1799517 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 886522 | 20230107 | 2347 | 20230108 | 2320 | 1929867 | 1413 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 18066 | 37.6634 | -121.6803 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009432 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1799265 | 0 | EPSS Ckt | N | 2023 | A&#9578-- B & GRD
MISSION | MISSION | GRANT-1108 | 14381108 | OCB | 1108/2 | 20230107 | 2348 | 20230108 | 1812 | 1929716 | 1104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6027 | 302985 | 37.6718 | -122.1595 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0009424 | OH | Sus | 0 | BAY AREA | JAN | Multi-Fault | 0 | No | No | No | 1799257 | 0 | Non-EPSS | N | 2023 | ABC PHASE T
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11248 | 20230107 | 2358 | 20230108 | 2317 | 1930086 | 1399 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 22384 | 37.687 | -121.6968 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009718 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1799552 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2104 | 14402104 | FUSE | 11437 | 20230107 | 2359 | 20230108 | 1215 | 1930082 | 736 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 14720 | 37.6874 | -121.7835 | Yes | Clear;32-90F |  |  | 23-0010100 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1799948 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LIVERMORE-1101 | 12141101 | FUSE | 9773 | 20230108 | 4 | 20230108 | 207 | 1930451 | 123 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 17147 | 37.6769 | -121.7908 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009662 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1799495 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | RECLOSER | MR735 | 20230108 | 339 | 20230108 | 349 | 1930624 | 10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1006 | 10060 | 37.5331 | -121.9235 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009794 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1799633 | 0 | Non-EPSS | N | 2023 | NONE
MISSION | MISSION | MT EDEN-1105 | 13761105 | TRANSFORMER | 315326142836 | 20230108 | 744 | 20230109 | 848 | 1932883 | 1504 | Transformer only | Vegetation | Tree - branch fell on line | 68 | 102272 | 37.6652 | -122.1158 | Yes | Clear;32-90F | Service conductor | Broken | 23-0010123 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1799972 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1105 | 13761105 | TRANSFORMER | 315326342801 | 20230108 | 909 | 20230108 | 2215 | 1932872 | 786 | Transformer only | Vegetation | Tree - fell into line | 61 | 47946 | 37.6643 | -122.1158 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0010119 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1799968 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 11587 | 20230108 | 1122 | 20230108 | 1355 | 1933304 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 612 | 37.5927 | -121.8853 | Yes | Clear;32-90F |  |  | 23-0010185 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1800037 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | TRANSFORMER | 315385342286 | 20230108 | 1527 | 20230109 | 340 | 1934351 | 733 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 13927 | 37.6505 | -122.0951 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Secondary | Broken- wire on ground | 23-0010694 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1800552 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-2111 | 14472111 | JUMPER | BURNT OPEN JUMPER | 20230108 | 1657 | 20230108 | 1811 | 1934331 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 384 | 4637 | 37.5365 | -122.0547 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0010401 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1800248 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | RECLOSER | MR376 | 20230108 | 2129 | 20230109 | 135 | 1934601 | 246 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 41082 | 37.7198 | -121.9352 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0010530 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1800381 | 0 | Non-EPSS | N | 2023 | N/A
MISSION | MISSION | FREMONT-1104 | 14351104 | RECLOSER | MR584 | 20230108 | 2211 | 20230109 | 301 | 1935261 | 290 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1249 | 362210 | 37.5463 | -121.9342 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Normal | 23-0010709 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1800570 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
MISSION | MISSION | DIXON LANDING 2109 | 14722109 | TRANSFORMER | 315879036037 | 20230109 | 308 | 20230109 | 2044 | 1935402 | 1056 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 17952 | 37.4812 | -121.9214 | Yes | Strong Winds-Heavy Rain-Clear;32-90 F | Transformer | Failed/Faulted | 23-0011053 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1800875 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 9590 | 20230109 | 448 | 20230109 | 507 | 1935688 | 19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 384 | 7296 | 37.538 | -122.0594 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Jumper | Normal | 23-0010779 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1800642 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 50214 | 20230109 | 651 | 20230109 | 1850 | 1936696 | 719 | Distribution Circuit | Equipment Failure/Involved | Underground | 756 | 161964 | 37.6923 | -122.1302 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0010871 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1800722 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | 315760937409 | 20230109 | 1109 | 20230109 | 1413 | 1937241 | 184 | Transformer only | Vegetation | Tree - grew into line | 19 | 3496 | 37.5182 | -121.9627 | Yes | Strong Winds-Heavy Rain-Clear;32-90 F | Service conductor | Broken- wire on object | 23-0011129 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1800938 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON 2107 | 14232107 | FUSE | 11475 | 20230109 | 1209 | 20230109 | 1425 | 1938212 | 136 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 1904 | 37.7179 | -122.0055 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Fuse | Burned Open | 23-0011289 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1801064 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | FUSE | 779893 | 20230109 | 1301 | 20230109 | 2105 | 1938202 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 484 | 37.6214 | -121.9437 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011302 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1801080 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 9461 | 20230109 | 1716 | 20230110 | 146 | 1939016 | 510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 85170 | 37.7188 | -121.9358 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Pole-Wood | Broken | 23-0011465 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1801223 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | FUSE | 9083 | 20230109 | 1820 | 20230109 | 1952 | 1939264 | 92 | Distribution Circuit | Animal | Squirrel | 43 | 3989 | 37.5127 | -121.9601 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Fuse | Burned Open | 23-0011569 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1801332 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1107 | 13761107 | OCB | 1107/2 | 20230109 | 1953 | 20230109 | 2025 | 1939522 | 32 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 3168 | 37.6319 | -122.1025 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Crossarm- Wood | Broken | 23-0011498 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1801342 | 0 | Non-EPSS | N | 2023 | N/A
MISSION | MISSION | DUMBARTON-1106 | 14471106 | FUSE | 1385 | 20230109 | 2020 | 20230110 | 335 | 1939551 | 435 | Distribution Circuit | Equipment Failure/Involved | Underground | 588 | 53556 | 37.5821 | -122.076 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Elbow | Failed/Faulted | 23-0011614 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1801376 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1106 | 14471106 | OCB | 1106/2 | 20230110 | 223 | 20230110 | 335 | 1940615 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5039 | 358351 | 37.5571 | -122.0584 | Yes | Heavy Rain-Strong Winds-Clear;32-90F |  |  | 23-0011767 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1801527 | 0 | Non-EPSS | N | 2023 | PHASE OC
MISSION | MISSION | DUMBARTON-1102 | 14471102 | FUSE | 15059 | 20230110 | 225 | 20230110 | 2058 | 1940645 | 1113 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 96831 | 37.5542 | -122.0162 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011906 | OH | Sus | 0 | BAY AREA | JAN | Multi-Fault | 0 | No | Yes | No | 1801676 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10668 | 20230110 | 229 | 20230110 | 1227 | 1940797 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1196 | 37.5597 | -121.9235 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0012345 | OH | Sus | 0 | BAY AREA | JAN | Multi-Fault | 0 | No | No | No | 1802086 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10808 | 20230110 | 249 | 20230110 | 728 | 1941037 | 279 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 4464 | 37.6608 | -121.6715 | Yes | Rain-Strong Winds; |  |  | 23-0011975 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1801755 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1105 | 14381105 | FUSE | 14711 | 20230110 | 422 | 20230110 | 615 | 1941825 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 678 | 37.6674 | -122.1539 | Yes | Heavy Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Together | 23-0011907 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1801677 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1106 | 14471106 | OCB | 1106/2 | 20230110 | 629 | 20230110 | 639 | 1943041 | 10 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5059 | 50590 | 37.5571 | -122.0584 | Yes | Rain-Strong Winds; |  |  | 23-0011954 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1801733 | 0 | Non-EPSS | N | 2023 | PHASE OC
MISSION | MISSION | DUMBARTON-1106 | 14471106 | OCB | 1106/2 | 20230110 | 715 | 20230110 | 945 | 1943249 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5059 | 713890 | 37.5571 | -122.0584 | Yes | Rain-Strong Winds; |  |  | 23-0011984 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1801764 | 0 | Non-EPSS | N | 2023 | PHASE OC B & C I
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | SWITCH | 40067 | 20230110 | 1915 | 20230110 | 2320 | 1946368 | 245 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 658 | 37.6968 | -121.7253 | Yes | Clear;32-90F | Transformer (UG) | Leaking | 23-0012582 | UG | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1802518 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | RADUM 1105 | 13151105 | FUSE | 72826 | 20230110 | 2228 | 20230112 | 106 | 1946700 | 1598 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 59930 | 37.6377 | -121.8967 | Yes | Clear;32-90F | Secondary | Broken | 23-0013378 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1802916 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 9191 | 20230111 | 524 | 20230112 | 700 | 1946981 | 1536 | Distribution Circuit | Environmental/External | Flood/Erosion | 21 | 6056 | 37.594 | -121.8879 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0013374 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | Yes | No | 1802912 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | T7274 | 20230111 | 856 | 20230111 | 1035 | 1947238 | 99 | Transformer only | Equipment Failure/Involved | Underground | 15 | 1485 | 37.7239 | -122.1337 | No | Clear;32-90F | Secondary | Burned/flashed | 23-0013412 | UG | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1802941 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1110 | 14351110 | FUSE | 60954 | 20230112 | 949 | 20230112 | 1154 | s1803681 | 125 | Distribution Circuit | Equipment Failure/Involved | Underground | 155 | 19375 | 37.5349 | -121.9624 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0014369 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1803681 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1110 | 14351110 | SWITCH | 60954SW | 20230112 | 2217 | 20230112 | 2231 | 1951100 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 155 | 2170 | 37.5349 | -121.9624 | No | Clear;32-90F | Conductor- Underground | Normal | 23-0014369 | UG | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1804067 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 9704 | 20230113 | 819 | 20230113 | 1141 | 1951403 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 153 | 22722 | 37.6301 | -122.0889 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0015121 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1804188 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1104 | 14471104 | TRANSFORMER | 315547237935 | 20230114 | 811 | 20230114 | 913 | 1953226 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 620 | 37.5319 | -122.037 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0015980 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1804806 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD 2107 | 14502107 | FUSE | 299333 | 20230114 | 1055 | 20230114 | 1610 | 1953860 | 315 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 945 | 37.6389 | -121.8709 | Yes | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0016101 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1804896 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NORTH DUBLIN 2103 | 14052103 | FUSE | 15799 | 20230114 | 1659 | 20230115 | 1413 | 1954824 | 1274 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1274 | 37.7642 | -121.8668 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016346 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1805101 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1105 | 13761105 | TRANSFORMER | 315326242714 | 20230114 | 1918 | 20230114 | 1946 | 1955115 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 224 | 37.662 | -122.1157 | Yes | Clear;32-90F | Fuse | Broken | 23-0016393 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1805144 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | FUSE | 9134 | 20230114 | 2206 | 20230115 | 1413 | 1955261 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 50284 | 37.5309 | -121.9864 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0016562 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1805313 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | SWITCH | 85746 | 20230115 | 1034 | 20230115 | 1043 | 1955804 | 9 | Distribution Circuit | 3rd Party | Metallic Balloon | 219 | 1971 | 37.7045 | -121.9156 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0016625 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1805365 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | INTERRUPTER | 257022 | 20230115 | 1606 | 20230115 | 1951 | 1956152 | 225 | Distribution Circuit | Vegetation | Tree - bark fell into line | 116 | 23316 | 37.6865 | -122.1304 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016749 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1805452 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | 315296244887 | 20230116 | 119 | 20230116 | 907 | 1956504 | 468 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2808 | 37.7215 | -122.1274 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0016938 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1805644 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1110 | 14471110 | OCB | 1110/2 | 20230116 | 308 | 20230116 | 2150 | 1956653 | 1122 | Distribution Circuit | Equipment Failure/Involved | Underground | 2355 | 531747 | 37.5571 | -122.0582 | Yes | Clear;32-90F | Connector or Splice (UG) | Failed/Faulted | 23-0016887 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1805588 | 0 | Non-EPSS | N | 2023 | C PHASE & GRD
MISSION | MISSION | CAYETANO 2109 | 14422109 | RECLOSER | MR572 | 20230116 | 415 | 20230116 | 1524 | 1956767 | 669 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 27896 | 37.74 | -121.7469 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016909 | OH | Sus | 35419778 | BAY AREA | JAN | Multi-Fault | 0 | No | Yes | No | 1805614 | 0 | EPSS Ckt | N | 2023 | A/B/C & GRD
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 70536 | 20230116 | 456 | 20230116 | 1400 | 1956836 | 544 | Distribution Circuit | Equipment Failure/Involved | Underground | 71 | 37474 | 37.7733 | -121.9887 | Yes | Clear;32-90F | Elbow | Burned/flashed | 23-0016954 | UG | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1805659 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 70666 | 20230116 | 613 | 20230116 | 1120 | 1956929 | 307 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 23025 | 37.6589 | -121.7754 | Yes | Clear;32-90F |  |  | 23-0017026 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1805730 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | MR297 | 20230116 | 921 | 20230116 | 1712 | 1957477 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 22427 | 37.5946 | -121.8882 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0017075 | OH | Sus | 35419778 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1805772 | 0 | EPSS Ckt | N | 2023 | A- GRD
MISSION | MISSION | DUMBARTON-1108 | 14471108 | FUSE | 15354 | 20230116 | 1009 | 20230116 | 1503 | 1957394 | 294 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 5880 | 37.5804 | -122.0555 | Yes | Clear;32-90F | Connector or Splice (UG) | Failed/Faulted | 23-0017112 | UG | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1805804 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 10589 | 20230116 | 1216 | 20230116 | 1337 | 1958025 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 4855 | 37.5285 | -122.0435 | Yes | Clear;32-90F |  |  | 23-0017209 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1805886 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | CAYETANO 2111 | 14422111 | TRANSFORMER | 316214545240 | 20230116 | 1343 | 20230116 | 1858 | 1958241 | 315 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 315 | 37.7343 | -121.8105 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0017278 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1805957 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS 1111 | 13501111 | OCB | 1111/2 | 20230116 | 1352 | 20230117 | 639 | 1958223 | 1007 | Distribution Circuit | Vegetation | Tree - fell into line | 6437 | 383137 | 37.5953 | -122.0174 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0017231 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1805907 | 0 | EPSS Ckt | N | 2023 | B/U RLY OC TARGET
MISSION | MISSION | SAN LEANDRO-1109 | 13111109 | SWITCH | 2672SW | 20230117 | 954 | 20230117 | 1225 | 1959369 | 151 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 67 | 10117 | 37.7264 | -122.1572 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 23-0017593 | UG | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1806190 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | FUSE | 6088 | 20230117 | 1516 | 20230118 | 1231 | 1959868 | 1275 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1275 | 37.7131 | -122.1723 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0017801 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1806255 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 7555 | 20230117 | 1556 | 20230119 | 243 | 1960055 | 247 | Distribution Circuit | Equipment Failure/Involved | Underground | 280 | 92698 | 37.5791 | -121.9962 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0017870 | UG | Sus | 31634674 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1806285 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | 315510937307 | 20230118 | 1053 | 20230118 | 1502 | 1960847 | 249 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 249 | 37.5143 | -122.0488 | No | Clear;32-90 F |  |  | 23-0018495 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1806610 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | TRANSFORMER | 315817039067 | 20230118 | 1929 | 20230119 | 2225 | 1961464 | 1616 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 4 | 2462 | 37.564 | -121.9444 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0018864 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1806789 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD 2108 | 14502108 | FUSE | 51079 | 20230118 | 2153 | 20230118 | 2354 | 1961548 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 6776 | 37.6615 | -121.8895 | No | Clear;32-90 F |  |  | 23-0018635 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1806693 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | 315606638919 | 20230118 | 2233 | 20230119 | 1159 | 1961701 | 806 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 7254 | 37.559 | -122.0167 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0018867 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1806790 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS 1110 | 13501110 | FUSE | 11470 | 20230118 | 2307 | 20230119 | 1015 | 1961712 | 668 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 161 | 107548 | 37.6003 | -122.0074 | No | Clear;32-90 F |  |  | 23-0018762 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1806760 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1110 | 13501110 | TRANSFORMER | 315687040439 | 20230119 | 1319 | 20230120 | 1615 | 1962205 | 1472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3232 | 37.6011 | -121.9898 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0019011 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1806829 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS 1108 | 13501108 | TRANSFORMER | 315552941044 | 20230119 | 1641 | 20230120 | 331 | 1962591 | 650 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 7800 | 37.6171 | -122.0365 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0019037 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1806844 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 14350 | 20230120 | 851 | 20230120 | 923 | 1963041 | 32 | Distribution Circuit | Animal | Squirrel | 220 | 7040 | 37.6957 | -122.0617 | No | Clear;32-90F | Pothead(Riser Termination) | Normal | 23-0019284 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807008 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1110 | 13501110 | TRANSFORMER | 315682340429 | 20230120 | 1026 | 20230120 | 1941 | 1963151 | 555 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1110 | 37.6008 | -121.9914 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0019601 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807084 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | SWITCH | 51523 | 20230120 | 1057 | 20230120 | 1105 | 1963194 | 8 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 288 | 37.6726 | -122.0808 | No | Clear;32-90F | Fuse | Burned Open | 23-0019362 | UG | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1807042 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1103 | 14471103 | TRANSFORMER | 15230 | 20230120 | 1143 | 20230120 | 1827 | 1963235 | 404 | Transformer only | Equipment Failure/Involved | Fire- pole | 14 | 5656 | 37.5663 | -122.044 | No | Clear;32-90 F | Crossarm- Wood | Failed/Faulted | 23-0019495 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807064 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1105 | 14471105 | INTERRUPTER | 278008 | 20230120 | 1423 | 20230121 | 1 | 1963710 | 547 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 1154 | 37.5483 | -122.0602 | No | Clear;32-90F | Customer Equipment | Failed/Faulted | 23-0019664 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807138 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1103 | 14471103 | TRANSFORMER | 15230 | 20230120 | 1827 | 20230121 | 134 | 1963639 | 427 | Distribution Circuit | Equipment Failure/Involved | Underground | 81 | 10289 | 37.5663 | -122.044 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0019495 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807094 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | RECLOSER | 818336 | 20230121 | 1636 | 20230121 | 2104 | 1964227 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4439 | 570141 | 37.708 | -121.9371 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0019765 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | Yes | No | 1807228 | 0 | EPSS Ckt | N | 2023 | LR DID NOT TARGET
MISSION | MISSION | SAN RAMON-2107 | 14232107 | RECLOSER | 818336 | 20230121 | 2332 | 20230122 | 443 | 1964400 | 311 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 404 | 125644 | 37.708 | -121.9371 | No | Clear;32-90F |  |  | 23-0019811 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1807270 | 0 | EPSS Ckt | N | 2023 | NONE
MISSION | MISSION | SAN RAMON 2106 | 14232106 | FUSE | 76044 | 20230122 | 909 | 20230122 | 1136 | 1964569 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2646 | 37.703 | -122.0024 | No | Clear;32-90F |  |  | 23-0019858 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807304 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY 1102 | 14091102 | FUSE | 14014 | 20230122 | 1341 | 20230122 | 1451 | 1964763 | 70 | Distribution Circuit | 3rd Party | Metallic Balloon | 179 | 12530 | 37.6863 | -122.0479 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019895 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1807332 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY 1107 | 14091107 | TRANSFORMER | T7211 | 20230122 | 1645 | 20230123 | 1410 | 1964941 | 1285 | Distribution Circuit | Equipment Failure/Involved | Underground | 290 | 104572 | 37.6618 | -122.0657 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0019928 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807362 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN 1112 | 13761112 | TRANSFORMER | T7201 | 20230122 | 2223 | 20230123 | 1410 | 1965135 | 947 | Transformer only | Equipment Failure/Involved | Underground | 72 | 68184 | 37.6606 | -122.0654 | No | Clear;32-90F | Conductor- Underground | Normal | 23-0019994 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807427 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1106 | 13501106 | FUSE | 12376 | 20230123 | 303 | 20230123 | 1624 | 1965251 | 801 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3740 | 37.6022 | -122.0366 | No | Clear;32-90F | Jumper | Burned Open | 23-0020106 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807545 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | OTHER | WIRE DOWN SSD OF 15315 | 20230123 | 356 | 20230123 | 1456 | 1965262 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1187 | 87066 | 37.4951 | -121.9131 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0020027 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | Yes | 1807443 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | TRANSFORMER | 315766139639 | 20230124 | 1142 | 20230124 | 1245 | 1966964 | 63 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 441 | 37.5794 | -121.9621 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0020764 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807881 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | 315294844281 | 20230124 | 1332 | 20230124 | 1857 | 1967086 | 325 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 3250 | 37.7049 | -122.1275 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0020862 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1807905 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | SWITCH | 1388 | 20230124 | 1518 | 20230124 | 1626 | 1967311 | 68 | Distribution Circuit | Equipment Failure/Involved | Underground | 280 | 17576 | 37.578 | -121.9946 | No | Clear;32-90F | Connector or Splice (UG) | Broken | 23-0017870 | UG | Sus | 31634674 | BAY AREA | JAN | Open Circuit | 0 | No | No | No | 1807932 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 13085 | 20230126 | 945 | 20230127 | 221 | 1968735 | 995 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 50 | 13182 | 37.6759 | -121.8739 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0021694 | UG | Sus | 31635682 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1808390 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY 1105 | 14091105 | TRANSFORMER | 315483444215 | 20230126 | 1038 | 20230126 | 1526 | 1968820 | 288 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 2016 | 37.7039 | -122.0624 | No | Clear;32-90 F |  |  | 23-0021755 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1808412 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | OCB | 1114/2 | 20230126 | 1540 | 20230126 | 1556 | 1969100 | 16 | Distribution Circuit | 3rd Party | Other | 4817 | 77072 | 37.7106 | -122.1486 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0021965 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1808470 | 0 | EPSS Ckt | N | 2023 | NA
MISSION | MISSION | BANCROFT 0401 | 13030401 | TRANSFORMER | 315185445465 | 20230128 | 558 | 20230128 | 655 | 1970254 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 627 | 37.7369 | -122.1661 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0022590 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1808765 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2110 | 14502110 | RECLOSER | 472595 | 20230129 | 1334 | 20230129 | 1545 | 1970987 | 131 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 1610 | 37.7051 | -121.8234 | No | Clear;32-90 F | Customer Equipment | Broken | 23-0022738 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1808936 | 0 | EPSS Ckt | N | 2023 | A PHASE
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 8156 | 20230131 | 900 | 20230131 | 1218 | 1972514 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 27126 | 37.7163 | -121.94 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0023321 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1809389 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT 1109 | 14351109 | FUSE | 10956 | 20230131 | 1737 | 20230201 | 533 | 1973211 | 716 | Distribution Circuit | Equipment Failure/Involved | Underground | 233 | 45348 | 37.5316 | -121.9345 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0023662 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1809532 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | TRANSFORMER | 315513542457 | 20230201 | 1800 | 20230202 | 436 | 1974313 | 636 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1272 | 37.6557 | -122.0509 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0024152 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1809838 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | 315434243635 | 20230202 | 1536 | 20230202 | 2108 | 1975195 | 332 | Transformer only | Unknown Cause | Patrol - found nothing | 20 | 6640 | 37.6877 | -122.079 | No | Clear;32-90 F |  |  | 23-0024580 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1810090 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | EDES-1110 | 13681110 | TRANSFORMER | 315106845005 | 20230202 | 1949 | 20230202 | 2247 | 1975394 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 178 | 37.724 | -122.193 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0024684 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1810157 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 298061 | 20230203 | 715 | 20230203 | 853 | 1975664 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 205 | 20090 | 37.5958 | -121.8897 | No | Overcast;32-90 F |  |  | 23-0024753 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1810203 | 0 | EPSS Ckt | N | 2023 | A/B / 51 TIME
MISSION | MISSION | FREMONT-1103 | 14351103 | FUSE | 61001 | 20230203 | 921 | 20230203 | 1933 | 1975806 | 551 | Distribution Circuit | Equipment Failure/Involved | Underground | 608 | 93882 | 37.5587 | -121.9726 | No | Overcast;32-90 F | Switch (UG) | Failed/Faulted | 23-0024846 | UG | Sus | 35424906 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1810306 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1104 | 14471104 | TRANSFORMER | 315521338406 | 20230203 | 1935 | 20230203 | 1952 | 1976279 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 221 | 37.5446 | -122.046 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Arcing | 23-0025129 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1810401 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | 315605036990 | 20230203 | 2038 | 20230203 | 2215 | 1976326 | 97 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 97 | 37.5073 | -122.0149 | No | Clear;32-90 F |  |  | 23-0025152 | OH | Sus | 0 | BAY AREA | FEB | None | 0 | No | No | No | 1810420 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | 315469943531 | 20230204 | 1140 | 20230204 | 1151 | 1976573 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 77 | 37.6851 | -122.0666 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0025198 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1810508 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 639241 | 20230205 | 1323 | 20230205 | 1416 | 1977482 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 1378 | 37.617 | -122.0415 | No | Clear;32-90 F |  |  | 23-0025415 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1810704 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 134120 | 20230205 | 1753 | 20230205 | 2005 | 1977645 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 7260 | 37.7899 | -121.8435 | No | Clear;32-90 F |  |  | 23-0025452 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1810737 | 0 | EPSS Ckt | N | 2023 | 50 INST
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 70666 | 20230205 | 2238 | 20230206 | 1105 | 1977758 | 747 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 29872 | 37.6589 | -121.7754 | No | Partly Cloudy;32-90 F | Elbow | Broken | 23-0025512 | UG | Sus | 45659034 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1810794 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | SWITCH | 72403 | 20230205 | 2254 | 20230206 | 514 | 1977759 | 380 | Distribution Circuit | 3rd Party | Vehicle | 24 | 9120 | 37.6611 | -121.782 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0025506 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1810791 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | 315469943531 | 20230206 | 1831 | 20230207 | 441 | 1978634 | 610 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4270 | 37.6851 | -122.0666 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0025995 | OH | Sus | 35425383 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1811091 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1102 | 13111102 | TRANSFORMER | 315232545123 | 20230206 | 2118 | 20230207 | 148 | 1978673 | 270 | Transformer only | Equipment Failure/Involved | Overhead | 40 | 10800 | 37.7277 | -122.1496 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0025987 | OH | Sus | 31636402 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1811082 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | INTERRUPTER | 408134 | 20230207 | 347 | 20230207 | 1249 | 1978787 | 542 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 32526 | 37.6763 | -121.8611 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0026007 | UG | Sus | 45659614 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1811106 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | FUSE | 14029 | 20230207 | 430 | 20230207 | 732 | 1978790 | 182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 11102 | 37.7204 | -122.1722 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0026033 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1811129 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1114 | 13761114 | TRANSFORMER | 20495 | 20230207 | 632 | 20230207 | 651 | 1978806 | 19 | Transformer only | 3rd Party | Customer Equipment | 15 | 285 | 37.6243 | -122.1277 | No | Clear;32-90 F | Transformer | Normal | 23-0026019 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1811123 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1102 | 14381102 | TRANSFORMER | 100000041648 | 20230207 | 1308 | 20230208 | 940 | 1979296 | 1232 | Transformer only | 3rd Party | Customer Equipment | 1 | 1232 | 37.6469 | -122.1199 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 23-0026301 | OH | Sus | 35425563 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1811334 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | TRANSFORMER | 315695539497 | 20230207 | 1414 | 20230208 | 320 | 1979344 | 786 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3144 | 37.5752 | -121.9864 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0026421 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1811370 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | TRANSFORMER | 315270243956 | 20230208 | 1041 | 20230208 | 1814 | 1979977 | 453 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 7701 | 37.6958 | -122.1358 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0026660 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1811629 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1107 | 13761107 | SWITCH | 50940 | 20230210 | 1806 | 20230212 | 1453 | 1982105 | 2687 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 2687 | 37.6076 | -122.0589 | No | Clear;32-90F | Transformer (UG) | Normal | 23-0019198 | UG | Sus | 47022687 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1812298 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1111 | 13761111 | SWITCH | 3366 | 20230210 | 1938 | 20230211 | 403 | 1982132 | 505 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 505 | 37.6021 | -122.0819 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0027682 | UG | Sus | 35424220 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1812302 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | FUSE | 12141 | 20230211 | 808 | 20230211 | 1005 | 1982237 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 5026 | 37.4861 | -121.9234 | No | Clear;32-90F |  |  | 23-0027820 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1812404 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | TRANSFORMER | 315811940336 | 20230211 | 857 | 20230211 | 1320 | 1982286 | 263 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 789 | 37.599 | -121.9466 | No | Clear;32-90F | Transformer (OH) | Burned/flashed | 23-0027837 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1812424 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1108 | 13501108 | OCB | 1108/2 | 20230211 | 1702 | 20230212 | 109 | 1982574 | 487 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4037 | 382017 | 37.5953 | -122.0175 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0027858 | OH | Sus | 31636607 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1812443 | 0 | EPSS Ckt | N | 2023 | A-B-C TGTS
MISSION | MISSION | VINEYARD-2106 | 14502106 | FUSE | 40073 | 20230213 | 1157 | 20230214 | 207 | 1983651 | 850 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 17049 | 37.6727 | -121.9038 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0028158 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1812796 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-2111 | 14472111 | SWITCH | 383476 | 20230213 | 1414 | 20230214 | 15 | 1983788 | 601 | Distribution Circuit | Equipment Failure/Involved | Underground | 163 | 97963 | 37.5194 | -122.0559 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0028132 | UG | Sus | 35426233 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1812821 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1102 | 13761102 | SWITCH | 1761 | 20230215 | 1119 | 20230216 | 1425 | 1986081 | 1626 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 1626 | 37.6587 | -122.129 | No | Clear;32-90F | Switch (UG) | Normal | 23-0029196 | UG | Sus | 0 | BAY AREA | FEB | None | 0 | No | No | No | 1813506 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1106 | 14471106 | FUSE | 10674 | 20230216 | 1132 | 20230216 | 1350 | 1986895 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 414 | 37.5832 | -122.0824 | No | Clear;32-90F |  |  | 23-0029728 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1813763 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315557039035 | 20230217 | 2208 | 20230218 | 615 | 1987995 | 487 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3896 | 37.562 | -122.034 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0030395 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1814118 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1110 | 13501110 | FUSE | 11431 | 20230218 | 950 | 20230218 | 1036 | 1988165 | 46 | Distribution Circuit | Animal | Bird found | 50 | 2300 | 37.5941 | -122.0019 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0030457 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1814190 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | OTHER | 7580 POTHEADS | 20230218 | 2154 | 20230219 | 0 | 1988386 | 126 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4945 | 238686 | 37.5092 | -121.9621 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0030510 | OH | Sus | 31638780 | BAY AREA | FEB | Open Circuit | 0 | No | No | No | 1814244 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | TRANSFORMER | 315839337030 | 20230219 | 708 | 20230219 | 1811 | 1988510 | 663 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 5967 | 37.5082 | -121.9356 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0030546 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1814298 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 30965 | 20230219 | 802 | 20230219 | 2342 | 1988521 | 178 | Distribution Circuit | Equipment Failure/Involved | Underground | 133 | 34048 | 37.5716 | -122.0149 | Yes | Clear;32-90 F | Conductor- Underground | Broken | 23-0030535 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1814284 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | BANCROFT-0401 | 13030401 | SWITCH | 9307 | 20230219 | 1302 | 20230220 | 1439 | 1989118 | 1537 | Distribution Circuit | Equipment Failure/Involved | Substation | 342 | 525654 | 37.7391 | -122.1547 | Yes | Clear;32-90 F | Bus | Burned/flashed | 23-0030591 | OH | Sus | 0 | BAY AREA | FEB | Open Circuit | 0 | No | No | No | 1814343 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10882 | 20230219 | 1759 | 20230219 | 1900 | 1988992 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 244 | 37.5977 | -121.6341 | Yes | Clear;32-90 F |  |  | 23-0030580 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1814331 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1107 | 14471107 | TRANSFORMER | 315588738382 | 20230220 | 26 | 20230220 | 832 | 1989144 | 486 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 5832 | 37.5442 | -122.0226 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0030611 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1814365 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1115 | 13111115 | INTERRUPTER | 35434 | 20230221 | 1301 | 20230222 | 234 | 1990566 | 813 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 57000 | 37.7057 | -122.1687 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0031129 | OH | Sus | 45681058 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1814834 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1103 | 14351103 | RECLOSER | MR127 | 20230221 | 1328 | 20230222 | 841 | 1990716 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 3610 | 339855 | 37.5627 | -121.9591 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031098 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1814809 | 0 | Non-EPSS | N | 2023 | ABC
MISSION | MISSION | VINEYARD-2105 | 14502105 | OCB | 2105/2 | 20230221 | 1330 | 20230221 | 1625 | 1990750 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3162 | 530490 | 37.6697 | -121.8544 | Yes | Clear;32-90 F |  |  | 23-0031107 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1814815 | 0 | Non-EPSS | N | 2023 | SET A
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 50952 | 20230221 | 1338 | 20230221 | 1551 | 1990838 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 256 | 34048 | 37.7026 | -122.1857 | Yes | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0031277 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1814936 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 15195 | 20230221 | 1347 | 20230221 | 1918 | 1990927 | 331 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 180 | 11916 | 37.5304 | -122.0428 | Yes | Strong Winds; | Fuse | Burned Open | 23-0031751 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1815353 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | RECLOSER | MR117 | 20230221 | 1349 | 20230221 | 1820 | 1991117 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 45799 | 37.4956 | -121.9484 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0031256 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1814921 | 0 | Non-EPSS | N | 2023 | B-C TGTS
MISSION | MISSION | GRANT-1104 | 14381104 | RECLOSER | 379664 | 20230221 | 1403 | 20230221 | 2124 | 1991240 | 441 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 748 | 329868 | 37.6802 | -122.1263 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0031757 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1815359 | 0 | Non-EPSS | N | 2023 | B & C PHASE
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | FUSE | 8710 | 20230221 | 1407 | 20230222 | 204 | 1991270 | 717 | Distribution Circuit | Equipment Failure/Involved | Overhead | 468 | 335556 | 37.4803 | -121.924 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031560 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1815184 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | RECLOSER | MR339 | 20230221 | 1424 | 20230222 | 1911 | 1991480 | 1727 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 105347 | 37.5421 | -121.9223 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031212 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1814893 | 0 | EPSS Ckt | N | 2023 | B PHASE GRD
MISSION | MISSION | BANCROFT-0401 | 13030401 | TRANSFORMER | 315192845167 | 20230221 | 1457 | 20230222 | 1032 | 1992105 | 1175 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 11750 | 37.7288 | -122.1633 | Yes | Strong Winds; | Transformer (OH) | Failed/Faulted | 23-0031965 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1815562 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315629938579 | 20230221 | 1500 | 20230222 | 1915 | 1992074 | 1695 | Transformer only | Vegetation | Tree - grew into line | 9 | 15255 | 37.5498 | -122.0085 | Yes | Strong Winds;32-90 F | Transformer | Bent or Twisted | 23-0031934 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1815533 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1105 | 13761105 | FUSE | 14492 | 20230221 | 1639 | 20230221 | 2318 | 1991421 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 8379 | 37.6454 | -122.1008 | Yes | Strong Winds; | Secondary | Burned/flashed | 23-0031500 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1815130 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | RECLOSER | 306824 | 20230221 | 1642 | 20230221 | 1831 | 1993183 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2061 | 221605 | 37.5782 | -121.9845 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0031513 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1815141 | 0 | EPSS Ckt | N | 2023 | N/A
MISSION | MISSION | GRANT-1103 | 14381103 | OCB | 1103/2 | 20230221 | 2023 | 20230222 | 1315 | 1995869 | 1012 | Distribution Circuit | Equipment Failure/Involved | Overhead | 415 | 27475 | 37.6718 | -122.1596 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031849 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1815447 | 0 | Non-EPSS | N | 2023 | C PHASE GRD T
MISSION | MISSION | MT EDEN-1112 | 13761112 | FUSE | 10903 | 20230222 | 821 | 20230222 | 1026 | 1996805 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 750 | 37.651 | -122.0666 | No | Strong Winds; | Conductor- Overhead | Together | 23-0032183 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1815759 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315711037839 | 20230222 | 1706 | 20230223 | 300 | 1998307 | 594 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4158 | 37.5297 | -121.9801 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 23-0032674 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1816062 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | TRANSFORMER | 315884935873 | 20230222 | 1842 | 20230222 | 2221 | 1990796 | 219 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1752 | 37.4767 | -121.9194 | No | Strong Winds; | Transformer (OH) | Leaking | 23-0032686 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1816072 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 51054 | 20230223 | 1135 | 20230223 | 1145 | 1999377 | 10 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 97 | 970 | 37.7201 | -121.7249 | Yes | Clear;32-90F |  |  | 23-0033109 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1816289 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1107 | 14351107 | FUSE | 56157 | 20230223 | 1154 | 20230223 | 1652 | 1999406 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 47382 | 37.5418 | -121.9953 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0033112 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1816291 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | TRANSFORMER | 315356343808 | 20230223 | 1637 | 20230223 | 1816 | 2000006 | 99 | Transformer only | Company Initiated | Improper Construction | 2 | 198 | 37.6921 | -122.106 | Yes | Clear;32-90 F | Transformer | Malfunctioning | 23-0033361 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1816414 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 315864644738 | 20230223 | 2059 | 20230224 | 55 | 2000473 | 236 | Transformer only | Vegetation | Tree - grew into line | 12 | 2832 | 37.72 | -121.9309 | Yes | Clear;32-90 F | Transformer | Normal | 23-0033442 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1816474 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 12204 | 20230223 | 2208 | 20230223 | 2308 | 2000764 | 60 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 4200 | 37.7009 | -122.0615 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033482 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1816514 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1102 | 14471102 | FUSE | 10518 | 20230223 | 2356 | 20230224 | 1430 | 2000667 | 874 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 17312 | 37.5646 | -122.0355 | Yes | Overcast-Rain;32-90 F | Secondary | Broken | 23-0033506 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1816538 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | TASSAJARA 2113 | 14662113 | FUSE | 14246 | 20230224 | 609 | 20230224 | 902 | 2004233 | 173 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 1557 | 37.7535 | -122.0075 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033839 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1816850 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 6878 | 20230224 | 632 | 20230224 | 1645 | 2003468 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 11034 | 37.8133 | -122.0446 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034027 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1816988 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 73969 | 20230224 | 1524 | 20230225 | 1540 | 2008151 | 1456 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2912 | 37.5778 | -121.586 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035120 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1817983 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | TRANSFORMER | T21543 | 20230225 | 3 | 20230225 | 334 | 2007543 | 211 | Transformer only | Equipment Failure/Involved | Underground | 4 | 844 | 37.6524 | -121.8699 | Yes | Clear;32-90F | Service conductor | Contaminated | 23-0035028 | UG | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1817894 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | JUMPER | 8888 | 20230225 | 1433 | 20230225 | 1726 | 2008560 | 173 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 2 | 332 | 37.5137 | -122.0495 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035309 | OH | Sus | 0 | BAY AREA | FEB | Open Circuit | 0 | No | Yes | No | 1818156 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | SWITCH | 62632 | 20230225 | 2054 | 20230226 | 638 | 2009431 | 584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1982 | 413825 | 37.5668 | -122.0244 | Yes | Partly Cloudy;32-90 F | Jumper | Arcing | 23-0035509 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1818357 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | FUSE | 59465 | 20230226 | 130 | 20230226 | 638 | 2009549 | 308 | Distribution Circuit | 3rd Party | Vehicle | 19 | 5852 | 37.6817 | -122.0675 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0035577 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1818429 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1104 | 14471104 | TRANSFORMER | 315579537990 | 20230226 | 1156 | 20230226 | 1844 | 2009988 | 408 | Transformer only | Environmental/External | Water | 20 | 8160 | 37.5332 | -122.0256 | Yes | Overcast-Drizzle;32-90 F | Transformer | Broken- wire on ground | 23-0035703 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1818543 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315452944416 | 20230226 | 2209 | 20230226 | 2246 | 2010990 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 444 | 37.7093 | -122.0729 | Yes | Clear;32-90F | Fuse | Broken | 23-0036046 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1818851 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2105 | 14502105 | TRANSFORMER | T1361 | 20230226 | 2240 | 20230226 | 2249 | 2010977 | 9 | Transformer only | Equipment Failure/Involved | Underground | 15 | 135 | 37.6723 | -121.8933 | Yes | Clear;32-90F | Secondary | Broken | 23-0036044 | UG | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1818849 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | OCB | 1102/2/NORM | 20230227 | 1506 | 20230227 | 1655 | 2012815 | 109 | Distribution Circuit | Equipment Failure/Involved | Underground | 2275 | 132756 | 37.5014 | -121.9891 | Yes | Overcast-Rain;32-90 F | Conductor- Underground | Burned/flashed | 23-0036574 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1819157 | 0 | Non-EPSS | N | 2023 | GRD TIME
MISSION | MISSION | VINEYARD-2108 | 14502108 | TRANSFORMER | T1874 | 20230227 | 1559 | 20230227 | 1712 | 2012943 | 73 | Transformer only | Equipment Failure/Involved | Underground | 13 | 949 | 37.6741 | -121.9178 | Yes |  | Connector or Splice (UG) | Deteriorated | 23-0036677 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1819241 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | SWITCH | 4461 | 20230227 | 2127 | 20230228 | 330 | 2013864 | 346 | Distribution Circuit | Company Initiated | Return Circuit Normal | 87 | 4952 | 37.5177 | -121.9986 | Yes |  | Conductor- Underground | Normal | 23-0036692 | UG | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1819375 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315593939001 | 20230228 | 911 | 20230228 | 1756 | 2014613 | 525 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 8925 | 37.5612 | -122.0212 | Yes | Overcast-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 23-0037275 | OH | Sus | 0 | BAY AREA | FEB | None | 0 | No | No | No | 1819708 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 11673 | 20230228 | 1345 | 20230228 | 1621 | 2015761 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 8112 | 37.6206 | -122.0795 | Yes | Clear;32-90F | Transformer (OH) | Deteriorated | 23-0037514 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1819876 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 12704 | 20230228 | 1951 | 20230228 | 2234 | 2016616 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 489 | 37.727 | -122.0795 | Yes | Clear;32-90F |  |  | 23-0037839 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1820168 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | SWITCH | 655 | 20230301 | 29 | 20230301 | 806 | 2017255 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 14086 | 37.6869 | -122.1133 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0037869 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1820198 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 8310 | 20230301 | 1701 | 20230302 | 1418 | 2018670 | 1277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 29955 | 37.673 | -122.1492 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0038369 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1820557 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | RECLOSER | MR235 | 20230301 | 2255 | 20230302 | 1856 | 2019301 | 1201 | Distribution Circuit | 3rd Party | Vehicle | 158 | 40688 | 37.6704 | -122.0726 | No | Clear;32-90F | Pole-Wood | Broken | 23-0038547 | OH | Sus | 35429476 | BAY AREA | MAR | Multi-Fault | 0 | No | No | No | 1820729 | 0 | EPSS Ckt | N | 2023 | ABC GRD
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | SWITCH | 383476 | 20230302 | 13 | 20230302 | 31 | 2019311 | 18 | Distribution Circuit | Equipment Failure/Involved | Underground | 181 | 3258 | 37.5194 | -122.0559 | No | Clear;32-90F | Transformer (UG) | Broken | 23-0038543 | UG | Sus | 45686637 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1820733 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | SWITCH | 51523 | 20230302 | 1210 | 20230302 | 1506 | 2019792 | 176 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 6336 | 37.6726 | -122.0808 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0038877 | UG | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1820908 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | SWITCH | 383476 | 20230302 | 1254 | 20230302 | 1301 | 2019603 | 7 | Distribution Circuit | Equipment Failure/Involved | Underground | 181 | 1267 | 37.5194 | -122.0559 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0038543 | UG | Sus | 45686637 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1820831 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | SWITCH | 51523 | 20230303 | 606 | 20230303 | 1010 | 2020705 | 244 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 8784 | 37.6726 | -122.0808 | No | Clear;32-90F | Secondary | Burned/flashed | 23-0039341 | UG | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1821231 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1106 | 14471106 | OCB | 1106/2 | 20230304 | 1141 | 20230304 | 1501 | 2022350 | 200 | Distribution Circuit | Equipment Failure/Involved | Underground | 5058 | 421671 | 37.5571 | -122.0584 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Deteriorated | 23-0039958 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1821713 | 0 | Non-EPSS | N | 2023 | PHASE OC
MISSION | MISSION | DIXON LANDING-2105 | 14722105 | FUSE | 60137 | 20230304 | 1814 | 20230305 | 7 | 2022809 | 353 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 17982 | 37.4662 | -121.9334 | No | Partly Cloudy;32-90 F |  |  | 23-0040169 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1821917 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1106 | 13761106 | OCB | 1106/2 | 20230304 | 2026 | 20230304 | 2148 | 2022942 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 5084 | 37.6319 | -122.1025 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040087 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | Yes | No | 1821834 | 0 | Non-EPSS | N | 2023 | B&C PHASE OC
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | INTERRUPTER | 702762 | 20230305 | 424 | 20230305 | 950 | 2023346 | 326 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 13366 | 37.4831 | -121.9257 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0040257 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1822004 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CAYETANO-2111 | 14422111 | FUSE | 71361 | 20230306 | 640 | 20230306 | 1150 | s1822392 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 620 | 37.7284 | -121.77 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0040781 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1822392 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | T1136 | 20230307 | 4 | 20230307 | 29 | 2025169 | 25 | Transformer only | Equipment Failure/Involved | Underground | 10 | 250 | 37.668 | -121.9015 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0041003 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1822538 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | OTHER | J71114 TWD T7488 | 20230307 | 1837 | 20230308 | 228 | 2025975 | 471 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 4239 | 37.584 | -121.693 | No | Clear;32-90F | Transformer (UG) | Broken | 23-0041188 | UG | Sus | 35430857 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1822712 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1101 | 13111101 | FUSE | 51089 | 20230308 | 713 | 20230308 | 1357 | 2026225 | 404 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1212 | 37.7094 | -122.1833 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0041532 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1822829 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON 2101 | 14232101 | TRANSFORMER | 28834 | 20230308 | 1526 | 20230309 | 157 | 2026853 | 631 | Distribution Circuit | Equipment Failure/Involved | Underground | 78 | 12878 | 37.7631 | -121.8915 | No |  | Transformer (UG) | Failed/Faulted | 23-0041827 | UG | Sus | 35431132 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1822970 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | JUMPER | BURNT OPEN VERTICAL JUMPER | 20230309 | 1743 | 20230309 | 1953 | 2028350 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4526 | 65279 | 37.5256 | -122.0391 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0042420 | OH | Sus | 0 | BAY AREA | MAR | Open Circuit | 0 | No | No | No | 1823256 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 9055 | 20230309 | 1750 | 20230309 | 1834 | 2028381 | 44 | Distribution Circuit | Vegetation | Tree - bark fell into line | 387 | 17028 | 37.5807 | -121.9956 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042412 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1823250 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2101 | 14232101 | FUSE | 73532 | 20230309 | 2109 | 20230310 | 148 | 2029384 | 279 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 11340 | 37.7621 | -121.8924 | Yes | Overcast-Heavy Rain;32-90 F | Transformer (UG) | Burned/flashed | 23-0042596 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1823411 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DIXON LANDING-2105 | 14722105 | FUSE | 60137 | 20230310 | 206 | 20230310 | 1655 | 2029907 | 889 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 25519 | 37.4662 | -121.9334 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Underground | Burned/flashed | 23-0042710 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1823522 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | OCB | 2107/2 | 20230310 | 617 | 20230310 | 1300 | 2030185 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 511 | 72994 | 37.6697 | -121.8543 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042758 | OH | Sus | 45690269 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1823570 | 1 | EPSS Ckt | N | 2023 | PHASE G I & BU
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 12704 | 20230310 | 1103 | 20230310 | 1238 | 2030892 | 95 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 285 | 37.727 | -122.0795 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0043031 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1823704 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | SWITCH | 6300 | 20230310 | 1224 | 20230310 | 2116 | 2030948 | 532 | Distribution Circuit | 3rd Party | Vehicle | 61 | 32452 | 37.5237 | -122.03 | No | Clear;32-90F | Pole-Wood | Broken | 23-0043062 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1823717 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 51382 | 20230311 | 1726 | 20230311 | 1812 | 2032739 | 46 | Distribution Circuit | 3rd Party | Metallic Balloon | 269 | 12374 | 37.6919 | -122.1101 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0043544 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1824084 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | FUSE | 11459 | 20230312 | 329 | 20230312 | 1025 | 2033005 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 16640 | 37.7031 | -122.0886 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0043650 | OH | Sus | 31639778 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1824186 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DIXON LANDING-2106 | 14722106 | OCB | 2106/2 | 20230312 | 853 | 20230401 | 950 | 2033128 | 28857 | Distribution Circuit | Equipment Failure/Involved | Underground | 242 | 37051 | 37.457 | -121.9209 | No | Clear;32-90 F | Customer Equipment | Arcing | 23-0043653 | UG | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1824188 | 0 | Non-EPSS | N | 2023 | N/A
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | OCB | 2105/2 | 20230312 | 922 | 20230312 | 1901 | 2033154 | 579 | Distribution Circuit | Equipment Failure/Involved | Overhead | 746 | 122707 | 37.5029 | -121.9817 | No | Clear;32-90F | Switch (OH) | Failed/Faulted | 23-0043666 | OH | Sus | 35431062 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1824200 | 0 | Non-EPSS | N | 2023 | C PH
MISSION | MISSION | FREMONT-1110 | 14351110 | TRANSFORMER | 16038 | 20230312 | 1141 | 20230312 | 1259 | 2033230 | 78 | Transformer only | Equipment Failure/Involved | Underground | 17 | 1326 | 37.5181 | -121.9233 | No | Overcast-Drizzle;32-90 F | Transformer | Normal | 23-0043716 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1824232 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | OTHER | J71114 TWD T7488 | 20230312 | 1425 | 20230312 | 1445 | 2033367 | 20 | Distribution Circuit | 3rd Party | Customer Equipment | 13 | 204 | 37.584 | -121.693 | No | Overcast-Fog;32-90 F | Transformer (UG) | Normal | 23-0043738 | UG | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1824255 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1105 | 13111105 | FUSE | 180902 | 20230312 | 1735 | 20230312 | 1911 | 2033510 | 96 | Distribution Circuit | 3rd Party | Metallic Balloon | 68 | 6528 | 37.7042 | -122.1232 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0043780 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1824293 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | SWITCH | 298686 | 20230312 | 1913 | 20230312 | 2031 | -2033154 | 49 | Distribution Circuit | Company Initiated | Return Circuit Normal | 43 | 1261 | 37.5013 | -121.9403 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0043666 | OH | Sus | 35431062 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1824315 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1108 | 13501108 | OCB | 1108/2 | 20230312 | 2328 | 20230313 | 1136 | 2033803 | 728 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 728 | 37.5953 | -122.0175 | No | Overcast;32-90 F | Fuse | Arcing | 23-0043916 | OH | Sus | 45697838 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1824430 | 0 | EPSS Ckt | N | 2023 | N/A
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 10984 | 20230313 | 1225 | 20230314 | 231 | 2034381 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 21336 | 37.6842 | -122.0582 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044184 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1824553 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2104 | 14402104 | FUSE | 11437 | 20230314 | 1108 | 20230315 | 1034 | 2036393 | 1406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 28120 | 37.6874 | -121.7835 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Transformer (OH) | Burned/flashed | 23-0046183 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826066 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2106 | 14502106 | FUSE | 13127 | 20230314 | 1110 | 20230316 | 1322 | 2036664 | 3012 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12048 | 37.6611 | -121.8685 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045055 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1825125 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1110 | 14471110 | OCB | 1110/2 | 20230314 | 1127 | 20230315 | 1436 | 2037058 | 1629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2357 | 209214 | 37.5571 | -122.0582 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0044872 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1824978 | 0 | Non-EPSS | N | 2023 | B- C- GRD & TIME
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | FUSE | 10883 | 20230314 | 1129 | 20230314 | 1606 | 2036454 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 173 | 47921 | 37.5368 | -121.9971 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0045075 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825139 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | RECLOSER | MR118 | 20230314 | 1132 | 20230315 | 1723 | 2037193 | 1761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1920 | 636932 | 37.5298 | -121.9877 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044839 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1824949 | 0 | Non-EPSS | N | 2023 | A & GRD PHASE OC
MISSION | MISSION | FREMONT-1110 | 14351110 | TRANSFORMER | 315806937832 | 20230314 | 1137 | 20230315 | 838 | 2037508 | 1261 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 8827 | 37.53 | -121.9471 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0046135 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1826030 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 13363 | 20230314 | 1138 | 20230316 | 2340 | 2040958 | 3602 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18010 | 37.6592 | -121.7715 | Yes | Partly Cloudy-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0045221 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825252 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1107 | 14471107 | FUSE | 9107 | 20230314 | 1140 | 20230314 | 2002 | 2037353 | 502 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 187 | 94088 | 37.5549 | -122.0047 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0045838 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825760 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 11433 | 20230314 | 1141 | 20230315 | 1758 | 2037390 | 1817 | Distribution Circuit | Equipment Failure/Involved | Overhead | 335 | 359403 | 37.5617 | -121.9928 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045308 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1825315 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | RECLOSER | MR334 | 20230314 | 1148 | 20230316 | 1613 | 2037711 | 3145 | Distribution Circuit | Vegetation | Tree - fell into line | 1572 | 332856 | 37.6745 | -122.0316 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0044886 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1824990 | 0 | EPSS Ckt | N | 2023 | A & B PHASE GRD
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | FUSE | 51430 | 20230314 | 1149 | 20230314 | 1255 | 2037644 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 1429 | 37.6917 | -122.1085 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0045038 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825109 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1106 | 14471106 | JUMPER | 8247 A PH JUMPER | 20230314 | 1201 | 20230315 | 359 | 2037944 | 958 | Distribution Circuit | Equipment Failure/Involved | Overhead | 378 | 350829 | 37.5864 | -122.0722 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0046055 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825973 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | INTERRUPTER | 257022 | 20230314 | 1202 | 20230314 | 1505 | 2038018 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 21228 | 37.6865 | -122.1304 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0045389 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825375 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | OCB | 1111/2 | 20230314 | 1203 | 20230317 | 1633 | 2038132 | 4590 | Distribution Circuit | Vegetation | Tree - fell into line | 6133 | 874193 | 37.5953 | -122.0174 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0044967 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1825050 | 0 | EPSS Ckt | N | 2023 | B & GRD
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 62538 | 20230314 | 1203 | 20230316 | 2129 | 2042258 | 3446 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 486336 | 37.5656 | -121.9613 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0044967 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1825335 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 166727 | 20230314 | 1203 | 20230315 | 1911 | 2044997 | 1868 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 34130 | 37.5795 | -122.0002 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0046016 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825936 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1105 | 13501105 | TRANSFORMER | 315692838882 | 20230314 | 1218 | 20230316 | 1253 | 2044866 | 2915 | Transformer only | Vegetation | Tree - fell into line | 7 | 20405 | 37.5584 | -121.987 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Normal | 23-0046208 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826087 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1112 | 14351112 | FUSE | 8475 | 20230314 | 1219 | 20230317 | 42 | 2038448 | 3623 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18115 | 37.5684 | -121.9761 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045770 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1825698 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2110 | 14502110 | RECLOSER | 472595 | 20230314 | 1220 | 20230314 | 1739 | 2039188 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 9570 | 37.7051 | -121.8234 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045667 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825609 | 0 | EPSS Ckt | Y | 2023 | NA
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | OCB | 1102/2/NORM | 20230314 | 1222 | 20230314 | 1541 | 2038689 | 199 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2275 | 379198 | 37.5014 | -121.9891 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Arcing | 23-0045209 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825247 | 0 | Non-EPSS | N | 2023 | ABC
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315573940779 | 20230314 | 1225 | 20230314 | 1951 | 2038674 | 446 | Transformer only | Unknown Cause | Patrol - found nothing | 14 | 6244 | 37.61 | -122.0292 | Yes | Strong Winds-Rain-Clear;32-90 F |  |  | 23-0045811 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1825734 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 8305 | 20230314 | 1233 | 20230314 | 1435 | 2038974 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 153 | 18666 | 37.7101 | -121.9379 | Yes | Rain-Strong Winds-Clear;32-90F |  |  | 23-0045375 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825361 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1112 | 14351112 | FUSE | 8405 | 20230314 | 1235 | 20230314 | 2035 | 2041268 | 480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 17357 | 37.5667 | -121.9749 | Yes | Strong Winds-Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0045848 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1825770 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315664538336 | 20230314 | 1236 | 20230315 | 948 | 2039062 | 1272 | Transformer only | Vegetation | Tree - grew into line | 13 | 16536 | 37.5432 | -121.9965 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Fuse | Normal | 23-0046177 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826060 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10859 | 20230314 | 1237 | 20230316 | 1812 | 2039079 | 3215 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 379370 | 37.5431 | -121.9337 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045719 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1825655 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | FUSE | 10728 | 20230314 | 1238 | 20230314 | 1358 | 2039118 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 7920 | 37.6971 | -122.0484 | Yes | Rain-Strong Winds-Clear;32-90F |  |  | 23-0045232 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825261 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | OCB | 2107/2 | 20230314 | 1238 | 20230315 | 1903 | 2039129 | 1825 | Distribution Circuit | Vegetation | Tree - fell into line | 3552 | 6111104 | 37.6697 | -121.8543 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0045184 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825230 | 0 | EPSS Ckt | N | 2023 | PHASE OC
MISSION | MISSION | LIVERMORE-1101 | 12141101 | TRANSFORMER | 316296042800 | 20230314 | 1239 | 20230315 | 1627 | 2037437 | 1668 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 33360 | 37.6683 | -121.781 | Yes | Partly Cloudy-Strong Winds;32-90 F | Crossarm- Wood | Broken | 23-0046524 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1826267 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | FUSE | 15403 | 20230314 | 1243 | 20230315 | 1215 | 2046068 | 1412 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 29652 | 37.5061 | -121.964 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0046290 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1826130 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1107 | 13761107 | FUSE | 15311 | 20230314 | 1244 | 20230314 | 1644 | 2039279 | 240 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 720 | 37.6116 | -122.0667 | Yes | Rain-Strong Winds-Clear;32-90F |  |  | 23-0045502 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825469 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 13152 | 20230314 | 1244 | 20230314 | 2020 | 2039281 | 456 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 201 | 91656 | 37.7016 | -121.9386 | Yes | Strong Winds-Rain-Clear;32-90 F |  |  | 23-0045841 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825763 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 12026 | 20230314 | 1245 | 20230314 | 2143 | s1825834 | 538 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6456 | 37.7314 | -121.9337 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0045909 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825834 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 8215 | 20230314 | 1246 | 20230314 | 1456 | 2039343 | 130 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 3640 | 37.7121 | -121.9387 | Yes | Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Normal | 23-0045400 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825384 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11230 | 20230314 | 1247 | 20230315 | 1805 | 2040239 | 1758 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 49224 | 37.6454 | -121.6472 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0046593 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1826313 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 11799 | 20230314 | 1249 | 20230314 | 1551 | 2039415 | 182 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 33124 | 37.6718 | -121.8805 | Yes | Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Normal | 23-0045488 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825459 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | 315744837267 | 20230314 | 1250 | 20230315 | 531 | 2045274 | 1001 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4004 | 37.5142 | -121.9681 | Yes | Clear;32-90 F | Transformer (OH) | Normal | 23-0046076 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825997 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2106 | 14232106 | TRANSFORMER | 315851244285 | 20230314 | 1257 | 20230314 | 2308 | 2039651 | 611 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 3055 | 37.7075 | -121.9353 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0045993 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1825917 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | TRANSFORMER | T7198 | 20230314 | 1300 | 20230315 | 1015 | 2036687 | 1275 | Transformer only | Equipment Failure/Involved | Underground | 18 | 22950 | 37.6925 | -121.77 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Burned Open | 23-0045141 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825192 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 10616 | 20230314 | 1305 | 20230316 | 1631 | 2039889 | 3086 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 191332 | 37.6826 | -121.9173 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0047126 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | Yes | No | 1826622 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2104 | 14502104 | OCB | 2104/2 | 20230314 | 1307 | 20230314 | 1752 | 2038249 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2321 | 645820 | 37.6697 | -121.8545 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | On Ground | 23-0045189 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825234 | 0 | Non-EPSS | N | 2023 | B- C & GRD
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 632697 | 20230314 | 1315 | 20230314 | 1945 | 2040210 | 387 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 13158 | 37.6669 | -122.1137 | Yes | Rain-Strong Winds-Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0045775 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1825702 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10847 | 20230314 | 1318 | 20230316 | 200 | 2040345 | 2202 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 245028 | 37.5379 | -121.9339 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0045644 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825587 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | RECLOSER | MR310 | 20230314 | 1323 | 20230314 | 1713 | 2040504 | 230 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3115 | 716450 | 37.6784 | -121.7702 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045203 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825242 | 0 | Non-EPSS | N | 2023 | B & C
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 10251 | 20230314 | 1323 | 20230315 | 1735 | 2040573 | 1692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 12396 | 37.6834 | -121.7779 | Yes | Overcast-Strong Winds;32-90 F | Jumper | Burned Open | 23-0045979 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825905 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10808 | 20230314 | 1328 | 20230315 | 1041 | 2040596 | 1273 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 20368 | 37.6608 | -121.6715 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0046111 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1826012 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 8919 | 20230314 | 1331 | 20230315 | 1111 | 2040657 | 1300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 27300 | 37.633 | -121.8 | Yes | Overcast-Strong Winds;32-90 F | Other | Broken | 23-0046194 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1826075 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1101 | 13751101 | FUSE | 71471 | 20230314 | 1337 | 20230314 | 1846 | 2040756 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 6489 | 37.7067 | -121.7421 | Yes | Rain-Strong Winds-Clear;32-90F | Transformer (OH) | Broken | 23-0045736 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825672 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10187 | 20230314 | 1339 | 20230317 | 1714 | 2041475 | 4535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 16167 | 37.5617 | -121.9486 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | On Ground | 23-0046415 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826205 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 12274 | 20230314 | 1339 | 20230315 | 1621 | 2040834 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 81702 | 37.5346 | -121.9409 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0045516 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1825480 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 9117 | 20230314 | 1342 | 20230314 | 1710 | 2040949 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 560 | 116480 | 37.5331 | -121.9214 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0045633 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825576 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 12776 | 20230314 | 1343 | 20230316 | 636 | 2041026 | 2453 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 39248 | 37.5939 | -121.8855 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045531 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | Yes | No | 1825493 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRIP-SAVER | 8971 | 20230314 | 1344 | 20230315 | 2315 | 2040940 | 2011 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 156858 | 37.7112 | -122.0551 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045635 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | Yes | Yes | No | 1825578 | 1 | EPSS Ckt | N | 2023 | NONE
MISSION | MISSION | CAYETANO-2109 | 14422109 | SWITCH | 630224 | 20230314 | 1349 | 20230315 | 1617 | 2044446 | 1588 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 84164 | 37.7886 | -121.77 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045803 | OH | Sus | 35431491 | BAY AREA | MAR | Line to Line | 0 | No | Yes | No | 1825725 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 13908 | 20230314 | 1349 | 20230317 | 1221 | 2044470 | 4232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 38088 | 37.8131 | -121.7954 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0045808 | OH | Sus | 0 | BAY AREA | MAR | Multi-Fault | 0 | No | Yes | No | 1825730 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LIVERMORE-1104 | 12141104 | FUSE | 9960 | 20230314 | 1349 | 20230314 | 2120 | 2041087 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 28864 | 37.6683 | -121.7916 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0045852 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825773 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | TRIP-SAVER | 8721 | 20230314 | 1351 | 20230314 | 1628 | 2041363 | 157 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 3768 | 37.5659 | -121.8832 | Yes | Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Normal | 23-0045545 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825502 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 8873 | 20230314 | 1357 | 20230315 | 1115 | 2041397 | 1278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 76 | 97128 | 37.6381 | -121.8943 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0046247 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1826107 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2104 | 14402104 | FUSE | 9698 | 20230314 | 1407 | 20230314 | 2041 | 2041766 | 394 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 29127 | 37.6814 | -121.7819 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0045889 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1825812 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | LIVERMORE-1103 | 12141103 | FUSE | 12784 | 20230314 | 1415 | 20230316 | 1600 | 2042079 | 2985 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 41790 | 37.6796 | -121.7453 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0046923 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826504 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | TRANSFORMER | 315641338026 | 20230314 | 1649 | 20230315 | 1515 | 2043519 | 1346 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 12114 | 37.5347 | -122.0043 | Yes | Overcast;32-90 F | Secondary | Broken- wire on ground | 23-0046436 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1826219 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 9461 | 20230314 | 2242 | 20230316 | 2018 | 2044909 | 2736 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 432288 | 37.7188 | -121.9358 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0045975 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1825901 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LIVERMORE-1104 | 12141104 | FUSE | 9960 | 20230315 | 611 | 20230315 | 1230 | 2045294 | 379 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 24256 | 37.6683 | -121.7916 | No | Partly Cloudy;32-90 F |  |  | 23-0046313 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1826140 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315600038715 | 20230315 | 920 | 20230315 | 2036 | 2046236 | 668 | Distribution Circuit | Equipment Failure/Involved | Overhead | 182 | 15320 | 37.5534 | -122.0189 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0046358 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826171 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | TRANSFORMER | T7635 | 20230315 | 1024 | 20230315 | 1150 | 2045843 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 20 | 1720 | 37.5863 | -122.0303 | No | Clear;32-90 F |  |  | 23-0046321 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1826149 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2104 | 14402104 | FUSE | 9698 | 20230315 | 1124 | 20230315 | 1332 | 2045977 | 128 | Distribution Circuit | Animal | Bird found | 74 | 9463 | 37.6814 | -121.7819 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0046366 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826176 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 632697 | 20230315 | 1126 | 20230315 | 1809 | 2045982 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 13702 | 37.6669 | -122.1137 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0046267 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826114 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 9875 | 20230315 | 1247 | 20230315 | 1842 | 2046174 | 355 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 31 | 11005 | 37.5369 | -121.9443 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0046332 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1826156 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | JUMPER | OPEN JUMPER @ 13152 | 20230315 | 1341 | 20230315 | 1534 | 2046287 | 113 | Distribution Circuit | Vegetation | Tree - branch fell on line | 202 | 22826 | 37.7016 | -121.9386 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0046380 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826186 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 13132 | 20230315 | 2112 | 20230315 | 2238 | 2047310 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 139 | 11954 | 37.6527 | -121.8795 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0046731 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826387 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | TRANSFORMER | 316011741610 | 20230315 | 2118 | 20230316 | 1638 | 2048845 | 1160 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4640 | 37.6347 | -121.8782 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0047174 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826650 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | TRANSFORMER | 316011342268 | 20230315 | 2145 | 20230315 | 2304 | 2047389 | 79 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 474 | 37.6527 | -121.879 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0046730 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1826386 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 316028942389 | 20230316 | 48 | 20230316 | 55 | 2047540 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 91 | 37.6561 | -121.873 | No | Clear;32-90 F | Secondary | Burned Open | 23-0046826 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1826450 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1103 | 14471103 | SWITCH | 921 | 20230316 | 343 | 20230316 | 353 | 2047599 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 210 | 37.586 | -122.0721 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0046055 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1826459 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10847 | 20230316 | 1326 | 20230316 | 2130 | 2048540 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 55176 | 37.5379 | -121.9339 | No | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Together | 23-0047228 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1826692 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1110 | 14351110 | TRANSFORMER | 315730038144 | 20230316 | 1948 | 20230316 | 2230 | 2049223 | 162 | Transformer only | Vegetation | Tree - grew into line | 6 | 972 | 37.5382 | -121.9738 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0047257 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1826720 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315573940779 | 20230317 | 102 | 20230317 | 248 | 2049409 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1484 | 37.61 | -122.0292 | No | Overcast-Drizzle-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047340 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826780 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | TRIP-SAVER | 8721 | 20230317 | 1036 | 20230317 | 1519 | 2049845 | 283 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 24 | 6792 | 37.5659 | -121.8832 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0047504 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1826857 | 0 | EPSS Ckt | N | 2023 | NA
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 8934 | 20230318 | 723 | 20230318 | 925 | 2050901 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 854 | 37.7604 | -122.0276 | No | Clear;32-90 F |  |  | 23-0048264 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1827488 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | TASSAJARA-2113 | 14662113 | TRANSFORMER | 315681846201 | 20230318 | 933 | 20230318 | 1726 | 2050993 | 473 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 473 | 37.7594 | -121.9944 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0048351 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1827554 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 9865 | 20230318 | 1546 | 20230318 | 1650 | 2051347 | 64 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 2476 | 37.548 | -121.9412 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0048349 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1827553 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | OCB | 1108/2 | 20230318 | 1945 | 20230318 | 2100 | 2051514 | 75 | Distribution Circuit | Animal | Bird found | 5876 | 229318 | 37.6319 | -122.1025 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048356 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1827560 | 1 | Non-EPSS | N | 2023 | BU RLY CO TARGET
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 12735 | 20230319 | 1934 | 20230321 | 235 | 2052332 | 1861 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 16749 | 37.5323 | -122.071 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048558 | OH | Sus | 31640125 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1827766 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1107 | 13761107 | SWITCH | 6936 | 20230320 | 1042 | 20230320 | 1050 | 2052922 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 75 | 600 | 37.6253 | -122.0906 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0048356 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1827895 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1105 | 14381105 | TRANSFORMER | 315218443668 | 20230320 | 1242 | 20230320 | 1636 | 2053039 | 234 | Transformer only | Vegetation | Other ground vegetation | 8 | 1872 | 37.6876 | -122.1535 | No | Partly Cloudy;32-90 F | Transformer | Normal | 23-0048920 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1827929 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1101 | 13751101 | TRANSFORMER | 18099 | 20230320 | 1536 | 20230321 | 321 | 2052829 | 705 | Distribution Circuit | Equipment Failure/Involved | Underground | 142 | 12975 | 37.7138 | -121.7495 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0049020 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1827978 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1103 | 13751103 | SWITCH | 8039 | 20230321 | 1003 | 20230321 | 1655 | 2053912 | 412 | Distribution Circuit | 3rd Party | Vehicle | 17 | 6628 | 37.7121 | -121.7153 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0049090 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1828093 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1110 | 14351110 | RECLOSER | MR131 | 20230321 | 1331 | 20230321 | 1941 | 2055489 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1371 | 330300 | 37.5366 | -121.9667 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049533 | OH | Sus | 0 | BAY AREA | MAR | Three Phase Fault | 0 | No | Yes | No | 1828293 | 0 | Non-EPSS | N | 2023 | A/B/C & GRD
MISSION | MISSION | DUMBARTON-1102 | 14471102 | OCB | 1102/2 | 20230321 | 1347 | 20230322 | 1815 | 2055903 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 4906 | 1043431 | 37.5571 | -122.0585 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049575 | OH | Sus | 35432924 | BAY AREA | MAR | Line to Line | 0 | No | Yes | No | 1828323 | 0 | Non-EPSS | N | 2023 | UNK
MISSION | MISSION | JARVIS-1105 | 13501105 | RECLOSER | MR474 | 20230321 | 1347 | 20230321 | 2216 | 2055994 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 1563 | 458718 | 37.5618 | -121.9971 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049573 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1828321 | 0 | Non-EPSS | N | 2023 | A B C & GRD
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 10802 | 20230321 | 1350 | 20230322 | 1110 | 2056033 | 1280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 23040 | 37.6427 | -122.0557 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050320 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828983 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | FUSE | 607 | 20230321 | 1352 | 20230321 | 2157 | 2055999 | 485 | Distribution Circuit | Vegetation | Tree - branch fell on line | 626 | 303610 | 37.6773 | -122.0674 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0050003 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828688 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRIP-SAVER | 11986 | 20230321 | 1352 | 20230322 | 1125 | 2056005 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 654 | 398220 | 37.6607 | -122.1097 | Yes | Strong Winds-Rain; | Conductor- Overhead | Broken- wire on ground | 23-0049665 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1828395 | 1 | Non-EPSS | N | 2023 | N/A
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 9036 | 20230321 | 1353 | 20230321 | 1506 | 2056018 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 243 | 17724 | 37.6986 | -122.1302 | Yes | Strong Winds-Rain; |  |  | 23-0049629 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828367 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315400841755 | 20230321 | 1356 | 20230322 | 1417 | 2060289 | 1461 | Transformer only | Vegetation | Tree - fell into line | 15 | 21915 | 37.636 | -122.0894 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken | 23-0050081 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1828756 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | BANCROFT-0402 | 13030402 | FUSE | 10403 | 20230321 | 1357 | 20230321 | 1552 | 2056079 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 160 | 18400 | 37.7345 | -122.1457 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 23-0049757 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828469 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1107 | 13761107 | FUSE | 15311 | 20230321 | 1357 | 20230321 | 1528 | 2056083 | 91 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 273 | 37.6116 | -122.0667 | Yes | Strong Winds-Rain; | Conductor- Overhead | Normal | 23-0049705 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828427 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | FUSE | 51430 | 20230321 | 1357 | 20230321 | 1835 | 2056077 | 278 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 18070 | 37.6917 | -122.1085 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0049902 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828593 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | STATION O-0401 | 12240401 | OCB | 401/2 | 20230321 | 1401 | 20230322 | 1728 | 2056190 | 1647 | Distribution Circuit | Vegetation | Tree - fell into line | 661 | 276035 | 37.6862 | -122.1025 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050109 | OH | Sus | 0 | BAY AREA | MAR | Multi-Fault | 0 | No | Yes | No | 1828778 | 0 | Non-EPSS | N | 2023 | A PHASE OC
MISSION | MISSION | MT EDEN-1102 | 13761102 | OCB | 1102/2 | 20230321 | 1523 | 20230321 | 1552 | 2056004 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1463 | 42427 | 37.6319 | -122.1024 | Yes | Strong Winds-Rain; | Conductor- Overhead | Normal | 23-0049738 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828454 | 0 | Non-EPSS | N | 2023 | PHASE TIME
MISSION | MISSION | MT EDEN-1107 | 13761107 | FUSE | 15311 | 20230321 | 1531 | 20230321 | 1700 | 2057309 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 267 | 37.6116 | -122.0667 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049771 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828480 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | FUSE | 10718 | 20230321 | 1545 | 20230321 | 1904 | 2057407 | 199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 6368 | 37.6612 | -122.0885 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0050049 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828729 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | RECLOSER | 635054 | 20230321 | 1603 | 20230321 | 1751 | 2056591 | 108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1848 | 199584 | 37.6685 | -122.0849 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049824 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1828527 | 0 | Non-EPSS | N | 2023 | A PHASE GRD
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | FUSE | 8058 | 20230321 | 1614 | 20230321 | 1744 | 2057943 | 90 | Distribution Circuit | Vegetation | Tree - bark fell into line | 132 | 11880 | 37.7015 | -122.0932 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049904 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828595 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1112 | 13761112 | FUSE | 48780 | 20230321 | 1656 | 20230322 | 1532 | 2058829 | 1356 | Distribution Circuit | Vegetation | Tree - branch fell on line | 186 | 51472 | 37.6581 | -122.0714 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0050123 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828791 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | SECTIONALIZER | 6250 | 20230321 | 1800 | 20230321 | 2211 | 2059810 | 251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 623 | 156373 | 37.6695 | -122.0887 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0050182 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1828843 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | INTERRUPTER | 257022 | 20230321 | 1921 | 20230321 | 2052 | 2060349 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 10556 | 37.6865 | -122.1304 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050146 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1828809 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 11673 | 20230321 | 2019 | 20230322 | 1739 | 2058734 | 1280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 18604 | 37.6206 | -122.0795 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken | 23-0050156 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1828818 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1109 | 13761109 | TRANSFORMER | 315388741691 | 20230321 | 2122 | 20230321 | 2150 | 2056488 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 504 | 37.6342 | -122.0935 | Yes | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 23-0050175 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1828837 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | FUSE | 51205 | 20230321 | 2144 | 20230322 | 2158 | 2061107 | 1454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 46010 | 37.7075 | -122.1273 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050499 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1829083 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315726237920 | 20230322 | 1907 | 20230322 | 2140 | 2063681 | 153 | Transformer only | Vegetation | Tree - bark fell into line | 6 | 918 | 37.532 | -121.975 | No | Overcast;32-90 F | Secondary | Normal | 23-0050992 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1829379 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315550439077 | 20230322 | 1954 | 20230322 | 2018 | 2063682 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 168 | 37.5631 | -122.0363 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0051018 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1829399 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1105 | 13761105 | FUSE | 11934 | 20230322 | 2140 | 20230322 | 2210 | 2063905 | 30 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 630 | 37.6456 | -122.0998 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0051113 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1829494 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | OCB | 2111/2 | 20230323 | 641 | 20230323 | 1641 | 2064057 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2040 | 256503 | 37.7448 | -121.9369 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0051152 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | Yes | No | 1829521 | 0 | Non-EPSS | N | 2023 | A/C PHASE TIME
MISSION | MISSION | MT EDEN-1105 | 13761105 | FUSE | 11934 | 20230323 | 1103 | 20230323 | 1221 | 2064532 | 78 | Distribution Circuit | Vegetation | Tree - grew into line | 21 | 1638 | 37.6456 | -122.0998 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0051323 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1829606 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 62482 | 20230323 | 1142 | 20230323 | 1428 | 2064595 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 166 | 37.7485 | -122.0219 | No | Partly Cloudy;32-90 F |  |  | 23-0051467 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1829684 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315423441765 | 20230323 | 1355 | 20230323 | 1422 | 2064769 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 270 | 37.6365 | -122.0816 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0051456 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1829680 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 315878644632 | 20230323 | 1527 | 20230323 | 2325 | 2065478 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 9864 | 37.7171 | -121.926 | No | Overcast;32-90 F | Secondary | Broken- wire on ground | 23-0051653 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1829805 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315423441765 | 20230323 | 1532 | 20230323 | 1735 | 2064986 | 123 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1230 | 37.6365 | -122.0816 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0051515 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1829710 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | FUSE | 532667 | 20230323 | 1600 | 20230323 | 1651 | 2064935 | 51 | Distribution Circuit | Vegetation | Tree - grew into line | 74 | 3774 | 37.7182 | -122.1732 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0051530 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1829721 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LIVERMORE-1104 | 12141104 | TRANSFORMER | T1207 | 20230324 | 1453 | 20230324 | 1551 | 2066256 | 58 | Transformer only | Equipment Failure/Involved | Underground | 18 | 1044 | 37.6688 | -121.8006 | No | Clear;32-90 F | Secondary | Broken | 23-0051959 | UG | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1829944 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1107 | 14351107 | FUSE | 11209 | 20230324 | 1837 | 20230325 | 312 | 2066543 | 515 | Distribution Circuit | Vegetation | Tree - bark fell into line | 124 | 63860 | 37.5221 | -121.9738 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052040 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1830001 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 9707 | 20230325 | 1759 | 20230326 | 329 | 2067210 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 613 | 94247 | 37.6409 | -122.0808 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052540 | OH | Sus | 35434000 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1830489 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315551739022 | 20230325 | 2002 | 20230326 | 1311 | 2067239 | 1029 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 10290 | 37.5615 | -122.0358 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0052560 | OH | Sus | 45708772 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1830504 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 36046 | 20230326 | 349 | 20230327 | 132 | 2067460 | 1303 | Distribution Circuit | Equipment Failure/Involved | Underground | 207 | 127412 | 37.6895 | -121.8838 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0052640 | UG | Sus | 45709063 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1830583 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1110 | 14471110 | FUSE | 12517 | 20230326 | 858 | 20230326 | 2017 | 2067541 | 679 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1358 | 37.5555 | -122.0679 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on object | 23-0052647 | OH | Sus | 45709122 | BAY AREA | MAR | Line to Line | 0 | No | Yes | No | 1830589 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 9911 | 20230326 | 1343 | 20230326 | 1435 | 2067728 | 52 | Distribution Circuit | 3rd Party | Other | 34 | 1749 | 37.6586 | -121.8893 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052679 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1830620 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 8267 | 20230328 | 651 | 20230328 | 927 | 2069528 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 175 | 27300 | 37.6683 | -122.1395 | No | Overcast;32-90 F |  |  | 23-0053304 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1831024 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 13069 | 20230328 | 946 | 20230328 | 1133 | 2070065 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 428 | 37.5569 | -121.8959 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0053468 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1831124 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | INTERRUPTER | 257022 | 20230328 | 1005 | 20230328 | 1205 | 2070100 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 13920 | 37.6865 | -122.1304 | No | Overcast-Strong Winds;32-90 F |  |  | 23-0053524 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831159 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | RECLOSER | 379664 | 20230328 | 1027 | 20230328 | 1126 | 2070178 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 748 | 44132 | 37.6802 | -122.1263 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0053478 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831131 | 0 | Non-EPSS | N | 2023 | A PHASE GRD
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | RECLOSER | 837904 | 20230328 | 1140 | 20230328 | 1333 | 2070399 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 207 | 23391 | 37.6674 | -122.055 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053497 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1831146 | 0 | EPSS Ckt | N | 2023 | A PH- B PH- SENSITIVE GRD
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 71291 | 20230328 | 1202 | 20230328 | 1425 | 2070492 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 381 | 37.6316 | -121.7866 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0053691 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831259 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315393941529 | 20230328 | 1247 | 20230328 | 1722 | 2070588 | 275 | Transformer only | Environmental/External | Water | 15 | 4125 | 37.6299 | -122.0919 | No | Rain-Overcast;32-90 F | Crossarm- Wood | Broken | 23-0053582 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1831194 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 315872644726 | 20230328 | 1250 | 20230328 | 1607 | 2070401 | 197 | Transformer only | Vegetation | Tree - branch fell on line | 16 | 3152 | 37.7197 | -121.928 | No | Rain-Overcast;32-90 F | Secondary | Broken | 23-0053601 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831207 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | TRANSFORMER | 315443243858 | 20230328 | 1600 | 20230328 | 2112 | 2071002 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 22010 | 37.6939 | -122.076 | No | Overcast-Rain;32-90 F | Jumper | Burned Open | 23-0053791 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831305 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 36926 | 20230328 | 1841 | 20230328 | 2200 | 2071461 | 199 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 199 | 37.6627 | -122.1351 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053877 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | Yes | No | 1831361 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 36046 | 20230328 | 1937 | 20230329 | 110 | 2071930 | 333 | Distribution Circuit | Equipment Failure/Involved | Underground | 207 | 24276 | 37.6895 | -121.8838 | No | Partly Cloudy;32-90 F | Elbow | Burned/flashed | 23-0053918 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831399 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 20876 | 20230328 | 2202 | 20230328 | 2246 | 2072129 | 44 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 440 | 37.6696 | -121.9014 | No | Partly Cloudy;32-90 F |  |  | 23-0053974 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1831451 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 20876 | 20230329 | 447 | 20230329 | 1233 | 2072271 | 466 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 6360 | 37.6696 | -121.9014 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 23-0054005 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831474 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | OCB | 1111/2 | 20230329 | 655 | 20230329 | 1430 | 2072344 | 455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6321 | 433451 | 37.5953 | -122.0174 | No | Overcast-Drizzle;32-90 F | Other | Deteriorated | 23-0054018 | OH | Sus | 35434245 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831477 | 0 | EPSS Ckt | N | 2023 | B/U RLY OC TRGT
MISSION | MISSION | DIXON LANDING-2107 | 14722107 | SWITCH | 41264 | 20230329 | 1323 | 20230329 | 1406 | 2073136 | 43 | Distribution Circuit | Company Initiated | Other Circuits | 1 | 43 | 37.4767 | -121.932 | No | Overcast;32-90 F | Metering Equipment |  | 23-0054398 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1831643 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | TRANSFORMER | 315378843822 | 20230329 | 1937 | 20230330 | 216 | 2073670 | 399 | Transformer only | Vegetation | Tree - grew into line | 13 | 5187 | 37.6926 | -122.0983 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 23-0054649 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831749 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | TRANSFORMER | 315376743842 | 20230329 | 1942 | 20230329 | 2357 | 2073669 | 255 | Transformer only | Vegetation | Tree - grew into line | 12 | 3060 | 37.6932 | -122.099 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 23-0054650 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831750 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316507241228 | 20230330 | 916 | 20230330 | 2200 | 2073854 | 764 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1528 | 37.626 | -121.7077 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 23-0054843 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1831883 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1108 | 14381108 | RECLOSER | MR354 | 20230330 | 1025 | 20230330 | 2130 | 2074227 | 665 | Distribution Circuit | 3rd Party | Vehicle | 1547 | 93015 | 37.6726 | -122.1055 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 23-0054909 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | Yes | 1831928 | 0 | Non-EPSS | N | 2023 | NONE
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315401643310 | 20230330 | 1327 | 20230330 | 2114 | 2074496 | 467 | Transformer only | Unknown Cause | Patrol - found nothing | 23 | 10741 | 37.6786 | -122.0901 | No | Partly Cloudy;32-90 F |  |  | 23-0055075 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1831981 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 11246 | 20230330 | 1546 | 20230330 | 1610 | 2074479 | 24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 24 | 37.5101 | -122.0142 | No | Clear;32-90 F |  |  | 23-0055161 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1832003 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | TRANSFORMER | 315890835805 | 20230330 | 1815 | 20230331 | 356 | 2074736 | 581 | Transformer only | Vegetation | Tree - grew into line | 17 | 9877 | 37.4749 | -121.9172 | No | Clear;32-90 F | Transformer | Contaminated | 23-0055223 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1832025 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316643242157 | 20230330 | 2046 | 20230331 | 345 | 2074828 | 419 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1257 | 37.652 | -121.6606 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Broken | 23-0055264 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1832056 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON 2102 | 14232102 | INTERRUPTER | 47302 | 20230331 | 1710 | 20230331 | 1813 | 2075704 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 4662 | 37.7551 | -121.9204 | No | Clear;32-90 F |  |  | 23-0055670 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1832267 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1109 | 14471109 | RECLOSER | MR241 | 20230331 | 1721 | 20230401 | 1811 | 2075713 | 1490 | Distribution Circuit | 3rd Party | Metallic Balloon | 1613 | 175032 | 37.5951 | -122.0793 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0055669 | OH | Sus | 31641115 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1832266 | 0 | Non-EPSS | N | 2023 | A PHASE GRD
MISSION | MISSION | JARVIS-1109 | 13501109 | FUSE | 60034 | 20230331 | 2228 | 20230401 | 1051 | 2076360 | 743 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 86 | 33882 | 37.5919 | -122.038 | No | Clear;32-90 F |  |  | 23-0055788 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1832389 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2102 | 14232102 | TRANSFORMER | T473499 | 20230401 | 4 | 20230401 | 2040 | 2076395 | 1236 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 16849 | 37.7544 | -121.9194 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0055841 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1832451 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1103 | 13751103 | FUSE | 12265 | 20230401 | 643 | 20230401 | 850 | 2076466 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2540 | 37.6941 | -121.6757 | No | Clear;32-90 F |  |  | 23-0055822 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1832415 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2106 | 14502106 | FUSE | 73041 | 20230401 | 908 | 20230401 | 1130 | 2076674 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 142 | 37.6635 | -121.8821 | No | Clear;32-90 F |  |  | 23-0055845 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1832457 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | OCB | 1107/2 | 20230402 | 244 | 20230402 | 2328 | 2077112 | 1244 | Distribution Circuit | 3rd Party | Vehicle | 6424 | 143609 | 37.7107 | -122.1488 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0055991 | OH | Sus | 35435901 | BAY AREA | APR | Force Out | 0 | No | No | No | 1832584 | 0 | Non-EPSS | N | 2023 | N/A
MISSION | MISSION | JARVIS-1106 | 13501106 | FUSE | 7358 | 20230402 | 1107 | 20230402 | 1147 | 2077308 | 40 | Distribution Circuit | Animal | Squirrel | 7 | 280 | 37.5993 | -122.0392 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0056032 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1832625 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 9374 | 20230402 | 1827 | 20230403 | 1857 | 2077572 | 1470 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 105238 | 37.679 | -122.0497 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0056056 | OH | Sus | 45713930 | BAY AREA | APR | Force Out | 0 | No | Yes | No | 1832648 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | T11281 | 20230403 | 856 | 20230403 | 1100 | 2078012 | 124 | Transformer only | Equipment Failure/Involved | Underground | 3 | 372 | 37.6678 | -121.8591 | No | Clear;32-90 F | Service conductor | Broken | 23-0056202 | UG | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1832766 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | 315605539716 | 20230403 | 1708 | 20230403 | 2131 | 2079025 | 263 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2104 | 37.581 | -122.0178 | No | Partly Cloudy-Strong Winds;32-90 F | Jumper | Broken | 23-0056591 | OH | Sus | 45715083 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1832988 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 71428 | 20230404 | 625 | 20230404 | 721 | 2079532 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 147 | 8224 | 37.72 | -121.7244 | No | Clear;32-90 F |  |  | 23-0056741 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1833087 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | TRANSFORMER | 315304143598 | 20230404 | 1154 | 20230404 | 1252 | 2079944 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 812 | 37.6861 | -122.1238 | No | Clear;32-90 F | Fuse | Broken | 23-0057033 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1833241 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10633 | 20230405 | 1234 | 20230405 | 1727 | 2080841 | 293 | Distribution Circuit | 3rd Party | Other | 1 | 293 | 37.5786 | -121.5877 | No | Clear;32-90 F | Fuse | Normal | 23-0057687 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1833559 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | SWITCH | 664480 | 20230405 | 2047 | 20230406 | 118 | 2081200 | 271 | Distribution Circuit | Company Initiated | Improper Construction | 6 | 1626 | 37.7808 | -121.9898 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0046079 | UG | Sus | 35309003 | BAY AREA | APR | Force Out | 0 | No | No | No | 1833573 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | BANCROFT-0401 | 13030401 | SWITCH | 9307 | 20230407 | 548 | 20230407 | 800 | 2082395 | 132 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 342 | 45144 | 37.7391 | -122.1547 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 23-0058324 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1833990 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | FUSE | 10150 | 20230407 | 1116 | 20230407 | 1512 | 2082607 | 236 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 18880 | 37.7166 | -122.0452 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0058550 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1834094 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2119 | 14232119 | TRANSFORMER | 11242 | 20230407 | 1529 | 20230409 | 140 | 2082928 | 2051 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 2051 | 37.6961 | -121.9031 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0058698 | UG | Sus | 35436855 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1834136 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON 2119 | 14232119 | FUSE | 5104 | 20230407 | 1531 | 20230407 | 1727 | 2082783 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 193 | 37.6962 | -121.9033 | No | Overcast;32-90 F |  |  | 23-0058660 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1834114 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1112 | 14351112 | OCB | 1112/2 | 20230408 | 1124 | 20230409 | 521 | 2083187 | 1077 | Distribution Circuit | 3rd Party | Vehicle | 4488 | 482568 | 37.5418 | -121.9619 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0058769 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | Yes | No | 1834227 | 0 | Non-EPSS | N | 2023 | A-B-C- GRD TIME OC -BK RMAIT
MISSION | MISSION | VINEYARD-2110 | 14502110 | OTHER | J73695 TWD 73697 | 20230408 | 1158 | 20230408 | 1700 | 2083222 | 302 | Distribution Circuit | Equipment Failure/Involved | Underground | 144 | 43488 | 37.7073 | -121.8666 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 23-0058737 | UG | Sus | 35436837 | BAY AREA | APR | Force Out | 0 | No | No | No | 1834234 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 40585 | 20230408 | 1835 | 20230408 | 2250 | 2083393 | 255 | Distribution Circuit | Equipment Failure/Involved | Underground | 88 | 22175 | 37.7742 | -121.9799 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0058816 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1834268 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | SWITCH | 40343SW | 20230410 | 942 | 20230410 | 1128 | 2084306 | 106 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 1802 | 37.701 | -121.7194 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0059068 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1834529 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 12460 | 20230411 | 1106 | 20230411 | 1454 | 2085525 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1824 | 37.5276 | -121.8775 | No | Clear;32-90 F |  |  | 23-0059856 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1835019 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DIXON LANDING-2107 | 14722107 | SWITCH | 41264 | 20230411 | 1204 | 20230411 | 1210 | 2085621 | 6 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 6 | 37.4767 | -121.932 | No | Partly Cloudy;32-90 F | Customer Equipment | Malfunctioning | 23-0059447 | UG | Sus | 40227022 | BAY AREA | APR | None | 0 | No | No | No | 1834901 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2106 | 14502106 | FUSE | 73041 | 20230411 | 1458 | 20230411 | 1515 | 2085794 | 17 | Distribution Circuit | Animal | Bird found | 1 | 17 | 37.6635 | -121.8821 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0059714 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1834925 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 12460 | 20230412 | 700 | 20230412 | 1023 | 2086185 | 203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1624 | 37.5276 | -121.8775 | No | Clear;32-90 F |  |  | 23-0060028 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1835189 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRIP-SAVER | 9473 | 20230412 | 1319 | 20230412 | 2106 | 2086774 | 467 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 72 | 32043 | 37.7864 | -121.8632 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0060251 | OH | Sus | 31642128 | BAY AREA | APR | Line to Ground | 0 | Yes | Yes | No | 1835256 | 0 | EPSS Ckt | N | 2023 | NA
MISSION | MISSION | DIXON LANDING-2101 | 14722101 | OCB | 2101/2 | 20230413 | 317 | 20230414 | 1958 | 2087199 | 2441 | Distribution Circuit | Equipment Failure/Involved | Underground | 4015 | 324548 | 37.457 | -121.921 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0060446 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1835353 | 0 | EPSS Ckt | N | 2023 | A PHASE INST OC & GRD
MISSION | MISSION | DIXON LANDING-2103 | 14722103 | OCB | 2103/2 | 20230413 | 317 | 20230413 | 421 | 2087208 | 64 | Distribution Circuit | Equipment Failure/Involved | Underground | 495 | 31680 | 37.457 | -121.921 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0060447 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1835354 | 0 | Non-EPSS | N | 2023 | A PHASE INST OC & GRD
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 36926 | 20230414 | 1511 | 20230414 | 1650 | 2088827 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 99 | 37.6627 | -122.1351 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0061257 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1835918 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | FUSE | 60172 | 20230414 | 2147 | 20230415 | 2037 | 2088990 | 1370 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 3075 | 37.5101 | -121.9582 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0061290 | UG | Sus | 31642307 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1835947 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 9537 | 20230415 | 1320 | 20230415 | 1420 | 2089268 | 60 | Distribution Circuit | 3rd Party | Metallic Balloon | 473 | 28380 | 37.6949 | -122.1135 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0061369 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1836053 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | SWITCH | 36208 | 20230417 | 505 | 20230417 | 555 | 2089929 | 50 | Distribution Circuit | Company Initiated | Improper Construction | 353 | 16150 | 37.6812 | -121.7765 | No | Overcast;32-90 F | Conductor- Underground | Normal | 23-0026939 | UG | Sus | 35125450 | BAY AREA | APR | Force Out | 0 | No | No | No | 1836223 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON 2103 | 14232103 | FUSE | 13123 | 20230417 | 641 | 20230417 | 945 | 2089965 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 12328 | 37.7278 | -121.9241 | No | Overcast;32-90 F |  |  | 23-0061594 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1836377 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | FUSE | 8160 | 20230417 | 838 | 20230418 | 118 | 2090028 | 1000 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 38000 | 37.5481 | -122.003 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0061607 | UG | Sus | 45732368 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1836389 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | RECLOSER | MR565 | 20230417 | 1202 | 20230418 | 335 | 2090469 | 700 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3916 | 1252943 | 37.5719 | -122.0348 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0061672 | OH | Sus | 45733236 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1836415 | 0 | Non-EPSS | N | 2023 | B PHASE- GRD
MISSION | MISSION | JARVIS-1112 | 13501112 | FUSE | 9576 | 20230417 | 2309 | 20230418 | 819 | 2090962 | 550 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 284 | 156278 | 37.5863 | -122.0393 | No | Overcast;32-90 F |  |  | 23-0061865 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1836547 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | SWITCH | 912 | 20230418 | 1105 | 20230418 | 1142 | 2091516 | 37 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 1530 | 37.5812 | -122.0334 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 23-0061989 | UG | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1836737 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRIP-SAVER | 8971 | 20230418 | 1619 | 20230418 | 1828 | 2091743 | 129 | Distribution Circuit | Vegetation | Tree - bark fell into line | 78 | 10062 | 37.7112 | -122.0551 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0062233 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | Yes | No | No | 1836794 | 0 | EPSS Ckt | N | 2023 | NONE
MISSION | MISSION | JARVIS-1112 | 13501112 | SWITCH | 1592 | 20230419 | 641 | 20230419 | 659 | 2092002 | 18 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 638 | 37.58 | -122.036 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0061989 | UG | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1836845 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 40146 | 20230419 | 915 | 20230420 | 555 | 2092404 | 1240 | Distribution Circuit | Equipment Failure/Involved | Underground | 176 | 59801 | 37.6788 | -121.921 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0062437 | UG | Sus | 45735677 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1837024 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 12KV-1101 | 12221101 | FUSE | 60792 | 20230419 | 1741 | 20230419 | 1837 | 2092768 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 5040 | 37.5257 | -122.0068 | No | Clear;32-90 F |  |  | 23-0062706 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1837089 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | FUSE | 40343 | 20230420 | 1225 | 20230420 | 1511 | 2093181 | 125 | Distribution Circuit | Animal | Bird found | 17 | 2822 | 37.701 | -121.7194 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0063079 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1837277 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | FUSE | 10683 | 20230420 | 1306 | 20230420 | 1335 | 2093201 | 29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 125 | 3625 | 37.6884 | -121.7861 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0063012 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1837266 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | FUSE | 11004 | 20230420 | 1425 | 20230420 | 1732 | 2093250 | 187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 4488 | 37.7227 | -121.9368 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0063092 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1837279 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1107 | 13761107 | RECLOSER | MR138 | 20230421 | 204 | 20230421 | 757 | 2093461 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 747 | 62811 | 37.6177 | -122.0874 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0063261 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | Yes | No | 1837351 | 0 | Non-EPSS | N | 2023 | NA
MISSION | MISSION | MT EDEN-1107 | 13761107 | FUSE | 9638 | 20230421 | 740 | 20230421 | 926 | 2093507 | 106 | Distribution Circuit | Animal | Bird found | 5 | 530 | 37.6125 | -122.0664 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0063376 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1837487 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRIP-SAVER | 8971 | 20230421 | 2019 | 20230421 | 2310 | 2094322 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 13338 | 37.7112 | -122.0551 | No | Clear;32-90 F |  |  | 23-0063662 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1837630 | 0 | EPSS Ckt | N | 2023 | N/A
MISSION | MISSION | JARVIS-1103 | 13501103 | SWITCH | 4155 | 20230422 | 2005 | 20230423 | 122 | 2094811 | 317 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 3983 | 37.6121 | -122.0571 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0063776 | UG | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1837808 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | FUSE | 8710 | 20230423 | 340 | 20230423 | 736 | 2094896 | 236 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 467 | 110212 | 37.4803 | -121.924 | No | Partly Cloudy;32-90 F |  |  | 23-0063810 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1837838 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 14015 | 20230423 | 1402 | 20230423 | 1544 | 2095069 | 102 | Distribution Circuit | 3rd Party | Metallic Balloon | 28 | 2857 | 37.6869 | -122.0476 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0063865 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1837890 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1104 | 14471104 | TRANSFORMER | T9898 | 20230424 | 1957 | 20230424 | 2055 | 2096053 | 58 | Transformer only | 3rd Party | Fire- house or bldg. | 7 | 406 | 37.5404 | -122.0264 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0064268 | UG | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1838200 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1102 | 14381102 | OCB | 1102/2 | 20230425 | 2246 | 20230426 | 4 | 2097108 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 486 | 35508 | 37.6718 | -122.1597 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0064740 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1838542 | 0 | Non-EPSS | N | 2023 | B GRD TIME OC
MISSION | MISSION | MT EDEN-1102 | 13761102 | FUSE | 50751 | 20230426 | 1054 | 20230427 | 1558 | 2097497 | 1744 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 5232 | 37.6496 | -122.1225 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0064964 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1838741 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | TRANSFORMER | 315467741367 | 20230426 | 1538 | 20230427 | 147 | 2097739 | 609 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 6090 | 37.6258 | -122.0661 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0065192 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1838802 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1102 | 14381102 | FUSE | 11045 | 20230427 | 929 | 20230427 | 1412 | 2098267 | 283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 566 | 37.6485 | -122.1397 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0065520 | OH | Sus | 31643444 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1839036 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315410841434 | 20230427 | 1347 | 20230427 | 1558 | 2098527 | 131 | Transformer only | 3rd Party | Customer Equipment | 1 | 131 | 37.6274 | -122.0857 | No | Clear;32-90 F | Circuit Breaker | Broken | 23-0065701 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1839070 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2103 | 14722103 | OCB | 2103/2 | 20230427 | 1645 | 20230427 | 1733 | 2098718 | 48 | Distribution Circuit | Equipment Failure/Involved | Underground | 495 | 20939 | 37.457 | -121.921 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0065712 | UG | Sus | 45743900 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839075 | 0 | Non-EPSS | N | 2023 | C PHASE & GRD
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | FUSE | 14414 | 20230427 | 1709 | 20230427 | 2116 | 2098741 | 247 | Distribution Circuit | 3rd Party | Metallic Balloon | 66 | 16302 | 37.6871 | -122.0684 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0065759 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1839118 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2103 | 14232103 | RECLOSER | MR279 | 20230427 | 1822 | 20230428 | 238 | 2098785 | 468 | Distribution Circuit | Equipment Failure/Involved | Underground | 735 | 79701 | 37.7029 | -121.9121 | No | Clear;32-90 F | Elbow | Broken | 23-0065731 | UG | Sus | 45744037 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839092 | 0 | EPSS Ckt | N | 2023 | C & GRD
MISSION | MISSION | MT EDEN-1112 | 13761112 | TRANSFORMER | 315472442353 | 20230427 | 2315 | 20230428 | 445 | 2098919 | 330 | Transformer only | 3rd Party | Vehicle | 13 | 4290 | 37.6527 | -122.0652 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0065799 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1839151 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2103 | 14402103 | TRANSFORMER | T27781 | 20230428 | 2004 | 20230428 | 2030 | 2099719 | 26 | Distribution Circuit | 3rd Party | Customer Equipment | 10 | 260 | 37.7003 | -121.7379 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0066181 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839388 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | TRANSFORMER | 316014842165 | 20230428 | 2036 | 20230428 | 2112 | 2099732 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 180 | 37.6499 | -121.8777 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0066183 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1839389 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | FUSE | 10658 | 20230429 | 511 | 20230429 | 608 | 2099792 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 224 | 12768 | 37.6833 | -122.0767 | No | Overcast;32-90 F |  |  | 23-0066228 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839428 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 14877 | 20230429 | 941 | 20230429 | 2045 | 2100001 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2656 | 37.564 | -121.683 | No | Clear;32-90 F | Jumper | Burned Open | 23-0066323 | OH | Sus | 45745135 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839544 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LIVERMORE-1103 | 12141103 | FUSE | 6705 | 20230429 | 2101 | 20230430 | 1410 | 2100280 | 1029 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 989 | 17200 | 37.6761 | -121.7397 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 23-0066343 | OH | Sus | 45745321 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1839560 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | 315542937719 | 20230430 | 912 | 20230430 | 1000 | 2100439 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 1104 | 37.5258 | -122.0381 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0066404 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839632 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1101 | 13751101 | TRANSFORMER | T10199 | 20230430 | 1025 | 20230430 | 1310 | 2100486 | 165 | Transformer only | Equipment Failure/Involved | Underground | 11 | 1815 | 37.7132 | -121.7451 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0066414 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839642 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 10563 | 20230430 | 1048 | 20230430 | 1154 | 2100494 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 66 | 37.6268 | -121.7565 | No | Clear;32-90 F |  |  | 23-0066422 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839649 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | TRANSFORMER | 315139744932 | 20230430 | 1523 | 20230501 | 4 | 2100822 | 521 | Transformer only | 3rd Party | Other | 6 | 3126 | 37.722 | -122.1816 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 23-0066456 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839672 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | TRANSFORMER | 315141044947 | 20230430 | 1529 | 20230501 | 153 | 2100830 | 624 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 11856 | 37.7224 | -122.1812 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0066457 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839673 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 62769 | 20230430 | 1625 | 20230430 | 1652 | 2100853 | 27 | Distribution Circuit | 3rd Party | Metallic Balloon | 51 | 1377 | 37.5258 | -122.0392 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0066459 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1839675 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1115 | 13111115 | FUSE | 50952 | 20230502 | 501 | 20230502 | 703 | 2102102 | 122 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 259 | 31598 | 37.7026 | -122.1857 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0066899 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1840026 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1105 | 13501105 | SWITCH | 30965SW | 20230502 | 900 | 20230502 | 1302 | 2102537 | 242 | Distribution Circuit | Equipment Failure/Involved | Underground | 133 | 17339 | 37.5716 | -122.0149 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Broken | 23-0067044 | UG | Sus | 45746564 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1840176 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1109 | 14471109 | OTHER | J30731 TWD 22866 | 20230503 | 1256 | 20230503 | 1454 | 2103798 | 118 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 912 | 37.5982 | -122.0669 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 23-0067576 | UG | Sus | 0 | BAY AREA | MAY | None | 0 | No | No | No | 1840534 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | RECLOSER | MR332 | 20230503 | 1347 | 20230503 | 1944 | 2103887 | 313 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 416 | 111699 | 37.6659 | -121.8416 | No | Overcast-Drizzle;32-90 F |  |  | 23-0067738 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1840548 | 0 | EPSS Ckt | N | 2023 | C- GRD ABOVE MTT
MISSION | MISSION | GRANT-1102 | 14381102 | TRANSFORMER | 315310842097 | 20230503 | 1549 | 20230504 | 448 | 2104008 | 779 | Transformer only | Unknown Cause | Patrol - not conducted | 6 | 4674 | 37.645 | -122.1206 | No | Overcast;32-90 F |  |  | 23-0067823 | OH | Sus | 0 | BAY AREA | MAY | None | 0 | No | No | No | 1840574 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1109 | 14351109 | SWITCH | 60390SW | 20230504 | 1331 | 20230505 | 105 | 2104782 | 694 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1388 | 37.523 | -121.9282 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0068276 | UG | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1840873 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | SWITCH | 1190 | 20230504 | 1342 | 20230504 | 1744 | 2104843 | 242 | Distribution Circuit | Equipment Failure/Involved | Underground | 32 | 3802 | 37.5693 | -122.0164 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0067044 | UG | Sus | 45746564 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1840878 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | FUSE | 73207 | 20230505 | 145 | 20230505 | 555 | 2105177 | 250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2414 | 37.6519 | -121.8046 | No | Overcast;32-90 F |  |  | 23-0068545 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1841002 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | TRANSFORMER | 316087039360 | 20230505 | 958 | 20230505 | 1622 | 2105421 | 384 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 384 | 37.5728 | -121.8509 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0068742 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1841161 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LIVERMORE-1103 | 12141103 | FUSE | 6688 | 20230505 | 1300 | 20230505 | 1326 | 2105606 | 26 | Distribution Circuit | Company Initiated | Return Circuit Normal | 20 | 520 | 37.6777 | -121.7398 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0066343 | UG | Sus | 45745321 | BAY AREA | MAY | None | 0 | No | No | No | 1841179 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN 2101 | 14052101 | RECLOSER | MR765 | 20230505 | 1403 | 20230505 | 1414 | 2105659 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6902 | 75922 | 37.7482 | -121.8719 | No | Partly Cloudy;32-90 F |  |  | 23-0068888 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1841192 | 0 | EPSS Ckt | N | 2023 | A- INST OC
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | SWITCH | 1634 | 20230506 | 257 | 20230506 | 415 | 2105932 | 78 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 133 | 10374 | 37.6805 | -121.7726 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Broken | 23-0069056 | UG | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1841287 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | TRANSFORMER | 316170042348 | 20230508 | 807 | 20230508 | 1409 | 2107132 | 362 | Transformer only | Company Initiated | Construction Activity/equip- company | 2 | 724 | 37.6555 | -121.8242 | No | Overcast;32-90 F | Other | On Ground | 23-0069450 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1841665 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CAYETANO-2111 | 14422111 | FUSE | 71911 | 20230508 | 1724 | 20230508 | 2017 | 2108036 | 173 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 203 | 37.7101 | -121.8047 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0069616 | UG | Sus | 0 | BAY AREA | MAY | None | 0 | No | No | No | 1841782 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | SWITCH | 70601SW | 20230509 | 1121 | 20230509 | 1220 | 2108615 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 118 | 37.7008 | -121.7054 | No | Partly Cloudy;32-90 F |  |  | 23-0069964 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1842009 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1105 | 14381105 | FUSE | 223804 | 20230509 | 1534 | 20230511 | 1431 | 2108820 | 2817 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 2817 | 37.6698 | -122.157 | No | Partly Cloudy;32-90 F |  |  | 23-0070169 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1842067 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | TRANSFORMER | 17293 | 20230510 | 1454 | 20230510 | 1504 | 2109505 | 10 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 90 | 37.6975 | -121.7196 | No | Clear;32-90 F |  |  | 23-0070572 | OH | Sus | 0 | BAY AREA | MAY | None | 0 | No | No | No | 1842349 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | TRIP-SAVER | 8721 | 20230511 | 830 | 20230511 | 1201 | 2110102 | 211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 5064 | 37.5659 | -121.8832 | No | Partly Cloudy;32-90 F |  |  | 23-0070869 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1842561 | 0 | EPSS Ckt | N | 2023 | TRIP SAVER
MISSION | MISSION | RADUM-1105 | 13151105 | TRANSFORMER | 12464 | 20230512 | 622 | 20230512 | 1400 | 2110818 | 458 | Transformer only | Equipment Failure/Involved | Underground | 16 | 7328 | 37.6775 | -121.871 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0071198 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1842730 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 10563 | 20230512 | 950 | 20230512 | 1105 | 2111181 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 75 | 37.6268 | -121.7565 | No | Clear;32-90 F |  |  | 23-0071341 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1842878 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 12607 | 20230512 | 1322 | 20230512 | 1442 | 2111301 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 202 | 9954 | 37.7022 | -121.939 | No | Clear;32-90 F |  |  | 23-0071414 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1842905 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 9425 | 20230512 | 1441 | 20230512 | 1555 | 2111366 | 74 | Distribution Circuit | 3rd Party | Metallic Balloon | 50 | 3702 | 37.6485 | -122.076 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0071464 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1842922 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1108 | 14381108 | FUSE | 80349 | 20230513 | 459 | 20230513 | 735 | 2111606 | 156 | Distribution Circuit | 3rd Party | Metallic Balloon | 2 | 312 | 37.6747 | -122.0965 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0071538 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1842980 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 64737 | 20230513 | 1723 | 20230513 | 1837 | 2111895 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 250 | 16772 | 37.5458 | -121.9443 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0071590 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843045 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | FUSE | 10275 | 20230513 | 1738 | 20230514 | 1208 | 2111903 | 1110 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 25 | 14268 | 37.535 | -122.005 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071601 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1843050 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1109 | 13501109 | OCB | 1109/2 | 20230514 | 1657 | 20230515 | 501 | 2112263 | 724 | Distribution Circuit | 3rd Party | Vehicle | 1736 | 205124 | 37.5953 | -122.0175 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0071682 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843131 | 0 | Non-EPSS | N | 2023 | PH & GRD INST
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10648 | 20230514 | 2003 | 20230514 | 2210 | 2112398 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 125 | 15875 | 37.5468 | -121.9467 | No | Clear;32-90 F |  |  | 23-0071709 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843159 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRANSFORMER | 316152046833 | 20230515 | 1053 | 20230515 | 1303 | 2113032 | 130 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 130 | 37.7786 | -121.8317 | No | Clear;32-90 F |  |  | 23-0071990 | OH | Sus | 0 | BAY AREA | MAY | None | 0 | No | No | No | 1843363 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | FUSE | 10736 | 20230515 | 1124 | 20230515 | 1348 | 2113078 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 10224 | 37.4753 | -121.9212 | No | Clear;32-90 F |  |  | 23-0071976 | OH | Sus | 0 | BAY AREA | MAY | None | 0 | No | No | No | 1843356 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NORTH DUBLIN-2101 | 14052101 | OCB | 2101/2/NORM | 20230516 | 302 | 20230517 | 223 | 2113653 | 1401 | Distribution Circuit | 3rd Party | Vehicle | 4128 | 379428 | 37.7448 | -121.8576 | No | Partly Cloudy;32-90 F | Switch (UG) | Burned/flashed | 23-0072127 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843450 | 0 | EPSS Ckt | N | 2023 | TIME OC
MISSION | MISSION | NEWARK 12KV-1101 | 12221101 | TRANSFORMER | T22819 | 20230516 | 1042 | 20230516 | 1125 | 2114059 | 43 | Transformer only | 3rd Party | Customer Equipment | 17 | 731 | 37.5192 | -121.9893 | No | Partly Cloudy;32-90 F | Customer Equipment | Normal | 23-0072298 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843623 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2107 | 14722107 | TRANSFORMER | 12021 | 20230516 | 1133 | 20230517 | 417 | 2114111 | 1004 | Transformer only | Equipment Failure/Involved | Underground | 1 | 1004 | 37.4816 | -121.9324 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0072327 | UG | Sus | 31645456 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843632 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | FUSE | 785709 | 20230516 | 1152 | 20230516 | 1259 | 2114143 | 67 | Distribution Circuit | 3rd Party | Metallic Balloon | 74 | 4958 | 37.6615 | -122.0863 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0072335 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843635 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 13152 | 20230516 | 1739 | 20230517 | 39 | 2114395 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 22432 | 37.7016 | -121.9386 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0072473 | OH | Sus | 45765293 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843693 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2106 | 14232106 | SWITCH | J7286 TWD T21560 | 20230516 | 1832 | 20230517 | 4 | 2114423 | 332 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 14086 | 37.6878 | -121.9235 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0072343 | UG | Sus | 35447149 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1843685 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | OCB | 2111/2 | 20230516 | 1845 | 20230516 | 1939 | 2114437 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2041 | 110214 | 37.7448 | -121.9369 | No | Clear;32-90 F |  |  | 23-0072470 | OH | Sus | 0 | BAY AREA | MAY | Open Circuit | 0 | No | No | No | 1843688 | 0 | Non-EPSS | N | 2023 | OC
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 11468 | 20230516 | 2235 | 20230516 | 2245 | 2114527 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 1020 | 37.5471 | -121.9471 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0072405 | OH | Sus | 35446701 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843733 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | SWITCH | 6268 | 20230516 | 2254 | 20230516 | 2340 | 2114534 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 369 | 37.5479 | -121.9474 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0072405 | OH | Sus | 35446701 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843734 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | SWITCH | 9895 | 20230517 | 8 | 20230517 | 15 | 2114555 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 714 | 37.5479 | -121.9534 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0072405 | OH | Sus | 35446701 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843741 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 12607 | 20230517 | 346 | 20230517 | 355 | 2114596 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2 | 18 | 37.7022 | -121.939 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0072473 | OH | Sus | 45765293 | BAY AREA | MAY | None | 0 | No | No | No | 1843751 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1105 | 14381105 | FUSE | 10726 | 20230517 | 655 | 20230517 | 825 | 2114628 | 90 | Distribution Circuit | Animal | Squirrel | 154 | 13860 | 37.6848 | -122.1431 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0072599 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1843804 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1108 | 12221108 | FUSE | 12290 | 20230517 | 2022 | 20230518 | 407 | 2115439 | 465 | Distribution Circuit | Equipment Failure/Involved | Underground | 66 | 5790 | 37.5176 | -121.9814 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0072893 | UG | Sus | 31645902 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1844027 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 8934 | 20230518 | 607 | 20230518 | 745 | 2115530 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 686 | 37.7604 | -122.0276 | No | Partly Cloudy;32-90 F |  |  | 23-0072976 | OH | Sus | 0 | BAY AREA | MAY | None | 0 | No | No | No | 1844091 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2106 | 14232106 | SWITCH | 986 | 20230519 | 31 | 20230519 | 345 | 2116569 | 194 | Distribution Circuit | Equipment Failure/Involved | Underground | 249 | 48306 | 37.6891 | -121.929 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0073312 | UG | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1844324 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1112 | 13761112 | FUSE | 14038 | 20230519 | 1638 | 20230519 | 1717 | 2117245 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 101 | 3939 | 37.6508 | -122.0783 | No | Partly Cloudy;32-90 F |  |  | 23-0073725 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1844552 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | FUSE | 10271 | 20230519 | 2051 | 20230520 | 22 | 2117345 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 14089 | 37.5074 | -121.9351 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073737 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1844562 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1102 | 13111102 | TRANSFORMER | 315210745347 | 20230521 | 1905 | 20230522 | 1359 | 2118139 | 1134 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 12474 | 37.7337 | -122.1572 | No | Partly Cloudy;32-90 F | Transformer (OH) | Arcing | 23-0074012 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1844841 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1102 | 13111102 | TRANSFORMER | 315207745402 | 20230521 | 1905 | 20230522 | 536 | 2118138 | 631 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 11358 | 37.7353 | -122.1583 | No | Partly Cloudy;32-90 F | Transformer (OH) | Arcing | 23-0074014 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1844842 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 14471 | 20230522 | 2115 | 20230523 | 530 | 2119169 | 495 | Distribution Circuit | 3rd Party | Vandalism | 1 | 495 | 37.6971 | -122.1938 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0074421 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1845144 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | FUSE | 9524 | 20230522 | 2235 | 20230524 | 142 | 2119193 | 1627 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 32318 | 37.6962 | -122.0497 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0074439 | UG | Sus | 35448569 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1845165 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | TRANSFORMER | 315793438343 | 20230523 | 1410 | 20230523 | 1423 | 2119850 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 104 | 37.544 | -121.9521 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0074796 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1845398 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1112 | 13761112 | TRANSFORMER | 315462542541 | 20230524 | 40 | 20230524 | 947 | 2120188 | 547 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4923 | 37.6578 | -122.0687 | No | Overcast;32-90 F | Fuse | Broken | 23-0075030 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1845613 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1109 | 13111109 | TRANSFORMER | 315186145352 | 20230524 | 1540 | 20230524 | 2241 | 2120718 | 421 | Transformer only | 3rd Party | Other | 25 | 10525 | 37.7338 | -122.1657 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0075278 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | Yes | No | 1845701 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | FUSE | 374669 | 20230524 | 1737 | 20230525 | 930 | 2120849 | 953 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 953 | 37.7187 | -122.097 | No | Partly Cloudy;32-90 F |  |  | 23-0075316 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1845720 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | EDES-1111 | 13681111 | SWITCH | 4079 | 20230524 | 2229 | 20230525 | 59 | 2120885 | 150 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 6312 | 37.7163 | -122.1873 | No | Partly Cloudy;32-90 F | Transformer (UG) | Deteriorated | 23-0075289 | UG | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1845730 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11230 | 20230525 | 1424 | 20230525 | 1530 | 2121404 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 1848 | 37.6454 | -121.6472 | No | Clear;32-90 F |  |  | 23-0075678 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1845948 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11230 | 20230525 | 1556 | 20230525 | 1729 | 2121470 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 2604 | 37.6454 | -121.6472 | No | Clear-Strong Winds;32-90 F | Fuse | Failed/Faulted | 23-0075728 | OH | Sus | 0 | BAY AREA | MAY | None | 0 | No | No | No | 1845964 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 14474 | 20230526 | 1055 | 20230526 | 1101 | 2122131 | 6 | Distribution Circuit | 3rd Party | Vandalism | 1 | 6 | 37.6985 | -122.1917 | No | Overcast;32-90 F | Customer Equipment | Contaminated | 23-0076008 | UG | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1846169 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 14471 | 20230526 | 1150 | 20230526 | 1204 | 2122165 | 14 | Distribution Circuit | 3rd Party | Vandalism | 1 | 14 | 37.6971 | -122.1938 | No | Overcast;32-90 F | Secondary | Contaminated | 23-0076051 | UG | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1846185 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1112 | 14351112 | OTHER | WIRE DOWN | 20230527 | 939 | 20230527 | 1934 | 2122626 | 595 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3551 | 30169 | 37.5646 | -121.9799 | No | Overcast;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0076300 | OH | Sus | 31649013 | BAY AREA | MAY | Multi-Fault | 0 | No | Yes | Yes | 1846325 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | FUSE | 7489 | 20230527 | 1010 | 20230527 | 1105 | 2122597 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 2200 | 37.5268 | -121.9556 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0076284 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1846305 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2110 | 12232110 | FUSE | 9715 | 20230528 | 546 | 20230528 | 1125 | 2122905 | 339 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1356 | 37.4994 | -121.9938 | No | Overcast;32-90 F |  |  | 23-0076432 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1846419 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | TRIP-SAVER | 10315 | 20230529 | 550 | 20230529 | 834 | 2123329 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 11972 | 37.6519 | -121.9824 | No | Overcast;32-90 F |  |  | 23-0076529 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1846497 | 0 | EPSS Ckt | N | 2023 | BC
MISSION | MISSION | VASCO-1103 | 13751103 | FUSE | 12266 | 20230529 | 929 | 20230529 | 1517 | 2123384 | 348 | Distribution Circuit | 3rd Party | Vehicle | 1 | 348 | 37.6937 | -121.6745 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0076541 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1846506 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315606438231 | 20230529 | 945 | 20230529 | 1649 | 2123400 | 424 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 7208 | 37.5401 | -122.0165 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0076551 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1846513 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | TRANSFORMER | 316285241767 | 20230530 | 1143 | 20230530 | 1303 | 2123945 | 80 | Transformer only | Animal | Other | 2 | 160 | 37.6401 | -121.7843 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0076843 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1846774 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 12274 | 20230530 | 1618 | 20230530 | 1742 | 2124257 | 84 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 4284 | 37.5346 | -121.9409 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0076983 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1846821 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315256843013 | 20230530 | 1742 | 20230531 | 300 | 2124166 | 558 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 6696 | 37.6698 | -122.1399 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0076987 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1846823 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | TRANSFORMER | 315370642565 | 20230531 | 1517 | 20230601 | 647 | 2124935 | 930 | Transformer only | Equipment Failure/Involved | Overhead | 35 | 32550 | 37.658 | -122.1004 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0077408 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1847078 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | TRANSFORMER | 315164043994 | 20230531 | 1824 | 20230531 | 2058 | 2125062 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 308 | 37.6964 | -122.1726 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0077487 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1847099 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1108 | 14471108 | SWITCH | 635672 | 20230531 | 1843 | 20230601 | 30 | 2125134 | 347 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 3123 | 37.596 | -122.0538 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0077289 | UG | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1847111 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 15082 | 20230531 | 2022 | 20230531 | 2210 | 2125110 | 108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 4927 | 37.544 | -122.0475 | No | Clear;32-90 F | Other | Normal | 23-0077513 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1847112 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2119 | 14232119 | TRANSFORMER | T1253 | 20230531 | 2250 | 20230601 | 239 | 2125069 | 229 | Transformer only | Equipment Failure/Involved | Underground | 37 | 8473 | 37.688 | -121.9052 | No | Clear;32-90 F | Secondary | Broken | 23-0077545 | UG | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1847132 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1107 | 13761107 | FUSE | 50799 | 20230603 | 1844 | 20230604 | 1705 | 2128090 | 1336 | Distribution Circuit | 3rd Party | Vehicle | 25 | 10000 | 37.6071 | -122.0638 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0078634 | OH | Sus | 35452840 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1847748 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1110 | 14351110 | FUSE | 15002 | 20230604 | 1302 | 20230604 | 1334 | 2128422 | 32 | Distribution Circuit | 3rd Party | Metallic Balloon | 6 | 192 | 37.5241 | -121.9484 | No | Clear;32-90 F | Fuse | Burned Open | 23-0078715 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1847819 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2104 | 12232104 | OCB | 2104/2 | 20230604 | 2027 | 20230605 | 127 | 2128693 | 300 | Distribution Circuit | Equipment Failure/Involved | Underground | 311 | 87592 | 37.5029 | -121.9817 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0078750 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1847853 | 0 | Non-EPSS | N | 2023 | GRD
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | FUSE | 11981 | 20230604 | 2130 | 20230605 | 2152 | 2128740 | 1462 | Distribution Circuit | 3rd Party | Vehicle | 4 | 5848 | 37.5094 | -121.9494 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0078762 | OH | Sus | 0 | BAY AREA | JUN | Multi-Fault | 0 | No | No | No | 1847863 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 50952 | 20230605 | 39 | 20230605 | 1359 | 2128786 | 800 | Distribution Circuit | 3rd Party | Vandalism | 257 | 67405 | 37.7026 | -122.1857 | No | Partly Cloudy;32-90 F | Pole - Tower- steel | Broken | 23-0078777 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1847878 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315273443115 | 20230605 | 406 | 20230605 | 1640 | 2128828 | 754 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 9048 | 37.6727 | -122.1342 | No | Overcast;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0078885 | OH | Sus | 45824140 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1848026 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | TRANSFORMER | T7644 | 20230605 | 1252 | 20230605 | 1531 | 2129093 | 159 | Transformer only | Equipment Failure/Involved | Underground | 4 | 636 | 37.6587 | -121.8856 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on object | 23-0078948 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | No | 1848054 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DIXON LANDING-2105 | 14722105 | SWITCH | 55014SW | 20230605 | 2303 | 20230605 | 2331 | 2130070 | 28 | Distribution Circuit | Company Initiated | Return Circuit Normal | 95 | 2492 | 37.4785 | -121.9456 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Normal | 23-0078750 | OH | Sus | 35452856 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1848163 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | TRANSFORMER | 315489843129 | 20230606 | 240 | 20230606 | 349 | 2130099 | 69 | Transformer only | Unknown Cause | Patrol - found nothing | 22 | 1518 | 37.6741 | -122.0595 | No | Partly Cloudy;32-90 F |  |  | 23-0079180 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1848185 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | TRANSFORMER | 315484043137 | 20230606 | 240 | 20230606 | 349 | 2130123 | 69 | Transformer only | Environmental/External | Flood/Erosion | 15 | 1035 | 37.6744 | -122.0614 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 23-0079181 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | No | 1848186 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | OCB | 2109/2/NORM | 20230607 | 651 | 20230607 | 755 | 2131527 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3150 | 201600 | 37.7383 | -121.7706 | No | Clear;32-90 F |  |  | 23-0079678 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1848582 | 0 | EPSS Ckt | N | 2023 | PHASE OR GRD OC
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 12787 | 20230607 | 718 | 20230607 | 825 | 2131491 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 5628 | 37.6138 | -121.8989 | No | Clear;32-90 F |  |  | 23-0079722 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1848641 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2105 | 14502105 | FUSE | 8258 | 20230608 | 546 | 20230608 | 1107 | 2132305 | 321 | Distribution Circuit | Equipment Failure/Involved | Underground | 273 | 81139 | 37.6692 | -121.8863 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0080194 | UG | Sus | 45834203 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1848959 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1110 | 13501110 | TRANSFORMER | 315673639795 | 20230608 | 1908 | 20230608 | 1946 | 2132993 | 38 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 456 | 37.5833 | -121.9942 | No | Clear;32-90 F | Secondary | Arcing | 23-0080541 | OH | Sus | 31651689 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1849142 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LIVERMORE-1104 | 12141104 | RECLOSER | MR271 | 20230608 | 1948 | 20230608 | 2036 | 2133082 | 48 | Distribution Circuit | 3rd Party | Metallic Balloon | 258 | 12384 | 37.6674 | -121.7904 | No | Clear;32-90 F | Recloser | Normal | 23-0080547 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1849153 | 0 | Non-EPSS | N | 2023 | C PHASE & GRD
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 51233 | 20230610 | 822 | 20230610 | 1122 | 2134171 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 16740 | 37.6422 | -122.059 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0081114 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1849576 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 51208 | 20230611 | 1345 | 20230611 | 1518 | 2134646 | 93 | Distribution Circuit | 3rd Party | Metallic Balloon | 209 | 19437 | 37.6423 | -122.0606 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0081322 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1849740 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | EDES-1111 | 13681111 | TRANSFORMER | 315127644744 | 20230612 | 859 | 20230612 | 2334 | 2135092 | 875 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1750 | 37.7168 | -122.1856 | No | Overcast;32-90 F | Cable Termination(live front | Broken | 23-0081507 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1849974 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1103 | 14471103 | SWITCH | 1172 | 20230613 | 1810 | 20230614 | 205 | 2136407 | 475 | Distribution Circuit | Equipment Failure/Involved | Underground | 181 | 17271 | 37.5916 | -122.0611 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0081957 | UG | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1850379 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 50810 | 20230613 | 2357 | 20230614 | 1512 | 2136497 | 915 | Distribution Circuit | Equipment Failure/Involved | Underground | 414 | 243870 | 37.7504 | -121.9601 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0082115 | UG | Sus | 45846457 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1850423 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | OCB | 1104/2 | 20230614 | 116 | 20230614 | 224 | 2136508 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3397 | 130934 | 37.6319 | -122.1025 | No | Overcast;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0082108 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1850418 | 0 | Non-EPSS | N | 2023 | GRD OC
MISSION | MISSION | DUMBARTON-1109 | 14471109 | OCB | 1109/2 | 20230614 | 612 | 20230614 | 1307 | 2136557 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3524 | 392135 | 37.5571 | -122.0583 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0082131 | OH | Sus | 31652072 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | No | 1850435 | 0 | Non-EPSS | N | 2023 | PHASE & GRD TARGETS
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | FUSE | 14218 | 20230614 | 649 | 20230614 | 940 | 2136567 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 855 | 37.6762 | -122.0783 | No | Overcast;32-90 F |  |  | 23-0082220 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1850578 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 50529 | 20230614 | 1744 | 20230614 | 2025 | 2137216 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3381 | 37.7336 | -121.9489 | No | Partly Cloudy;32-90 F |  |  | 23-0082492 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1850699 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | OTHER | J92317 TWD T28016 | 20230615 | 916 | 20230615 | 1247 | 2137572 | 211 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 211 | 37.7306 | -121.9466 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0082693 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1850838 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | TRANSFORMER | 316353945320 | 20230615 | 1239 | 20230615 | 1502 | 2137717 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 143 | 37.7385 | -121.7613 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0082778 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1850869 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1109 | 13761109 | RECLOSER | MR206 | 20230615 | 1716 | 20230616 | 414 | 2137931 | 658 | Distribution Circuit | 3rd Party | Vehicle | 1233 | 123614 | 37.6347 | -122.062 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0082910 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1850911 | 0 | Non-EPSS | N | 2023 | B- GRD TGTS
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | TRANSFORMER | 315674537902 | 20230616 | 544 | 20230616 | 1437 | 2138164 | 533 | Transformer only | Vegetation | Other ground vegetation | 4 | 2132 | 37.5312 | -121.9927 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 23-0083018 | OH | Sus | 45850805 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1850982 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 9374 | 20230616 | 1049 | 20230616 | 1404 | 2138477 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 12226 | 37.679 | -122.0497 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned Open | 23-0083240 | OH | Sus | 45851401 | BAY AREA | JUN | None | 0 | No | No | No | 1851173 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315412541431 | 20230616 | 1652 | 20230616 | 1902 | 2138808 | 130 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 1690 | 37.6273 | -122.0852 | No | Clear;32-90 F |  |  | 23-0083287 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1851197 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | RECLOSER | MR172 | 20230617 | 237 | 20230617 | 1442 | 2139127 | 715 | Distribution Circuit | Equipment Failure/Involved | Underground | 3046 | 438594 | 37.657 | -121.9009 | No | Partly Cloudy;32-90 F | Elbow | Broken | 23-0083320 | UG | Sus | 45851641 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1851242 | 0 | EPSS Ckt | N | 2023 | A & GRD
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 9389 | 20230617 | 844 | 20230617 | 2019 | 2139209 | 695 | Distribution Circuit | 3rd Party | Vandalism | 1 | 695 | 37.6986 | -122.191 | No | Overcast;32-90 F | Fuse | Normal | 23-0083359 | OH | Sus | 45851646 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1851313 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 14219 | 20230617 | 1414 | 20230618 | 1054 | 2139494 | 1240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1240 | 37.7336 | -122.0325 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0083430 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1851374 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1112 | 14351112 | OCB | 1112/2 | 20230617 | 1500 | 20230618 | 12 | 2139419 | 552 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4488 | 585851 | 37.5418 | -121.9619 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083399 | OH | Sus | 45851499 | BAY AREA | JUN | Line to Line | 0 | No | Yes | No | 1851348 | 0 | Non-EPSS | N | 2023 | NO TGTS ON SCADA TGT ON MR473
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10187 | 20230617 | 1515 | 20230618 | 845 | 2139428 | 1050 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 4200 | 37.5617 | -121.9486 | No | Clear;32-90 F | Other | Normal | 23-0083475 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1851420 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 8873 | 20230618 | 1808 | 20230619 | 1116 | 2139950 | 1028 | Distribution Circuit | Vegetation | Tree - branch fell on line | 76 | 48368 | 37.6381 | -121.8943 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0083556 | OH | Sus | 45851792 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1851500 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315267042896 | 20230619 | 826 | 20230619 | 1524 | 2140291 | 418 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 6270 | 37.6667 | -122.1363 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0083649 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1851630 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | TRANSFORMER | 315886041070 | 20230619 | 836 | 20230622 | 1503 | 2140235 | 4707 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 9414 | 37.6198 | -121.9222 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0083621 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1851614 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 20383 | 20230620 | 1215 | 20230620 | 1356 | 2141361 | 101 | Distribution Circuit | Equipment Failure/Involved | Underground | 133 | 13433 | 37.6702 | -121.8916 | No | Clear;32-90 F | Bushing | Normal | 23-0083911 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1851926 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1110 | 13501110 | TRANSFORMER | 315673639795 | 20230620 | 1853 | 20230621 | 559 | 2141655 | 666 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 7992 | 37.5833 | -121.9942 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0084031 | OH | Sus | 31652970 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1851961 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | FUSE | 6541 | 20230621 | 338 | 20230621 | 546 | 2141895 | 128 | Distribution Circuit | Animal | Squirrel | 150 | 19200 | 37.6505 | -122.0932 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0084082 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1852017 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2101 | 14232101 | FUSE | 74893 | 20230621 | 1618 | 20230621 | 1834 | 2142610 | 136 | Distribution Circuit | Equipment Failure/Involved | Underground | 67 | 3487 | 37.774 | -121.9 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0084303 | UG | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1852224 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1103 | 14471103 | SWITCH | 3882 | 20230621 | 1624 | 20230621 | 2152 | s1852237 | 328 | Distribution Circuit | Equipment Failure/Involved | Underground | 164 | 16010 | 37.5859 | -122.0571 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0084398 | UG | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1852237 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 71474 | 20230622 | 1120 | 20230622 | 1254 | 2143161 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 6768 | 37.7156 | -121.7405 | No | Partly Cloudy;32-90 F |  |  | 23-0084715 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1852463 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | PARSONS SUB | 1366 | OCB | 402/2 | 20230624 | 1343 | 20230624 | 1429 | 2144938 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 982 | 45172 | 37.7023 | -122.0827 | No | Partly Cloudy;32-90 F |  |  | 23-0085347 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1852894 | 0 | Non-EPSS | N | 2023 | A-B- GRD TGTS
MISSION | MISSION | FREMONT-1109 | 14351109 | TRANSFORMER | 26132 | 20230624 | 1636 | 20230624 | 1718 | 2145029 | 42 | Transformer only | Unknown Cause | Patrol - found nothing | 18 | 756 | 37.5294 | -121.9271 | No | Clear;32-90 F |  |  | 23-0085362 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1852905 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | EDES-1111 | 13681111 | TRANSFORMER | 10749 | 20230625 | 1047 | 20230625 | 1207 | 2145288 | 80 | Transformer only | Equipment Failure/Involved | Underground | 4 | 320 | 37.7203 | -122.1917 | No | Overcast;32-90 F | Secondary | Broken | 23-0085424 | UG | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1852974 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | OCB | 2109/2 | 20230625 | 1654 | 20230626 | 1920 | 2145419 | 821 | Distribution Circuit | Equipment Failure/Involved | Underground | 4569 | 310774 | 37.6697 | -121.8543 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0085441 | UG | Sus | 35461380 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1852990 | 0 | Non-EPSS | N | 2023 | GRD PHASE TIME
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | SWITCH | 3714 | 20230625 | 2109 | 20230626 | 206 | 2145475 | 297 | Distribution Circuit | Equipment Failure/Involved | Underground | 97 | 7471 | 37.6934 | -122.1381 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 23-0085436 | UG | Sus | 35461282 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1852998 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 8026 | 20230626 | 718 | 20230626 | 805 | 2145605 | 47 | Distribution Circuit | Animal | Squirrel | 23 | 1080 | 37.6629 | -121.8791 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0085500 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1853052 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | TRANSFORMER | 315886041070 | 20230626 | 1324 | 20230627 | 1156 | 2146180 | 1352 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 2704 | 37.6198 | -121.9222 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0085784 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1853269 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 10985 | 20230626 | 1418 | 20230626 | 1533 | 2146236 | 75 | Distribution Circuit | Animal | Bird found | 22 | 1650 | 37.6696 | -122.0522 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0085763 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1853254 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1106 | 14471106 | TRANSFORMER | T8278 | 20230626 | 1422 | 20230626 | 1450 | 2146224 | 28 | Transformer only | Equipment Failure/Involved | Underground | 14 | 392 | 37.5733 | -122.0776 | No | Clear;32-90 F | Secondary | Broken | 23-0085716 | UG | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1853240 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | SWITCH | 70532SW | 20230627 | 902 | 20230627 | 1133 | 2146814 | 151 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 6644 | 37.6896 | -121.8787 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0086004 | UG | Sus | 45862180 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1853464 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | MR186 | 20230627 | 1618 | 20230627 | 1807 | 2147203 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1308 | 37.7324 | -121.7123 | No | Clear;32-90 F |  |  | 23-0086267 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1853528 | 0 | EPSS Ckt | Y | 2023 | A-B PHASE ABOVE MTT
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | TRANSFORMER | 315415943156 | 20230627 | 1717 | 20230627 | 2015 | 2147240 | 178 | Transformer only | Unknown Cause | Patrol - not conducted | 14 | 2492 | 37.6745 | -122.085 | No | Partly Cloudy;32-90 F |  |  | 23-0086291 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1853534 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 70967 | 20230627 | 2346 | 20230628 | 149 | 2147381 | 123 | Distribution Circuit | Animal | Bird found | 6 | 738 | 37.6555 | -121.8207 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0086356 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1853587 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | 560528 | 20230628 | 2204 | 20230628 | 2252 | 2148498 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1893 | 84239 | 37.6973 | -122.0469 | No | Partly Cloudy;32-90 F |  |  | 23-0086893 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1853889 | 0 | EPSS Ckt | Y | 2023 | SGF
MISSION | MISSION | VINEYARD-2110 | 14502110 | TRANSFORMER | 316171044839 | 20230629 | 1740 | 20230630 | 213 | 2149200 | 513 | Transformer only | Environmental/External | Flood/Erosion | 1 | 513 | 37.724 | -121.8251 | No | Clear;Above 90 | Transformer | Failed/Faulted | 23-0087346 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1854153 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | OCB | 2107/2 | 20230629 | 2052 | 20230630 | 510 | 2149373 | 498 | Distribution Circuit | Equipment Failure/Involved | Underground | 4240 | 382164 | 37.7009 | -121.7335 | No | Clear;32-90 F | Elbow | Burned/flashed | 23-0087368 | UG | Sus | 45864959 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1854177 | 0 | EPSS Ckt | N | 2023 | GRD T GRD OC
MISSION | MISSION | SAN RAMON-2102 | 14232102 | FUSE | 35110 | 20230629 | 2202 | 20230630 | 307 | 2149410 | 305 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 413 | 37.6956 | -121.8942 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0087424 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1854226 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | TRANSFORMER | 315580445338 | 20230630 | 1603 | 20230630 | 1724 | 2150088 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 243 | 37.7351 | -122.0296 | No | Clear;Above 90 | Fuse | Burned Open | 23-0087759 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1854428 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 884904 | 20230630 | 1952 | 20230701 | 1058 | 2150305 | 906 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 184 | 166704 | 37.752 | -121.7699 | No | Clear;32-90 F |  |  | 23-0087790 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1854455 | 0 | EPSS Ckt | Y | 2023 | b & C PHASE OC
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | 560528 | 20230630 | 2051 | 20230630 | 2235 | 2150371 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1893 | 196872 | 37.6973 | -122.0469 | No | Clear;32-90 F |  |  | 23-0087804 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1854466 | 0 | EPSS Ckt | Y | 2023 | no phase oc/sgf
MISSION | MISSION | LIVERMORE-1103 | 12141103 | FUSE | 12294 | 20230701 | 700 | 20230701 | 750 | 2150602 | 50 | Distribution Circuit | Animal | Squirrel | 28 | 1400 | 37.679 | -121.7723 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0087855 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854538 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | 315609238878 | 20230701 | 958 | 20230701 | 1154 | 2150706 | 116 | Transformer only | Vegetation | Tree - grew into line | 12 | 1392 | 37.5579 | -122.0158 | No | Clear;32-90 F | Transformer | Normal | 23-0087904 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854574 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2114 | 14232114 | SWITCH | 5264 | 20230701 | 1149 | 20230701 | 1156 | 2150777 | 7 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 7 | 37.6931 | -121.8931 | No | Clear;Above 90 | Conductor- Underground | Broken | 23-0087424 | UG | Sus | 31653913 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1854578 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2104 | 14502104 | FUSE | 35094 | 20230701 | 1802 | 20230701 | 2232 | 2151149 | 270 | Distribution Circuit | Equipment Failure/Involved | Underground | 151 | 30619 | 37.6842 | -121.8709 | No | Clear;Above 90 | Elbow | Burned/flashed | 23-0087992 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854636 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2110 | 14232110 | FUSE | 20229 | 20230701 | 1838 | 20230702 | 218 | 2151193 | 460 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 23920 | 37.7581 | -121.9466 | No | Clear;Above 90 | Conductor- Underground | Broken | 23-0088088 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854727 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2114 | 14232114 | SWITCH | 5264 | 20230701 | 1920 | 20230701 | 1929 | 2151324 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 9 | 37.6931 | -121.8931 | No | Clear;Above 90 | Conductor- Underground | Broken | 23-0087424 | UG | Sus | 31653913 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1854641 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | TASSAJARA-2113 | 14662113 | OCB | 2113/2 | 20230701 | 1957 | 20230702 | 817 | 2151542 | 740 | Distribution Circuit | Equipment Failure/Involved | Underground | 5777 | 975208 | 37.8002 | -121.9078 | No | Clear;32-90 F | Switch (UG) | Broken | 23-0088026 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854668 | 0 | EPSS Ckt | N | 2023 | TARGETS
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 605520 | 20230701 | 2012 | 20230702 | 1618 | 2151499 | 1206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 35277 | 37.575 | -121.8795 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0088018 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854661 | 0 | EPSS Ckt | Y | 2023 | AB GRD INST PHASE OC
MISSION | MISSION | SAN RAMON-2111 | 14232111 | INTERRUPTER | 90810 | 20230701 | 2058 | 20230702 | 721 | 2151540 | 547 | Distribution Circuit | Equipment Failure/Involved | Overhead | 137 | 75211 | 37.7039 | -121.9129 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0088097 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854735 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | SWITCH | 630224 | 20230702 | 944 | 20230702 | 1830 | 2151975 | 526 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 32612 | 37.7886 | -121.77 | No | Clear;32-90 F |  |  | 23-0088175 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1854803 | 0 | EPSS Ckt | Y | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | TRANSFORMER | 25178 | 20230702 | 1027 | 20230703 | 237 | 2151998 | 970 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 3410 | 37.7024 | -121.9332 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0088166 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854796 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1108 | 14351108 | SWITCH | 1341 | 20230702 | 1225 | 20230702 | 1325 | 2151985 | 60 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 3240 | 37.5434 | -121.9749 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0088161 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1854790 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 20383 | 20230702 | 1405 | 20230702 | 1616 | 2152146 | 131 | Distribution Circuit | Vegetation | Other ground vegetation | 133 | 17423 | 37.6702 | -121.8916 | No | Clear;Above 90 | Pothead/Riser Termination | Failed/Faulted | 23-0088192 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854818 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2105 | 14722105 | FUSE | 15021 | 20230702 | 1644 | 20230703 | 854 | 2152217 | 970 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 9054 | 37.4773 | -121.9411 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0088202 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1854825 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1108 | 14351108 | SWITCH | 1341 | 20230703 | 44 | 20230703 | 255 | 2152137 | 131 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 7074 | 37.5434 | -121.9749 | No | Clear-Heat Wave;32-90 F | Transformer (UG) | Broken | 23-0088238 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1854927 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | FUSE | 9459 | 20230703 | 819 | 20230703 | 831 | 2153072 | 12 | Distribution Circuit | Company Initiated | Operating error | 14 | 168 | 37.7109 | -121.925 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0081804 | OH | Sus | 35172231 | BAY AREA | JUL | None | 0 | No | No | No | 1854976 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | 560528 | 20230703 | 1944 | 20230703 | 2051 | 2153762 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1893 | 126831 | 37.6973 | -122.0469 | No | Clear;32-90 F |  |  | 23-0088668 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1855086 | 0 | EPSS Ckt | Y | 2023 | SGF
MISSION | MISSION | FREMONT-1110 | 14351110 | FUSE | 12582 | 20230704 | 410 | 20230704 | 440 | 2153927 | 30 | Distribution Circuit | 3rd Party | Vehicle | 84 | 2520 | 37.5335 | -121.958 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 23-0088708 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1855129 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315256843013 | 20230704 | 1145 | 20230704 | 1250 | 2154028 | 65 | Transformer only | Unknown Cause | Patrol - found nothing | 12 | 780 | 37.6698 | -122.1399 | No | Clear;32-90 F |  |  | 23-0088752 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1855160 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1111 | 13761111 | TRANSFORMER | 315373541167 | 20230704 | 1201 | 20230704 | 1730 | 2154032 | 329 | Transformer only | 3rd Party | Vehicle | 3 | 987 | 37.6199 | -122.0985 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0088757 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1855163 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | TRANSFORMER | 315888744425 | 20230704 | 2149 | 20230705 | 17 | 2154262 | 148 | Transformer only | 3rd Party | Other | 18 | 2664 | 37.7114 | -121.9224 | No | Clear;32-90 F | Secondary | Broken | 23-0088802 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1855210 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2110 | 14232110 | FUSE | 20262 | 20230705 | 1143 | 20230705 | 1152 | 2154629 | 9 | Distribution Circuit | Company Initiated | Other Circuits | 37 | 333 | 37.758 | -121.9466 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0088088 | UG | Sus | 45867500 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1855323 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2110 | 14232110 | SWITCH | 40257 | 20230705 | 1504 | 20230705 | 1525 | 2154817 | 19 | Distribution Circuit | Company Initiated | Return Circuit Normal | 89 | 1691 | 37.7569 | -121.9488 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0088088 | UG | Sus | 45867500 | BAY AREA | JUL | None | 0 | No | No | No | 1855349 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRANSFORMER | 315291842394 | 20230705 | 1548 | 20230706 | 7 | 2154830 | 499 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4491 | 37.6531 | -122.1274 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0089131 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1855360 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRANSFORMER | 315291842394 | 20230706 | 940 | 20230706 | 1014 | 2155284 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 306 | 37.6531 | -122.1274 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0089341 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1855511 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1110 | 14471110 | INTERRUPTER | 61505 | 20230707 | 900 | 20230707 | 1635 | 2156112 | 455 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 455 | 37.5506 | -122.0646 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 23-0089725 | UG | Sus | 35465965 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1855678 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 11092 | 20230707 | 1737 | 20230708 | 238 | 2156481 | 541 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 18955 | 37.6389 | -122.0838 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0089994 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1855758 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 14998 | 20230707 | 1818 | 20230707 | 1931 | 2156533 | 73 | Distribution Circuit | 3rd Party | Metallic Balloon | 842 | 61466 | 37.6298 | -122.0886 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0090023 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1855768 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | TRANSFORMER | 315367043768 | 20230708 | 207 | 20230708 | 325 | 2156891 | 78 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 546 | 37.6911 | -122.1023 | No | Overcast;32-90 F | Fuse | Broken | 23-0090051 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1855805 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | 560528 | 20230710 | 725 | 20230710 | 1131 | 2158107 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1893 | 144267 | 37.6973 | -122.0469 | No | Overcast;32-90 F |  |  | 23-0090312 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | Yes | No | No | 1856026 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD EVENT
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 8888 | 20230710 | 1201 | 20230710 | 1304 | 2158666 | 63 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 126 | 37.5137 | -122.0495 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0090480 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1856202 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 248212 | 20230710 | 1348 | 20230710 | 1725 | 2158720 | 217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 184 | 37784 | 37.7461 | -121.8719 | No | Clear;32-90 F |  |  | 23-0090528 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | Yes | No | No | 1856213 | 0 | EPSS Ckt | Y | 2023 | C- GRD TGTS
MISSION | MISSION | NEWARK 21KV-2102 | 12232102 | OCB | 2102/2 | 20230710 | 1456 | 20230711 | 728 | 2158787 | 992 | Distribution Circuit | Equipment Failure/Involved | Underground | 348 | 110842 | 37.5029 | -121.9818 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0090567 | UG | Sus | 45881754 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1856231 | 0 | Non-EPSS | N | 2023 | GRD TGT
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 8037 | 20230710 | 1638 | 20230710 | 1850 | 2158867 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 12942 | 37.714 | -122.0663 | No | Clear;32-90 F |  |  | 23-0090621 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1856245 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | TRANSFORMER | 26900 | 20230711 | 1508 | 20230712 | 540 | 2160275 | 872 | Transformer only | Equipment Failure/Involved | Underground | 1 | 872 | 37.5032 | -121.9754 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0091070 | UG | Sus | 45883250 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1856632 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | TASSAJARA-2113 | 14662113 | RECLOSER | MR276 | 20230712 | 121 | 20230712 | 537 | 2160294 | 256 | Distribution Circuit | Animal | Bird found | 542 | 138752 | 37.7625 | -121.9841 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091081 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1856637 | 0 | EPSS Ckt | Y | 2023 | B&#9578- & C
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | OTHER | J26456 TWD 57980 | 20230712 | 135 | 20230712 | 517 | 2160295 | 222 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 444 | 37.5027 | -121.9752 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0091067 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1856638 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | SWITCH | 3484 | 20230712 | 520 | 20230712 | 534 | 2160340 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 14 | 37.7009 | -121.933 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0083766 | UG | Sus | 35088384 | BAY AREA | JUL | None | 0 | No | No | No | 1856647 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 9580 | 20230712 | 2201 | 20230713 | 1245 | 2161244 | 884 | Distribution Circuit | 3rd Party | Vehicle | 225 | 75676 | 37.6314 | -122.0755 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0091575 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1856957 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315637638568 | 20230713 | 10 | 20230713 | 1710 | 2161262 | 1020 | Transformer only | Environmental/External | Flood/Erosion | 12 | 12240 | 37.5495 | -122.0059 | No | Clear;32-90 F | Transformer | Broken | 23-0091582 | OH | Sus | 45885053 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1856962 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1103 | 13501103 | FUSE | 31086 | 20230713 | 739 | 20230713 | 1024 | 2161297 | 165 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 1155 | 37.6091 | -122.0546 | No | Partly Cloudy;32-90 F | Elbow | Burned/flashed | 23-0091627 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1856984 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRANSFORMER | 315372141687 | 20230713 | 959 | 20230713 | 1453 | 2161542 | 294 | Transformer only | Vegetation | Tree - grew into line | 6 | 1764 | 37.634 | -122.0992 | No | Clear;32-90 F | Transformer (OH) |  | 23-0091940 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857212 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1103 | 13501103 | SWITCH | 1152 | 20230713 | 1154 | 20230713 | 1208 | 2161695 | 14 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 14 | 37.6102 | -122.0563 | No | Clear;32-90 F | Elbow | Burned/flashed | 23-0091627 | UG | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1857182 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1103 | 13501103 | SWITCH | 1152 | 20230713 | 1154 | 20230713 | 1512 | 2161848 | 198 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 198 | 37.6102 | -122.0563 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091627 | OH | Sus | 45885381 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1857217 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1103 | 13501103 | SWITCH | 7831 | 20230713 | 1520 | 20230713 | 1533 | 2161841 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 5 | 65 | 37.6092 | -122.0545 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091627 | OH | Sus | 45885381 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1857219 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | FUSE | 11222 | 20230713 | 2017 | 20230714 | 1223 | 2162026 | 966 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 17388 | 37.5063 | -121.9496 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0092065 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1857255 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 36400 | 20230713 | 2322 | 20230714 | 1609 | 2162071 | 1007 | Distribution Circuit | Equipment Failure/Involved | Underground | 313 | 244121 | 37.7542 | -121.9503 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0092129 | UG | Sus | 45886810 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857300 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2104 | 14232104 | SWITCH | 5289 | 20230714 | 1639 | 20230714 | 1647 | 2162844 | 8 | Distribution Circuit | Equipment Failure/Involved | Underground | 183 | 1220 | 37.7571 | -121.9536 | No | Clear;Above 90 | Conductor- Underground | Broken | 23-0092129 | UG | Sus | 45886810 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1857541 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | OCB | 1104/2 | 20230715 | 653 | 20230715 | 1506 | 2163227 | 493 | Distribution Circuit | Animal | Bird found | 5344 | 489007 | 37.6718 | -122.1596 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0092540 | OH | Sus | 31655628 | BAY AREA | JUL | Line to Ground | 0 | No | Yes | No | 1857606 | 0 | Non-EPSS | N | 2023 | A PH- GRD- TIME OC
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316442543359 | 20230715 | 745 | 20230716 | 839 | 2163942 | 1494 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 18360 | 37.6842 | -121.7305 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0092777 | OH | Sus | 45888822 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1857803 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1116 | 13111116 | RECLOSER | MR212 | 20230715 | 805 | 20230715 | 1838 | 2163269 | 633 | Distribution Circuit | Animal | Bird found | 238 | 36640 | 37.7264 | -122.1629 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0092544 | OH | Sus | 0 | BAY AREA | JUL | Multi-Fault | 0 | No | No | No | 1857627 | 0 | Non-EPSS | N | 2023 | B- C PH & GRD
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | MR190 | 20230715 | 838 | 20230715 | 1543 | 2163313 | 394 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1874 | 476410 | 37.6652 | -121.7354 | No | Clear;32-90 F |  |  | 23-0092550 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | Yes | No | No | 1857647 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
MISSION | MISSION | CAYETANO-2109 | 14422109 | OCB | 2109/2/NORM | 20230715 | 1727 | 20230716 | 546 | 2163679 | 605 | Distribution Circuit | Equipment Failure/Involved | Underground | 3150 | 641066 | 37.7383 | -121.7706 | No | Clear;Above 90 | Connector or Splice (UG) | Failed/Faulted | 23-0092683 | UG | Sus | 45888699 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857713 | 0 | EPSS Ckt | Y | 2023 | A TO GROUND
MISSION | MISSION | STATION O-0401 | 12240401 | FUSE | 651347 | 20230715 | 1827 | 20230715 | 1905 | 2163736 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 1140 | 37.6876 | -122.1031 | No | Clear;32-90 F |  |  | 23-0092702 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857724 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | 315297244747 | 20230716 | 100 | 20230716 | 1144 | 2163953 | 644 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 6440 | 37.7176 | -122.1269 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0092756 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857775 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 10007 | 20230716 | 902 | 20230716 | 1030 | 2164084 | 88 | Distribution Circuit | Animal | Squirrel | 30 | 2640 | 37.6676 | -122.0553 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0092790 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857820 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 40300 | 20230716 | 1007 | 20230716 | 1302 | 2164136 | 175 | Distribution Circuit | Equipment Failure/Involved | Underground | 110 | 18330 | 37.6859 | -121.884 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0092799 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857831 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315644038593 | 20230716 | 1032 | 20230716 | 1424 | 2164156 | 232 | Transformer only | Vegetation | Other ground vegetation | 11 | 2552 | 37.5499 | -122.004 | No | Partly Cloudy;32-90 F | Anchor or Guy | Normal | 23-0092813 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857842 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | TRANSFORMER | 316323343165 | 20230716 | 1706 | 20230716 | 1759 | 2164499 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 265 | 37.6785 | -121.7716 | No | Clear;Above 90 | Secondary | Burned Open | 23-0092884 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857907 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1101 | 12221101 | TRANSFORMER | T5459 | 20230716 | 1820 | 20230716 | 1901 | 2164532 | 41 | Transformer only | Equipment Failure/Involved | Underground | 2 | 82 | 37.526 | -121.9863 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0092900 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1857920 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | 560528 | 20230716 | 1941 | 20230717 | 1436 | 2164685 | 1135 | Distribution Circuit | 3rd Party | Kite | 1893 | 360155 | 37.6973 | -122.0469 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0092911 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1857932 | 0 | EPSS Ckt | Y | 2023 | DCD
MISSION | MISSION | MT EDEN-1107 | 13761107 | FUSE | 10213 | 20230716 | 2046 | 20230716 | 2213 | 2164778 | 87 | Distribution Circuit | Animal | Bird found | 116 | 10092 | 37.6199 | -122.0903 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0092946 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1857960 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | FUSE | 72318 | 20230717 | 455 | 20230717 | 1249 | 2165003 | 474 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 14859 | 37.718 | -121.8652 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0093028 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1858052 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1109 | 13501109 | SWITCH | MR678 | 20230717 | 548 | 20230718 | 219 | 2165004 | 1231 | Distribution Circuit | 3rd Party | Vandalism | 125 | 10623 | 37.5909 | -122.0343 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0092978 | UG | Sus | 31655786 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1857994 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 10007 | 20230717 | 921 | 20230717 | 941 | 2165276 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 600 | 37.6676 | -122.0553 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0092790 | OH | Sus | 45888785 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1858128 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | SWITCH | 1881 | 20230717 | 1103 | 20230717 | 1117 | 2165448 | 14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 420 | 37.6667 | -122.0559 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0092790 | OH | Sus | 45888785 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1858162 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 11936 | 20230717 | 1239 | 20230717 | 1726 | 2165566 | 287 | Distribution Circuit | Equipment Failure/Involved | Underground | 311 | 17425 | 37.6922 | -122.1784 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0093065 | UG | Sus | 35469327 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1858188 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | FUSE | 9459 | 20230717 | 1523 | 20230717 | 1537 | 2165752 | 14 | Distribution Circuit | Company Initiated | Operating error | 18 | 252 | 37.7109 | -121.925 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0081804 | OH | Sus | 35172231 | BAY AREA | JUL | None | 0 | No | No | No | 1858228 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315618638565 | 20230717 | 1724 | 20230718 | 215 | 2165729 | 531 | Transformer only | Unknown Cause | Patrol - found nothing | 14 | 7434 | 37.5493 | -122.0124 | No | Clear;32-90 F |  |  | 23-0093379 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1858251 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | FUSE | 14094 | 20230718 | 1753 | 20230718 | 1824 | 2167039 | 31 | Distribution Circuit | 3rd Party | Metallic Balloon | 159 | 4929 | 37.6943 | -122.1142 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0093923 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1858568 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | FUSE | 62017 | 20230719 | 828 | 20230719 | 1038 | 2167608 | 130 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 129 | 14610 | 37.5293 | -122.0198 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0094085 | UG | Sus | 31656228 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1858768 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | SWITCH | 3418 | 20230720 | 231 | 20230720 | 239 | 2168554 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 43 | 344 | 37.53 | -122.0184 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0094085 | UG | Sus | 31656228 | BAY AREA | JUL | None | 0 | No | No | No | 1858975 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | JUMPER | 2/POLES/N/OF/315605539716 | 20230720 | 844 | 20230720 | 1607 | 2168709 | 443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 14619 | 37.5822 | -122.0174 | No | Partly Cloudy;32-90 F | Pole - Tower- steel | Broken | 23-0094556 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1859039 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1105 | 14381105 | TRANSFORMER | 315213843337 | 20230720 | 1430 | 20230720 | 1725 | 2169071 | 175 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 4375 | 37.6785 | -122.1549 | No | Clear;32-90 F | Transformer | Leaking | 23-0094828 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1859150 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | WARD-0401 | 12980401 | FUSE | 11140 | 20230720 | 1809 | 20230720 | 2212 | 2169278 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 11907 | 37.7227 | -122.1457 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0094915 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1859177 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1107 | 14471107 | TRANSFORMER | 315663938879 | 20230720 | 2021 | 20230720 | 2323 | 2169360 | 182 | Transformer only | 3rd Party | Fire- house or bldg. | 10 | 1820 | 37.5581 | -121.997 | No | Clear;32-90 F | Service conductor | Broken | 23-0094944 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1859193 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | TRANSFORMER | 315383041823 | 20230720 | 2048 | 20230721 | 309 | 2169336 | 381 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 5715 | 37.6377 | -122.0956 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0094934 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1859188 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 886522 | 20230721 | 630 | 20230721 | 1338 | 2169536 | 428 | Distribution Circuit | Animal | Bird found | 153 | 61988 | 37.6634 | -121.6803 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0095014 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1859250 | 0 | EPSS Ckt | Y | 2023 | A AND C
MISSION | MISSION | FREMONT-1107 | 14351107 | FUSE | 9490 | 20230721 | 817 | 20230721 | 1015 | 2169615 | 118 | Distribution Circuit | Animal | Squirrel | 111 | 13065 | 37.547 | -121.9927 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0095155 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1859411 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 9434 | 20230721 | 1616 | 20230721 | 2025 | 2170150 | 249 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 249 | 37.703 | -122.1695 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0095388 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1859475 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | OCB | 2110/2 | 20230721 | 1808 | 20230721 | 2142 | 2170235 | 214 | Distribution Circuit | Equipment Failure/Involved | Underground | 4201 | 681594 | 37.7009 | -121.7335 | No | Clear;Above 90 | Connector or Splice (UG) | Failed/Faulted | 23-0095420 | UG | Sus | 45897325 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1859486 | 0 | EPSS Ckt | N | 2023 | B PH GRD INST
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 74181 | 20230722 | 1823 | 20230723 | 1251 | 2171087 | 1108 | Distribution Circuit | Equipment Failure/Involved | Underground | 174 | 138984 | 37.6761 | -121.8613 | No | Clear;Above 90 | Elbow | Failed/Faulted | 23-0095654 | UG | Sus | 45897603 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1859747 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | OCB | 2103/2/NORM | 20230722 | 1850 | 20230723 | 340 | 2171100 | 530 | Distribution Circuit | Equipment Failure/Involved | Underground | 4934 | 879938 | 37.7448 | -121.8576 | No | Partly Cloudy;Above 90 | Other | Burned/flashed | 23-0095600 | UG | Sus | 45897562 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1859691 | 0 | EPSS Ckt | Y | 2023 | PH/GRD INST OC
MISSION | MISSION | VINEYARD-2107 | 14502107 | OCB | 2107/2 | 20230722 | 2058 | 20230723 | 647 | 2171155 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 3559 | 1338247 | 37.6697 | -121.8543 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0095619 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | Yes | No | 1859709 | 0 | EPSS Ckt | Y | 2023 | PH GRD- BU RLY
MISSION | MISSION | VINEYARD-2110 | 14502110 | OCB | 2110/2 | 20230722 | 2236 | 20230723 | 441 | 2171249 | 365 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6914 | 2523610 | 37.6697 | -121.8542 | No | Partly Cloudy;32-90 F |  |  | 23-0095640 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1859728 | 0 | EPSS Ckt | Y | 2023 | OC & GRD
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 74181 | 20230723 | 1338 | 20230723 | 1822 | 2171525 | 284 | Distribution Circuit | Equipment Failure/Involved | Underground | 174 | 24775 | 37.6761 | -121.8613 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0095698 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1859796 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 10453 | 20230724 | 828 | 20230726 | 1639 | 2172223 | 3049 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 3371 | 37.631 | -122.0684 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0096063 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1860087 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 39468 | 20230724 | 904 | 20230724 | 1332 | 2172301 | 268 | Distribution Circuit | Company Initiated | Dig in- company | 73 | 16415 | 37.6307 | -122.0484 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0095954 | UG | Sus | 31656610 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1860051 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 9828 | 20230724 | 924 | 20230724 | 1031 | 2172334 | 67 | Distribution Circuit | 3rd Party | Metallic Balloon | 330 | 22110 | 37.6107 | -122.0254 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0095903 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1860017 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | TRANSFORMER | 315888744425 | 20230725 | 1237 | 20230725 | 1254 | 2173543 | 17 | Transformer only | Company Initiated | Personnel- company | 18 | 306 | 37.7114 | -121.9224 | No | Clear;32-90 F |  |  | 23-0096547 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1860400 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | JUMPER | SMITHWHICK OPENED JUMPERS, FOR TAPELINE | 20230726 | 807 | 20230726 | 847 | 2174185 | 40 | Distribution Circuit | Company Initiated | Personnel- company | 34 | 1360 | 37.5137 | -121.9485 | No | Partly Cloudy;32-90 F |  |  | 23-0096919 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1860604 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 9473 | 20230726 | 1024 | 20230726 | 1339 | 2174320 | 195 | Distribution Circuit | Animal | Bird found | 72 | 13864 | 37.7864 | -121.8632 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0096988 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1860666 | 0 | EPSS Ckt | Y | 2023 | A PH
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 134120 | 20230726 | 1024 | 20230726 | 1455 | -2174331 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 14705 | 37.7899 | -121.8435 | No | Clear;32-90 F |  |  | 23-0096988 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1860717 | 0 | EPSS Ckt | N | 2023 | 50 INST
MISSION | MISSION | VINEYARD-2109 | 14502109 | SWITCH | 5433 | 20230727 | 1159 | 20230727 | 1207 | 2175455 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 110 | 328 | 37.6864 | -121.8785 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0092799 | UG | Sus | 45888886 | BAY AREA | JUL | None | 0 | No | No | No | 1860999 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | 315289544633 | 20230728 | 2131 | 20230729 | 37 | 2176822 | 186 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2418 | 37.7145 | -122.1296 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0098231 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1861352 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | RADUM-1105 | 13151105 | JUMPER | OJ AT TV212 | 20230729 | 2134 | 20230730 | 1428 | 2177428 | 1014 | Distribution Circuit | Equipment Failure/Involved | Overhead | 985 | 810310 | 37.636 | -121.8903 | No | Clear;32-90 F | Jumper | Broken | 23-0098409 | OH | Sus | 0 | BAY AREA | JUL | Open Circuit | 0 | No | No | No | 1861545 | 0 | EPSS Ckt | Y | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | SWITCH | 50651 | 20230730 | 1848 | 20230731 | 634 | 2177945 | 706 | Distribution Circuit | 3rd Party | Vehicle | 14 | 9308 | 37.6651 | -121.7101 | No | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0098488 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | Yes | No | 1861627 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | TRANSFORMER | 27896 | 20230730 | 1916 | 20230731 | 331 | 2177958 | 495 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 6612 | 37.6766 | -122.0556 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0098492 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1861630 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | TRANSFORMER | 315422643960 | 20230731 | 1304 | 20230731 | 2007 | 2178585 | 423 | Transformer only | Equipment Failure/Involved | Overhead | 36 | 15228 | 37.6967 | -122.0832 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0098752 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1861861 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | RECLOSER | MR310 | 20230731 | 1310 | 20230801 | 1042 | 2178545 | 564 | Distribution Circuit | Equipment Failure/Involved | Underground | 2327 | 493538 | 37.6784 | -121.7702 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0098728 | UG | Sus | 35473944 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1861855 | 0 | Non-EPSS | N | 2023 | A PHASE GRD
MISSION | MISSION | VINEYARD-2108 | 14502108 | TRANSFORMER | 21967 | 20230731 | 1331 | 20230801 | 309 | 2178607 | 818 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 4048 | 37.645 | -121.9013 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0098885 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1861912 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | MR190 | 20230731 | 1438 | 20230731 | 1448 | 2179066 | 10 | Distribution Circuit | Equipment Failure/Involved | Underground | 1874 | 18600 | 37.6652 | -121.7354 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0098728 | UG | Sus | 35473944 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1861939 | 0 | EPSS Ckt | N | 2023 | C GRD
MISSION | MISSION | VINEYARD-2104 | 14502104 | FUSE | 46705 | 20230801 | 44 | 20230801 | 2004 | 2179059 | 1160 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 8120 | 37.6717 | -121.8437 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0098987 | UG | Sus | 31657750 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1862073 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 74380 | 20230801 | 750 | 20230802 | 228 | 2179175 | 588 | Distribution Circuit | Equipment Failure/Involved | Underground | 3057 | 162489 | 37.6892 | -121.7419 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0099079 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1862135 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | TRANSFORMER | 316433944459 | 20230802 | 236 | 20230802 | 1540 | 2180066 | 784 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 6272 | 37.7145 | -121.7339 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0099430 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1862294 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CAYETANO-2111 | 14422111 | OCB | 2111/2/NORM | 20230802 | 339 | 20230802 | 624 | 2180081 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2088 | 271789 | 37.7383 | -121.7706 | No | Overcast;32-90 F |  |  | 23-0099392 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1862268 | 0 | EPSS Ckt | Y | 2023 | OR GRD & BU OC RLY
MISSION | MISSION | LAS POSITAS-2103 | 14402103 | RECLOSER | MR444 | 20230802 | 339 | 20230802 | 1509 | 2180139 | 690 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 2070 | 37.7111 | -121.8037 | No | Partly Cloudy;32-90 F |  |  | 23-0099399 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | Yes | No | No | 1862276 | 0 | Non-EPSS | Y | 2023 | B PHASE- 50 INST
MISSION | MISSION | MT EDEN-1104 | 13761104 | TRANSFORMER | 11404 | 20230802 | 654 | 20230802 | 1344 | 2180149 | 410 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1230 | 37.6153 | -122.0552 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0099508 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1862439 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | TRANSFORMER | 315459541340 | 20230802 | 941 | 20230802 | 1257 | 2180382 | 196 | Transformer only | 3rd Party | Metallic Balloon | 10 | 1960 | 37.625 | -122.0688 | No | Partly Cloudy;32-90 F | Transformer | Normal | 23-0099548 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1862462 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | 315777837310 | 20230802 | 1031 | 20230802 | 1911 | 2180497 | 520 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3640 | 37.5156 | -121.9568 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0099527 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1862454 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | SWITCH | 51017 | 20230802 | 1141 | 20230802 | 1157 | 2180688 | 16 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 1152 | 37.6155 | -122.0552 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0099476 | UG | Sus | 35474334 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1862496 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1102 | 14471102 | FUSE | 6102 | 20230802 | 1945 | 20230803 | 517 | 2180981 | 389 | Distribution Circuit | Equipment Failure/Involved | Underground | 71 | 40057 | 37.5651 | -122.0299 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0099825 | UG | Sus | 35474477 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1862584 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2110 | 14232110 | FUSE | 35139 | 20230803 | 10 | 20230803 | 327 | 2181074 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 189 | 32165 | 37.7642 | -121.9492 | No | Partly Cloudy;32-90 F |  |  | 23-0099877 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1862592 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315244142906 | 20230803 | 147 | 20230803 | 323 | 2181078 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 1536 | 37.6668 | -122.1443 | No | Overcast;32-90 F | Transformer | Normal | 23-0099876 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1862591 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1105 | 14381105 | FUSE | 10726 | 20230803 | 627 | 20230803 | 859 | 2181126 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 154 | 23408 | 37.6848 | -122.1431 | No | Overcast;32-90 F |  |  | 23-0099959 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1862668 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2110 | 14232110 | TRANSFORMER | 18004 | 20230803 | 1446 | 20230804 | 107 | 2181918 | 621 | Distribution Circuit | Equipment Failure/Involved | Underground | 161 | 3285 | 37.769 | -121.9492 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0100206 | UG | Sus | 0 | BAY AREA | AUG | None | 0 | No | No | No | 1862878 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1102 | 14471102 | SWITCH | 6282 | 20230803 | 2215 | 20230803 | 2251 | 2182010 | 36 | Distribution Circuit | Company Initiated | Return Circuit Normal | 71 | 2481 | 37.5644 | -122.0286 | No | Overcast;32-90 F | Conductor- Underground | Normal | 23-0099825 | UG | Sus | 35474477 | BAY AREA | AUG | None | 0 | No | No | No | 1862920 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1103 | 14471103 | FUSE | 9047 | 20230804 | 1941 | 20230805 | 946 | 2182742 | 845 | Distribution Circuit | Equipment Failure/Involved | Underground | 213 | 170427 | 37.5822 | -122.055 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0100805 | UG | Sus | 45912113 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1863185 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2103 | 14232103 | OTHER | J72002 TWD 25964 | 20230804 | 2033 | 20230804 | 2347 | 2182759 | 194 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 388 | 37.7058 | -121.9099 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0100728 | UG | Sus | 35474856 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1863186 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 11658 | 20230805 | 2026 | 20230806 | 518 | 2183370 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3724 | 37.5314 | -121.9183 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0100952 | OH | Sus | 45913580 | BAY AREA | AUG | Line to Line | 0 | No | Yes | No | 1863352 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | TRANSFORMER | 315150843834 | 20230806 | 901 | 20230806 | 1116 | 2183542 | 135 | Transformer only | Equipment Failure/Involved | Underground | 16 | 2160 | 37.692 | -122.1771 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0100990 | UG | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1863396 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 10383 | 20230806 | 1417 | 20230806 | 2031 | 2183665 | 374 | Distribution Circuit | Equipment Failure/Involved | Underground | 187 | 69105 | 37.5378 | -122.0598 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0101025 | UG | Sus | 45914708 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1863428 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | TRANSFORMER | 315580445338 | 20230806 | 1826 | 20230806 | 2156 | 2183772 | 210 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 630 | 37.7351 | -122.0296 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0101053 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1863451 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 11799 | 20230807 | 28 | 20230807 | 648 | 2183919 | 380 | Distribution Circuit | Equipment Failure/Involved | Underground | 182 | 64128 | 37.6718 | -121.8805 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0101084 | UG | Sus | 45915280 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1863483 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2102 | 14232102 | OCB | 2102/2 | 20230807 | 244 | 20230808 | 2049 | 2183956 | 2525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4877 | 500563 | 37.7449 | -121.9369 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0101091 | OH | Sus | 31662143 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1863491 | 0 | EPSS Ckt | N | 2023 | A - B - & C
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 9775 | 20230807 | 842 | 20230807 | 953 | 2184201 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1421 | 37.626 | -122.0521 | No | Clear;32-90 F |  |  | 23-0101184 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1863652 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | RECLOSER | MR172 | 20230807 | 1234 | 20230807 | 1357 | 2184626 | 83 | Distribution Circuit | Company Initiated | Coordination failure | 3046 | 128242 | 37.657 | -121.9009 | No | Clear;Above 90 | Recloser | Normal | 23-0101267 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1863708 | 0 | EPSS Ckt | Y | 2023 | B & GRD
MISSION | MISSION | JARVIS-1110 | 13501110 | FUSE | 11676 | 20230807 | 1236 | 20230807 | 1436 | 2184628 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3000 | 37.5802 | -121.9885 | No | Clear;32-90 F |  |  | 23-0101341 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1863745 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 8026 | 20230807 | 1506 | 20230807 | 2336 | 2184815 | 478 | Distribution Circuit | Equipment Failure/Involved | Underground | 69 | 6210 | 37.6629 | -121.8791 | No | Clear;Above 90 | Conductor- Underground | Burned/flashed | 23-0101364 | UG | Sus | 45916405 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1863752 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | FUSE | 51342 | 20230808 | 2027 | 20230809 | 854 | 2186140 | 747 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 2241 | 37.6529 | -122.0074 | No | Clear;32-90 F |  |  | 23-0101953 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1864121 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1115 | 13111115 | TRANSFORMER | 315173044280 | 20230809 | 841 | 20230809 | 921 | 2186414 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 200 | 37.7042 | -122.1697 | No | Overcast;32-90 F | Fuse | Broken | 23-0102071 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1864317 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 14229 | 20230809 | 1108 | 20230809 | 1338 | 2186623 | 150 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 300 | 37.7396 | -122.0255 | No | Clear;32-90 F | Secondary | Together | 23-0102130 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1864346 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | RECLOSER | MR172 | 20230809 | 1730 | 20230810 | 1345 | 2186962 | 1215 | Distribution Circuit | Equipment Failure/Involved | Underground | 3046 | 708783 | 37.657 | -121.9009 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0102379 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | Yes | No | No | 1864413 | 0 | EPSS Ckt | Y | 2023 | B PH- GRD TGTS
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 11428 | 20230810 | 1259 | 20230810 | 1628 | 2187845 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 323 | 67610 | 37.5624 | -121.9895 | No | Partly Cloudy;32-90 F |  |  | 23-0102867 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1864729 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | JUMPER | 9558 HIGH SIDE JUMPERS | 20230810 | 1723 | 20230811 | 145 | 2188123 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 502 | 37.535 | -122.0437 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0103043 | OH | Sus | 31662831 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1864809 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | FUSE | 8160 | 20230811 | 817 | 20230811 | 907 | 2188384 | 50 | Distribution Circuit | Animal | Squirrel | 38 | 1900 | 37.5481 | -122.003 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0103147 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1864902 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 10993 | 20230811 | 1631 | 20230812 | 557 | 2188977 | 806 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 12250 | 37.6547 | -121.8697 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0103501 | UG | Sus | 35480342 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1865112 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | TRANSFORMER | 315232344145 | 20230812 | 1326 | 20230812 | 1346 | 2189221 | 20 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 220 | 37.7009 | -122.149 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0103620 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1865223 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRIP-SAVER | 9473 | 20230812 | 1552 | 20230812 | 1744 | 2189316 | 112 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 8064 | 37.7864 | -121.8632 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0103661 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1865248 | 0 | EPSS Ckt | Y | 2023 | NO TGTS
MISSION | MISSION | LAS POSITAS-2106 | 14402106 | FUSE | 13196 | 20230812 | 2338 | 20230813 | 345 | 2189461 | 247 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 166 | 41002 | 37.6828 | -121.7421 | No | Clear;32-90 F |  |  | 23-0103699 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1865298 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | MR190 | 20230812 | 2338 | 20230813 | 642 | 2189454 | 424 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1874 | 702058 | 37.6652 | -121.7354 | No | Partly Cloudy;32-90 F |  |  | 23-0103696 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | Yes | No | No | 1865289 | 0 | EPSS Ckt | Y | 2023 | A PHASE GRD
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | TRANSFORMER | 22893 | 20230813 | 242 | 20230813 | 539 | 2189488 | 177 | Transformer only | 3rd Party | Fire- house or bldg. | 4 | 708 | 37.5063 | -121.9397 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0103706 | UG | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1865302 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 61788 | 20230813 | 1901 | 20230814 | 1327 | 2189755 | 638 | Distribution Circuit | Equipment Failure/Involved | Underground | 251 | 200822 | 37.5504 | -121.9412 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0103795 | UG | Sus | 45924859 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1865375 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2118 | 14232118 | SWITCH | 80132SW | 20230814 | 1826 | 20230815 | 211 | 2190846 | 465 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 930 | 37.6943 | -121.9095 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0104051 | UG | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1865669 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2101 | 14232101 | FUSE | 73998 | 20230814 | 2239 | 20230815 | 720 | 2191167 | 521 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 11312 | 37.7617 | -121.887 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0104315 | UG | Sus | 35480881 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1865720 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON 2117 | 14232117 | TRANSFORMER | 27642 | 20230814 | 2240 | 20230815 | 1149 | 2191168 | 789 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 12057 | 37.713 | -121.8734 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0104319 | UG | Sus | 35480882 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1865724 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 12KV-1101 | 12221101 | TRANSFORMER | T9396 | 20230815 | 1637 | 20230815 | 1743 | 2192014 | 66 | Transformer only | Equipment Failure/Involved | Underground | 1 | 66 | 37.526 | -121.9864 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0104778 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1865981 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | FUSE | 403369 | 20230815 | 2104 | 20230816 | 1009 | 2192271 | 785 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 15830 | 37.6753 | -122.032 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0104831 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | Yes | No | 1866019 | 0 | EPSS Ckt | Y | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | MR243 | 20230816 | 1416 | 20230817 | 224 | 2193005 | 728 | Distribution Circuit | 3rd Party | Vehicle | 393 | 58639 | 37.7022 | -122.0452 | No | Clear;32-90 F | Pole-Wood | On Ground | 23-0105148 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1866286 | 0 | EPSS Ckt | N | 2023 | A- C PHASE
MISSION | MISSION | CAYETANO-2111 | 14422111 | OCB | 2111/2/NORM | 20230816 | 1702 | 20230817 | 401 | 2193157 | 430 | Distribution Circuit | Equipment Failure/Involved | Underground | 2088 | 802183 | 37.7383 | -121.7706 | No | Partly Cloudy;Above 90 | Switch (UG) | Failed/Faulted | 23-0105266 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1866320 | 0 | EPSS Ckt | Y | 2023 | B/U TGT- B PHASE TGT
MISSION | MISSION | NORTH DUBLIN-2101 | 14052101 | OTHER | J71422 TWD 25722 | 20230816 | 2023 | 20230816 | 2228 | 2193312 | 125 | Distribution Circuit | Equipment Failure/Involved | Underground | 101 | 12625 | 37.7081 | -121.8821 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0105230 | UG | Sus | 35481396 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1866355 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1112 | 13111112 | TRANSFORMER | 315235644811 | 20230817 | 1020 | 20230817 | 1330 | 2193654 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1710 | 37.7191 | -122.1483 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0105509 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1866519 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1112 | 13761112 | FUSE | 10627 | 20230818 | 745 | 20230818 | 1103 | 2194492 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 188 | 17589 | 37.6379 | -122.0984 | No | Overcast;32-90 F |  |  | 23-0105941 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1866742 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 72822 | 20230818 | 1319 | 20230818 | 1423 | 2194954 | 64 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 299 | 19136 | 37.6389 | -122.0563 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106167 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1866892 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2106 | 14402106 | TRANSFORMER | 20079 | 20230818 | 1353 | 20230818 | 1413 | 2194981 | 20 | Transformer only | Equipment Failure/Involved | Underground | 10 | 200 | 37.6876 | -121.7525 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0106155 | UG | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1866887 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1108 | 14471108 | FUSE | 62578 | 20230819 | 851 | 20230819 | 1256 | 2195530 | 245 | Distribution Circuit | Equipment Failure/Involved | Underground | 1235 | 36039 | 37.5708 | -122.0714 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0106337 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867036 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | OTHER | J30512 TWD 20672 | 20230819 | 1750 | 20230819 | 1817 | 2195981 | 27 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 1458 | 37.5515 | -121.9383 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0103795 | UG | Sus | 45924859 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867110 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRANSFORMER | 316172546375 | 20230820 | 625 | 20230820 | 723 | 2196734 | 58 | Transformer only | 3rd Party | Vehicle | 2 | 116 | 37.7661 | -121.8253 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0106583 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867258 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | TRANSFORMER | 70890 | 20230820 | 1515 | 20230821 | 335 | 2197113 | 740 | Distribution Circuit | Equipment Failure/Involved | Underground | 141 | 44600 | 37.6938 | -121.778 | No | Partly Cloudy;Above 90 | Conductor- Underground | Burned/flashed | 23-0106702 | UG | Sus | 31664018 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867352 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | RECLOSER | 343456 | 20230820 | 2052 | 20230821 | 935 | 2197358 | 763 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1852 | 418314 | 37.7103 | -122.0738 | No | Overcast;32-90 F |  |  | 23-0106757 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1867405 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE OC
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | TRANSFORMER | T7192 | 20230821 | 841 | 20230821 | 1740 | 2197618 | 539 | Distribution Circuit | Equipment Failure/Involved | Underground | 100 | 9610 | 37.6919 | -121.7682 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0106868 | UG | Sus | 0 | BAY AREA | AUG | Open Circuit | 0 | No | No | No | 1867525 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | BANCROFT-0402 | 13030402 | FUSE | 50705 | 20230821 | 851 | 20230821 | 1052 | 2197736 | 121 | Distribution Circuit | Animal | Bird found | 11 | 1370 | 37.7346 | -122.1416 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0106985 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867627 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | BANCROFT-0402 | 13030402 | TRANSFORMER | 315257945407 | 20230821 | 1437 | 20230821 | 1650 | 2198079 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 398 | 37.7356 | -122.141 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 23-0107148 | OH | Sus | 31663896 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1867704 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | TASSAJARA-2113 | 14662113 | TRANSFORMER | 18206 | 20230821 | 1719 | 20230822 | 52 | 2198589 | 453 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 5588 | 37.7892 | -121.9467 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0107259 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867762 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | TRANSFORMER | 315388841892 | 20230821 | 2025 | 20230822 | 15 | 2198232 | 230 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 3450 | 37.6397 | -122.0937 | No | Overcast;32-90 F | Service conductor | Broken | 23-0107218 | OH | Sus | 31664344 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867735 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 7733 | 20230821 | 2034 | 20230822 | 836 | 2198692 | 722 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 12996 | 37.6426 | -122.0815 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0107292 | UG | Sus | 45935798 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867792 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | FUSE | 91439 | 20230821 | 2207 | 20230822 | 15 | 2198699 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1920 | 37.6394 | -122.0937 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0107294 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1867793 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | TRANSFORMER | 315413544359 | 20230822 | 1008 | 20230822 | 1126 | 2199161 | 78 | Transformer only | Vegetation | Tree - branch fell on line | 15 | 1170 | 37.7075 | -122.0865 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0107553 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1868021 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | 100000106353 | 20230822 | 1227 | 20230822 | 1320 | 2199341 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 424 | 37.6845 | -122.0872 | No | Clear;32-90 F | Secondary | Broken | 23-0107574 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1868030 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1112 | 13111112 | FUSE | 14502 | 20230822 | 1428 | 20230822 | 1533 | 2199455 | 65 | Distribution Circuit | 3rd Party | Metallic Balloon | 9 | 585 | 37.7142 | -122.1637 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0107715 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1868064 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | 315413543535 | 20230822 | 1429 | 20230822 | 1518 | 2199436 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 441 | 37.6849 | -122.086 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0107628 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1868054 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | 315286145105 | 20230823 | 1256 | 20230823 | 1315 | 2200217 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 228 | 37.7274 | -122.1311 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0108127 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1868363 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | 315302243364 | 20230823 | 2203 | 20230824 | 445 | 2200739 | 402 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 6432 | 37.6797 | -122.1244 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0108388 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1868477 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 14232 | 20230824 | 1048 | 20230824 | 1116 | 2201174 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 196 | 37.7341 | -122.0305 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0108520 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1868647 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 9803 | 20230824 | 1823 | 20230825 | 147 | 2201632 | 444 | Distribution Circuit | Animal | Bird found | 264 | 117216 | 37.617 | -122.042 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0108809 | OH | Sus | 31664685 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1868778 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | 315282243498 | 20230825 | 1017 | 20230825 | 1218 | 2202112 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1452 | 37.6833 | -122.1314 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0109044 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1869010 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | TRANSFORMER | 315153144591 | 20230825 | 1102 | 20230828 | 804 | 2202149 | 4142 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 12426 | 37.7127 | -122.1768 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109236 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869073 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 11687 | 20230825 | 1235 | 20230826 | 539 | 2202233 | 591 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 14645 | 37.5351 | -121.9203 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0109210 | UG | Sus | 45941338 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869067 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | FUSE | 73938 | 20230825 | 1307 | 20230825 | 1437 | 2202258 | 90 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 2878 | 37.7139 | -121.8642 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0109024 | UG | Sus | 35483938 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1869061 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | FUSE | 7899 | 20230825 | 1406 | 20230825 | 1600 | 2202296 | 114 | Distribution Circuit | 3rd Party | Metallic Balloon | 383 | 43662 | 37.6741 | -122.0699 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0109266 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1869083 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | TRANSFORMER | 315107244962 | 20230825 | 2326 | 20230826 | 930 | 2202596 | 604 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 1208 | 37.7227 | -122.1929 | No | Partly Cloudy;32-90 F |  |  | 23-0109371 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869195 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2106 | 14402106 | TRANSFORMER | 316385943395 | 20230826 | 1934 | 20230826 | 2112 | 2203000 | 98 | Transformer only | 3rd Party | Vandalism | 15 | 1470 | 37.685 | -121.7501 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0109452 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1869259 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LIVERMORE-1102 | 12141102 | FUSE | 7767 | 20230827 | 816 | 20230827 | 924 | 2203236 | 68 | Distribution Circuit | Vegetation | Tree - fell into line | 260 | 17689 | 37.6745 | -121.7802 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109492 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869313 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | LIVERMORE-1102 | 12141102 | FUSE | 7767 | 20230827 | 925 | 20230827 | 1036 | 2203272 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 390 | 24738 | 37.6745 | -121.7802 | No | Clear;32-90 F |  |  | 23-0109500 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869322 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2101 | 14052101 | FUSE | 74532 | 20230828 | 237 | 20230828 | 1548 | 2203562 | 791 | Distribution Circuit | 3rd Party | Vehicle | 151 | 118430 | 37.7445 | -121.889 | No | Clear;32-90 F | Switch (UG) | Broken | 23-0109592 | UG | Sus | 35484285 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869383 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | TRANSFORMER | 315153144591 | 20230828 | 926 | 20230828 | 1228 | 2204423 | 182 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 546 | 37.7127 | -122.1768 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0109948 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869655 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2105 | 14502105 | FUSE | 40218 | 20230828 | 1800 | 20230828 | 1955 | 2204412 | 115 | Distribution Circuit | Equipment Failure/Involved | Underground | 53 | 5651 | 37.6783 | -121.9031 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0109949 | UG | Sus | 45943345 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869656 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 11837 | 20230829 | 836 | 20230829 | 1700 | 2204740 | 504 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1008 | 37.6782 | -121.7725 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0110113 | UG | Sus | 45944889 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869862 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | TRANSFORMER | 315477741351 | 20230829 | 838 | 20230829 | 1002 | 2204854 | 84 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 924 | 37.6254 | -122.0627 | No | Clear;32-90 F |  |  | 23-0110143 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869883 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1107 | 14471107 | SWITCH | 62492 | 20230829 | 907 | 20230829 | 1124 | 2204806 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 104 | 14248 | 37.5563 | -122.0037 | No | Clear;32-90 F |  |  | 23-0110178 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869900 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2103 | 14402103 | TRANSFORMER | 30621 | 20230829 | 1208 | 20230830 | 230 | 2205133 | 862 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 862 | 37.6829 | -121.8068 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0110424 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1869984 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | TRANSFORMER | T6300 | 20230829 | 1525 | 20230829 | 1810 | 2205257 | 165 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 165 | 37.7099 | -122.1858 | No | Clear;32-90 F |  |  | 23-0110454 | OH | Sus | 0 | BAY AREA | AUG | None | 0 | No | No | No | 1869989 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | JUMPER | 12KV JUMPERS @IFO 5489 VALPEY PARK AVE. | 20230829 | 2235 | 20230830 | 307 | 2205462 | 272 | Distribution Circuit | Vegetation | Tree - grew into line | 40 | 10880 | 37.5198 | -121.9765 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0110480 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1870007 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2108 | 14232108 | RECLOSER | 53732 | 20230830 | 1009 | 20230830 | 2107 | 2205841 | 658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 50860 | 37.7758 | -121.9974 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0110669 | OH | Sus | 31666263 | BAY AREA | AUG | Line to Line | 0 | No | Yes | No | 1870190 | 0 | EPSS Ckt | Y | 2023 | B & C
MISSION | MISSION | LIVERMORE-1103 | 12141103 | FUSE | 6688 | 20230831 | 1307 | 20230831 | 1624 | 2207132 | 197 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 3940 | 37.6777 | -121.7398 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0111384 | UG | Sus | 45947805 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1870598 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 11721 | 20230831 | 1440 | 20230831 | 1936 | 2207210 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 174 | 51504 | 37.6311 | -122.074 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0111423 | OH | Sus | 31665958 | BAY AREA | AUG | Line to Ground | 0 | No | Yes | No | 1870605 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2102 | 14232102 | SWITCH | 74250 | 20230831 | 1805 | 20230901 | 0 | 2207274 | 355 | Distribution Circuit | 3rd Party | Vehicle | 71 | 25205 | 37.7635 | -121.919 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0111522 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1870619 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315569240815 | 20230831 | 1929 | 20230901 | 302 | 2207364 | 453 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 10419 | 37.611 | -122.0305 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0111530 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1870629 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1102 | 14381102 | TRANSFORMER | 315313242235 | 20230901 | 1554 | 20230901 | 2350 | 2207974 | 476 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4760 | 37.6488 | -122.12 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111961 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1870840 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 10978 | 20230903 | 813 | 20230903 | 1010 | 2209061 | 117 | Distribution Circuit | Animal | Squirrel | 1 | 117 | 37.6844 | -121.7715 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0112230 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1871041 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315766137809 | 20230903 | 920 | 20230903 | 1105 | 2209039 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 2100 | 37.5292 | -121.9612 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0112218 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1871029 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1102 | 13761102 | OCB | 1102/2 | 20230906 | 1228 | 20230907 | 921 | 2210946 | 1253 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 3759 | 37.6319 | -122.1024 | No | Clear;32-90 F | Transformer (OH) | Arcing | 23-0113163 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1871633 | 0 | Non-EPSS | N | 2023 | N/A
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 11322 | 20230908 | 904 | 20230908 | 1005 | 2212562 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 3355 | 37.6369 | -122.0839 | No | Clear;32-90 F |  |  | 23-0114075 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1872141 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRANSFORMER | 316078246744 | 20230909 | 935 | 20230909 | 1050 | 2213560 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 75 | 37.7761 | -121.8571 | Yes | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0114415 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1872359 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | TRANSFORMER | 12053 | 20230909 | 2211 | 20230910 | 1825 | 2214351 | 1214 | Distribution Circuit | Equipment Failure/Involved | Underground | 81 | 53646 | 37.489 | -121.9275 | Yes | Clear;32-90 F | Transformer (UG) | Broken | 23-0114643 | UG | Sus | 35487663 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1872591 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315275043125 | 20230910 | 1506 | 20230910 | 1559 | 2214792 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 212 | 37.673 | -122.1337 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0114694 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1872654 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1101 | 13761101 | TRANSFORMER | 315353241779 | 20230911 | 901 | 20230911 | 1010 | 2215142 | 69 | Transformer only | Vegetation | Tree - branch fell on line | 14 | 966 | 37.6365 | -122.1059 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 23-0114899 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1872938 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1108 | 14351108 | OCB | 1108/2 | 20230911 | 1517 | 20230911 | 2126 | 2215728 | 369 | Distribution Circuit | Equipment Failure/Involved | Underground | 4381 | 1246711 | 37.5418 | -121.9619 | No | Clear;32-90 F | Elbow | Burned/flashed | 23-0115138 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1873045 | 0 | Non-EPSS | N | 2023 | GRD OC
MISSION | MISSION | FREMONT-1111 | 14351111 | OCB | 1111/2 | 20230911 | 1517 | 20230911 | 1859 | 2215727 | 222 | Distribution Circuit | Company Initiated | Personnel- company | 1832 | 406704 | 37.5418 | -121.9619 | No | Clear;32-90 F | Switch (UG) | Normal | 23-0115136 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1873044 | 0 | Non-EPSS | N | 2023 | GRD OC
MISSION | MISSION | NORTH DUBLIN-2101 | 14052101 | OCB | 2101/2/NORM | 20230911 | 1822 | 20230912 | 423 | 2215920 | 436 | Distribution Circuit | Equipment Failure/Involved | Underground | 5550 | 837549 | 37.7448 | -121.8576 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0115212 | UG | Sus | 45217596 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1873088 | 0 | EPSS Ckt | Y | 2023 | A PH & GRD INST OC TGT
MISSION | MISSION | VINEYARD-2110 | 14502110 | FUSE | 73926 | 20230912 | 610 | 20230912 | 915 | 2216096 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 5914 | 37.7128 | -121.8675 | No | Partly Cloudy;32-90 F |  |  | 23-0115358 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1873233 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2110 | 14502110 | TRANSFORMER | T28781 | 20230912 | 1733 | 20230913 | 240 | 2216929 | 547 | Distribution Circuit | Equipment Failure/Involved | Underground | 92 | 18838 | 37.7128 | -121.8682 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0115723 | UG | Sus | 35488417 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1873431 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2110 | 14502110 | FUSE | 74934 | 20230912 | 2304 | 20230913 | 51 | 2217095 | 107 | Distribution Circuit | Equipment Failure/Involved | Underground | 77 | 4618 | 37.7128 | -121.8676 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0115444 | UG | Sus | 35488288 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1873442 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | OCB | 1104/2 | 20230913 | 612 | 20230913 | 1228 | 2217337 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1861 | 279173 | 37.6319 | -122.1025 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0115848 | OH | Sus | 45978028 | BAY AREA | SEP | Line to Line | 0 | No | Yes | No | 1873518 | 0 | Non-EPSS | N | 2023 | B & C OC 51 TIME
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10720 | 20230913 | 1817 | 20230914 | 1630 | 2218235 | 1333 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 41323 | 37.5481 | -121.9538 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0116313 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1873793 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SUNOL-1101 | 14241101 | TRANSFORMER | 100000006692 | 20230914 | 856 | 20230914 | 1023 | 2218623 | 87 | Transformer only | 3rd Party | Vehicle | 1 | 87 | 37.6146 | -121.8494 | No | Clear;32-90 F | Transformer (OH) |  | 23-0116549 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1874023 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | T5901 | 20230916 | 1231 | 20230916 | 1250 | 2220631 | 19 | Transformer only | Equipment Failure/Involved | Underground | 30 | 570 | 37.5124 | -121.955 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0117456 | UG | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1874544 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 73258 | 20230917 | 1523 | 20230917 | 1628 | 2221053 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 930 | 37.6652 | -121.7323 | No | Clear;32-90 F |  |  | 23-0117564 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1874645 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | TRANSFORMER | 315232244165 | 20230917 | 2104 | 20230917 | 2205 | 2221134 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 15 | 915 | 37.7014 | -122.149 | No | Partly Cloudy;32-90 F |  |  | 23-0117590 | OH | Sus | 0 | BAY AREA | SEP | None | 0 | No | No | No | 1874670 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | MR198 | 20230918 | 631 | 20230918 | 841 | 2221200 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2864 | 306724 | 37.7306 | -121.7355 | No | Partly Cloudy;32-90 F |  |  | 23-0117613 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1874685 | 0 | EPSS Ckt | Y | 2023 | A & C
MISSION | MISSION | VINEYARD-2104 | 14502104 | FUSE | 12336 | 20230918 | 724 | 20230918 | 1053 | 2221228 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 209 | 37.6854 | -121.8756 | No | Clear;32-90 F |  |  | 23-0117733 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1874865 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1101 | 13111101 | FUSE | 9161 | 20230918 | 1235 | 20230918 | 1247 | 2221641 | 12 | Distribution Circuit | 3rd Party | Vandalism | 1 | 12 | 37.7138 | -122.1859 | No | Clear;32-90 F | Fuse | Broken | 23-0117799 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1874898 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1103 | 13761103 | FUSE | 6541 | 20230918 | 1852 | 20230918 | 2007 | 2221979 | 75 | Distribution Circuit | 3rd Party | Metallic Balloon | 100 | 7504 | 37.6505 | -122.0932 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0117998 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1874971 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2110 | 14502110 | OTHER | J72935 TWD 28329 | 20230919 | 1429 | 20230919 | 1622 | 2222606 | 113 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 4068 | 37.7163 | -121.8537 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0118161 | UG | Sus | 35489715 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1875258 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1111 | 13761111 | TRANSFORMER | 29040 | 20230920 | 1117 | 20230920 | 1950 | 2223597 | 513 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 8269 | 37.6086 | -122.0948 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0118751 | UG | Sus | 35490283 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1875640 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRIP-SAVER | 9473 | 20230920 | 1316 | 20230920 | 1400 | 2223452 | 44 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 1100 | 37.7864 | -121.8632 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118817 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | Yes | No | No | 1875609 | 0 | EPSS Ckt | Y | 2023 | N/A
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 13085 | 20230920 | 1338 | 20230920 | 1737 | 2223473 | 239 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 3977 | 37.6759 | -121.8739 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0118614 | UG | Sus | 35490043 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1875616 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | JUMPER | OJ'S 2 SP/W/O SW 7257 | 20230921 | 1523 | 20230922 | 40 | 2224179 | 557 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 6127 | 37.6797 | -122.1127 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0119367 | OH | Sus | 35490582 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1875810 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1103 | 14351103 | TRANSFORMER | T10250 | 20230922 | 906 | 20230922 | 933 | 2224527 | 27 | Transformer only | 3rd Party | Customer Equipment | 1 | 27 | 37.5547 | -121.9623 | No | Clear;32-90 F | Secondary | Broken | 23-0119622 | OH | Sus | 0 | BAY AREA | SEP | None | 0 | No | No | No | 1875980 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | FUSE | 9075 | 20230923 | 642 | 20230923 | 1010 | 2225191 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 177 | 36816 | 37.5177 | -121.9543 | No | Clear;32-90 F |  |  | 23-0120024 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1876207 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 248212 | 20230923 | 1009 | 20230923 | 1305 | 2225387 | 176 | Distribution Circuit | 3rd Party | Vehicle | 184 | 28514 | 37.7461 | -121.8719 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0120026 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1876210 | 0 | EPSS Ckt | Y | 2023 | C & INT
MISSION | MISSION | JARVIS-1111 | 13501111 | SWITCH | 3644 | 20230923 | 2055 | 20230924 | 400 | 2225645 | 425 | Distribution Circuit | Equipment Failure/Involved | Underground | 270 | 42427 | 37.5875 | -122.0274 | No | Clear;32-90 F | Transformer (UG) | Arcing | 23-0120099 | UG | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1876251 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | FUSE | 12008 | 20230925 | 734 | 20230925 | 930 | 2226145 | 116 | Distribution Circuit | Animal | Bird found | 10 | 1160 | 37.7108 | -121.9238 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0120301 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1876551 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1110 | 14471110 | FUSE | 10816 | 20230925 | 1033 | 20230926 | 311 | 2226505 | 998 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1606 | 37.5367 | -122.0279 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0120401 | UG | Sus | 45989604 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1876599 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | 315730137333 | 20230925 | 1805 | 20230926 | 254 | 2226953 | 529 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 11638 | 37.5159 | -121.9732 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 23-0120667 | OH | Sus | 45990016 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1876715 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 14095 | 20230926 | 849 | 20230926 | 1231 | 2227372 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 219 | 17895 | 37.6948 | -122.1061 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken | 23-0120810 | OH | Sus | 31670216 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1876905 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1106 | 14471106 | FUSE | 10369 | 20230926 | 1238 | 20230926 | 1257 | 2227664 | 19 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 38 | 37.5961 | -122.0908 | No | Partly Cloudy;32-90 F |  |  | 23-0120970 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1876974 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 71291 | 20230927 | 1314 | 20230927 | 1402 | 2228688 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 384 | 37.6316 | -121.7866 | No | Clear;32-90 F |  |  | 23-0121612 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1877344 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | BANCROFT-0401 | 13030401 | JUMPER | BANCROFT 401/2 FORCED OUT | 20230927 | 1547 | 20230927 | 1656 | 2228874 | 69 | Distribution Circuit | Equipment Failure/Involved | Substation | 1226 | 84594 | 37.7393 | -122.1551 | No | Partly Cloudy;32-90 F | Stepdown | Broken | 23-0121748 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1877369 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VINEYARD-2110 | 14502110 | OTHER | J73835 TWD 73841 | 20230927 | 1924 | 20230927 | 2326 | 2228949 | 242 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 13794 | 37.7059 | -121.8604 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0121448 | UG | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1877377 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | TRANSFORMER | 315489942712 | 20230928 | 659 | 20230928 | 932 | 2229112 | 153 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1377 | 37.6626 | -122.0593 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0121937 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1877550 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 9434 | 20230928 | 1305 | 20230928 | 1641 | 2229581 | 216 | Distribution Circuit | 3rd Party | Vandalism | 1 | 216 | 37.703 | -122.1695 | No | Clear;32-90 F | Secondary | Normal | 23-0122139 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1877645 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 73258 | 20230928 | 1627 | 20230928 | 2258 | 2229763 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 5865 | 37.6652 | -121.7323 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0122320 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1877733 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | OCB | 2105/2 | 20230928 | 1646 | 20230929 | 732 | 2229774 | 886 | Distribution Circuit | Equipment Failure/Involved | Underground | 2056 | 133022 | 37.7009 | -121.7336 | No | Clear;32-90 F | Switch (UG) | Burned/flashed | 23-0122272 | UG | Sus | 31670715 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1877695 | 0 | Non-EPSS | N | 2023 | ABC TIME PHASE OC
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 10495 | 20230929 | 1928 | 20230930 | 440 | 2230691 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 28684 | 37.6294 | -122.0951 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0122768 | OH | Sus | 31670786 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1877997 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1108 | 14381108 | FUSE | 8266 | 20230930 | 225 | 20230930 | 1151 | 2231171 | 566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5970 | 268422 | 37.6713 | -122.1387 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0122822 | OH | Sus | 45994844 | BAY AREA | SEP | Line to Ground | 0 | No | Yes | No | 1878058 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRIP-SAVER | 9473 | 20230930 | 310 | 20230930 | 541 | 2231195 | 151 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 10872 | 37.7864 | -121.8632 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0122833 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1878069 | 0 | EPSS Ckt | N | 2023 | A-B
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 12431 | 20230930 | 313 | 20230930 | 1341 | 2231197 | 628 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 36424 | 37.6715 | -122.1483 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0122829 | OH | Sus | 31670908 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1878065 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 13349 | 20230930 | 525 | 20231001 | 130 | 2231278 | 1205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 4820 | 37.803 | -121.7866 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0122910 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1878169 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 9389 | 20230930 | 910 | 20230930 | 1605 | 2231439 | 415 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 415 | 37.6986 | -122.191 | No | Overcast;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0122898 | UG | Sus | 45994855 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1878157 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | FUSE | 850396 | 20230930 | 1245 | 20230930 | 2258 | 2231617 | 613 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1226 | 37.6752 | -121.8272 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0122951 | UG | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1878198 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1112 | 13761112 | FUSE | 14163 | 20231001 | 1616 | 20231002 | 225 | 2232229 | 609 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 41412 | 37.6427 | -122.0959 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0123121 | OH | Sus | 31671023 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1878361 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | INTERRUPTER | 685688 | 20231002 | 1609 | 20231002 | 2038 | 2233110 | 269 | Distribution Circuit | Equipment Failure/Involved | Underground | 106 | 21780 | 37.6939 | -122.0863 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0123536 | UG | Sus | 45997534 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1878661 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1102 | 14381102 | OCB | 1102/2 | 20231004 | 30 | 20231004 | 1850 | 2234138 | 1100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 487 | 6688 | 37.6718 | -122.1597 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0124122 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1879071 | 0 | Non-EPSS | N | 2023 | N/A
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 11104 | 20231004 | 1502 | 20231006 | 208 | 2234805 | 2106 | Distribution Circuit | Equipment Failure/Involved | Underground | 131 | 179025 | 37.7171 | -121.9408 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0124581 | UG | Sus | 45999989 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1879376 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1112 | 13761112 | TRANSFORMER | 315445242628 | 20231004 | 1503 | 20231004 | 1912 | 2234806 | 249 | Transformer only | 3rd Party | Vehicle | 1 | 249 | 37.6601 | -122.0747 | No | Clear;32-90 F | Jumper | Broken | 23-0124570 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1879372 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | RECLOSER | 824562 | 20231004 | 1701 | 20231004 | 1852 | 2234913 | 111 | Distribution Circuit | Company Initiated | Coordination failure | 829 | 92019 | 37.7013 | -121.9389 | No | Clear;32-90 F | Recloser | Normal | 23-0124610 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1879380 | 0 | EPSS Ckt | Y | 2023 | GRD
MISSION | MISSION | GRANT-1102 | 14381102 | FUSE | 11659 | 20231005 | 1433 | 20231006 | 1415 | 2235839 | 1422 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 5688 | 37.6449 | -122.1209 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0124994 | UG | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1879687 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1111 | 13501111 | TRANSFORMER | 315692839507 | 20231005 | 1839 | 20231005 | 2244 | 2236012 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1470 | 37.5755 | -121.9874 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0125105 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1879724 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | TRANSFORMER | T8575 | 20231006 | 329 | 20231006 | 517 | 2236229 | 108 | Transformer only | Equipment Failure/Involved | Underground | 10 | 1080 | 37.7169 | -121.943 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0125157 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1879789 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | FUSE | 284557 | 20231007 | 2220 | 20231008 | 1028 | 2238008 | 728 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 11648 | 37.7193 | -122.1253 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0125815 | OH | Sus | 31671900 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1880281 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1107 | 14351107 | FUSE | 62085 | 20231008 | 1112 | 20231008 | 1427 | 2238218 | 195 | Distribution Circuit | Vegetation | Tree - grew into line | 181 | 35295 | 37.5307 | -121.9772 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125842 | OH | Sus | 46002919 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1880328 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | MR186 | 20231009 | 654 | 20231009 | 900 | 2238551 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1512 | 37.7324 | -121.7123 | No | Overcast;32-90 F |  |  | 23-0125917 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1880414 | 0 | EPSS Ckt | Y | 2023 | B & C
MISSION | MISSION | FREMONT-1112 | 14351112 | FUSE | 10156 | 20231009 | 850 | 20231009 | 1153 | 2238961 | 183 | Distribution Circuit | Animal | Squirrel | 2 | 366 | 37.5571 | -121.9836 | No | Overcast;32-90 F | Fuse | Normal | 23-0126077 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1880626 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | TRANSFORMER | 316266043641 | 20231009 | 1259 | 20231009 | 1805 | 2239059 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 3978 | 37.6915 | -121.7914 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 23-0126118 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1880649 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1106 | 13761106 | TRANSFORMER | T9031 | 20231009 | 2015 | 20231010 | 536 | 2239438 | 561 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1122 | 37.6356 | -122.1238 | No | Partly Cloudy | Secondary | Burned Open | 23-0126305 | UG | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1880732 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1101 | 13761101 | OCB | 1101/2 | 20231012 | 1240 | 20231013 | 248 | 2241877 | 848 | Distribution Circuit | Animal | Bird found | 2210 | 514654 | 37.6319 | -122.1024 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0127557 | OH | Sus | 35496106 | BAY AREA | OCT | Line to Ground | 0 | No | Yes | No | 1881665 | 0 | Non-EPSS | N | 2023 | A - B & GRD
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 9393 | 20231014 | 1447 | 20231014 | 1538 | 2243475 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 3927 | 37.6647 | -122.0519 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0128326 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1882192 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | OCB | 2107/2 | 20231014 | 1650 | 20231014 | 1800 | 2243504 | 70 | Distribution Circuit | 3rd Party | Metallic Balloon | 8 | 560 | 37.5029 | -121.9816 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0128342 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1882199 | 0 | Non-EPSS | N | 2023 | C OC
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 64737 | 20231014 | 1809 | 20231014 | 1922 | 2243520 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 250 | 16108 | 37.5458 | -121.9443 | No | Overcast;32-90 F |  |  | 23-0128350 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1882204 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | TRANSFORMER | T168512 | 20231015 | 1722 | 20231015 | 2108 | 2243903 | 226 | Transformer only | 3rd Party | Vandalism | 2 | 452 | 37.6621 | -121.7785 | No | Clear;32-90 F | Secondary | Broken | 23-0128458 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1882295 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | SWITCH | MR419 | 20231016 | 1805 | 20231016 | 1811 | 2244821 | 6 | Distribution Circuit | 3rd Party | Vehicle | 4254 | 25524 | 37.6894 | -121.7686 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0128883 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1882582 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315430441747 | 20231017 | 614 | 20231017 | 1516 | 2244936 | 542 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 2168 | 37.636 | -122.0792 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0129063 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1882816 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | 315566839323 | 20231017 | 1145 | 20231017 | 1313 | 2245374 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 88 | 37.5699 | -122.0308 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 23-0129160 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1882868 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315586238999 | 20231017 | 2125 | 20231018 | 454 | 2245733 | 449 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 4939 | 37.5611 | -122.0238 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0129386 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1882958 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | TRANSFORMER | 315223744199 | 20231018 | 1724 | 20231018 | 1918 | 2246419 | 114 | Transformer only | Vegetation | Tree - fell into line | 13 | 1482 | 37.7023 | -122.152 | No | Clear;32-90 F | Secondary | Broken | 23-0129865 | OH | Sus | 46025521 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1883238 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1103 | 14381103 | TRANSFORMER | 315284642434 | 20231018 | 1829 | 20231018 | 2118 | 2246465 | 169 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 169 | 37.654 | -122.1299 | No | Clear;32-90 F | Service conductor | Arcing | 23-0129898 | OH | Sus | 46025486 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1883250 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1111 | 13111111 | TRANSFORMER | 315247844349 | 20231019 | 156 | 20231019 | 313 | 2246591 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 77 | 37.7065 | -122.1438 | No | Clear;32-90 F | Fuse | Broken | 23-0129944 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1883284 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1112 | 13761112 | TRANSFORMER | 315391342515 | 20231019 | 1143 | 20231019 | 1544 | 2246868 | 241 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 241 | 37.6568 | -122.0932 | No | Clear;32-90 F |  |  | 23-0130310 | OH | Sus | 46026241 | BAY AREA | OCT | None | 0 | No | No | No | 1883418 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1112 | 13761112 | TRANSFORMER | 315389242546 | 20231019 | 1501 | 20231019 | 1715 | 2247054 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 536 | 37.6576 | -122.094 | No | Clear;32-90 F | Transformer | Burned Open | 23-0130309 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1883417 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2118 | 14232118 | FUSE | 20915 | 20231019 | 1702 | 20231019 | 2131 | 2247109 | 269 | Distribution Circuit | Equipment Failure/Involved | Underground | 91 | 24419 | 37.7486 | -121.9337 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0130374 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1883439 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1101 | 13761101 | TRANSFORMER | 315343841750 | 20231019 | 1913 | 20231019 | 2220 | 2247138 | 187 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2992 | 37.6357 | -122.1096 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0130373 | OH | Sus | 31673478 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1883438 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | TRANSFORMER | T15266 | 20231021 | 1015 | 20231021 | 1523 | 2248190 | 308 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 2222 | 37.4851 | -121.9277 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0130897 | UG | Sus | 35506220 | BAY AREA | OCT | Three Phase Fault | 0 | No | No | No | 1883856 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 11433 | 20231021 | 1249 | 20231021 | 1408 | 2248301 | 79 | Distribution Circuit | 3rd Party | Metallic Balloon | 335 | 26465 | 37.5617 | -121.9928 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0130919 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1883886 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2116 | 14232116 | OCB | 2116/2 | 20231022 | 213 | 20231022 | 1034 | 2248677 | 278 | Distribution Circuit | Equipment Failure/Involved | Underground | 994 | 274005 | 37.745 | -121.9369 | No | Partly Cloudy;32-90 F | Switch (UG) | Failed/Faulted | 23-0130979 | UG | Sus | 31673682 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1883942 | 0 | Non-EPSS | N | 2023 | B/U TGT -TGT A - B- TIME OC AN
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 13376 | 20231022 | 745 | 20231022 | 1110 | 2248804 | 205 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 820 | 37.7107 | -121.7071 | No | Clear;32-90 F | Switch (UG) | Arcing | 23-0131008 | UG | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1883977 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 90603 | 20231022 | 1416 | 20231022 | 2220 | 2249053 | 484 | Distribution Circuit | Equipment Failure/Involved | Overhead | 249 | 31292 | 37.6364 | -122.0813 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 23-0131060 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1884027 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1104 | 13761104 | TRANSFORMER | 315435541389 | 20231022 | 1423 | 20231023 | 215 | 2249018 | 712 | Transformer only | Equipment Failure/Involved | Overhead | 28 | 19936 | 37.6262 | -122.0772 | No | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 23-0131051 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1884019 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2110 | 14232110 | OTHER | T23764 TWD T7975 | 20231022 | 1433 | 20231022 | 1445 | 2248980 | 12 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 144 | 37.7543 | -121.947 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Underground | Burned/flashed | 23-0130979 | UG | Sus | 31673682 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1884017 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2110 | 14232110 | OTHER | T23764 TWD T7975 | 20231022 | 1844 | 20231022 | 1909 | 2249131 | 25 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 300 | 37.7543 | -121.947 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Burned/flashed | 23-0130979 | UG | Sus | 31673682 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1884043 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2116 | 14232116 | SWITCH | 3386 | 20231022 | 2104 | 20231022 | 2120 | 2249313 | 16 | Distribution Circuit | Equipment Failure/Involved | Underground | 98 | 968 | 37.7543 | -121.9421 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Burned/flashed | 23-0130979 | UG | Sus | 31673682 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1884059 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | FUSE | 72303 | 20231023 | 2141 | 20231024 | 741 | 2250237 | 600 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 19865 | 37.7195 | -121.8708 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0131614 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1884416 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1110 | 14471110 | FUSE | 70879 | 20231024 | 1406 | 20231024 | 1820 | 2250845 | 254 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2182 | 37.5588 | -122.0631 | No | Clear;32-90 F |  |  | 23-0132038 | OH | Sus | 0 | BAY AREA | OCT | None | 0 | No | No | No | 1884691 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 73646 | 20231024 | 1810 | 20231025 | 238 | 2250987 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 32004 | 37.6425 | -121.8813 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0132053 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1884699 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | TRANSFORMER | 315490943248 | 20231024 | 1909 | 20231024 | 1947 | 2250977 | 38 | Transformer only | Environmental/External | Flood/Erosion | 3 | 114 | 37.6773 | -122.0592 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0132065 | OH | Sus | 46030498 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1884705 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 9790 | 20231025 | 955 | 20231025 | 1129 | 2251212 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 264 | 24816 | 37.6206 | -122.037 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0132256 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1884909 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 8343 | 20231025 | 2001 | 20231026 | 431 | 2251947 | 510 | Distribution Circuit | 3rd Party | Vehicle | 8 | 4080 | 37.6383 | -121.8868 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0132621 | OH | Sus | 31674162 | BAY AREA | OCT | Line to Line | 0 | No | Yes | No | 1885047 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | FUSE | 11208 | 20231026 | 952 | 20231027 | 434 | 2252392 | 1122 | Distribution Circuit | Equipment Failure/Involved | Underground | 108 | 41797 | 37.509 | -121.949 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0132801 | UG | Sus | 35507642 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1885301 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 13159 | 20231027 | 1127 | 20231027 | 2047 | 2253326 | 560 | Distribution Circuit | 3rd Party | Vehicle | 16 | 8960 | 37.6657 | -121.9175 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0133239 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1885647 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1101 | 13501101 | SWITCH | 14190 | 20231027 | 1803 | 20231028 | 1820 | 2253681 | 895 | Distribution Circuit | Equipment Failure/Involved | Underground | 166 | 61722 | 37.6341 | -122.0471 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0133429 | UG | Sus | 35508155 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1885712 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1110 | 13501110 | FUSE | 11676 | 20231028 | 1622 | 20231028 | 1735 | 2254401 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1217 | 37.5802 | -121.9885 | No | Clear;32-90 F |  |  | 23-0133591 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1885888 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1109 | 13761109 | TRANSFORMER | 315457541725 | 20231028 | 2333 | 20231029 | 1224 | 2254542 | 771 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 6939 | 37.6356 | -122.0698 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0133669 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1885956 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | FUSE | 11169 | 20231029 | 815 | 20231029 | 1012 | 2254688 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 9126 | 37.6749 | -122.0663 | No | Clear;32-90 F |  |  | 23-0133674 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1885969 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | FUSE | 10030 | 20231029 | 1545 | 20231030 | 310 | 2254975 | 685 | Distribution Circuit | 3rd Party | Vandalism | 11 | 7310 | 37.7233 | -122.1878 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0133727 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1886017 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1101 | 13501101 | SWITCH | 31009 | 20231029 | 1731 | 20231029 | 1759 | s1886658 | 11 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 377 | 37.633 | -122.0452 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0133429 | UG | Sus | 35508155 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1886658 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | OCB | 2109/2 | 20231030 | 1340 | 20231031 | 928 | 2255878 | 1188 | Distribution Circuit | 3rd Party | Vehicle | 4086 | 242732 | 37.457 | -121.9211 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0134060 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | Yes | No | 1886288 | 0 | EPSS Ckt | N | 2023 | GRD TGTS
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 11884 | 20231031 | 1134 | 20231031 | 1340 | 2256648 | 126 | Distribution Circuit | Animal | Squirrel | 1 | 126 | 37.6272 | -122.0323 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0134326 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1886616 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | MT EDEN-1101 | 13761101 | FUSE | 14610 | 20231031 | 1138 | 20231031 | 1227 | 2256651 | 49 | Distribution Circuit | 3rd Party | Metallic Balloon | 2 | 98 | 37.6386 | -122.1097 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0134305 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1886585 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2104 | 14502104 | FUSE | 12336 | 20231031 | 1806 | 20231101 | 550 | 2256927 | 704 | Distribution Circuit | Animal | Squirrel | 1 | 704 | 37.6854 | -121.8756 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0134469 | OH | Sus | 31674515 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1886681 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 64737 | 20231031 | 1819 | 20231031 | 2157 | 2256931 | 218 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 250 | 51980 | 37.5458 | -121.9443 | No | Clear;32-90 F |  |  | 23-0134446 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1886661 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | 315297444568 | 20231101 | 928 | 20231101 | 1013 | 2257314 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 225 | 37.7128 | -122.1268 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0134631 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1886898 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 9874 | 20231103 | 2115 | 20231103 | 2245 | 2259589 | 90 | Distribution Circuit | Vegetation | Tree - grew into line | 126 | 11340 | 37.5323 | -121.9306 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0135816 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1887651 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | OTHER | T7386 TWD T7371 | 20231105 | 2150 | 20231105 | 2229 | 2260725 | 39 | Distribution Circuit | Company Initiated | Return Circuit Normal | 33 | 887 | 37.7218 | -122.1875 | No | Overcast-Fog;32-90 F | Conductor- Underground | Normal | 23-0136030 | UG | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1887952 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | FUSE | 49227 | 20231105 | 2237 | 20231106 | 52 | 2260749 | 135 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 30 | 4050 | 37.6917 | -122.1594 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 23-0136073 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1887957 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | OCB | 2103/2/NORM | 20231106 | 12 | 20231106 | 1625 | 2260877 | 780 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5000 | 395377 | 37.7448 | -121.8576 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0136083 | OH | Sus | 31675429 | BAY AREA | NOV | Line to Ground | 0 | No | Yes | No | 1887964 | 0 | EPSS Ckt | Y | 2023 | PHASE OC OR GRD 1
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | FUSE | 11489 | 20231106 | 21 | 20231106 | 1524 | 2260918 | 903 | Distribution Circuit | Environmental/External | Water | 2 | 1806 | 37.6891 | -121.7961 | No | Overcast-Rain;32-90 F | Transformer (OH) | Arcing | 23-0136085 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1887966 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316481342497 | 20231106 | 824 | 20231106 | 1117 | 2261157 | 173 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 346 | 37.6609 | -121.7167 | No | Clear;32-90 F |  |  | 23-0136253 | OH | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1888182 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1101 | 13501101 | OTHER | J14942 TWD 50491 | 20231106 | 937 | 20231106 | 954 | 2261382 | 17 | Distribution Circuit | Company Initiated | Operating error | 106 | 1802 | 37.6288 | -122.0483 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0131372 | UG | Sus | 35053627 | BAY AREA | NOV | None | 0 | No | No | No | 1888151 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 9781 | 20231106 | 1322 | 20231106 | 1437 | 2261743 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 144 | 10800 | 37.622 | -122.0386 | No | Overcast;32-90 F |  |  | 23-0136369 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1888238 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | SWITCH | 1781 | 20231106 | 1330 | 20231106 | 1336 | 2261487 | 6 | Distribution Circuit | 3rd Party | Vandalism | 1 | 6 | 37.694 | -122.0687 | No | Partly Cloudy;32-90 F | Transformer (UG) | Contaminated | 23-0136325 | UG | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1888223 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315431541189 | 20231107 | 1215 | 20231107 | 1401 | 2262907 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1484 | 37.6207 | -122.0784 | No | Clear;32-90 F | Transformer | Leaking | 23-0136737 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1888575 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | RECLOSER | MR334 | 20231107 | 1231 | 20231107 | 1336 | 2262914 | 65 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1364 | 55844 | 37.6745 | -122.0316 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0136637 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1888577 | 0 | EPSS Ckt | N | 2023 | B & C
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 72825 | 20231108 | 2001 | 20231109 | 155 | 2264598 | 354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 708 | 37.671 | -121.6968 | No | Clear;32-90 F | Jumper | Burned/flashed | 23-0137273 | OH | Sus | 31675578 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1889015 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315459144518 | 20231110 | 1609 | 20231110 | 1710 | 2266427 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 1037 | 37.7121 | -122.0709 | No | Clear;32-90 F | Fuse | Broken | 23-0138006 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1889646 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | T608713 | 20231111 | 1642 | 20231112 | 244 | 2266867 | 602 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 14694 | 37.5182 | -122.0537 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0138129 | UG | Sus | 35511286 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1889780 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | FUSE | 10867 | 20231112 | 716 | 20231112 | 842 | 2267038 | 86 | Distribution Circuit | Animal | Squirrel | 41 | 3526 | 37.538 | -121.993 | No | Clear;32-90 F | Fuse | Normal | 23-0138184 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1889849 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1106 | 13501106 | FUSE | 9467 | 20231112 | 1331 | 20231112 | 1450 | 2267228 | 79 | Distribution Circuit | Animal | Squirrel | 2 | 158 | 37.6002 | -122.0418 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0138215 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1889887 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | RECLOSER | 645342 | 20231113 | 210 | 20231113 | 930 | 2267397 | 440 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 11440 | 37.5586 | -121.9197 | No | Partly Cloudy;32-90 F |  |  | 23-0138275 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1889947 | 0 | EPSS Ckt | Y | 2023 | A
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 8026 | 20231113 | 740 | 20231113 | 1613 | 2267469 | 513 | Distribution Circuit | Animal | Squirrel | 69 | 35397 | 37.6629 | -121.8791 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0138382 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | Yes | Yes | 1890140 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | RECLOSER | 645342 | 20231113 | 949 | 20231113 | 1016 | 2267727 | 27 | Distribution Circuit | 3rd Party | Other | 26 | 702 | 37.5586 | -121.9197 | No | Partly Cloudy;32-90 F | Customer Equipment | Broken | 23-0138368 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1890127 | 0 | EPSS Ckt | Y | 2023 | C- GRD 50 INST
MISSION | MISSION | FREMONT-1104 | 14351104 | TRANSFORMER | 315875039210 | 20231113 | 1313 | 20231114 | 315 | 2267940 | 842 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 842 | 37.5684 | -121.9241 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0138534 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1890211 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 8780 | 20231113 | 1441 | 20231113 | 2033 | 2267997 | 352 | Distribution Circuit | Equipment Failure/Involved | Underground | 234 | 80523 | 37.716 | -121.7408 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0138541 | UG | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1890213 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | FUSE | 11964 | 20231113 | 1934 | 20231114 | 356 | 2268362 | 502 | Distribution Circuit | Equipment Failure/Involved | Underground | 66 | 28716 | 37.4858 | -121.9246 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 23-0138605 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1890261 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 546328 | 20231115 | 727 | 20231115 | 1458 | 2269452 | 451 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 226 | 86080 | 37.6641 | -121.733 | No | Overcast;32-90 F |  |  | 23-0139127 | OH | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1890598 | 0 | EPSS Ckt | Y | 2023 | A & C PHASE
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | FUSE | 51430 | 20231115 | 935 | 20231115 | 1310 | 2269670 | 215 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 66 | 5874 | 37.6917 | -122.1085 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0139243 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | Yes | No | 1890760 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 11017 | 20231115 | 1154 | 20231115 | 1347 | 2269829 | 113 | Distribution Circuit | Animal | Squirrel | 9 | 1016 | 37.7115 | -121.7332 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0139478 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1890849 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10882 | 20231115 | 1731 | 20231116 | 135 | 2270341 | 484 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1936 | 37.5977 | -121.6341 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0139660 | OH | Sus | 46059257 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1890923 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | FUSE | 1843 | 20231116 | 650 | 20231116 | 1013 | 2270758 | 203 | Distribution Circuit | Animal | Bird found | 2 | 406 | 37.7008 | -121.7057 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0139845 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1891040 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | FUSE | 40386 | 20231116 | 1608 | 20231117 | 1622 | 2271011 | 1400 | Distribution Circuit | Equipment Failure/Involved | Underground | 69 | 28192 | 37.4697 | -121.9127 | No | Overcast;32-90 F | Conductor- Underground | Deteriorated | 23-0140172 | UG | Sus | 46060024 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1891109 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1109 | 14471109 | OTHER | J62079 TWD 26603 | 20231116 | 1700 | 20231117 | 109 | 2271041 | 489 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 489 | 37.6024 | -122.0669 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 23-0139945 | UG | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1891110 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1105 | 13761105 | FUSE | 11928 | 20231116 | 1956 | 20231117 | 1358 | 2271103 | 1082 | Distribution Circuit | Equipment Failure/Involved | Underground | 88 | 27913 | 37.6454 | -122.1017 | No | Overcast-Rain;32-90 F | Transformer (UG) | Broken | 23-0140197 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1891118 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1105 | 13761105 | TRANSFORMER | 315369242078 | 20231116 | 1956 | 20231117 | 1927 | 2271102 | 1411 | Transformer only | Equipment Failure/Involved | Underground | 21 | 29631 | 37.6447 | -122.1005 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 23-0140238 | UG | Sus | 46060015 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1891152 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315409644800 | 20231117 | 2206 | 20231117 | 2332 | 2271955 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 774 | 37.7196 | -122.088 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0140738 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1891453 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | OCB | 2107/2 | 20231118 | 736 | 20231118 | 1124 | 2272168 | 228 | Distribution Circuit | Animal | Bird found | 4240 | 310748 | 37.7009 | -121.7335 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0140775 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1891485 | 0 | EPSS Ckt | N | 2023 | PH TIME OC & B/U PH GRD OC
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | SWITCH | 895 | 20231118 | 2138 | 20231119 | 214 | 2273327 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 914 | 57312 | 37.6891 | -121.7974 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140989 | OH | Sus | 35512833 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1891693 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | MR379 | 20231120 | 705 | 20231120 | 1407 | 2273916 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 341 | 101282 | 37.7032 | -122.0461 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0141199 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | Yes | Yes | 1891853 | 0 | EPSS Ckt | N | 2023 | NA
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | T6763 | 20231120 | 835 | 20231120 | 1125 | 2274020 | 170 | Transformer only | Equipment Failure/Involved | Underground | 43 | 7310 | 37.5861 | -122.023 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0136306 | UG | Sus | 45648129 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1891879 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | FUSE | 12740 | 20231120 | 1201 | 20231120 | 1516 | 2274302 | 195 | Distribution Circuit | Animal | Squirrel | 35 | 6825 | 37.5133 | -121.9703 | No | Clear;32-90 F | Insulator | Broken | 23-0141383 | OH | Sus | 46062940 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1891971 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | TRANSFORMER | 15375 | 20231120 | 1747 | 20231121 | 750 | 2274600 | 843 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 843 | 37.5345 | -121.9961 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0141606 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1892039 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | SWITCH | 20379 | 20231120 | 2147 | 20231120 | 2207 | 2274656 | 20 | Distribution Circuit | Animal | Squirrel | 35 | 700 | 37.5132 | -121.9676 | No | Clear;32-90 F | Insulator | Broken | 23-0141383 | OH | Sus | 46062940 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1892042 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2111 | 14232111 | TRANSFORMER | 21069 | 20231121 | 1251 | 20231121 | 1322 | 2274975 | 31 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 62 | 37.7045 | -121.9184 | No | Partly Cloudy;32-90 F |  |  | 23-0141863 | UG | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1892195 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2111 | 12232111 | FUSE | 62359 | 20231121 | 1406 | 20231122 | 126 | 2275237 | 680 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 7008 | 37.5042 | -121.9697 | No | Partly Cloudy;32-90 F | Switch (UG) | Leaking | 23-0142000 | UG | Sus | 35513218 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1892216 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | SWITCH | 35165SW | 20231121 | 1713 | 20231122 | 48 | 2275313 | 455 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 7735 | 37.7006 | -121.8686 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0141912 | UG | Sus | 35513304 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1892224 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | OCB | 2107/2 | 20231122 | 449 | 20231122 | 1600 | 2275479 | 671 | Distribution Circuit | Animal | Bird found | 5143 | 587103 | 37.7448 | -121.9369 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0142133 | OH | Sus | 46063672 | BAY AREA | NOV | Line to Line | 0 | No | Yes | No | 1892294 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD- TIME
MISSION | MISSION | JARVIS-1106 | 13501106 | OTHER | WIRE DOWN ON B | 20231123 | 135 | 20231123 | 1440 | 2276021 | 785 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 9849 | 37.6015 | -122.0393 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0142497 | OH | Sus | 46064901 | BAY AREA | NOV | Line to Ground | 0 | No | Yes | Yes | 1892435 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1103 | 13501103 | FUSE | 7123 | 20231123 | 945 | 20231123 | 1030 | 2276086 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 1441 | 37.604 | -122.0594 | No | Clear;32-90 F |  |  | 23-0142504 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1892443 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1107 | 14471107 | FUSE | 6796 | 20231123 | 1912 | 20231124 | 1344 | 2276234 | 1112 | Distribution Circuit | Equipment Failure/Involved | Underground | 336 | 70929 | 37.5483 | -122.0324 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0142552 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1892484 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1112 | 13761112 | FUSE | 12280 | 20231124 | 847 | 20231124 | 959 | 2276438 | 72 | Distribution Circuit | Animal | Squirrel | 54 | 3888 | 37.6381 | -122.0982 | No | Clear;32-90 F | Fuse | Normal | 23-0142621 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1892550 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | 610800 | 20231124 | 1205 | 20231124 | 1322 | 2276582 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1067 | 82159 | 37.7009 | -122.0337 | No | Clear;32-90 F |  |  | 23-0142642 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1892562 | 0 | EPSS Ckt | Y | 2023 | A - B . C & SGF
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | 610800 | 20231125 | 443 | 20231125 | 704 | 2276840 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1067 | 150447 | 37.7009 | -122.0337 | No | Clear;32-90 F |  |  | 23-0142732 | OH | Sus | 46065451 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1892639 | 0 | EPSS Ckt | Y | 2023 | UNKNOWN
MISSION | MISSION | FREMONT-1107 | 14351107 | INTERRUPTER | 906230 | 20231125 | 830 | 20231125 | 923 | 2276905 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 305 | 16165 | 37.5311 | -121.9587 | No | Clear;32-90 F |  |  | 23-0142750 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1892654 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 11295 | 20231125 | 1411 | 20231125 | 1627 | 2277051 | 136 | Distribution Circuit | Animal | Bird found | 23 | 3128 | 37.6236 | -122.0397 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0142815 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1892685 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | RADUM-1105 | 13151105 | RECLOSER | 806392 | 20231126 | 226 | 20231126 | 1614 | 2277233 | 828 | Distribution Circuit | 3rd Party | Vehicle | 233 | 6877 | 37.6386 | -121.8864 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0142874 | OH | Sus | 35513700 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1892719 | 0 | EPSS Ckt | N | 2023 | N/A
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | TRANSFORMER | T6342 | 20231126 | 616 | 20231126 | 1216 | 2277285 | 360 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 9096 | 37.6621 | -121.7716 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0142891 | UG | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1892733 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1101 | 13501101 | OCB | 1101/2 | 20231128 | 824 | 20231128 | 1111 | 2278666 | 167 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 17 | 2839 | 37.5953 | -122.0177 | No | Clear;32-90 F | Other | Normal | 23-0137810 | OH | Sus | 74035682 | BAY AREA | NOV | None | 0 | No | No | No | 1893284 | 0 | EPSS Ckt | N | 2023 | NA
MISSION | MISSION | JARVIS-1109 | 13501109 | FUSE | 10404 | 20231128 | 1651 | 20231128 | 1828 | 2279137 | 97 | Distribution Circuit | Animal | Squirrel | 3 | 259 | 37.5948 | -122.0399 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0143618 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1893406 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1103 | 14351103 | FUSE | 61202 | 20231128 | 2157 | 20231128 | 2206 | 2279293 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 128 | 1153 | 37.5581 | -121.9726 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0143658 | OH | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1893446 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1106 | 13501106 | TRANSFORMER | 315585040430 | 20231129 | 32 | 20231129 | 305 | 2279334 | 153 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 2448 | 37.6005 | -122.0251 | No | Partly Cloudy;32-90 F |  |  | 23-0143672 | OH | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1893468 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | OTHER | J76012 TWD 82424 | 20231201 | 1504 | 20231201 | 1531 | 2281735 | 27 | Distribution Circuit | 3rd Party | Vehicle | 2 | 54 | 37.6609 | -121.7835 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0144795 | UG | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1894410 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1103 | 13751103 | JUMPER | 12KV FLYING BELLS 1/E OF TV597 | 20231202 | 938 | 20231202 | 1454 | 2282087 | 316 | Distribution Circuit | Company Initiated | Other Circuits | 11 | 3476 | 37.7139 | -121.7141 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0144885 | OH | Sus | 35514686 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1894535 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NORTH DUBLIN-2101 | 14052101 | FUSE | 74520 | 20231203 | 41 | 20231203 | 1743 | 2282569 | 1022 | Distribution Circuit | Equipment Failure/Involved | Underground | 60 | 38040 | 37.749 | -121.8941 | No | Overcast;32-90 F | Transformer (UG) | Broken | 23-0145014 | UG | Sus | 35514944 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1894660 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 11926 | 20231203 | 931 | 20231203 | 1139 | 2282692 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1024 | 37.7009 | -121.9486 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0145025 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1894674 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | FUSE | 10998 | 20231204 | 1123 | 20231204 | 1313 | 2283498 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 660 | 37.6598 | -122.0358 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0145152 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1895004 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1103 | 13751103 | FUSE | 10955 | 20231204 | 1228 | 20231204 | 1512 | 2283557 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 3936 | 37.7127 | -121.6972 | No | Clear;32-90 F |  |  | 23-0145305 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 1895023 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | FUSE | 73314 | 20231204 | 1717 | 20231204 | 1913 | 2283784 | 116 | Distribution Circuit | Equipment Failure/Involved | Underground | 180 | 13411 | 37.6641 | -121.7985 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0145383 | UG | Sus | 31678221 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1895053 | 1 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | SWITCH | 3602 | 20231206 | 136 | 20231206 | 217 | 2284749 | 41 | Distribution Circuit | Equipment Failure/Involved | Underground | 51 | 2056 | 37.6645 | -121.8033 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0145383 | UG | Sus | 31678221 | BAY AREA | DEC | None | 0 | No | No | No | 1895438 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | TRANSFORMER | T9355 | 20231206 | 1022 | 20231206 | 1108 | 2285104 | 46 | Transformer only | 3rd Party | Customer Equipment | 7 | 322 | 37.5092 | -121.946 | No | Overcast;32-90 F | Other | Malfunctioning | 23-0145848 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1895605 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | FUSE | 8264 | 20231206 | 1622 | 20231206 | 1710 | 2285401 | 48 | Distribution Circuit | 3rd Party | Metallic Balloon | 161 | 7728 | 37.5204 | -121.9793 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0146011 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1895688 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1104 | 14471104 | FUSE | 8983 | 20231207 | 1237 | 20231207 | 2113 | 2286231 | 516 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 139 | 71724 | 37.5362 | -122.0345 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0146227 | OH | Sus | 35165388 | BAY AREA | DEC | Force Out | 0 | No | Yes | No | 1895963 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 11129 | 20231207 | 1616 | 20231208 | 155 | 2286412 | 579 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1158 | 37.7154 | -121.9403 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0146315 | OH | Sus | 31678515 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1896013 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 51796 | 20231208 | 1711 | 20231208 | 1815 | 2287355 | 64 | Distribution Circuit | Animal | Bird found | 7 | 448 | 37.7664 | -121.6804 | No | Clear;32-90 F | Fuse | Burned Open | 23-0146600 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1896324 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | OCB | 2107/2 | 20231208 | 2102 | 20231209 | 1234 | 2287456 | 932 | Distribution Circuit | Equipment Failure/Involved | Underground | 4240 | 492973 | 37.7009 | -121.7335 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0146612 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1896337 | 0 | EPSS Ckt | N | 2023 | GRD BU OC
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 51794 | 20231209 | 1011 | 20231209 | 1354 | 2287867 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2007 | 37.7662 | -121.6779 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0146649 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1896466 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2119 | 14232119 | TRANSFORMER | 20152 | 20231210 | 702 | 20231210 | 1616 | 2288239 | 554 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 7202 | 37.7291 | -121.914 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0146736 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1896580 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2119 | 14232119 | SWITCH | 90532 | 20231210 | 1150 | 20231210 | 1615 | 2288366 | 20 | Distribution Circuit | Equipment Failure/Involved | Underground | 83 | 2988 | 37.7259 | -121.9104 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0146731 | UG | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1896607 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | DUMBARTON-1107 | 14471107 | TRANSFORMER | 100000029042 | 20231210 | 1215 | 20231210 | 1710 | 2288364 | 295 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 590 | 37.5502 | -122.0421 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0146753 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 1896610 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1104 | 14351104 | RECLOSER | 645342 | 20231212 | 344 | 20231212 | 1112 | 2289671 | 448 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 11648 | 37.5586 | -121.9197 | No | Partly Cloudy;32-90 F |  |  | 23-0146969 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1896978 | 0 | EPSS Ckt | N | 2023 | A & C TIME PHASE OC
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 30312 | 20231214 | 1943 | 20231214 | 2209 | 2292129 | 146 | Distribution Circuit | Equipment Failure/Involved | Underground | 138 | 19608 | 37.5472 | -122.0518 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0147496 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1897924 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 10801 | 20231216 | 1213 | 20231216 | 1250 | 2293199 | 37 | Distribution Circuit | Animal | Squirrel | 34 | 1258 | 37.5645 | -121.9827 | No | Clear;32-90 F | Fuse | Burned Open | 23-0147656 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1898372 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 21KV-2102 | 12232102 | FUSE | 9725 | 20231216 | 2243 | 20231217 | 2253 | 2293409 | 1450 | Distribution Circuit | Equipment Failure/Involved | Underground | 349 | 268040 | 37.488 | -121.9252 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0147724 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1898453 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | SAN RAMON-2119 | 14232119 | FUSE | 12173 | 20231217 | 154 | 20231218 | 119 | 2293439 | 1405 | Distribution Circuit | Equipment Failure/Involved | Underground | 161 | 185241 | 37.6885 | -121.9032 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0147737 | UG | Sus | 46093503 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1898475 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | TRANSFORMER | 12108 | 20231218 | 1940 | 20231219 | 625 | 2295083 | 645 | Distribution Circuit | Equipment Failure/Involved | Underground | 37 | 13193 | 37.5001 | -121.9559 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 23-0147987 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1898799 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1106 | 13501106 | TRANSFORMER | T22936 | 20231219 | 425 | 20231219 | 2023 | 2295310 | 958 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 958 | 37.6014 | -122.037 | No | Overcast-Fog-Drizzle;32-90 F | Secondary | Broken- wire on ground | 23-0148066 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1898893 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | NEWARK 12KV-1108 | 12221108 | OCB | 1108/2/NORM | 20231219 | 901 | 20231220 | 1542 | 2295488 | 1841 | Distribution Circuit | Equipment Failure/Involved | Underground | 231 | 33556 | 37.5014 | -121.9888 | No | Overcast-Fog-Drizzle;32-90 F | Switch (UG) | Failed/Faulted | 23-0148071 | UG | Sus | 35518415 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1898904 | 0 | Non-EPSS | N | 2023 | C TO GRD
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 62482 | 20231219 | 947 | 20231219 | 1128 | 2295540 | 101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 101 | 37.7485 | -122.0219 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0148082 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1898944 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | SWITCH | MR580 | 20231219 | 1144 | 20231219 | 1406 | 2295673 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4490 | 268163 | 37.7034 | -122.0607 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0148098 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1898961 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 10179 | 20231219 | 1233 | 20231219 | 1256 | 2295714 | 23 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 275 | 6320 | 37.6979 | -122.1101 | No | Overcast;32-90 F |  |  | 23-0148105 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1898966 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | FREMONT-1107 | 14351107 | FUSE | 12463 | 20231219 | 1423 | 20231219 | 2143 | 2295712 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 19360 | 37.5274 | -121.9617 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0148116 | OH | Sus | 31679858 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1898977 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 11673 | 20231219 | 1719 | 20231219 | 1829 | 2295970 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 3710 | 37.6206 | -122.0795 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148153 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1899015 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315488344263 | 20231219 | 1946 | 20231220 | 205 | 2296092 | 379 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3411 | 37.705 | -122.0606 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0148170 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1899035 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | SAN RAMON-2110 | 14232110 | OCB | 2110/2 | 20231220 | 1423 | 20231221 | 236 | 2296648 | 727 | Distribution Circuit | Equipment Failure/Involved | Underground | 2929 | 443926 | 37.7448 | -121.9369 | No | Overcast-Rain;32-90 F | Elbow | Burned/flashed | 23-0148282 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1899217 | 0 | Non-EPSS | N | 2023 | PHASE & GRD
MISSION | MISSION | SAN RAMON-2101 | 14232101 | TRANSFORMER | T28834 | 20231220 | 1528 | 20231221 | 105 | 2296760 | 577 | Distribution Circuit | Equipment Failure/Involved | Underground | 78 | 10293 | 37.7631 | -121.8915 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0148334 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1899275 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | MR190 | 20231221 | 739 | 20231221 | 752 | 2297392 | 13 | Distribution Circuit | Company Initiated | Personnel- company | 1873 | 24349 | 37.6652 | -121.7354 | No | Partly Cloudy-Fog;32-90 F | Recloser | Malfunctioning | 23-0148437 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1899400 | 0 | EPSS Ckt | Y | 2023 | B & GRD
MISSION | MISSION | SAN RAMON-2117 | 14232117 | SWITCH | MR756 | 20231221 | 805 | 20231221 | 811 | 2297419 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 30 | 37.7159 | -121.8928 | No | Partly Cloudy-Fog;32-90 F | Customer Equipment | Broken | 23-0148453 | UG | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 1899430 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 94683 | 20231221 | 1717 | 20231221 | 1905 | 2297954 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 324 | 37.6792 | -122.138 | No | Clear;32-90 F |  |  | 23-0148521 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1899516 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | DUMBARTON-1112 | 14471112 | OCB | 1112/2 | 20231222 | 1015 | 20231222 | 1038 | 2298308 | 23 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 45 | 1035 | 37.5571 | -122.0582 | No | Partly Cloudy;32-90 F |  |  | 23-0148584 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1899635 | 0 | Non-EPSS | N | 2023 | & GRD
MISSION | MISSION | FREMONT-1107 | 14351107 | OCB | 1107/2 | 20231223 | 1849 | 20231224 | 440 | 2298938 | 591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3383 | 404538 | 37.5418 | -121.962 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0148686 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | Yes | No | 1899755 | 0 | Non-EPSS | N | 2023 | A/B PHASE
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | 22128 | 20231223 | 2346 | 20231224 | 740 | 2299010 | 474 | Transformer only | Unknown Cause | Patrol - found nothing | 27 | 12798 | 37.5869 | -122.0405 | No | Clear;32-90 F |  |  | 23-0148735 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 1899803 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | 22128 | 20231225 | 40 | 20231225 | 1402 | 2299348 | 802 | Distribution Circuit | Equipment Failure/Involved | Underground | 58 | 22460 | 37.5869 | -122.0405 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 23-0148808 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1899880 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 72674 | 20231226 | 2014 | 20231226 | 2136 | 2300167 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 2952 | 37.7185 | -121.7173 | No | Overcast;32-90 F |  |  | 23-0148922 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1900040 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1102 | 14381102 | FUSE | 11045 | 20231227 | 718 | 20231227 | 816 | 2300372 | 58 | Distribution Circuit | Animal | Squirrel | 2 | 116 | 37.6485 | -122.1397 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0148973 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1900100 | 1 | Non-EPSS | N | 2023
MISSION | MISSION | MT EDEN-1109 | 13761109 | FUSE | 50731 | 20231229 | 1308 | 20231229 | 1357 | 2301996 | 49 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 735 | 37.6424 | -122.0658 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0149228 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1900525 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 11376 | 20231229 | 1501 | 20231229 | 1531 | 2302073 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 215 | 6450 | 37.7054 | -122.131 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 23-0149241 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1900538 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 13068 | 20231230 | 822 | 20231230 | 1005 | 2302496 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 3193 | 37.6656 | -121.8399 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0149344 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1900653 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | GRANT-1105 | 14381105 | RECLOSER | MR362 | 20231230 | 1229 | 20231231 | 445 | 2302778 | 976 | Distribution Circuit | Equipment Failure/Involved | Overhead | 854 | 58872 | 37.6818 | -122.1524 | No | Overcast;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0149369 | OH | Sus | 31680583 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1900680 | 1 | Non-EPSS | N | 2023 | C PHASE TO GRD
MISSION | MISSION | MT EDEN-1109 | 13761109 | TRANSFORMER | 315431842133 | 20231230 | 1648 | 20231230 | 1857 | 2302936 | 129 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 903 | 37.6465 | -122.079 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Leaking | 23-0149396 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1900708 | 0 | Non-EPSS | N | 2023
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 73258 | 20231231 | 1214 | 20231231 | 1305 | 2303221 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 765 | 37.6652 | -121.7323 | No | Overcast;32-90 F |  |  | 23-0149480 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1900800 | 0 | EPSS Ckt | N | 2023
MISSION | MISSION | VASCO-1103 | 13751103 | RECLOSER | 964102 | 20231231 | 2254 | 20240101 | 935 | 2303373 | 624 | Distribution Circuit | 3rd Party | Vehicle | 35 | 7045 | 37.6944 | -121.6953 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149512 | OH | Sus | 31680684 | BAY AREA | DEC | Line to Line | 0 | No | Yes | No | 1900832 | 0 | EPSS Ckt | N | 2023 | A
MISSION | MISSION | DUMBARTON-1106 | 14471106 | SWITCH | 191760 | 20240101 | 1657 | 20240101 | 2201 | 2304380 | 304 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 4560 | 37.5922 | -122.0803 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0005794 | UG | Sus | 35520494 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1900913 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | RECLOSER | MR353 | 20240102 | 1926 | 20240103 | 553 | 2305340 | 622 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4066 | 418808 | 37.6722 | -122.111 | No | Overcast-Rain;32-90 F | Switch (OH) | Burned/flashed | 24-0006229 | OH | Sus | 35520820 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1901129 | 0 | Non-EPSS | N | 2024 | B & C
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | JUMPER | FB'S 1 SPAN S/OF CGC# 315165545075 | 20240102 | 2041 | 20240103 | 230 | 2305479 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 5235 | 37.7253 | -122.1726 | No | Overcast-Rain;32-90 F | Pole-Wood | Deteriorated | 24-0006240 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1901139 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315210544210 | 20240103 | 848 | 20240103 | 949 | 2306110 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 488 | 37.7026 | -122.1566 | No | Partly Cloudy-Rain;32-90 F | Fuse | Broken | 24-0006410 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1901324 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | JUMPER | 12KV OJ @ W BLOSSOM & HATHAWAY | 20240103 | 957 | 20240103 | 1424 | 2306216 | 267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3471 | 37.6747 | -122.1123 | No | Overcast;32-90 F | Switch (OH) | Broken | 24-0006269 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1901313 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | TRANSFORMER | T1433 | 20240103 | 1331 | 20240103 | 1404 | 2306450 | 33 | Transformer only | Equipment Failure/Involved | Underground | 20 | 660 | 37.6701 | -121.9124 | No | Overcast;32-90 F | Secondary | Broken | 24-0006523 | UG | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1901366 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | FUSE | 10831 | 20240103 | 2229 | 20240104 | 256 | 2306724 | 267 | Distribution Circuit | Equipment Failure/Involved | Underground | 65 | 8374 | 37.7017 | -122.1445 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0006676 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1901436 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | TRANSFORMER | T25287 | 20240104 | 1046 | 20240104 | 2035 | 2307072 | 589 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 10830 | 37.7195 | -121.7126 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0006880 | UG | Sus | 35521289 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1901608 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | FUSE | 11601 | 20240104 | 1139 | 20240104 | 2137 | 2307120 | 598 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 27508 | 37.6729 | -122.1009 | No | Clear;32-90 F |  |  | 24-0007134 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1901690 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1112 | 13501112 | FUSE | 61004 | 20240105 | 411 | 20240105 | 2137 | 2307562 | 1046 | Distribution Circuit | Equipment Failure/Involved | Underground | 131 | 100330 | 37.5681 | -122.0273 | No | Overcast-Fog;32-90 F | Conductor- Underground | Broken | 24-0007157 | UG | Sus | 46130432 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1901712 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1112 | 13761112 | FUSE | 10627 | 20240106 | 932 | 20240106 | 1039 | 2308531 | 67 | Distribution Circuit | Animal | Bird found | 188 | 12596 | 37.6379 | -122.0984 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0007591 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1901984 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2105 | 14502105 | FUSE | 11304 | 20240106 | 1046 | 20240106 | 1250 | 2308585 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 4170 | 37.6679 | -121.884 | No | Clear;32-90 F |  |  | 24-0007625 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1902007 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1109 | 13761109 | RECLOSER | MR523 | 20240106 | 1535 | 20240107 | 148 | 2308858 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1056 | 121567 | 37.6395 | -122.0839 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0007658 | OH | Sus | 35521635 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1902030 | 0 | Non-EPSS | N | 2024 | AB GRD
MISSION | MISSION | GRANT-1105 | 14381105 | FUSE | 9757 | 20240106 | 1904 | 20240107 | 732 | 2308928 | 748 | Distribution Circuit | 3rd Party | Vehicle | 20 | 12098 | 37.6699 | -122.1569 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0007676 | OH | Sus | 35521636 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1902046 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2111 | 14422111 | RECLOSER | 644731 | 20240107 | 644 | 20240107 | 1553 | 2309097 | 549 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 3762 | 37.7114 | -121.8059 | No | Clear;Below 32 F | Transformer (OH) | Broken | 24-0007731 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1902104 | 0 | EPSS Ckt | N | 2024 | C
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | FUSE | 12796 | 20240107 | 2108 | 20240107 | 2142 | 2309378 | 34 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 1224 | 37.7006 | -122.0736 | No | Clear;32-90 F | Fuse | Burned Open | 24-0007797 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1902159 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 10622 | 20240108 | 1256 | 20240108 | 1423 | 2309850 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 4959 | 37.6309 | -122.0802 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0008036 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1902387 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 315830045143 | 20240109 | 930 | 20240109 | 1641 | 2311013 | 431 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3879 | 37.731 | -121.943 | No | Overcast-Fog;32-90 F | Transformer (OH) | Broken | 24-0008282 | OH | Sus | 35486241 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1902706 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | OTHER | WIRE DOWN 1/SPAN SSD FUSE 10115 | 20240110 | 648 | 20240110 | 1015 | 2311310 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 153 | 20645 | 37.6513 | -121.6653 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0008783 | OH | Sus | 46139463 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | Yes | 1902783 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | TRANSFORMER | 315397540281 | 20240110 | 824 | 20240110 | 1000 | 2311396 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 192 | 37.5955 | -122.0897 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0008886 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1902937 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 11633 | 20240110 | 2126 | 20240111 | 533 | 2312404 | 487 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 4714 | 37.6483 | -121.8794 | No | Partly Cloudy;32-90 F | Elbow | Burned/flashed | 24-0009356 | UG | Sus | 46141053 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1903117 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | TRANSFORMER | 315143044873 | 20240111 | 625 | 20240111 | 1116 | 2312636 | 291 | Transformer only | Equipment Failure/Involved | Fire- pole | 19 | 5529 | 37.7204 | -122.1805 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0009435 | OH | Sus | 46145930 | BAY AREA | JAN | Open Circuit | 0 | No | No | No | 1903175 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | TRANSFORMER | 315587845430 | 20240112 | 314 | 20240112 | 1346 | 2313455 | 632 | Distribution Circuit | 3rd Party | Vehicle | 23 | 5636 | 37.7377 | -122.0271 | No | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0009965 | OH | Sus | 35523520 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1903469 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2101 | 14232101 | FUSE | 73530 | 20240113 | 1817 | 20240114 | 246 | 2314985 | 509 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 13520 | 37.7621 | -121.8924 | No | Clear;32-90 F | Elbow | Broken | 24-0010558 | UG | Sus | 46153420 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1903849 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | T1864 | 20240114 | 1125 | 20240114 | 1544 | 2315346 | 259 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 4403 | 37.5832 | -122.025 | No | Partly Cloudy;32-90 F |  |  | 24-0010714 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1903990 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1104 | 14471104 | OTHER | WIRE DOWN 1 SP SSD FUSE 15108 | 20240116 | 1908 | 20240117 | 246 | 2316884 | 458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1352 | 188640 | 37.5347 | -122.0357 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0011315 | OH | Sus | 31681871 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | Yes | 1904378 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | T1863 | 20240116 | 2110 | 20240116 | 2208 | 2317097 | 58 | Transformer only | Equipment Failure/Involved | Underground | 17 | 986 | 37.5831 | -122.0244 | No | Overcast;32-90 F | Secondary | Burned/flashed | 24-0011350 | UG | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1904410 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | FUSE | 60209 | 20240118 | 617 | 20240119 | 230 | 2318185 | 475 | Distribution Circuit | Equipment Failure/Involved | Underground | 130 | 37698 | 37.5881 | -122.0814 | No | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Deteriorated | 24-0011999 | UG | Sus | 46164477 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1904746 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2106 | 14402106 | TRANSFORMER | 316356443399 | 20240118 | 843 | 20240118 | 1338 | 2318268 | 295 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 590 | 37.685 | -121.7604 | No | Clear;32-90 F | Customer Equipment | Contaminated | 24-0012220 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1904837 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | TRANSFORMER | 10859 | 20240119 | 1211 | 20240119 | 1302 | 2319106 | 51 | Transformer only | Equipment Failure/Involved | Underground | 13 | 663 | 37.6498 | -121.8795 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0012659 | UG | Sus | 46165833 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1905099 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 10988 | 20240119 | 1748 | 20240120 | 643 | 2319387 | 775 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 9173 | 37.6533 | -121.8705 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 24-0012808 | UG | Sus | 35525182 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1905145 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | TRANSFORMER | 315463743991 | 20240120 | 805 | 20240120 | 1217 | 2319679 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 29 | 7308 | 37.6977 | -122.069 | No | Overcast-Drizzle;32-90 F | Cutout- fuse holder | Broken | 24-0012900 | OH | Sus | 31682089 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1905233 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | FUSE | 60235 | 20240120 | 1128 | 20240120 | 1358 | 2319881 | 150 | Distribution Circuit | Equipment Failure/Involved | Underground | 670 | 62666 | 37.5456 | -121.9821 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0012949 | UG | Sus | 46166291 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1905260 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 11786 | 20240121 | 1041 | 20240121 | 1418 | 2320381 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 7595 | 37.7083 | -122.062 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0013081 | OH | Sus | 31682241 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1905346 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 36478 | 20240122 | 416 | 20240123 | 514 | 2320906 | 1024 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 42177 | 37.6455 | -121.9011 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0013194 | UG | Sus | 35525687 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1905443 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10115 | 20240122 | 703 | 20240122 | 1400 | 2320974 | 417 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 6255 | 37.6515 | -121.6647 | No | Clear;32-90 F |  |  | 24-0013501 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1905608 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | SWITCH | 30312SW | 20240122 | 1242 | 20240122 | 1321 | 2321479 | 39 | Distribution Circuit | Company Initiated | Return Circuit Normal | 138 | 3222 | 37.5472 | -122.0518 | No | Partly Cloudy;32-90 F | Switch (OH) | Normal | 24-0008153 | OH | Sus | 46092175 | BAY AREA | JAN | None | 0 | No | No | No | 1905601 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | SWITCH | 3246 | 20240122 | 1424 | 20240122 | 1500 | 2321607 | 36 | Distribution Circuit | Equipment Failure/Involved | Underground | 87 | 2956 | 37.5446 | -121.9805 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0012949 | UG | Sus | 46166291 | BAY AREA | JAN | None | 0 | No | No | No | 1905622 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | FUSE | 779893 | 20240122 | 1445 | 20240123 | 150 | 2321603 | 665 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1 | 665 | 37.6214 | -121.9437 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0013541 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1905621 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 36480 | 20240123 | 222 | 20240123 | 429 | s1906325 | 127 | Distribution Circuit | Company Initiated | Personnel- company | 38 | 4826 | 37.6454 | -121.9008 | No | Overcast-Fog;32-90 F | Conductor- Underground | Normal | 24-0013194 | UG | Sus | 35525687 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1906325 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | FUSE | 1843 | 20240123 | 1218 | 20240123 | 1404 | 2322402 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 212 | 37.7008 | -121.7057 | No | Partly Cloudy;32-90 F |  |  | 24-0013899 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1905868 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | JUMPER | OJS | 20240123 | 1422 | 20240123 | 1708 | 2322485 | 166 | Distribution Circuit | Vegetation | Tree - grew into line | 41 | 6806 | 37.6871 | -122.1409 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0013971 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1905882 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 13173 | 20240124 | 1303 | 20240124 | 1400 | 2323185 | 57 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 57 | 37.6753 | -121.885 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 24-0014480 | UG | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1906082 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | JUMPER | 12KV JUMPERS 1/S OF 50697 | 20240125 | 355 | 20240125 | 1300 | 2323577 | 545 | Distribution Circuit | 3rd Party | Vehicle | 46 | 16900 | 37.6831 | -122.0537 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0014771 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1906167 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2119 | 14232119 | RECLOSER | 107418 | 20240125 | 940 | 20240125 | 1617 | 2324226 | 397 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 794 | 37.7167 | -121.9095 | No | Partly Cloudy;32-90 F | Customer Equipment | Malfunctioning | 24-0015283 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1906438 | 0 | EPSS Ckt | N | 2024 | B-C-GRD TGTS
MISSION | MISSION | STATION O-0401 | 12240401 | TRANSFORMER | 315356543332 | 20240126 | 846 | 20240126 | 1402 | 2324603 | 316 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3792 | 37.6791 | -122.1056 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0015524 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1906665 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | STATION O-0401 | 12240401 | TRANSFORMER | 315353243320 | 20240126 | 846 | 20240126 | 1402 | 2324602 | 316 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 3160 | 37.6787 | -122.1068 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0015570 | OH | Sus | 31682470 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1906675 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1105 | 14381105 | TRANSFORMER | 10064 | 20240127 | 2313 | 20240128 | 1249 | 2325772 | 816 | Distribution Circuit | Equipment Failure/Involved | Underground | 67 | 9471 | 37.6806 | -122.1468 | No | Partly Cloudy;32-90 F | Transformer (UG) | Deteriorated | 24-0015923 | UG | Sus | 35526720 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1906886 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 10991 | 20240130 | 2020 | 20240130 | 2303 | 2328611 | 163 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 1304 | 37.6544 | -121.8713 | No | Partly Cloudy;32-90 F |  |  | 24-0016965 | OH | Sus | 0 | BAY AREA | JAN | None | 0 | No | No | No | 1907635 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 10991 | 20240130 | 2353 | 20240131 | 1146 | 2328683 | 713 | Transformer only | Equipment Failure/Involved | Underground | 8 | 5704 | 37.6544 | -121.8713 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0017048 | UG | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1907691 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | FUSE | 12262 | 20240131 | 654 | 20240131 | 834 | 2328843 | 100 | Distribution Circuit | Animal | Bird found | 289 | 28900 | 37.6692 | -122.1063 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0017046 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1907688 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 12694 | 20240201 | 814 | 20240201 | 1138 | 2330972 | 201 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 1551 | 37.527 | -122.0323 | No | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Deteriorated | 24-0017974 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1908291 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1116 | 13111116 | RECLOSER | MR212 | 20240202 | 37 | 20240202 | 1246 | 2332025 | 729 | Distribution Circuit | 3rd Party | Vehicle | 238 | 61506 | 37.7264 | -122.1629 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 24-0018389 | OH | Sus | 35528616 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1908451 | 0 | Non-EPSS | N | 2024 | A & B
MISSION | MISSION | NORTH DUBLIN-2101 | 14052101 | FUSE | 74802 | 20240203 | 1754 | 20240204 | 403 | 2333845 | 609 | Distribution Circuit | 3rd Party | Vehicle | 10 | 6090 | 37.7047 | -121.8723 | No | Overcast;32-90 F | Transformer (UG) | Broken | 24-0018976 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1908869 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | WARD-0401 | 12980401 | TRANSFORMER | 315242844951 | 20240203 | 2016 | 20240204 | 453 | 2333892 | 517 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 5170 | 37.7231 | -122.146 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0019062 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1908955 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | JUMPER | BURNT OPEN JUMPER | 20240204 | 206 | 20240204 | 539 | 2334217 | 213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 210 | 20132 | 37.7151 | -122.0923 | Yes | Overcast-Rain;32-90 F | Jumper | Burned Open | 24-0019101 | OH | Sus | 46179121 | BAY AREA | FEB | Open Circuit | 0 | No | No | No | 1908986 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | FUSE | 8277 | 20240204 | 633 | 20240204 | 720 | 2334624 | 47 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 140 | 6580 | 37.5495 | -121.9989 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019204 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1909095 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11230 | 20240204 | 755 | 20240204 | 1509 | 2335115 | 434 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 12152 | 37.6454 | -121.6472 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020110 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1909939 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315726937539 | 20240204 | 808 | 20240204 | 1140 | 2334929 | 212 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 3392 | 37.5215 | -121.9745 | Yes | Strong Winds-Overcast-Heavy Rain;32-90 F |  |  | 24-0019286 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1909174 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LIVERMORE-1102 | 12141102 | FUSE | 7767 | 20240204 | 824 | 20240204 | 1010 | 2335350 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 390 | 41340 | 37.6745 | -121.7802 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0019341 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909224 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | RECLOSER | MR118 | 20240204 | 828 | 20240204 | 1629 | 2335417 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3129 | 635562 | 37.5298 | -121.9877 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019297 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | Yes | No | 1909184 | 0 | Non-EPSS | N | 2024 | A&B
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | 315751737454 | 20240204 | 854 | 20240204 | 905 | 2335267 | 11 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 77 | 37.5194 | -121.9658 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019385 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909270 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 9590 | 20240204 | 900 | 20240204 | 1319 | 2335814 | 259 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 387 | 100233 | 37.538 | -122.0594 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0019801 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909645 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | MR178 | 20240204 | 900 | 20240204 | 1406 | 2335818 | 306 | Distribution Circuit | Vegetation | Tree - fell into line | 249 | 51494 | 37.6665 | -121.6967 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0019345 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909227 | 0 | EPSS Ckt | N | 2024 | B & 50 INST
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | MR418 | 20240204 | 908 | 20240204 | 1257 | 2336007 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 6208 | 37.6799 | -121.7168 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019361 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1909244 | 0 | EPSS Ckt | N | 2024 | B & GRD
MISSION | MISSION | MT EDEN-1104 | 13761104 | JUMPER | 1 PH OJ 1 SPAN S/O 11082 FUCO | 20240204 | 955 | 20240204 | 1400 | 2336725 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3346 | 93043 | 37.6314 | -122.0745 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Jumper | Burned Open | 24-0019515 | OH | Sus | 0 | BAY AREA | FEB | Open Circuit | 0 | No | No | No | 1909389 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1107 | 13501107 | TRANSFORMER | 315577940076 | 20240204 | 1005 | 20240204 | 1323 | 2336956 | 198 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1386 | 37.5908 | -122.0274 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019836 | OH | Sus | 0 | BAY AREA | FEB | None | 0 | No | No | No | 1909675 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | RECLOSER | MR235 | 20240204 | 1008 | 20240204 | 1303 | 2336929 | 175 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1906 | 333550 | 37.6704 | -122.0726 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019459 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1909334 | 0 | EPSS Ckt | N | 2024 | A & B
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 8046 | 20240204 | 1010 | 20240204 | 1200 | 2336937 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 18150 | 37.5819 | -122.0006 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019638 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909501 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 10802 | 20240204 | 1018 | 20240204 | 1554 | 2337200 | 336 | Distribution Circuit | Vegetation | Tree - bark fell into line | 17 | 5712 | 37.6427 | -122.0557 | Yes | Overcast-Rain-Strong Winds;32-90 F | Cutout- fuse holder | Normal | 24-0019895 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1909730 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 72822 | 20240204 | 1021 | 20240204 | 1401 | 2337139 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 299 | 65780 | 37.6389 | -122.0563 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019593 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909463 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | FUSE | 607 | 20240204 | 1023 | 20240204 | 1142 | 2337194 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 623 | 49217 | 37.6773 | -122.0674 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019554 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1909423 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315428844636 | 20240204 | 1024 | 20240204 | 1349 | 2337253 | 205 | Transformer only | Unknown Cause | Patrol - not conducted | 14 | 2870 | 37.7152 | -122.0815 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019932 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909764 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1103 | 14381103 | OCB | 1103/2 | 20240204 | 1026 | 20240204 | 2231 | 2337241 | 725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 413 | 100485 | 37.6718 | -122.1596 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019504 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1909377 | 0 | Non-EPSS | N | 2024 | GRD & TIME OC
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | FUSE | 14970 | 20240204 | 1028 | 20240204 | 1310 | 2337215 | 162 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 5508 | 37.6839 | -122.0733 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019789 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1909634 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | OCB | 1110/2 | 20240204 | 1035 | 20240205 | 2201 | 2337356 | 2126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3550 | 607642 | 37.7107 | -122.1486 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0019637 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909500 | 0 | Non-EPSS | N | 2024 | C PH & GRD 50 INST
MISSION | MISSION | BANCROFT-0402 | 13030402 | FUSE | 10403 | 20240204 | 1037 | 20240204 | 1441 | 2337366 | 244 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 161 | 39284 | 37.7345 | -122.1457 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0020009 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909843 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 10725 | 20240204 | 1040 | 20240205 | 1540 | 2337150 | 1740 | Distribution Circuit | Vegetation | Tree - fell into line | 377 | 128571 | 37.6704 | -122.1312 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019622 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1909485 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | RECLOSER | MR587 | 20240204 | 1316 | 20240205 | 1429 | 2339893 | 1451 | Distribution Circuit | 3rd Party | Customer Equipment | 662 | 70246 | 37.6641 | -122.0755 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Generator | Failed/Faulted | 24-0019912 | UG | Sus | 0 | BAY AREA | FEB | Three Phase Fault | 0 | No | No | No | 1909746 | 0 | EPSS Ckt | N | 2024 | A-B-C PH TARGETS
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 9185 | 20240204 | 1333 | 20240204 | 1357 | 2340120 | 24 | Distribution Circuit | Vegetation | Tree - bark fell into line | 42 | 1008 | 37.6639 | -121.6817 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019853 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1909691 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 134120 | 20240204 | 1341 | 20240204 | 2005 | 2340565 | 384 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 21120 | 37.7899 | -121.8435 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0019956 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1909788 | 0 | EPSS Ckt | N | 2024 | A & 50 INST
MISSION | MISSION | MT EDEN-1107 | 13761107 | TRANSFORMER | 315351341538 | 20240204 | 1348 | 20240204 | 1515 | 2337638 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 4350 | 37.6299 | -122.1063 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken- wire on object | 24-0019876 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | Yes | 1909713 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 8873 | 20240204 | 1356 | 20240205 | 1414 | 2340671 | 1458 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 73909 | 37.6381 | -121.8943 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0022127 | OH | Sus | 0 | BAY AREA | FEB | None | 0 | No | No | No | 1911813 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 71291 | 20240204 | 1402 | 20240204 | 1958 | 2341201 | 356 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1823 | 37.6316 | -121.7866 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0020507 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1910330 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | TRANSFORMER | 315874635949 | 20240204 | 1410 | 20240204 | 1744 | 2335181 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 4922 | 37.4787 | -121.9229 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0020000 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1909834 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | RECLOSER | MR201 | 20240204 | 1411 | 20240204 | 2152 | 2341214 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 1988 | 283580 | 37.7018 | -122.0885 | Yes | Overcast-Rain-Strong Winds;32-90 F | Insulator | Broken | 24-0019968 | OH | Sus | 0 | BAY AREA | FEB | Three Phase Fault | 0 | No | No | No | 1909801 | 0 | EPSS Ckt | N | 2024 | A B C
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | 213524 | 20240204 | 1412 | 20240205 | 313 | 2341195 | 773 | Distribution Circuit | Equipment Failure/Involved | Overhead | 987 | 278743 | 37.717 | -122.1317 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0019973 | OH | Sus | 0 | BAY AREA | FEB | Multi-Fault | 0 | No | Yes | No | 1909807 | 0 | EPSS Ckt | N | 2024 | B & 51 TIME
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRIP-SAVER | 9473 | 20240204 | 1415 | 20240204 | 1742 | 2343237 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1172 | 37.7864 | -121.8632 | Yes | Clear-Strong Winds;32-90 F | Other | Together | 24-0020555 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1910378 | 1 | EPSS Ckt | N | 2024 | A PHASE OPEN
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 72822 | 20240204 | 1436 | 20240204 | 2300 | 2341791 | 504 | Distribution Circuit | Vegetation | Tree - branch fell on line | 299 | 150696 | 37.6389 | -122.0563 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0021140 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1910963 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | TRANSFORMER | 315850637046 | 20240204 | 1449 | 20240205 | 1108 | 2342168 | 1219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 9197 | 37.5087 | -121.9317 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0020959 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1910779 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 9919 | 20240204 | 1507 | 20240205 | 1329 | 2351640 | 1342 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2684 | 37.6684 | -121.919 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Burned/flashed | 24-0020793 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1910611 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315591439075 | 20240204 | 1548 | 20240205 | 8 | 2355319 | 500 | Transformer only | Vegetation | Tree - grew into line | 15 | 7500 | 37.5632 | -122.0221 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0021221 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1911049 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 315891444555 | 20240204 | 1621 | 20240205 | 1105 | 2346045 | 1124 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 11240 | 37.715 | -121.9215 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021882 | OH | Sus | 0 | BAY AREA | FEB | None | 0 | No | No | No | 1911617 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 9185 | 20240204 | 1626 | 20240204 | 2243 | 2346271 | 377 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 15834 | 37.6639 | -121.6817 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021209 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1911037 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1111 | 14351111 | FUSE | 10883 | 20240204 | 1632 | 20240204 | 1800 | 2347355 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 173 | 15224 | 37.5368 | -121.9971 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0020608 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1910428 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | FUSE | 15348 | 20240204 | 1639 | 20240204 | 1925 | 2346921 | 166 | Distribution Circuit | Vegetation | Tree - branch fell on line | 217 | 36022 | 37.5354 | -121.964 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020680 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1910499 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 886522 | 20240204 | 1649 | 20240205 | 211 | 2347590 | 562 | Distribution Circuit | Equipment Failure/Involved | Overhead | 153 | 85986 | 37.6634 | -121.6803 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020449 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | Yes | No | 1910275 | 0 | EPSS Ckt | N | 2024 | A & B
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | FUSE | 10728 | 20240204 | 1652 | 20240205 | 1404 | 2347639 | 1272 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 101724 | 37.6971 | -122.0484 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021532 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | Yes | No | 1911364 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 64737 | 20240204 | 1700 | 20240204 | 2251 | 2347878 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 250 | 87750 | 37.5458 | -121.9443 | Yes | Overcast-Rain-Strong Winds;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0020942 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1910762 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | TRANSFORMER | 315688338113 | 20240204 | 1710 | 20240205 | 1154 | 2348194 | 1124 | Transformer only | Vegetation | Tree - bark fell into line | 13 | 14612 | 37.5371 | -121.9881 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021709 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1911478 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 13213 | 20240204 | 1728 | 20240204 | 2025 | 2348941 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 267 | 47259 | 37.654 | -121.8535 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0020951 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1910770 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | 315274243444 | 20240204 | 1732 | 20240205 | 1643 | 2350276 | 1391 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 27820 | 37.6818 | -122.1342 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0020655 | OH | Sus | 0 | BAY AREA | FEB | Open Circuit | 0 | No | No | No | 1910475 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | 315270943508 | 20240204 | 1732 | 20240205 | 1142 | 2350306 | 1090 | Transformer only | Environmental/External | Water | 19 | 20710 | 37.6835 | -122.1353 | Yes | Strong Winds-Rain-Overcast;32-90 F | Secondary | Broken- wire on ground | 24-0020663 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1910484 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1109 | 13761109 | JUMPER | BURNT OPEN JUMPER | 20240204 | 1745 | 20240205 | 345 | 2347276 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 115 | 69000 | 37.6374 | -122.0707 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0020596 | OH | Sus | 0 | BAY AREA | FEB | Open Circuit | 0 | No | No | No | 1910418 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRIP-SAVER | 11101 | 20240204 | 1820 | 20240204 | 2012 | 2351666 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 5264 | 37.7942 | -121.8386 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020843 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1910661 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | LAS POSITAS-2104 | 14402104 | FUSE | 11437 | 20240204 | 1825 | 20240205 | 915 | 2350745 | 890 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 17800 | 37.6874 | -121.7835 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021639 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1911432 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | JUMPER | BURNED OPEN JUMPER 4/P/S OF EOL | 20240204 | 2236 | 20240205 | 2025 | 2361070 | 1204 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 6689 | 37.6185 | -121.9223 | Yes | Partly Cloudy-Strong Winds;32-90 F | Jumper | Burned Open | 24-0022407 | OH | Sus | 0 | BAY AREA | FEB | Open Circuit | 0 | No | No | No | 1912057 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 71428 | 20240205 | 35 | 20240205 | 835 | 2356022 | 480 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 147 | 70489 | 37.72 | -121.7244 | No | Clear;32-90 F |  |  | 24-0021593 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1911402 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 8290 | 20240205 | 1146 | 20240205 | 2048 | 2357417 | 542 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 39024 | 37.6756 | -122.1481 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0021926 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1911657 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | TRANSFORMER | 315444742951 | 20240205 | 1307 | 20240205 | 1500 | 2359846 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 339 | 37.669 | -122.0749 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0022260 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1911914 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2105 | 14232105 | SWITCH | 646576 | 20240205 | 2033 | 20240206 | 100 | 2362112 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 267 | 37.7728 | -121.9696 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0022484 | UG | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1912352 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | JUMPER | 10195 HIGH SIDE JUMPERS | 20240206 | 219 | 20240206 | 721 | 2362756 | 302 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 18120 | 37.6888 | -122.0624 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0022884 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1912517 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | TRIP-SAVER | 10315 | 20240206 | 721 | 20240206 | 1008 | 2363168 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 12191 | 37.6519 | -121.9824 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0023088 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | Yes | No | No | 1912645 | 0 | EPSS Ckt | N | 2024 | B & C
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 36396 | 20240206 | 924 | 20240206 | 1325 | 2363616 | 241 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 7544 | 37.6539 | -121.7685 | No | Overcast;32-90 F |  |  | 24-0023288 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1912776 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | 315299444916 | 20240206 | 1052 | 20240206 | 1218 | 2363950 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 1376 | 37.7223 | -122.1263 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0023209 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1912719 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | JUMPER | 12KV FLYING BELLS 4/P/S 8575 | 20240206 | 1152 | 20240206 | 1518 | 2364166 | 206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 8034 | 37.6786 | -122.087 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0022081 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1912774 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | JUMPER | 12KV FLYINGBELLS 1/W 4506 | 20240206 | 1322 | 20240206 | 1514 | 2364489 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 784 | 37.6731 | -122.1258 | No | Overcast;32-90 F | Conductor- Overhead | Burned/flashed | 24-0022832 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1912860 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | JUMPER | BURNED OPEN JUMPERS LINE SIDE OF FUCO 12796 | 20240206 | 1637 | 20240206 | 2224 | 2365155 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 12492 | 37.7006 | -122.0738 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0023694 | OH | Sus | 0 | BAY AREA | FEB | Open Circuit | 0 | No | No | No | 1913090 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 15082 | 20240206 | 2353 | 20240207 | 107 | 2365991 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 3376 | 37.544 | -122.0475 | No | Partly Cloudy;32-90 F |  |  | 24-0023921 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1913285 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | RECLOSER | 806392 | 20240207 | 410 | 20240208 | 200 | 2366102 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 90790 | 37.6386 | -121.8864 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0023948 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1913305 | 0 | EPSS Ckt | N | 2024 | SGF
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 40086 | 20240207 | 424 | 20240207 | 2322 | 2366090 | 1138 | Distribution Circuit | Equipment Failure/Involved | Underground | 89 | 60917 | 37.7436 | -121.946 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (UG) | Broken | 24-0024133 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1913397 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2104 | 12232104 | TRANSFORMER | 15211 | 20240207 | 1134 | 20240208 | 229 | 2367071 | 895 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 10305 | 37.4811 | -121.9468 | No | Overcast-Heavy Rain;32-90 F | Transformer (UG) | Broken | 24-0024244 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1913460 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1110 | 14471110 | FUSE | 10452 | 20240207 | 1544 | 20240207 | 1650 | 2367952 | 66 | Distribution Circuit | Vegetation | Tree - branch fell on line | 88 | 5808 | 37.5442 | -122.0341 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0024558 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1913635 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | EDES-1105 | 13681105 | TRANSFORMER | 20458 | 20240207 | 1714 | 20240208 | 1858 | 2366509 | 1544 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 1994 | 37.7244 | -122.1858 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 24-0024637 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1913698 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1107 | 13761107 | FUSE | 11372 | 20240208 | 527 | 20240209 | 943 | 2369112 | 1696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 32224 | 37.6163 | -122.064 | No | Clear;32-90 F | Jumper | Burned Open | 24-0026538 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1915266 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315422741635 | 20240208 | 1203 | 20240208 | 1519 | 2370021 | 196 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2548 | 37.6329 | -122.0818 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0026255 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1915122 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315596739072 | 20240208 | 1328 | 20240208 | 1750 | 2370141 | 262 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 1834 | 37.5632 | -122.0202 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 24-0026335 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1915162 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DIXON LANDING-2111 | 14722111 | INTERRUPTER | 355290 | 20240209 | 1755 | 20240210 | 1840 | 2372233 | 1485 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 6048 | 37.4717 | -121.9334 | No | Clear;32-90 F | Bushing | Failed/Faulted | 24-0027179 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1915694 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | SWITCH | 60775 | 20240211 | 937 | 20240212 | 452 | 2373165 | 1155 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 13429 | 37.534 | -121.9604 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0027444 | UG | Sus | 35530276 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1916014 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | FUSE | 8335 | 20240211 | 1610 | 20240211 | 1644 | 2373413 | 34 | Distribution Circuit | 3rd Party | Metallic Balloon | 57 | 1950 | 37.5486 | -121.9996 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0027635 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1916055 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2111 | 14232111 | FUSE | 7553 | 20240213 | 1041 | 20240213 | 1227 | 2375052 | 106 | Distribution Circuit | Animal | Squirrel | 69 | 7314 | 37.7086 | -121.9166 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0028383 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1916572 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | TRANSFORMER | 25451 | 20240214 | 130 | 20240214 | 1451 | 2375750 | 801 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 8010 | 37.644 | -121.8062 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0028642 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1916676 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1112 | 13501112 | RECLOSER | MR565 | 20240214 | 711 | 20240214 | 1604 | 2375816 | 533 | Distribution Circuit | Equipment Failure/Involved | Underground | 3919 | 215931 | 37.5719 | -122.0348 | No | Overcast;32-90 F | Connector or Splice (UG) | Broken | 24-0028679 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1916685 | 0 | Non-EPSS | N | 2024 | C & GRD PHASE OC
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 71066 | 20240214 | 936 | 20240214 | 1446 | 2375989 | 310 | Distribution Circuit | Equipment Failure/Involved | Underground | 107 | 16729 | 37.6429 | -121.8029 | No | Partly Cloudy;32-90 F | Switch (UG) | Failed/Faulted | 24-0028739 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1916798 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | FUSE | 8060 | 20240214 | 1015 | 20240214 | 1827 | 2376096 | 492 | Distribution Circuit | Vegetation | Tree - branch fell on line | 102 | 50184 | 37.7052 | -122.1037 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0028819 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1916836 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 11687 | 20240214 | 1526 | 20240215 | 302 | 2376486 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 9056 | 37.5351 | -121.9203 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0029152 | OH | Sus | 31684014 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1916916 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1112 | 13501112 | SWITCH | 8202 | 20240214 | 1615 | 20240214 | 1654 | 2376597 | 39 | Distribution Circuit | Equipment Failure/Involved | Underground | 141 | 5499 | 37.5752 | -122.0379 | No | Overcast;32-90 F | Connector or Splice (UG) | Broken | 24-0028679 | UG | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1916924 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1103 | 13761103 | OCB | 1103/2 | 20240214 | 1845 | 20240214 | 1934 | 2376667 | 49 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 3484 | 92741 | 37.6319 | -122.1023 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0029196 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1916926 | 0 | Non-EPSS | N | 2024 | PH & GRD TGTS
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | TRANSFORMER | 315552642933 | 20240214 | 2049 | 20240215 | 542 | 2376729 | 533 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 2665 | 37.669 | -122.0377 | No | Partly Cloudy-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0029254 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1916969 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 10896 | 20240215 | 2334 | 20240216 | 411 | 2377705 | 277 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 1385 | 37.5444 | -122.0556 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0029740 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1917179 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | FUSE | 7851 | 20240216 | 733 | 20240216 | 1105 | 2377797 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 212 | 37.5733 | -122.0871 | No | Overcast;32-90 F |  |  | 24-0029881 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1917345 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1109 | 13761109 | FUSE | 8484 | 20240217 | 853 | 20240217 | 1027 | 2378737 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 130 | 12220 | 37.6444 | -122.0757 | No | Overcast;32-90 F |  |  | 24-0030162 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1917492 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | OCB | 1102/2/NORM | 20240217 | 2141 | 20240217 | 2304 | 2379298 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2286 | 134933 | 37.5014 | -121.9891 | No | Overcast;32-90 F |  |  | 24-0030341 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1917620 | 0 | Non-EPSS | N | 2024 | C & GRD
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | OCB | 1102/2/NORM | 20240217 | 2344 | 20240218 | 239 | 2379336 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2286 | 124248 | 37.5014 | -121.9891 | No | Partly Cloudy;32-90 F |  |  | 24-0030352 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1917632 | 0 | Non-EPSS | N | 2024 | A - C - & GRD
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | JUMPER | DIG IN BET: 4415 & J2746 | 20240218 | 250 | 20240218 | 932 | 2379454 | 402 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 113 | 45315 | 37.5182 | -121.9984 | No | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Burned/flashed | 24-0030386 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1917659 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315542341464 | 20240218 | 1313 | 20240218 | 1941 | 2379645 | 388 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 4656 | 37.6287 | -122.0401 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Burned/flashed | 24-0030451 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1917699 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315538141443 | 20240218 | 1319 | 20240218 | 1955 | 2379646 | 396 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 5148 | 37.628 | -122.0418 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Burned/flashed | 24-0030450 | OH | Sus | 46192760 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1917698 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 11318 | 20240218 | 2117 | 20240219 | 1308 | 2380131 | 951 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 42001 | 37.7644 | -121.9821 | No | Overcast-Fog;32-90 F | Elbow | Broken | 24-0030569 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1917809 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 298061 | 20240219 | 1007 | 20240219 | 1831 | 2380665 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 83104 | 37.5958 | -121.8897 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030711 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | Yes | No | 1917930 | 0 | EPSS Ckt | N | 2024 | T- B & C
MISSION | MISSION | LIVERMORE-1101 | 12141101 | FUSE | 9599 | 20240219 | 1221 | 20240219 | 1323 | 2381096 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 142 | 8804 | 37.6693 | -121.782 | No | Overcast;32-90 F |  |  | 24-0030863 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1918041 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 11919 | 20240219 | 1411 | 20240220 | 2328 | 2381580 | 1997 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 9371 | 37.529 | -122.0338 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Deteriorated | 24-0030970 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1918116 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 30851 | 20240219 | 1614 | 20240219 | 2138 | 2381807 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 407 | 92564 | 37.7606 | -121.9791 | No | Overcast-Fog-Strong Winds;32-90 F |  |  | 24-0031019 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1918147 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 298061 | 20240219 | 1831 | 20240220 | 1114 | 2381993 | 1003 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 203 | 203609 | 37.5958 | -121.8897 | No | Overcast-Strong Winds;32-90 F |  |  | 24-0030711 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1918165 | 0 | EPSS Ckt | N | 2024 | SGF INST
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | RECLOSER | MR233 | 20240220 | 739 | 20240220 | 1454 | 2382484 | 435 | Distribution Circuit | 3rd Party | Vehicle | 290 | 59818 | 37.7049 | -122.0548 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0031185 | OH | Sus | 0 | BAY AREA | FEB | Three Phase Fault | 0 | No | Yes | No | 1918275 | 0 | EPSS Ckt | N | 2024 | A/B/C & GRD
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | SWITCH | 942 | 20240220 | 1211 | 20240220 | 1518 | 2382953 | 187 | Distribution Circuit | Company Initiated | Return Circuit Normal | 328 | 23655 | 37.4913 | -121.9244 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Normal | 24-0008152 | UG | Sus | 46094424 | BAY AREA | FEB | None | 0 | No | No | No | 1918455 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | OCB | 1108/2 | 20240220 | 1917 | 20240221 | 244 | 2383367 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5882 | 369675 | 37.6319 | -122.1025 | No | Overcast-Drizzle;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0031674 | OH | Sus | 46193378 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1918509 | 0 | Non-EPSS | N | 2024 | A & GRD
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 30851 | 20240220 | 2050 | 20240221 | 2312 | 2383417 | 1582 | Distribution Circuit | Equipment Failure/Involved | Underground | 429 | 123437 | 37.7606 | -121.9791 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0031740 | UG | Sus | 31684807 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1918571 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1104 | 14471104 | TRANSFORMER | 315556938172 | 20240221 | 911 | 20240221 | 1706 | 2383262 | 475 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 6650 | 37.5383 | -122.0335 | No | Partly Cloudy-Drizzle;32-90 F | Connector or Splice (OH) | Contaminated | 24-0031918 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1918749 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | FUSE | 8459 | 20240221 | 937 | 20240221 | 1045 | 2384010 | 68 | Distribution Circuit | 3rd Party | Vehicle | 356 | 24208 | 37.7078 | -122.1263 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0031950 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1918778 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | OTHER | J2314 TWD T5692 | 20240221 | 1108 | 20240221 | 1422 | 2383490 | 194 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 3492 | 37.5333 | -122.0535 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0031824 | UG | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1918801 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | FUSE | 76135 | 20240221 | 1242 | 20240222 | 31 | 2384236 | 709 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 11344 | 37.6869 | -122.148 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0032070 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1918816 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | JUMPER | 8459 | 20240221 | 1343 | 20240222 | 647 | 2384361 | 1024 | Distribution Circuit | Equipment Failure/Involved | Overhead | 356 | 49849 | 37.7078 | -122.1263 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0032194 | OH | Sus | 0 | BAY AREA | FEB | Open Circuit | 0 | No | No | No | 1918845 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | JUMPER | OJS C/O PARADISE & HARMONY DR | 20240222 | 2127 | 20240223 | 311 | 2385739 | 344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 6880 | 37.6861 | -122.1102 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0032928 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1919368 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2102 | 12232102 | FUSE | 30890 | 20240223 | 511 | 20240223 | 1150 | 2385845 | 399 | Distribution Circuit | 3rd Party | Vehicle | 18 | 2286 | 37.4886 | -121.9457 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0032967 | UG | Sus | 35533278 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1919389 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | SWITCH | 916526BP | 20240223 | 1711 | 20240223 | 1858 | 2386498 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 7490 | 37.7949 | -122.0183 | No | Partly Cloudy;32-90 F | Bushing | Broken | 24-0033357 | OH | Sus | 46195486 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1919637 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 10937 | 20240224 | 813 | 20240224 | 1819 | 2386692 | 606 | Distribution Circuit | Company Initiated | Return Circuit Normal | 70 | 42420 | 37.7681 | -121.9789 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0033450 | UG | Sus | 31684807 | BAY AREA | FEB | None | 0 | No | No | No | 1919716 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315607437654 | 20240224 | 1121 | 20240224 | 1425 | 2386813 | 184 | Transformer only | 3rd Party | Contact with High Voltage- 3rd party | 10 | 1840 | 37.5243 | -122.0158 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0033490 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1919762 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2104 | 12232104 | TRANSFORMER | 15517 | 20240225 | 811 | 20240225 | 1645 | 2387305 | 514 | Transformer only | 3rd Party | Customer Equipment | 27 | 13878 | 37.4842 | -121.9449 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0033607 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1919879 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 11362 | 20240225 | 903 | 20240225 | 932 | 2387307 | 29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 3944 | 37.6441 | -122.081 | No | Clear;32-90 F | Fuse | Broken | 24-0033597 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1919863 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2110 | 14502110 | TRANSFORMER | 13353 | 20240225 | 1157 | 20240226 | 300 | 2387403 | 903 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 903 | 37.6978 | -121.8347 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0033632 | UG | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1919895 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 94683 | 20240225 | 1454 | 20240225 | 1616 | 2387467 | 82 | Distribution Circuit | 3rd Party | Vehicle | 3 | 246 | 37.6792 | -122.138 | No | Clear;32-90 F | Anchor or Guy | Normal | 24-0033652 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1919911 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1102 | 14381102 | SWITCH | 8743 | 20240226 | 238 | 20240226 | 1104 | 2387663 | 506 | Distribution Circuit | 3rd Party | Vehicle | 169 | 30150 | 37.6464 | -122.1202 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0033692 | OH | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1919941 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1112 | 14351112 | OCB | 1112/2 | 20240226 | 725 | 20240227 | 146 | 2387713 | 1101 | Distribution Circuit | Equipment Failure/Involved | Underground | 939 | 109551 | 37.5418 | -121.9619 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0033710 | UG | Sus | 46199766 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1919957 | 0 | Non-EPSS | N | 2024 | C GRD / TIME
MISSION | MISSION | DUMBARTON-1108 | 14471108 | FUSE | 9681 | 20240227 | 1056 | 20240227 | 1513 | 2389002 | 222 | Distribution Circuit | Equipment Failure/Involved | Underground | 621 | 107005 | 37.5894 | -122.0474 | No | Clear;32-90 F | Secondary | Broken | 24-0034421 | UG | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1920509 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | TRANSFORMER | T956119 | 20240227 | 1608 | 20240227 | 1703 | 2389333 | 55 | Transformer only | Unknown Cause | Patrol - found nothing | 174 | 9570 | 37.5031 | -121.9358 | No | Clear;32-90 F |  |  | 24-0034587 | OH | Sus | 0 | BAY AREA | FEB | None | 0 | No | No | No | 1920546 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | INTERRUPTER | 624392 | 20240227 | 1613 | 20240227 | 1758 | 2389332 | 43 | Distribution Circuit | Equipment Failure/Involved | Underground | 91 | 4095 | 37.4986 | -121.9465 | No | Clear;32-90 F | Other | Failed/Faulted | 24-0012711 | UG | Sus | 35172213 | BAY AREA | FEB | Three Phase Fault | 0 | No | No | No | 1920542 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | INTERRUPTER | 968574 | 20240227 | 1756 | 20240227 | 1814 | 2389402 | 18 | Distribution Circuit | Equipment Failure/Involved | Underground | 136 | 2448 | 37.4991 | -121.9437 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0012711 | UG | Sus | 35172213 | BAY AREA | FEB | Three Phase Fault | 0 | No | No | No | 1920559 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | TRANSFORMER | T5692 | 20240227 | 1930 | 20240227 | 1945 | 2388595 | 15 | Transformer only | Equipment Failure/Involved | Underground | 18 | 270 | 37.5331 | -122.053 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0034614 | UG | Sus | 0 | BAY AREA | FEB | Force Out | 0 | No | No | No | 1920563 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | TRANSFORMER | 316390143614 | 20240228 | 1034 | 20240228 | 1730 | 2389967 | 416 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1248 | 37.6911 | -121.7488 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0035043 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1920865 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10115 | 20240229 | 612 | 20240229 | 1021 | 2390547 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 3735 | 37.6515 | -121.6647 | No | Clear;32-90 F |  |  | 24-0035376 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1921050 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1107 | 14471107 | TRANSFORMER | MTR#1008958756 | 20240301 | 1154 | 20240301 | 1349 | 2392005 | 115 | Transformer only | Unknown Cause | Patrol - not conducted | 12 | 1380 | 37.5519 | -122.0323 | Yes | Overcast;32-90 F |  |  | 24-0036078 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1921309 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | OCB | 1106/2 | 20240301 | 1458 | 20240301 | 1513 | 2392347 | 15 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5048 | 75720 | 37.5571 | -122.0584 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0036205 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1921355 | 0 | Non-EPSS | N | 2024 | PH OC
MISSION | MISSION | VASCO-1103 | 13751103 | FUSE | 10955 | 20240301 | 1516 | 20240301 | 1710 | 2392404 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 2736 | 37.7127 | -121.6972 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0036295 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1921389 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | RESEARCH-2102 | 14692102 | OTHER | J71462 TWD 11718 | 20240301 | 1905 | 20240301 | 2120 | 2392880 | 135 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 405 | 37.7841 | -121.9822 | Yes | Overcast-Strong Winds;32-90 F | Transformer (UG) | Leaking | 24-0036201 | UG | Sus | 35534618 | BAY AREA | MAR | Open Circuit | 0 | No | No | No | 1921442 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | 213524 | 20240301 | 2038 | 20240302 | 210 | 2393412 | 332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 988 | 131100 | 37.717 | -122.1317 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036462 | OH | Sus | 0 | BAY AREA | MAR | Multi-Fault | 0 | No | Yes | No | 1921507 | 0 | EPSS Ckt | N | 2024 | A B C 51 TIME
MISSION | MISSION | DUMBARTON-1106 | 14471106 | OCB | 1106/2 | 20240301 | 2049 | 20240301 | 2056 | 2393459 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5048 | 35336 | 37.5571 | -122.0584 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0036475 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1921519 | 0 | Non-EPSS | N | 2024 | PH OC TARGET
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | 315747337436 | 20240301 | 2058 | 20240302 | 1709 | 2393284 | 1211 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 10899 | 37.5189 | -121.9674 | Yes | Strong Winds-Overcast-Drizzle;32-90 F | Transformer | Arcing | 24-0036505 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1921550 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1108 | 14471108 | FUSE | 10940 | 20240301 | 2203 | 20240302 | 915 | 2393795 | 672 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 63840 | 37.5895 | -122.0469 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0036747 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1921778 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | RECLOSER | 806392 | 20240303 | 335 | 20240303 | 1940 | 2395697 | 965 | Distribution Circuit | Vegetation | Tree - fell into line | 263 | 99866 | 37.6386 | -121.8864 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0037102 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1922046 | 0 | EPSS Ckt | N | 2024 | B PHASE & GRD OC
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | FUSE | 40688 | 20240303 | 1421 | 20240303 | 2010 | 2396203 | 204 | Distribution Circuit | Equipment Failure/Involved | Underground | 95 | 32209 | 37.6953 | -121.7927 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Burned/flashed | 24-0037249 | UG | Sus | 31685292 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1922162 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1103 | 13501103 | RECLOSER | MR245 | 20240304 | 1919 | 20240305 | 1259 | 2397154 | 975 | Distribution Circuit | Equipment Failure/Involved | Overhead | 304 | 37839 | 37.6061 | -122.0458 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0037780 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | Yes | No | 1922367 | 0 | Non-EPSS | N | 2024 | A-B ABOVE MTT
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | TRANSFORMER | 315159143845 | 20240305 | 1900 | 20240305 | 1945 | 2397990 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 495 | 37.6923 | -122.1743 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0038409 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1922678 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2106 | 14232106 | FUSE | 65599 | 20240306 | 1721 | 20240306 | 1910 | 2398764 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 10791 | 37.7098 | -121.9417 | No | Partly Cloudy;32-90 F |  |  | 24-0038958 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1923003 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2106 | 14232106 | TRANSFORMER | 315831044431 | 20240306 | 1940 | 20240307 | 1200 | 2398835 | 980 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 9800 | 37.7114 | -121.9424 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0039015 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1923052 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1105 | 14351105 | OTHER | J30710 TWD 22848 | 20240307 | 1608 | 20240307 | 1809 | 2399541 | 121 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 5566 | 37.5464 | -121.975 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0039345 | UG | Sus | 35535955 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1923311 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2118 | 14232118 | TRANSFORMER | 11206 | 20240308 | 242 | 20240308 | 1232 | 2399762 | 590 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 4425 | 37.698 | -121.9109 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0039603 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1923394 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1110 | 14471110 | JUMPER | 40370 | 20240308 | 1548 | 20240309 | 1346 | 2400393 | 1318 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 5053 | 37.5619 | -122.0619 | No | Clear;32-90 F | Elbow | Burned/flashed | 24-0039974 | UG | Sus | 0 | BAY AREA | MAR | Open Circuit | 0 | No | No | No | 1923616 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 15251 | 20240309 | 1535 | 20240309 | 2105 | 2400888 | 330 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 9010 | 37.5763 | -121.9618 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0040118 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1923784 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2105 | 14232105 | INTERRUPTER | 327044 | 20240309 | 1543 | 20240309 | 1621 | 2400910 | 38 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 228 | 37.7737 | -121.9665 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0040119 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1923785 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | RESEARCH-2102 | 14692102 | INTERRUPTER | 177314 | 20240310 | 1649 | 20240311 | 128 | 2401241 | 519 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 18246 | 37.781 | -121.9899 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0040209 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1923878 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | TRANSFORMER | 315202944767 | 20240311 | 817 | 20240311 | 1105 | 2401481 | 168 | Transformer only | Equipment Failure/Involved | Underground | 1 | 168 | 37.7178 | -122.1596 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0040435 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1924100 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 879255 | 20240311 | 1205 | 20240311 | 1418 | 2401855 | 133 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 133 | 37.5942 | -121.8926 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0040573 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1924143 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | TRANSFORMER | 315530544183 | 20240312 | 701 | 20240312 | 759 | 2402349 | 58 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 580 | 37.7033 | -122.046 | No | Overcast-Drizzle;32-90 F |  |  | 24-0040786 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1924246 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1105 | 13761105 | OCB | 1105/2 | 20240312 | 1741 | 20240312 | 1847 | 2402944 | 66 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1525 | 61962 | 37.6319 | -122.1023 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0041205 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1924453 | 0 | Non-EPSS | N | 2024 | GRD TIME & BU RLY OC
MISSION | MISSION | MT EDEN SUB | 1376 | OCB | 1300/2 | 20240314 | 750 | 20240314 | 952 | s1925099 | 122 | Distribution Circuit | Equipment Failure/Involved | Substation | 14165 | 828041 | 37.6319 | -122.1022 | No | Clear;32-90 F | Circuit Breaker | Burned/flashed | 24-0018243 | OH | Sus | 45485172 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1925099 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 10206 | 20240314 | 946 | 20240315 | 657 | 2404586 | 1271 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 12710 | 37.6998 | -122.1835 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0042185 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1925155 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1104 | 14471104 | FUSE | 7514 | 20240314 | 1044 | 20240315 | 200 | 2404805 | 916 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 57708 | 37.5317 | -122.0309 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0042467 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1925260 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | FUSE | 73207 | 20240314 | 1337 | 20240314 | 1530 | 2405228 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 3277 | 37.6519 | -121.8046 | No | Clear;32-90 F |  |  | 24-0042306 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1925195 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | 315536737708 | 20240314 | 1435 | 20240314 | 2244 | 2405254 | 489 | Transformer only | Vegetation | Tree - fell into line | 13 | 6357 | 37.5255 | -122.0402 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 24-0042291 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1925191 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | 501762 | 20240314 | 1723 | 20240315 | 407 | 2405437 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 67564 | 37.7124 | -122.1215 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0042405 | OH | Sus | 35537599 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1925229 | 0 | EPSS Ckt | N | 2024 | A-B-C-GRD TGTS
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 4624 | 20240315 | 1307 | 20240315 | 1535 | 2406742 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 296 | 37.7472 | -122.0761 | No | Clear;32-90 F |  |  | 24-0042918 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1925615 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2103 | 14402103 | FUSE | 539620 | 20240315 | 1514 | 20240316 | 1029 | 2406751 | 1155 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 26234 | 37.6971 | -121.8057 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0042964 | UG | Sus | 46212433 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1925629 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 72674 | 20240315 | 1522 | 20240316 | 1339 | 2406755 | 1337 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 48132 | 37.7185 | -121.7173 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0043017 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1925656 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | RECLOSER | 457996 | 20240316 | 844 | 20240316 | 853 | 2407110 | 9 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 252 | 37.5243 | -122.0425 | No | Clear;32-90 F |  |  | 24-0043089 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1925756 | 0 | Non-EPSS | N | 2024 | 51 TIME
MISSION | MISSION | GRANT-1102 | 14381102 | TRANSFORMER | 315295842144 | 20240316 | 915 | 20240316 | 935 | 2407153 | 20 | Transformer only | 3rd Party | Vehicle | 4 | 80 | 37.6463 | -122.126 | No | Clear;32-90 F | Secondary | Broken | 24-0043097 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1925777 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 10108 | 20240316 | 1021 | 20240317 | 1325 | 2407190 | 1624 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 32480 | 37.7688 | -121.7813 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0043137 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1925805 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | RECLOSER | 457996 | 20240316 | 1127 | 20240316 | 1826 | 2407215 | 419 | Distribution Circuit | Animal | Bird found | 28 | 11732 | 37.5243 | -122.0425 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0043119 | OH | Sus | 46212622 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1925796 | 0 | Non-EPSS | N | 2024 | N/A
MISSION | MISSION | CAYETANO-2111 | 14422111 | SWITCH | 5345 | 20240316 | 1332 | 20240316 | 1658 | 2407322 | 206 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 2205 | 37.6977 | -121.8102 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0042964 | UG | Sus | 46212433 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1925812 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1103 | 14471103 | TRANSFORMER | 15017 | 20240316 | 1916 | 20240317 | 541 | 2407586 | 625 | Distribution Circuit | Equipment Failure/Involved | Underground | 131 | 14270 | 37.5691 | -122.0451 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0043184 | UG | Sus | 35538040 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1925877 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | FUSE | 73041 | 20240317 | 725 | 20240317 | 1052 | 2407727 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 207 | 37.6635 | -121.8821 | No | Clear;32-90 F |  |  | 24-0043245 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1925927 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | INTERRUPTER | 81604 | 20240317 | 2055 | 20240317 | 2101 | 2407880 | 6 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2 | 12 | 37.6679 | -121.8737 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0043291 | UG | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1925966 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | RECLOSER | 53732 | 20240318 | 700 | 20240318 | 1306 | 2407946 | 366 | Distribution Circuit | Animal | Bird found | 94 | 19950 | 37.7758 | -121.9974 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0043380 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1926051 | 0 | EPSS Ckt | N | 2024 | C/GRD
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | FUSE | 51161 | 20240318 | 1515 | 20240319 | 412 | 2408588 | 777 | Distribution Circuit | 3rd Party | Vehicle | 2439 | 407782 | 37.7186 | -122.1547 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0043694 | OH | Sus | 35538386 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1926334 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315485944211 | 20240318 | 1627 | 20240319 | 203 | 2408637 | 576 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2304 | 37.7038 | -122.0615 | No | Clear;32-90 F | Transformer | Leaking | 24-0043787 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1926375 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1113 | 13761113 | SWITCH | 8937 | 20240318 | 2002 | 20240319 | 1508 | 2408844 | 1146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1705 | 62390 | 37.6307 | -122.0937 | No | Clear;32-90 F | Switch (OH) | Burned/flashed | 24-0043027 | OH | Sus | 46211471 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1926370 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1107 | 14471107 | INTERRUPTER | 20399 | 20240319 | 2142 | 20240320 | 836 | 2409754 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 282 | 119042 | 37.5542 | -121.999 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0044394 | OH | Sus | 31687110 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | No | 1926725 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | JUMPER | T5180 COIS TWD T5181/8225 | 20240320 | 837 | 20240320 | 1638 | 2410512 | 481 | Distribution Circuit | Company Initiated | Personnel- company | 194 | 52107 | 37.555 | -122.0007 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0044394 | UG | Sus | 31687110 | BAY AREA | MAR | Open Circuit | 0 | No | No | No | 1927022 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1107 | 14471107 | TRANSFORMER | 315589038266 | 20240320 | 1442 | 20240320 | 2113 | 2410451 | 391 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2737 | 37.541 | -122.0224 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0044758 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1927002 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 8716 | 20240320 | 2011 | 20240321 | 1350 | 2410605 | 1059 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 8472 | 37.5993 | -121.921 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0044926 | OH | Sus | 0 | BAY AREA | MAR | Open Circuit | 0 | No | No | No | 1927065 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | OTHER | WIRE DOWN 1 S/O FUSE 14222 | 20240321 | 844 | 20240321 | 1547 | 2411039 | 423 | Distribution Circuit | 3rd Party | Vehicle | 98 | 16031 | 37.7446 | -122.0314 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0045073 | OH | Sus | 46214688 | BAY AREA | MAR | Line to Ground | 0 | No | Yes | Yes | 1927180 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 8919 | 20240323 | 21 | 20240323 | 1027 | 2412501 | 606 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 12726 | 37.633 | -121.8 | No | Overcast-Rain;32-90 F | Fuse | Failed/Faulted | 24-0045896 | UG | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1927632 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315303343019 | 20240323 | 1609 | 20240323 | 1651 | 2412969 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 420 | 37.6702 | -122.1238 | No | Overcast;32-90 F | Fuse | Broken | 24-0046073 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1927777 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1102 | 14381102 | FUSE | 11060 | 20240325 | 1002 | 20240325 | 1751 | 2414086 | 469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3283 | 37.6495 | -122.1314 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0046420 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1928157 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | 315528637820 | 20240325 | 1749 | 20240326 | 11 | 2414434 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 5348 | 37.5286 | -122.043 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0046691 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1928229 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1108 | 14471108 | FUSE | 10940 | 20240327 | 1943 | 20240327 | 2042 | 2416832 | 59 | Distribution Circuit | Animal | Bird found | 95 | 5605 | 37.5895 | -122.0469 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0047695 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1928902 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | TRANSFORMER | 315474342600 | 20240328 | 950 | 20240328 | 1431 | 2417285 | 281 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 562 | 37.6594 | -122.0647 | No | Overcast-Drizzle;32-90 F | Transformer | Broken | 24-0047923 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1929148 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2104 | 14402104 | OCB | 2104/2 | 20240329 | 954 | 20240329 | 1941 | 2417969 | 587 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4008 | 71764 | 37.7009 | -121.7336 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0048255 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1929375 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | JARVIS-1112 | 13501112 | RECLOSER | MR565 | 20240329 | 1145 | 20240329 | 1239 | 2418055 | 54 | Distribution Circuit | Equipment Failure/Involved | Underground | 3946 | 78651 | 37.5719 | -122.0348 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0041073 | UG | Sus | 46190609 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1929399 | 0 | Non-EPSS | N | 2024 | B AND GRD
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | FUSE | 11382 | 20240329 | 2059 | 20240329 | 2157 | 2418572 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 1334 | 37.6724 | -122.0667 | No | Overcast-Drizzle;32-90 F | Fuse | Burned Open | 24-0048628 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1929514 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 10563 | 20240330 | 1021 | 20240330 | 1155 | 2418973 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 94 | 37.6268 | -121.7565 | No | Clear;32-90 F |  |  | 24-0048751 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1929602 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | TRANSFORMER | 316364141213 | 20240330 | 1048 | 20240330 | 1618 | 2418988 | 330 | Transformer only | Environmental/External | Water | 3 | 990 | 37.6251 | -121.7566 | No | Clear;32-90 F | Transformer | Normal | 24-0048771 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1929609 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315447044378 | 20240330 | 1336 | 20240330 | 1813 | 2419065 | 277 | Transformer only | 3rd Party | Dig in- 3rd party | 1 | 277 | 37.7083 | -122.075 | No | Overcast;32-90 F | Pole-Wood | Normal | 24-0048819 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1929635 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DIXON LANDING-2106 | 14722106 | TRANSFORMER | 12386 | 20240330 | 1705 | 20240330 | 1718 | 2419180 | 13 | Transformer only | Environmental/External | Water | 2 | 26 | 37.4675 | -121.9253 | No | Partly Cloudy;32-90 F | Customer Equipment | Normal | 24-0048830 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1929645 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1104 | 12221104 | TRANSFORMER | T15115 | 20240330 | 2223 | 20240331 | 2004 | 2419351 | 1301 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 6319 | 37.5263 | -122.0078 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0048898 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1929708 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2116 | 14232116 | FUSE | 36457 | 20240331 | 921 | 20240331 | 1303 | 2419465 | 138 | Distribution Circuit | Equipment Failure/Involved | Underground | 140 | 21052 | 37.756 | -121.9435 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0048909 | UG | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1929718 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 15192 | 20240331 | 1505 | 20240331 | 1545 | 2419581 | 40 | Distribution Circuit | Animal | Squirrel | 28 | 1120 | 37.6078 | -122.0179 | No | Clear;32-90 F | Fuse | Normal | 24-0048930 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1929741 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 51336 | 20240331 | 1749 | 20240331 | 1951 | 2419676 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 4026 | 37.6651 | -122.131 | No | Partly Cloudy;32-90 F |  |  | 24-0048936 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1929751 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | INTERRUPTER | 20109 | 20240401 | 220 | 20240401 | 420 | 2419795 | 120 | Distribution Circuit | 3rd Party | Vandalism | 15 | 1800 | 37.6212 | -122.0567 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0048970 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1929787 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 8888 | 20240401 | 1315 | 20240401 | 1618 | 2420287 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 366 | 37.5137 | -122.0495 | No | Clear;32-90 F | Jumper | Burned Open | 24-0049217 | OH | Sus | 46218734 | BAY AREA | APR | Multi-Fault | 0 | No | No | No | 1929990 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 8888 | 20240401 | 1638 | 20240401 | 1652 | 2420421 | 14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 28 | 37.5137 | -122.0495 | No | Clear;32-90 F | Jumper | Broken | 24-0049345 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1930018 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1103 | 13761103 | TRANSFORMER | 315382042405 | 20240401 | 1707 | 20240402 | 500 | 2420398 | 713 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 12121 | 37.6537 | -122.0963 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0049361 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1930026 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1103 | 13761103 | TRANSFORMER | 315383242374 | 20240402 | 334 | 20240402 | 500 | 2420604 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1118 | 37.6529 | -122.0958 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0049461 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1930094 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | RECLOSER | MR353 | 20240402 | 1000 | 20240402 | 1025 | 2420925 | 25 | Distribution Circuit | 3rd Party | Other | 4799 | 47447 | 37.6722 | -122.111 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0049597 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1930268 | 0 | Non-EPSS | N | 2024 | NA
MISSION | MISSION | JARVIS-1111 | 13501111 | TRANSFORMER | 315666639706 | 20240402 | 1244 | 20240402 | 2004 | 2421032 | 440 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 3960 | 37.5809 | -121.9966 | No | Clear;32-90 F |  |  | 24-0049733 | OH | Sus | 31689431 | BAY AREA | APR | None | 0 | No | No | No | 1930319 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 71071 | 20240403 | 128 | 20240403 | 1329 | 2421438 | 494 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 27219 | 37.7178 | -121.7107 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0049988 | UG | Sus | 35541522 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1930417 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1103 | 14351103 | FUSE | 8405 | 20240403 | 1137 | 20240403 | 1224 | 2421790 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 1818 | 37.5667 | -121.9749 | No | Partly Cloudy;32-90 F |  |  | 24-0050189 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1930615 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1103 | 14351103 | FUSE | 8475 | 20240403 | 1344 | 20240403 | 1438 | 2421894 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 270 | 37.5684 | -121.9761 | No | Partly Cloudy;32-90 F |  |  | 24-0050287 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1930637 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2105 | 14502105 | OCB | 2105/2 | 20240403 | 1831 | 20240403 | 2149 | 2422066 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2940 | 212590 | 37.6697 | -121.8544 | No | Partly Cloudy;32-90 F |  |  | 24-0050425 | OH | Sus | 0 | BAY AREA | APR | None | 0 | No | No | No | 1930678 | 0 | Non-EPSS | N | 2024 | SET A RLY
MISSION | MISSION | MT EDEN-1103 | 13761103 | TRANSFORMER | 315379841736 | 20240404 | 1412 | 20240405 | 19 | 2422602 | 607 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 10926 | 37.6354 | -122.0967 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0050912 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | Yes | No | 1930894 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 51793 | 20240405 | 739 | 20240405 | 1417 | 2424078 | 398 | Distribution Circuit | Animal | Squirrel | 12 | 4776 | 37.7639 | -121.6775 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051390 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1931251 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 13066 | 20240405 | 1730 | 20240406 | 1143 | 2424743 | 1093 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 8744 | 37.6453 | -121.6404 | No | Clear-Lightning;32-90 F |  |  | 24-0051753 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1931527 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 30312 | 20240406 | 900 | 20240406 | 1157 | 2425135 | 177 | Distribution Circuit | Equipment Failure/Involved | Underground | 138 | 24096 | 37.5472 | -122.0518 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0051737 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1931515 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1105 | 13761105 | JUMPER | C?? BURNED OJ | 20240406 | 1018 | 20240406 | 1704 | 2425304 | 406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 115 | 39491 | 37.6465 | -122.0984 | No | Clear;32-90 F | Jumper | Burned Open | 24-0051775 | OH | Sus | 0 | BAY AREA | APR | Open Circuit | 0 | No | No | No | 1931540 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 8343 | 20240406 | 1102 | 20240406 | 1528 | 2425224 | 266 | Distribution Circuit | 3rd Party | Vehicle | 8 | 2128 | 37.6383 | -121.8868 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051751 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | Yes | No | 1931526 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316732542225 | 20240406 | 1208 | 20240406 | 1547 | 2425268 | 219 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 657 | 37.6548 | -121.6295 | No | Clear;32-90 F |  |  | 24-0051807 | OH | Sus | 0 | BAY AREA | APR | None | 0 | No | No | No | 1931558 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | WARD-0401 | 12980401 | JUMPER | OJ @ FULTON & EVERGREEN | 20240408 | 1025 | 20240408 | 1507 | 2426185 | 282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 5640 | 37.7217 | -122.1369 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0052047 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1931855 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 15082 | 20240408 | 2021 | 20240409 | 1351 | 2426620 | 1050 | Distribution Circuit | Equipment Failure/Involved | Underground | 245 | 134861 | 37.544 | -122.0475 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0052330 | UG | Sus | 46222050 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1931955 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1116 | 13111116 | SWITCH | 50516SW | 20240409 | 1532 | 20240409 | 1853 | 2427301 | 201 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 3015 | 37.7267 | -122.1663 | No | Clear;32-90 F | Fuse | Burned Open | 24-0052842 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1932290 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2107 | 14232107 | TRANSFORMER | 315817144156 | 20240409 | 1632 | 20240410 | 121 | 2427340 | 529 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 5819 | 37.7036 | -121.9471 | No | Clear;32-90 F |  |  | 24-0052834 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1932288 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2103 | 14232103 | RECLOSER | MR279 | 20240410 | 938 | 20240410 | 1316 | 2427741 | 218 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 14568 | 37.7029 | -121.9121 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0053022 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1932478 | 0 | EPSS Ckt | N | 2024 | A GRD
MISSION | MISSION | JARVIS-1103 | 13501103 | OCB | 1104/2 | 20240411 | 1215 | 20240411 | 1334 | 2428604 | 79 | Distribution Circuit | 3rd Party | Metallic Balloon | 1668 | 41325 | 37.5953 | -122.0177 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0053560 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1932809 | 0 | Non-EPSS | N | 2024 | NA
MISSION | MISSION | SAN RAMON-2103 | 14232103 | SWITCH | 7474 | 20240412 | 525 | 20240412 | 711 | 2429088 | 106 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2 | 212 | 37.6928 | -121.9265 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0053022 | UG | Sus | 31690261 | BAY AREA | APR | Force Out | 0 | No | No | No | 1932933 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1103 | 13751103 | FUSE | 10955 | 20240412 | 855 | 20240412 | 2004 | 2429354 | 669 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 12474 | 37.7127 | -121.6972 | No | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0053974 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1933089 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | TRANSFORMER | 315167744968 | 20240412 | 908 | 20240412 | 1509 | 2429287 | 361 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 4693 | 37.7232 | -122.1719 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0053953 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1933046 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | FUSE | 60171 | 20240414 | 1046 | 20240415 | 213 | 2431237 | 927 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 35859 | 37.508 | -121.9706 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0054677 | UG | Sus | 35544642 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1933551 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | TRANSFORMER | T21816 | 20240415 | 851 | 20240415 | 1620 | 2431691 | 449 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 1796 | 37.6523 | -121.8542 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0054998 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1933824 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | OTHER | T21154 TWD T21816 | 20240415 | 1432 | 20240415 | 1617 | 2432070 | 105 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 3255 | 37.6523 | -121.8543 | No | Partly Cloudy;32-90 F | Transformer (UG) | Burned/flashed | 24-0055010 | UG | Sus | 35544767 | BAY AREA | APR | None | 0 | No | No | No | 1933847 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2101 | 14232101 | FUSE | 73532 | 20240416 | 16 | 20240416 | 1130 | 2432303 | 674 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 27134 | 37.7621 | -121.8924 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0055233 | UG | Sus | 35545409 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1933938 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315206443983 | 20240416 | 2031 | 20240417 | 200 | 2433036 | 329 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 2961 | 37.6962 | -122.1579 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 24-0055638 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1934241 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1112 | 13111112 | TRANSFORMER | 315191244667 | 20240417 | 1106 | 20240417 | 1702 | 2433458 | 356 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1424 | 37.7149 | -122.1636 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0055913 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1934513 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | TRANSFORMER | T6824 | 20240417 | 1122 | 20240417 | 1252 | 2433425 | 90 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 90 | 37.4649 | -121.9159 | No | Clear;32-90 F |  |  | 24-0055940 | OH | Sus | 0 | BAY AREA | APR | None | 0 | No | No | No | 1934522 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | RECLOSER | 268916 | 20240417 | 1512 | 20240417 | 1549 | 2433638 | 37 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 769 | 28453 | 37.6803 | -122.1262 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0049068 | OH | Sus | 35463524 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1934563 | 0 | Non-EPSS | N | 2024 | UNK
MISSION | MISSION | DUMBARTON-1106 | 14471106 | TRANSFORMER | 315406139868 | 20240417 | 2007 | 20240417 | 2234 | 2433827 | 147 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 441 | 37.5843 | -122.0866 | No | Clear;32-90 F |  |  | 24-0056168 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1934629 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | TRANSFORMER | 315454443278 | 20240418 | 1859 | 20240418 | 1955 | 2434397 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 1120 | 37.6781 | -122.0717 | No | Clear;32-90 F | Fuse | Burned Open | 24-0056633 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1934806 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | TRANSFORMER | 315456843234 | 20240418 | 1859 | 20240418 | 1950 | 2434396 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 1122 | 37.6768 | -122.0709 | No | Clear;32-90 F | Fuse | Burned Open | 24-0056646 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1934813 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11281 | 20240419 | 143 | 20240419 | 335 | 2434503 | 112 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 112 | 37.6855 | -121.6335 | No | Clear;32-90 F |  |  | 24-0056677 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1934843 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1109 | 13501109 | OCB | 1109/2 | 20240419 | 653 | 20240419 | 1614 | 2434580 | 561 | Distribution Circuit | Vegetation | Tree - grew into line | 125 | 14949 | 37.5953 | -122.0175 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0056687 | OH | Sus | 0 | BAY AREA | APR | Three Phase Fault | 0 | No | Yes | No | 1934854 | 0 | Non-EPSS | N | 2024 | A/B/C
MISSION | MISSION | SAN RAMON-2102 | 14232102 | OTHER | 28290 TWD 28925 | 20240419 | 1500 | 20240419 | 1729 | 2435126 | 149 | Distribution Circuit | Equipment Failure/Involved | Underground | 290 | 43210 | 37.7739 | -121.9211 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0056916 | UG | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1935052 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | TRANSFORMER | 315755937999 | 20240422 | 1500 | 20240422 | 2027 | 2436800 | 327 | Transformer only | 3rd Party | Vandalism | 18 | 5886 | 37.5343 | -121.9649 | No | Clear;32-90 F | Customer Equipment | Contaminated | 24-0057710 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1935597 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2103 | 14232103 | RECLOSER | MR279 | 20240422 | 1909 | 20240423 | 1356 | 2436911 | 904 | Distribution Circuit | Equipment Failure/Involved | Underground | 190 | 33797 | 37.7029 | -121.9121 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0057759 | UG | Sus | 35547687 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1935614 | 0 | EPSS Ckt | N | 2024 | A & GRD
MISSION | MISSION | VINEYARD-2108 | 14502108 | TRANSFORMER | 28400 | 20240423 | 1139 | 20240423 | 1621 | 2437441 | 282 | Transformer only | 3rd Party | Customer Equipment | 9 | 2538 | 37.6576 | -121.8948 | No | Clear;32-90 F | Secondary | Normal | 24-0058205 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1935881 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 7843 | 20240423 | 1607 | 20240424 | 207 | 2437643 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1113 | 37.7672 | -122.0103 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0058250 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1935895 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 13026 | 20240424 | 943 | 20240424 | 1120 | 2438037 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 291 | 37.5951 | -121.6317 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0058391 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1936079 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2102 | 12232102 | FUSE | 30229 | 20240424 | 1657 | 20240424 | 1905 | 2438410 | 128 | Distribution Circuit | Animal | Squirrel | 68 | 6859 | 37.4928 | -121.9086 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0058679 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1936189 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10225 | 20240425 | 1230 | 20240425 | 1720 | 2438663 | 290 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 20 | 3800 | 37.579 | -121.6832 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0058937 | UG | Sus | 31692106 | BAY AREA | APR | Force Out | 0 | No | No | No | 1936445 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1103 | 14351103 | FUSE | 8405 | 20240426 | 622 | 20240426 | 834 | 2439484 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 5854 | 37.5667 | -121.9749 | No | Overcast;32-90 F |  |  | 24-0059188 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1936578 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRANSFORMER | 315349642493 | 20240426 | 1452 | 20240426 | 1653 | 2439887 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 968 | 37.656 | -122.1076 | No | Clear-Strong Winds;32-90 F | Connector or Splice (OH) | Arcing | 24-0059433 | OH | Sus | 46235355 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1936777 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 36262SW | 20240427 | 1301 | 20240427 | 2220 | 2440586 | 559 | Distribution Circuit | 3rd Party | Customer Equipment | 19 | 10585 | 37.7082 | -121.7077 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0059676 | UG | Sus | 35548967 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1936998 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 9185 | 20240427 | 1359 | 20240427 | 1752 | 2440630 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 9786 | 37.6639 | -121.6817 | No | Clear;32-90 F |  |  | 24-0059684 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1937003 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | 315605036990 | 20240428 | 737 | 20240428 | 836 | 2440930 | 59 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 59 | 37.5073 | -122.0149 | No | Partly Cloudy;32-90 F |  |  | 24-0059756 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1937083 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1103 | 13751103 | SWITCH | 6882 | 20240429 | 939 | 20240429 | 1515 | 2441327 | 336 | Distribution Circuit | 3rd Party | Vehicle | 75 | 11070 | 37.7115 | -121.6984 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0059911 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1937292 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | TRIP-SAVER | 10315 | 20240429 | 1613 | 20240430 | 409 | 2441963 | 716 | Distribution Circuit | 3rd Party | Vehicle | 193 | 58388 | 37.6519 | -121.9824 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 24-0060153 | OH | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | Yes | No | 1937405 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 9055 | 20240430 | 141 | 20240430 | 415 | 2442126 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 258 | 39752 | 37.5807 | -121.9956 | No | Clear;32-90 F |  |  | 24-0060222 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1937472 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | FUSE | 8474 | 20240430 | 510 | 20240430 | 856 | 2442147 | 226 | Distribution Circuit | Equipment Failure/Involved | Underground | 122 | 20588 | 37.5052 | -121.9598 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0060233 | UG | Sus | 0 | BAY AREA | APR | Line to Line | 0 | No | No | No | 1937479 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2104 | 12232104 | FUSE | 60589 | 20240430 | 728 | 20240430 | 1024 | 2442224 | 176 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 586 | 37.4764 | -121.9382 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0060338 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1937673 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2104 | 12232104 | FUSE | 60589 | 20240430 | 1055 | 20240430 | 1153 | 2442605 | 58 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 193 | 37.4764 | -121.9382 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0060439 | UG | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1937711 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2104 | 12232104 | FUSE | 60589 | 20240430 | 1234 | 20240430 | 1326 | 2442703 | 52 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 3 | 173 | 37.4764 | -121.9382 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0060502 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1937743 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1103 | 13111103 | FUSE | 8036 | 20240430 | 1714 | 20240430 | 1836 | 2442858 | 82 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 82 | 37.7009 | -122.167 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0060609 | UG | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1937771 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315476444118 | 20240501 | 214 | 20240501 | 410 | 2443047 | 116 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1624 | 37.7012 | -122.0646 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0060685 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1937822 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | OTHER | T6726 TWD T7511 | 20240501 | 638 | 20240501 | 2128 | 2443674 | 890 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 71102 | 37.5042 | -121.9599 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0060784 | UG | Sus | 35549637 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1938083 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1103 | 13761103 | OCB | 1103/2 | 20240501 | 1318 | 20240502 | 508 | 2443507 | 950 | Distribution Circuit | 3rd Party | Vehicle | 3483 | 137519 | 37.6319 | -122.1023 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0060939 | OH | Sus | 35549844 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1938045 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | MT EDEN-1101 | 13761101 | FUSE | 14610 | 20240501 | 1534 | 20240501 | 1616 | 2443675 | 42 | Distribution Circuit | 3rd Party | Metallic Balloon | 2 | 84 | 37.6386 | -122.1097 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0061043 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1938087 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2117 | 14232117 | OCB | 2117/2 | 20240501 | 1633 | 20240501 | 2005 | 2443719 | 197 | Distribution Circuit | Equipment Failure/Involved | Underground | 1252 | 229205 | 37.745 | -121.9369 | No | Clear;32-90 F | Bushing | Burned/flashed | 24-0061056 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1938090 | 0 | EPSS Ckt | N | 2024 | B GRD TIME
MISSION | MISSION | VINEYARD-2107 | 14502107 | RECLOSER | MR332 | 20240501 | 2130 | 20240502 | 1344 | 2443818 | 974 | Distribution Circuit | Equipment Failure/Involved | Underground | 416 | 180244 | 37.6659 | -121.8416 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0061102 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1938118 | 0 | EPSS Ckt | N | 2024 | A GRD
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 7228 | 20240502 | 613 | 20240502 | 845 | 2443865 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 608 | 37.6608 | -121.733 | No | Clear;32-90 F |  |  | 24-0061191 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1938210 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2110 | 14502110 | TRANSFORMER | T24837 | 20240502 | 1300 | 20240502 | 2323 | 2444555 | 623 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 19951 | 37.7092 | -121.8593 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0061429 | UG | Sus | 35550367 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1938434 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | FUSE | 40118 | 20240502 | 2357 | 20240503 | 1808 | 2444636 | 1091 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 72401 | 37.6791 | -121.9093 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0061549 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1938494 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | 213524 | 20240503 | 1119 | 20240503 | 1436 | 2445009 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 988 | 95711 | 37.717 | -122.1317 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0061718 | OH | Sus | 31692954 | BAY AREA | MAY | Line to Ground | 0 | No | Yes | No | 1938683 | 0 | EPSS Ckt | N | 2024 | A & 51
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11230 | 20240503 | 1840 | 20240503 | 1942 | 2445289 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 1736 | 37.6454 | -121.6472 | No | Clear-Strong Winds;32-90 F |  |  | 24-0061895 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1938748 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | OCB | 1106/2 | 20240504 | 947 | 20240504 | 1627 | 2445652 | 400 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1737 | 118448 | 37.7107 | -122.1488 | No | Overcast-Rain;32-90 F | Insulator | Broken | 24-0062023 | OH | Sus | 31693046 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1938870 | 0 | Non-EPSS | N | 2024 | OC
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 70834 | 20240504 | 1355 | 20240505 | 42 | 2445850 | 647 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 25880 | 37.6561 | -121.9039 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 24-0062124 | UG | Sus | 35550767 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1938924 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | TRANSFORMER | 315493141825 | 20240504 | 1433 | 20240504 | 2226 | 2445875 | 473 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 946 | 37.6384 | -122.0576 | No | Rain-Overcast;32-90 F | Transformer | Arcing | 24-0062131 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1938930 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | T5903 | 20240504 | 2345 | 20240505 | 822 | 2446257 | 517 | Transformer only | Unknown Cause | Patrol - found nothing | 36 | 18612 | 37.5127 | -121.9535 | No | Clear;32-90 F |  |  | 24-0062326 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1939091 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | TRANSFORMER | T209013 | 20240505 | 543 | 20240505 | 1331 | 2446278 | 468 | Distribution Circuit | Equipment Failure/Involved | Underground | 70 | 13434 | 37.7343 | -121.8725 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0062307 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1939073 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | T5903 | 20240505 | 1602 | 20240505 | 2100 | 2446612 | 298 | Transformer only | Equipment Failure/Involved | Underground | 36 | 10728 | 37.5127 | -121.9535 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0062435 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1939186 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 11979 | 20240505 | 2338 | 20240506 | 1949 | 2446622 | 1211 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4 | 4844 | 37.5423 | -122.0765 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0062439 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1939189 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | OTHER | J93160 TWD T1610 | 20240506 | 3 | 20240506 | 616 | s1939190 | 373 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 8579 | 37.5243 | -122.0097 | No | Clear;32-90 F | Secondary | Broken | 24-0062397 | UG | Sus | 35550886 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1939190 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | TRANSFORMER | T5903 | 20240506 | 644 | 20240506 | 2241 | 2446685 | 957 | Transformer only | Equipment Failure/Involved | Underground | 36 | 34452 | 37.5127 | -121.9535 | No | Clear;32-90 F | Transformer | Broken | 24-0062488 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1939271 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | ESTUDILLO-0401 | 13480401 | TRANSFORMER | 315242045172 | 20240506 | 908 | 20240506 | 1540 | 2446771 | 392 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3136 | 37.7291 | -122.1463 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0062538 | OH | Sus | 31693154 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1939346 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 9425 | 20240506 | 1745 | 20240506 | 1810 | 2447436 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 1875 | 37.6485 | -122.076 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0062787 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1939439 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315627838617 | 20240506 | 2018 | 20240507 | 130 | 2447489 | 312 | Transformer only | Equipment Failure/Involved | Overhead | 91 | 28392 | 37.5508 | -122.0093 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0062820 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1939460 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1103 | 13761103 | TRANSFORMER | 315369142751 | 20240507 | 1034 | 20240507 | 1400 | 2447587 | 206 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 3914 | 37.6632 | -122.101 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0063002 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1939650 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2107 | 14232107 | SWITCH | 4471 | 20240507 | 1725 | 20240508 | 28 | 2448170 | 423 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 903 | 37.7224 | -121.9441 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0063198 | UG | Sus | 35551423 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1939743 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1103 | 13761103 | FUSE | 10688 | 20240507 | 1819 | 20240508 | 307 | 2448201 | 528 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 20592 | 37.6394 | -122.0945 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0063285 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1939760 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1107 | 14381107 | OCB | 1107/2 | 20240508 | 624 | 20240508 | 1946 | 2448375 | 802 | Distribution Circuit | 3rd Party | Vehicle | 244 | 34700 | 37.6718 | -122.1595 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0063389 | OH | Sus | 35551498 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1939871 | 0 | Non-EPSS | N | 2024 | AC
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315671438552 | 20240508 | 1521 | 20240509 | 50 | 2449024 | 569 | Transformer only | Environmental/External | Fire- Forest/Grass | 9 | 5121 | 37.5491 | -121.9943 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0063868 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1940121 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315672938497 | 20240508 | 1521 | 20240508 | 1948 | 2449081 | 267 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2136 | 37.5476 | -121.9937 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0063870 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1940122 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1105 | 13761105 | FUSE | 10941 | 20240508 | 1613 | 20240508 | 2008 | 2449111 | 235 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 242 | 56870 | 37.6584 | -122.1131 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063922 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1940147 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1107 | 14381107 | FUSE | 14466 | 20240509 | 638 | 20240509 | 857 | 2449407 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 417 | 37.6906 | -122.1737 | No | Clear;32-90 F |  |  | 24-0064059 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1940268 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | FUSE | 8335 | 20240509 | 1438 | 20240509 | 1642 | 2450048 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 7113 | 37.5486 | -121.9996 | No | Clear;32-90 F |  |  | 24-0064409 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1940465 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315427541141 | 20240509 | 1650 | 20240509 | 1942 | 2450043 | 172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 3987 | 37.6194 | -122.0798 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0064405 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1940462 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1104 | 13761104 | OCB | 1104/2 | 20240510 | 940 | 20240510 | 1024 | 2450502 | 44 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3526 | 31120 | 37.6319 | -122.1025 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0064600 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1940662 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 12687 | 20240510 | 1340 | 20240510 | 1633 | 2451086 | 173 | Distribution Circuit | Animal | Other | 1 | 173 | 37.8062 | -121.7894 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0064847 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1940769 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | FUSE | 14223 | 20240510 | 1513 | 20240510 | 1628 | 2450818 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 75 | 37.7453 | -122.0314 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0064813 | OH | Sus | 46245238 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1940754 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2118 | 14232118 | OCB | 2118/2 | 20240510 | 1632 | 20240510 | 1820 | 2451091 | 108 | Distribution Circuit | Equipment Failure/Involved | Underground | 1548 | 85646 | 37.745 | -121.9369 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0064848 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1940770 | 0 | Non-EPSS | N | 2024 | PHASE & GRD TARGETS
MISSION | MISSION | NORTH DUBLIN-2101 | 14052101 | FUSE | 72049 | 20240510 | 2158 | 20240510 | 2330 | 2451220 | 92 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 184 | 37.7041 | -121.8877 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0064716 | UG | Sus | 35552236 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1940796 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2102 | 14232102 | OCB | 73584 | 20240511 | 1958 | 20240512 | 843 | 2451715 | 765 | Distribution Circuit | Equipment Failure/Involved | Underground | 4726 | 436717 | 37.7776 | -121.9198 | No | Clear;32-90 F | Switch (UG) | Burned/flashed | 24-0065086 | UG | Sus | 35552440 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1940954 | 0 | EPSS Ckt | N | 2024 | A PH & GRD 51 TIME
MISSION | MISSION | JARVIS-1103 | 13501103 | RECLOSER | MR245 | 20240512 | 1855 | 20240513 | 330 | 2452164 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 703 | 60677 | 37.6061 | -122.0458 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0065206 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | Yes | No | 1941057 | 0 | Non-EPSS | N | 2024 | B & GRD PHASE OC
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 13193 | 20240513 | 1909 | 20240513 | 2020 | 2453096 | 71 | Distribution Circuit | Animal | Bird found | 343 | 24353 | 37.6504 | -121.8801 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0065598 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1941392 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1105 | 14351105 | FUSE | 61592 | 20240513 | 1942 | 20240513 | 2141 | 2453081 | 119 | Distribution Circuit | Equipment Failure/Involved | Underground | 175 | 19745 | 37.5467 | -121.9721 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0065390 | UG | Sus | 35552599 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1941396 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1105 | 14351105 | SWITCH | 61592SW | 20240514 | 4 | 20240514 | 14 | 2453144 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 90 | 900 | 37.5468 | -121.9722 | No | Partly Cloudy;32-90 F | Other | Broken | 24-0065390 | OH | Sus | 35552599 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1941420 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1107 | 13761107 | FUSE | 8053 | 20240514 | 848 | 20240514 | 1840 | 2453359 | 592 | Distribution Circuit | Animal | Bird found | 1 | 592 | 37.6103 | -122.0679 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0065833 | OH | Sus | 0 | BAY AREA | MAY | Three Phase Fault | 0 | No | No | No | 1941617 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | TRANSFORMER | 315406139868 | 20240514 | 1702 | 20240514 | 2024 | 2453841 | 202 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 606 | 37.5843 | -122.0866 | No | Partly Cloudy;32-90 F |  |  | 24-0066050 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1941682 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316709541675 | 20240515 | 1046 | 20240515 | 1118 | 2454344 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 32 | 37.6393 | -121.6371 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0066275 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1941914 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1109 | 14471109 | FUSE | 61577 | 20240516 | 1644 | 20240517 | 328 | 2460826 | 644 | Distribution Circuit | Equipment Failure/Involved | Underground | 25 | 16100 | 37.603 | -122.0694 | No | Clear;32-90 F | Elbow | Burned/flashed | 24-0066983 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1942155 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 10505 | 20240516 | 1941 | 20240517 | 130 | 2460961 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 9373 | 37.6328 | -122.079 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0066998 | OH | Sus | 31694294 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1942166 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | OCB | 1104/2 | 20240517 | 1535 | 20240517 | 2052 | 2461755 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5348 | 96063 | 37.6718 | -122.1596 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0067376 | OH | Sus | 31694502 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1942445 | 0 | Non-EPSS | N | 2024 | N/A
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 11428 | 20240518 | 845 | 20240518 | 1010 | 2462111 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 486 | 41310 | 37.5624 | -121.9895 | No | Clear;32-90 F |  |  | 24-0067481 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1942554 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 10563 | 20240518 | 1314 | 20240518 | 1838 | 2462234 | 324 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 324 | 37.6268 | -121.7565 | No | Clear;32-90 F | Circuit Breaker | Broken | 24-0067516 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1942573 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | TRANSFORMER | 316286042589 | 20240519 | 312 | 20240519 | 1523 | 2462454 | 731 | Transformer only | Vegetation | Tree - grew into line | 12 | 8772 | 37.6625 | -121.7843 | No | Clear;32-90 F | Transformer | Broken | 24-0067611 | OH | Sus | 31694601 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1942642 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | OTHER | OJS LD SIDE 6564 | 20240519 | 1138 | 20240520 | 32 | 2462613 | 774 | Distribution Circuit | Equipment Failure/Involved | Overhead | 425 | 53212 | 37.6961 | -122.0784 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0067632 | OH | Sus | 46249003 | BAY AREA | MAY | Open Circuit | 0 | No | No | No | 1942667 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 8919 | 20240519 | 2029 | 20240519 | 2200 | 2462766 | 91 | Distribution Circuit | Vegetation | Tree - bark fell into line | 7 | 636 | 37.633 | -121.8 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0067670 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1942702 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | FUSE | 14134 | 20240521 | 134 | 20240521 | 1436 | 2463873 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7820 | 37.6312 | -121.8876 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0068119 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1943018 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LIVERMORE-1103 | 12141103 | FUSE | 73359 | 20240521 | 1455 | 20240521 | 1646 | 2464464 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 9403 | 37.6793 | -121.7572 | No | Clear;32-90 F |  |  | 24-0068498 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1943256 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 9915 | 20240521 | 1456 | 20240521 | 1845 | 2464465 | 229 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1374 | 37.6406 | -121.8951 | No | Clear;Above 90 |  |  | 24-0068515 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1943267 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315588638980 | 20240521 | 2122 | 20240522 | 1048 | 2464642 | 806 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 5642 | 37.5606 | -122.0229 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0068532 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1943286 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | FUSE | 56676 | 20240522 | 136 | 20240522 | 1222 | 2464741 | 646 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 7983 | 37.6757 | -121.7192 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0068563 | UG | Sus | 31694578 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1943313 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | TRANSFORMER | 16152 | 20240522 | 243 | 20240523 | 815 | 2464745 | 1772 | Distribution Circuit | Equipment Failure/Involved | Underground | 412 | 29968 | 37.509 | -121.9193 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0068604 | UG | Sus | 35554969 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1943338 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2104 | 12232104 | OCB | 2104/2 | 20240522 | 1106 | 20240522 | 1557 | 2465094 | 291 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 14 | 4074 | 37.5029 | -121.9817 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0061806 | OH | Sus | 35493206 | BAY AREA | MAY | Line to Ground | 0 | No | Yes | No | 1943505 | 0 | Non-EPSS | N | 2024 | GRD TGT
MISSION | MISSION | FREMONT-1107 | 14351107 | FUSE | 6646 | 20240522 | 1506 | 20240522 | 1849 | 2465306 | 116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 414 | 13745 | 37.5316 | -121.9742 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0068859 | OH | Sus | 46249920 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1943552 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1101 | 13761101 | TRANSFORMER | 13009 | 20240522 | 1655 | 20240523 | 305 | 2465336 | 610 | Transformer only | Equipment Failure/Involved | Underground | 11 | 6710 | 37.6394 | -122.1311 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0068966 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1943561 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1101 | 13761101 | SWITCH | 20487 | 20240522 | 2256 | 20240523 | 301 | 2465511 | 14 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 950 | 37.6394 | -122.1305 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0068959 | UG | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1943617 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1107 | 14471107 | OCB | 1107/2 | 20240523 | 2038 | 20240524 | 814 | 2466208 | 696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7313 | 447375 | 37.5571 | -122.0583 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0069447 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1943878 | 0 | Non-EPSS | N | 2024 | OC
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 172885 | 20240523 | 2058 | 20240523 | 2140 | 2466235 | 42 | Distribution Circuit | Animal | Bird found | 33 | 1386 | 37.6621 | -121.6966 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0069450 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1943884 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315429341686 | 20240524 | 1815 | 20240524 | 1851 | 2466876 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 72 | 37.6344 | -122.0795 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0069908 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1944109 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | FUSE | 14069 | 20240525 | 1325 | 20240525 | 1512 | 2467509 | 107 | Distribution Circuit | Animal | Squirrel | 25 | 2712 | 37.6809 | -122.0858 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0070020 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1944221 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 51054 | 20240525 | 1913 | 20240525 | 2004 | 2467628 | 51 | Distribution Circuit | Animal | Bird found | 32 | 1647 | 37.7201 | -121.7249 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070039 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1944238 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | OCB | 1106/2/NORM | 20240527 | 947 | 20240527 | 1529 | 2468150 | 342 | Distribution Circuit | 3rd Party | Metallic Balloon | 17 | 5814 | 37.5014 | -121.9889 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0070195 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1944368 | 0 | Non-EPSS | N | 2024 | B & GRD
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 11428 | 20240527 | 1053 | 20240527 | 1154 | 2468196 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 486 | 29646 | 37.5624 | -121.9895 | No | Clear;32-90 F |  |  | 24-0070204 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1944372 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 10937 | 20240527 | 1129 | 20240527 | 1623 | 2468231 | 294 | Distribution Circuit | Equipment Failure/Involved | Underground | 176 | 51238 | 37.7681 | -121.9789 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0070215 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1944381 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | TRANSFORMER | 316290142628 | 20240527 | 1444 | 20240528 | 200 | 2468294 | 676 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3380 | 37.6636 | -121.7829 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070249 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1944413 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2101 | 14232101 | OTHER | T-28283 TWD T-28282 | 20240527 | 1728 | 20240527 | 1927 | 2468355 | 119 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 1428 | 37.7805 | -121.9173 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0070220 | UG | Sus | 0 | BAY AREA | MAY | None | 0 | No | No | No | 1944411 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | OCB | 1103/2/NORM | 20240527 | 1752 | 20240527 | 1907 | 2468362 | 75 | Distribution Circuit | 3rd Party | Metallic Balloon | 4335 | 325125 | 37.5014 | -121.989 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070246 | OH | Sus | 0 | BAY AREA | MAY | Line to Line | 0 | No | No | No | 1944408 | 0 | Non-EPSS | N | 2024 | B- C & 50
MISSION | MISSION | SAN RAMON-2102 | 14232102 | OTHER | T-28295 TWD T-24884 | 20240528 | 1709 | 20240528 | 1904 | 2469264 | 115 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 5405 | 37.7737 | -121.9178 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0070558 | UG | Sus | 35556412 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1944697 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1112 | 13761112 | TRANSFORMER | 315434042512 | 20240528 | 1916 | 20240529 | 256 | 2469319 | 460 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 5520 | 37.6569 | -122.0784 | No | Clear;32-90 F | Bushing | Leaking | 24-0070721 | OH | Sus | 0 | BAY AREA | MAY | Force Out | 0 | No | No | No | 1944715 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2107 | 14232107 | TRANSFORMER | T41510 | 20240530 | 102 | 20240530 | 1541 | 2470499 | 879 | Transformer only | Equipment Failure/Involved | Underground | 8 | 7032 | 37.7012 | -121.9365 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0071305 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1945235 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1112 | 13761112 | TRANSFORMER | 315462542541 | 20240530 | 124 | 20240530 | 253 | 2470505 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 801 | 37.6578 | -122.0687 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0071189 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1945084 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | MR650 | 20240530 | 535 | 20240530 | 1209 | 2470516 | 394 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 501 | 191035 | 37.5934 | -121.8844 | No | Clear;32-90 F |  |  | 24-0071194 | OH | Sus | 0 | BAY AREA | MAY | Three Phase Fault | 0 | No | No | No | 1945091 | 0 | EPSS Ckt | Y | 2024 | ABC GRD
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 605520 | 20240530 | 757 | 20240530 | 1206 | 2470580 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 17285 | 37.575 | -121.8795 | No | Clear;32-90 F |  |  | 24-0071259 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1945146 | 0 | EPSS Ckt | Y | 2024 | BG GRD
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 48700 | 20240530 | 1104 | 20240530 | 1536 | 2470863 | 272 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 5066 | 37.701 | -121.938 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0071269 | UG | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1945273 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 10134 | 20240531 | 1107 | 20240531 | 1235 | 2471765 | 88 | Distribution Circuit | 3rd Party | Metallic Balloon | 265 | 23361 | 37.5698 | -121.965 | No | Clear;32-90 F | Fuse | Burned Open | 24-0071907 | OH | Sus | 0 | BAY AREA | MAY | Line to Ground | 0 | No | No | No | 1945591 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | RECLOSER | 610800 | 20240601 | 639 | 20240601 | 829 | 2472334 | 110 | Distribution Circuit | Animal | Bird found | 263 | 28875 | 37.7009 | -122.0337 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0072128 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1945695 | 0 | EPSS Ckt | Y | 2024 | B - C & INT
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | FUSE | 11459 | 20240602 | 101 | 20240602 | 800 | 2473015 | 419 | Distribution Circuit | 3rd Party | Metallic Balloon | 40 | 16760 | 37.7031 | -122.0886 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0072304 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1945870 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1105 | 13111105 | JUMPER | O/J TO 14400 E14TH ST | 20240602 | 1418 | 20240603 | 200 | 2473235 | 702 | Distribution Circuit | Animal | Squirrel | 76 | 53352 | 37.7107 | -122.1365 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0072337 | OH | Sus | 0 | BAY AREA | JUN | Open Circuit | 0 | No | No | No | 1945901 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | FUSE | 10658 | 20240602 | 1659 | 20240602 | 1834 | 2473282 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 225 | 21375 | 37.6833 | -122.0767 | No | Clear;32-90 F |  |  | 24-0072351 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1945913 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | INTERRUPTER | 276016 | 20240603 | 948 | 20240603 | 1135 | 2473976 | 107 | Distribution Circuit | Animal | Squirrel | 22 | 2354 | 37.7022 | -121.703 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0072558 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1946145 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 9185 | 20240603 | 1736 | 20240604 | 335 | 2474436 | 599 | Distribution Circuit | 3rd Party | Vehicle | 42 | 25158 | 37.6639 | -121.6817 | No | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0072760 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | No | 1946220 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LIVERMORE-1101 | 12141101 | TRANSFORMER | 316279142848 | 20240603 | 2213 | 20240603 | 2227 | 2474508 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 126 | 37.6695 | -121.7868 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0072787 | OH | Sus | 0 | BAY AREA | JUN | Open Circuit | 0 | No | No | No | 1946245 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 10174 | 20240605 | 608 | 20240606 | 226 | 2475774 | 1218 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 21924 | 37.7136 | -121.9422 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0073481 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1946785 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2109 | 14502109 | TRANSFORMER | 27405 | 20240605 | 1455 | 20240606 | 250 | 2476389 | 715 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1430 | 37.6908 | -121.8833 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0073748 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1946896 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315656638715 | 20240605 | 2012 | 20240605 | 2048 | 2476928 | 36 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 576 | 37.5536 | -121.9994 | No | Clear;32-90 F |  |  | 24-0073864 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1946984 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316428142934 | 20240605 | 2044 | 20240605 | 2332 | 2476902 | 168 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 2352 | 37.6725 | -121.7352 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073856 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1946978 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 99785 | 20240605 | 2056 | 20240605 | 2139 | 2477040 | 43 | Distribution Circuit | 3rd Party | Metallic Balloon | 151 | 6493 | 37.6998 | -122.1143 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073861 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1946982 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 11428 | 20240606 | 829 | 20240606 | 932 | 2477513 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 324 | 20422 | 37.5624 | -121.9895 | No | Clear;32-90 F |  |  | 24-0074034 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1947171 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1103 | 14351103 | FUSE | 11160 | 20240606 | 933 | 20240606 | 1016 | 2477632 | 43 | Distribution Circuit | Animal | Bird found | 22 | 946 | 37.563 | -121.9761 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0074063 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1947195 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | RECLOSER | MR118 | 20240606 | 1622 | 20240607 | 49 | s1955953 | 507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2103 | 93828 | 37.5298 | -121.9877 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0060848 | OH | Sus | 35457149 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | Yes | 1955953 | 0 | Non-EPSS | N | 2024 | A GRD
MISSION | MISSION | VINEYARD-2107 | 14502107 | SWITCH | MR716 | 20240606 | 1758 | 20240606 | 1854 | 2478405 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3117 | 171822 | 37.6706 | -121.8553 | No | Clear;32-90 F |  |  | 24-0074380 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1947312 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2105 | 14502105 | TRANSFORMER | T5291 | 20240606 | 2038 | 20240607 | 510 | 2478633 | 512 | Distribution Circuit | Equipment Failure/Involved | Underground | 43 | 8716 | 37.6751 | -121.9065 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0074436 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1947352 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 9965 | 20240607 | 1508 | 20240607 | 1838 | 2479475 | 210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 23520 | 37.6097 | -122.0257 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0074806 | OH | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1947578 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | TASSAJARA-2113 | 14662113 | RECLOSER | MR276 | 20240608 | 745 | 20240608 | 818 | 2479916 | 33 | Distribution Circuit | Company Initiated | Coordination failure | 451 | 14883 | 37.7625 | -121.9841 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0074927 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1947681 | 0 | EPSS Ckt | Y | 2024 | A - B & GRD
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 11318 | 20240608 | 847 | 20240608 | 1053 | 2479972 | 126 | Distribution Circuit | Animal | Squirrel | 49 | 6174 | 37.7644 | -121.9821 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0074953 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1947722 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1107 | 14471107 | FUSE | 9555 | 20240608 | 1322 | 20240608 | 1505 | 2480167 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2678 | 37.551 | -122.0132 | No | Partly Cloudy;32-90 F |  |  | 24-0074988 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1947741 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | OCB | 2110/2 | 20240608 | 2231 | 20240609 | 1218 | 2480332 | 743 | Distribution Circuit | Equipment Failure/Involved | Underground | 4580 | 2604225 | 37.7009 | -121.7335 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0075058 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1947813 | 0 | EPSS Ckt | N | 2024 | GRD TIME OC
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 11825 | 20240609 | 627 | 20240609 | 826 | 2480424 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 100 | 11906 | 37.6662 | -122.1012 | No | Partly Cloudy;32-90 F |  |  | 24-0075075 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1947829 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 11428 | 20240609 | 810 | 20240609 | 926 | 2480481 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 486 | 36936 | 37.5624 | -121.9895 | No | Overcast;32-90 F |  |  | 24-0075081 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1947844 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 9184 | 20240609 | 1629 | 20240610 | 401 | 2480636 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 75756 | 37.5402 | -121.9485 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0075133 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1947875 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON SUB | 1423 | OCB | 2600/2 | 20240610 | 1156 | 20240610 | 1416 | 2481404 | 140 | Distribution Circuit | Company Initiated | Dig in- company | 1252 | 142471 | 37.745 | -121.9369 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0075318 | UG | Sus | 31696662 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1948104 | 0 | Non-EPSS | N | 2024 | GRD TGT
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | TRANSFORMER | 316292343634 | 20240610 | 2201 | 20240610 | 2330 | 2481853 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 890 | 37.6907 | -121.7827 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0075531 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1948190 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 13338 | 20240611 | 905 | 20240611 | 1028 | 2482090 | 83 | Distribution Circuit | Animal | Bird found | 146 | 12118 | 37.691 | -121.7632 | No | Clear;32-90 F | Fuse | Burned Open | 24-0075710 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1948416 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | SWITCH | MR716 | 20240611 | 1524 | 20240611 | 1636 | 2482520 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3119 | 224568 | 37.6706 | -121.8553 | No | Clear;Above 90 |  |  | 24-0075916 | OH | Sus | 0 | BAY AREA | JUN | Three Phase Fault | 0 | No | No | No | 1948486 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1105 | 13761105 | TRANSFORMER | 315347042189 | 20240611 | 1622 | 20240611 | 1930 | 2482581 | 188 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 3008 | 37.6476 | -122.1083 | No | Clear;32-90 F |  |  | 24-0075997 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1948534 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | FUSE | 15064 | 20240611 | 1635 | 20240611 | 1734 | 2482599 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 767 | 37.5598 | -122.0131 | No | Clear;32-90 F |  |  | 24-0075969 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1948512 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2106 | 14402106 | TRANSFORMER | 316397043379 | 20240611 | 1714 | 20240612 | 43 | 2482618 | 449 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 7633 | 37.6846 | -121.7463 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 24-0075993 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1948528 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 40004 | 20240611 | 1851 | 20240612 | 15 | 2482727 | 285 | Distribution Circuit | Equipment Failure/Involved | Underground | 891 | 99308 | 37.727 | -121.7268 | No | Clear;Above 90 | Fuse | Broken | 24-0076007 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1948544 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | FUSE | 9329 | 20240611 | 2055 | 20240611 | 2132 | 2482517 | 37 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 37 | 37.709 | -122.1213 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0076005 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1948541 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | SWITCH | 1045 | 20240612 | 823 | 20240612 | 833 | 2483336 | 10 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 90 | 37.7263 | -121.7272 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0076007 | UG | Sus | 35559953 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1948663 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 50832 | 20240612 | 1614 | 20240612 | 2111 | 2483860 | 297 | Distribution Circuit | Equipment Failure/Involved | Underground | 111 | 30305 | 37.7304 | -121.9373 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0076430 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1948825 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2111 | 14422111 | RECLOSER | MR444 | 20240613 | 1200 | 20240613 | 1428 | 2484619 | 148 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 444 | 37.7111 | -121.8037 | No | Clear;32-90 F | Circuit Breaker | Malfunctioning | 24-0076712 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | Yes | No | No | 1949105 | 0 | EPSS Ckt | Y | 2024 | A-B-C INST
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | MR650 | 20240613 | 1424 | 20240613 | 1818 | 2484794 | 234 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 502 | 91840 | 37.5934 | -121.8844 | No | Clear;32-90 F |  |  | 24-0076805 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | Yes | No | No | 1949131 | 0 | EPSS Ckt | Y | 2024 | B-C TGTS
MISSION | MISSION | VASCO-1101 | 13751101 | TRANSFORMER | 316411244194 | 20240614 | 151 | 20240614 | 1449 | 2485108 | 778 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 6224 | 37.7071 | -121.7416 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0077066 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1949363 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | TRANSFORMER | 315439543038 | 20240614 | 923 | 20240614 | 1416 | 2485431 | 293 | Transformer only | Animal | Bird found | 1 | 293 | 37.6714 | -122.0768 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0077146 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1949398 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1103 | 14471103 | RECLOSER | MR369 | 20240614 | 958 | 20240614 | 1124 | 2485522 | 86 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1486 | 127796 | 37.581 | -122.0538 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0077073 | UG | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1949367 | 0 | Non-EPSS | N | 2024 | B- C TGTS
MISSION | MISSION | SAN LEANDRO-1102 | 13111102 | OCB | 1102/2 | 20240615 | 1148 | 20240616 | 252 | 2486448 | 904 | Distribution Circuit | Animal | Bird found | 3981 | 745708 | 37.7107 | -122.1487 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0077367 | OH | Sus | 35560905 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | No | 1949539 | 0 | Non-EPSS | N | 2024 | GRD
MISSION | MISSION | DUMBARTON-1106 | 14471106 | JUMPER | BURNED OPEN JUMPER SOURCE SIDE OF 62231 | 20240616 | 1722 | 20240617 | 1436 | 2487132 | 1274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1274 | 37.5658 | -122.111 | No | Clear;32-90 F | Jumper | Burned Open | 24-0077533 | OH | Sus | 0 | BAY AREA | JUN | Open Circuit | 0 | No | No | No | 1949683 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2109 | 14502109 | TRANSFORMER | T6785 | 20240617 | 902 | 20240617 | 1457 | 2487587 | 355 | Transformer only | 3rd Party | Customer Equipment | 1 | 355 | 37.6849 | -121.8763 | No | Clear;32-90 F | Transformer | Normal | 24-0071409 | OH | Sus | 35438474 | BAY AREA | JUN | None | 0 | No | No | No | 1949801 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1103 | 14351103 | TRANSFORMER | 315726539288 | 20240617 | 1339 | 20240617 | 1719 | 2487950 | 220 | Transformer only | Company Initiated | Personnel- company | 4 | 880 | 37.5697 | -121.9757 | No | Clear;32-90 F | Other | Normal | 24-0077835 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1949947 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | TRANSFORMER | T1082 | 20240617 | 1355 | 20240617 | 1420 | 2487967 | 25 | Transformer only | Equipment Failure/Involved | Underground | 29 | 725 | 37.6793 | -121.9215 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0077731 | UG | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1949903 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 11428 | 20240618 | 912 | 20240618 | 1218 | 2489109 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 486 | 90396 | 37.5624 | -121.9895 | No | Partly Cloudy;32-90 F |  |  | 24-0078119 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1950228 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1105 | 13501105 | JUMPER | FB'S IFO 38075 PARKMONT DR | 20240618 | 1046 | 20240618 | 2007 | 2489525 | 561 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 25806 | 37.5607 | -121.9885 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0078283 | OH | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1950285 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 7914 | 20240618 | 1056 | 20240618 | 1348 | 2489260 | 172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 496 | 28609 | 37.6941 | -122.1111 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0078120 | OH | Sus | 31697740 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1950229 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | TRANSFORMER | 315478143500 | 20240618 | 1334 | 20240618 | 1430 | 2489387 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 1288 | 37.6842 | -122.0638 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0078205 | OH | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1950257 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | TASSAJARA-2113 | 14662113 | OTHER | J71435 TWD 27406 | 20240619 | 839 | 20240619 | 955 | 2489864 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 76 | 37.7702 | -121.9304 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0078072 | UG | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1950393 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | JUMPER | WIRE DOWN | 20240619 | 934 | 20240619 | 1420 | 2489997 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 5625 | 37.6297 | -122.0897 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0078446 | OH | Sus | 46265398 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | No | 1950445 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | FUSE | 11788 | 20240620 | 1112 | 20240620 | 1346 | 2490790 | 154 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 112 | 17248 | 37.5586 | -122.0221 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078678 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1950610 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2109 | 14502109 | SWITCH | 72162 | 20240621 | 718 | 20240621 | 731 | 2491320 | 13 | Distribution Circuit | Company Initiated | Operating error | 6723 | 87399 | 37.6704 | -121.8548 | No | Partly Cloudy;32-90 F |  |  | 24-0051278 | OH | Sus | 7099076 | BAY AREA | JUN | None | 0 | No | No | No | 1950753 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DIXON LANDING-2106 | 14722106 | SWITCH | 85084 | 20240621 | 1109 | 20240621 | 1115 | 2495288 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 6 | 37.4766 | -121.932 | No | Clear;32-90 F | Customer Equipment | Normal | 24-0079064 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1951833 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | FUSE | 7650 | 20240621 | 1247 | 20240621 | 1433 | 2491911 | 106 | Distribution Circuit | 3rd Party | Metallic Balloon | 88 | 9328 | 37.7056 | -122.1523 | No | Clear;32-90 F | Fuse | Burned Open | 24-0079211 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1950940 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1108 | 12221108 | OCB | 1108/2/NORM | 20240621 | 2356 | 20240622 | 449 | 2492219 | 293 | Distribution Circuit | 3rd Party | Vandalism | 231 | 60228 | 37.5014 | -121.9888 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0079343 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1950987 | 0 | Non-EPSS | N | 2024 | B & GRD
MISSION | MISSION | JARVIS-1101 | 13501101 | TRANSFORMER | 315587740462 | 20240623 | 1540 | 20240623 | 1610 | 2493038 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 450 | 37.6014 | -122.0242 | No | Clear;32-90 F | Fuse | Broken | 24-0079553 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1951171 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | FUSE | 12492 | 20240623 | 1646 | 20240624 | 237 | 2493047 | 591 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 5679 | 37.6995 | -121.697 | No | Clear;Above 90 | Connector or Splice (UG) | Broken | 24-0079554 | UG | Sus | 46267866 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1951172 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 54968 | 20240623 | 1745 | 20240625 | 303 | 2493126 | 1998 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 9990 | 37.6184 | -122.0369 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0079561 | OH | Sus | 35562362 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1951181 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | 794616 | 20240624 | 512 | 20240624 | 805 | 2493304 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1805 | 210298 | 37.6566 | -121.7615 | No | Clear;32-90 F |  |  | 24-0079613 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1951227 | 0 | EPSS Ckt | Y | 2024 | NA
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | OTHER | WIRE DOWN RISER 10747 | 20240624 | 809 | 20240627 | 1010 | 2493415 | 4441 | Distribution Circuit | 3rd Party | Vehicle | 2 | 8882 | 37.7067 | -122.1531 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0079667 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | Yes | 1951307 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 8919 | 20240624 | 1759 | 20240624 | 1919 | 2494588 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 559 | 37.633 | -121.8 | No | Clear;32-90 F |  |  | 24-0079976 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1951546 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | TRANSFORMER | 315481044218 | 20240624 | 2137 | 20240624 | 2231 | 2494755 | 54 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 918 | 37.704 | -122.0631 | No | Clear;32-90 F |  |  | 24-0080056 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1951616 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | OCB | 2105/2 | 20240624 | 2350 | 20240625 | 4 | 2494809 | 14 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2126 | 29764 | 37.7009 | -121.7336 | No | Clear;32-90 F |  |  | 24-0080066 | OH | Sus | 0 | BAY AREA | JUN | Line to Line | 0 | No | No | No | 1951622 | 0 | Non-EPSS | N | 2024 | A-B PHASE & GRD (INST OC)
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | 263964 | 20240624 | 2351 | 20240625 | 815 | 2494806 | 504 | Distribution Circuit | Company Initiated | Personnel- company | 711 | 358344 | 37.6465 | -121.7858 | No | Clear;32-90 F | Recloser | Normal | 24-0080067 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1951623 | 0 | EPSS Ckt | Y | 2024 | NO TARGETS
MISSION | MISSION | GRANT-1102 | 14381102 | TRANSFORMER | 315309442082 | 20240625 | 543 | 20240626 | 253 | 2494913 | 1270 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 8890 | 37.6446 | -122.1212 | No | Clear;32-90 F | Transformer | Broken | 24-0080189 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1951764 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | FUSE | 60964 | 20240625 | 957 | 20240625 | 2152 | 2495279 | 678 | Distribution Circuit | Equipment Failure/Involved | Underground | 112 | 19017 | 37.5195 | -121.914 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0080291 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1951870 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | RECLOSER | 609690 | 20240625 | 1347 | 20240625 | 1642 | 2495536 | 175 | Distribution Circuit | Animal | Bird found | 1831 | 299306 | 37.6647 | -121.9162 | No | Clear;32-90 F | Fuse | Normal | 24-0080374 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1951914 | 0 | EPSS Ckt | Y | 2024 | A PH AND GRD TGT
MISSION | MISSION | NEWARK 21KV-2110 | 12232110 | OCB | 2110/2 | 20240625 | 1606 | 20240626 | 200 | 2495683 | 594 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 19008 | 37.5029 | -121.9815 | No | Clear;32-90 F | Switch (OH) | Arcing | 24-0046665 | OH | Sus | 46202824 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1951943 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | OCB | 2103/2 | 20240625 | 1607 | 20240626 | 435 | s1964163 | 748 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5519 | 772092 | 37.5029 | -121.9818 | No | Clear;32-90 F | Switch (OH) | Arcing | 24-0046665 | OH | Sus | 46202824 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1964163 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | LIVERMORE-1102 | 12141102 | OTHER | HOT WIRE DOWN @ 8747 | 20240625 | 1754 | 20240625 | 1915 | 2495783 | 81 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1835 | 97331 | 37.6705 | -121.7805 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0080539 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | Yes | 1951965 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1102 | 14381102 | TRANSFORMER | 315309442082 | 20240626 | 807 | 20240626 | 1800 | 2496371 | 593 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4151 | 37.6446 | -122.1212 | No | Overcast;32-90 F | Fuse | Burned Open | 24-0080764 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1952174 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | TRANSFORMER | T6881 | 20240626 | 1643 | 20240627 | 312 | 2497058 | 629 | Distribution Circuit | Equipment Failure/Involved | Underground | 121 | 13489 | 37.6957 | -122.0794 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0081067 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1952284 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1107 | 13501107 | TRANSFORMER | T7633 | 20240627 | 2040 | 20240628 | 959 | 2498029 | 799 | Distribution Circuit | Equipment Failure/Involved | Underground | 188 | 18356 | 37.5853 | -122.0289 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0081605 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1952651 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | T28136 | 20240628 | 304 | 20240628 | 1420 | 2498197 | 676 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 23484 | 37.5174 | -122.0488 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0081620 | UG | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1952672 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | TRANSFORMER | 315842636582 | 20240628 | 1959 | 20240628 | 2043 | 2499009 | 44 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 264 | 37.4959 | -121.934 | No | Clear;32-90 F |  |  | 24-0081971 | OH | Sus | 0 | BAY AREA | JUN | None | 0 | No | No | No | 1952907 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | TRANSFORMER | 315520741693 | 20240630 | 1835 | 20240630 | 2205 | 2500033 | 210 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 420 | 37.6348 | -122.048 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0082243 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1953156 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1104 | 14471104 | TRANSFORMER | 315576837903 | 20240701 | 1116 | 20240701 | 2025 | 2500657 | 549 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 5490 | 37.5309 | -122.0264 | No | Clear;32-90 F | Transformer | Broken | 24-0082469 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1953333 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | TRANSFORMER | 26257 | 20240701 | 1206 | 20240701 | 1310 | 2500759 | 64 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 64 | 37.5069 | -121.959 | No | Clear;Above 90 |  |  | 24-0082528 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1953349 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1104 | 14471104 | TRANSFORMER | 315576037892 | 20240701 | 1530 | 20240701 | 2023 | 2500996 | 293 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 4981 | 37.5306 | -122.0267 | No | Clear;32-90 F | Transformer | Contaminated | 24-0082617 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953363 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2116 | 14232116 | OCB | 2116/2 | 20240701 | 1743 | 20240702 | 151 | 2500906 | 488 | Distribution Circuit | Equipment Failure/Involved | Underground | 1978 | 324776 | 37.745 | -121.9369 | No | Clear;Above 90 | Elbow | Failed/Faulted | 24-0082689 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953384 | 0 | Non-EPSS | N | 2024 | PHASE & GRD
MISSION | MISSION | VINEYARD-2107 | 14502107 | OCB | 2107/2 | 20240701 | 1939 | 20240702 | 1436 | 2501237 | 1137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4254 | 1081468 | 37.6697 | -121.8543 | No | Clear;32-90 F |  |  | 24-0082718 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953401 | 0 | EPSS Ckt | Y | 2024 | PHASE & GRD
MISSION | MISSION | VINEYARD-2108 | 14502108 | OCB | 2108/2 | 20240701 | 1939 | 20240702 | 1227 | 2501294 | 659 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4085 | 1908271 | 37.6697 | -121.8543 | No | Clear;32-90 F | Jumper | Burned Open | 24-0082721 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953403 | 0 | EPSS Ckt | N | 2024 | NO TARGETS
MISSION | MISSION | RADUM-1105 | 13151105 | RECLOSER | 420576 | 20240701 | 1942 | 20240702 | 1201 | 2501278 | 979 | Distribution Circuit | Company Initiated | Personnel- company | 445 | 288479 | 37.6491 | -121.8809 | No | Clear;32-90 F | Recloser | Normal | 24-0082722 | OH | Sus | 0 | BAY AREA | JUL | Multi-Fault | 0 | No | No | No | 1953404 | 0 | EPSS Ckt | Y | 2024 | A- B- SGF
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | TRANSFORMER | 315223744199 | 20240701 | 2329 | 20240702 | 404 | 2501420 | 275 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 3575 | 37.7023 | -122.152 | No | Clear;32-90 F | Secondary | Broken | 24-0082759 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1953435 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 64737 | 20240702 | 630 | 20240702 | 940 | 2501565 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 250 | 45484 | 37.5458 | -121.9443 | No | Clear;32-90 F |  |  | 24-0082866 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953532 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 64737 | 20240702 | 951 | 20240702 | 1051 | 2501764 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 250 | 15000 | 37.5458 | -121.9443 | No | Clear-Heat Wave;32-90 F |  |  | 24-0082922 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1953576 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2111 | 14422111 | FUSE | 36076 | 20240702 | 1722 | 20240703 | 246 | 2502565 | 310 | Distribution Circuit | Equipment Failure/Involved | Underground | 53 | 10381 | 37.6986 | -121.8056 | No | Clear-Heat Wave;Above 90 | Connector or Splice (UG) | Failed/Faulted | 24-0083211 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953678 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 64876 | 20240702 | 1738 | 20240703 | 1518 | 2502598 | 1300 | Distribution Circuit | Equipment Failure/Involved | Underground | 43 | 43921 | 37.7388 | -121.9488 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Broken | 24-0083422 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953862 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2107 | 14232107 | OCB | 2107/2 | 20240702 | 1816 | 20240702 | 2150 | 2502757 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5148 | 1032924 | 37.7448 | -121.9369 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083230 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | Yes | No | No | 1953685 | 0 | EPSS Ckt | Y | 2024 | B- GRD INST TGTS
MISSION | MISSION | SAN RAMON-2108 | 14232108 | OCB | 2108/2 | 20240702 | 1816 | 20240704 | 513 | 2502752 | 1446 | Distribution Circuit | Equipment Failure/Involved | Underground | 6191 | 1722958 | 37.7448 | -121.9369 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Broken | 24-0083226 | UG | Sus | 35563984 | BAY AREA | JUL | Line to Ground | 0 | Yes | No | No | 1953681 | 0 | EPSS Ckt | Y | 2024 | B- GRD INST TGTS
MISSION | MISSION | LAS POSITAS-2106 | 14402106 | TRANSFORMER | 316370043435 | 20240702 | 1819 | 20240702 | 2143 | 2502812 | 204 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1836 | 37.6861 | -121.7557 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083347 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953771 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 70032 | 20240702 | 1832 | 20240702 | 2348 | 2502631 | 316 | Distribution Circuit | Equipment Failure/Involved | Underground | 160 | 17664 | 37.6815 | -121.7339 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0083240 | UG | Sus | 35563984 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953691 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315420244894 | 20240702 | 1850 | 20240703 | 659 | 2502856 | 729 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 13567 | 37.7223 | -122.0845 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 24-0083303 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953738 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 50832 | 20240702 | 1917 | 20240702 | 2022 | 2502926 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 1430 | 37.7304 | -121.9373 | No | Clear-Heat Wave;32-90 F |  |  | 24-0083288 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1953725 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | TRANSFORMER | 315532941128 | 20240702 | 1936 | 20240702 | 2033 | 2502955 | 57 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 912 | 37.6194 | -122.0435 | No | Clear-Heat Wave;32-90 F |  |  | 24-0083306 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953741 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | RECLOSER | 420576 | 20240702 | 1955 | 20240702 | 2103 | 2503053 | 68 | Distribution Circuit | Company Initiated | Personnel- company | 445 | 30260 | 37.6491 | -121.8809 | No | Clear;32-90 F | Recloser | Normal | 24-0083287 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953724 | 0 | EPSS Ckt | Y | 2024 | SGF
MISSION | MISSION | SAN RAMON-2110 | 14232110 | FUSE | 40921 | 20240702 | 2033 | 20240703 | 1119 | 2503120 | 886 | Distribution Circuit | Equipment Failure/Involved | Underground | 34 | 15496 | 37.752 | -121.9365 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0083372 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953790 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | TRANSFORMER | 315441843200 | 20240702 | 2220 | 20240703 | 905 | 2503064 | 645 | Transformer only | Equipment Failure/Involved | Electrical Overload | 40 | 25695 | 37.6758 | -122.0761 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0083352 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953777 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2107 | 14232107 | OCB | 2107/2 | 20240702 | 2223 | 20240702 | 2239 | 2503244 | 16 | Distribution Circuit | Company Initiated | Coordination failure | 5146 | 82336 | 37.7448 | -121.9369 | No | Clear;32-90 F | Circuit Breaker | Normal | 24-0083351 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953776 | 0 | EPSS Ckt | Y | 2024 | B6 GRD
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 9443 | 20240703 | 521 | 20240704 | 148 | 2503454 | 1227 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 22367 | 37.6541 | -121.8633 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0083444 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953884 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 13213 | 20240703 | 559 | 20240703 | 715 | 2503461 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 89 | 6757 | 37.654 | -121.8536 | No | Clear;32-90 F |  |  | 24-0083415 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953854 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315553041018 | 20240703 | 619 | 20240703 | 1218 | 2503472 | 359 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 1795 | 37.6164 | -122.0364 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0083446 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953886 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315557441005 | 20240703 | 708 | 20240703 | 1218 | 2503489 | 310 | Transformer only | Equipment Failure/Involved | Electrical Overload | 14 | 4340 | 37.6161 | -122.0349 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0083448 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953888 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315607138247 | 20240703 | 759 | 20240703 | 829 | 2503543 | 30 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 330 | 37.5406 | -122.0163 | No | Clear;32-90 F |  |  | 24-0083439 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953881 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | T6923 | 20240703 | 1003 | 20240703 | 1238 | 2503652 | 155 | Transformer only | Equipment Failure/Involved | Underground | 22 | 3410 | 37.5261 | -122.0505 | No | Clear-Heat Wave;32-90 F | Secondary | Contaminated | 24-0083587 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953918 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | TRANSFORMER | 315798336661 | 20240703 | 1309 | 20240703 | 2110 | 2503737 | 481 | Transformer only | Environmental/External | Fire- Forest/Grass | 13 | 6253 | 37.4979 | -121.9495 | No | Heat Wave-Clear;Above 90 | Transformer | Leaking | 24-0083615 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953925 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | TRANSFORMER | 315544742689 | 20240703 | 1618 | 20240704 | 506 | 2504034 | 768 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 7140 | 37.6623 | -122.0403 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083810 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954004 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | RECLOSER | MR168 | 20240703 | 1618 | 20240703 | 1840 | 2504021 | 142 | Distribution Circuit | Equipment Failure/Involved | Underground | 1946 | 121567 | 37.6621 | -121.8804 | No | Clear-Heat Wave;Above 90 | Elbow | Failed/Faulted | 24-0083726 | UG | Sus | 35563984 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953952 | 0 | Non-EPSS | N | 2024 | A PH & GRD
MISSION | MISSION | SAN LEANDRO-1101 | 13111101 | FUSE | 50190 | 20240703 | 1622 | 20240704 | 1513 | 2504032 | 1371 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1371 | 37.7135 | -122.1596 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Deteriorated | 24-0083787 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953991 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1108 | 14471108 | TRANSFORMER | T5317 | 20240703 | 1701 | 20240703 | 1811 | 2504173 | 70 | Transformer only | Unknown Cause | Patrol - found nothing | 29 | 2030 | 37.5879 | -122.0479 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083775 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1953982 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1108 | 14471108 | TRANSFORMER | T5321 | 20240703 | 1701 | 20240703 | 1756 | 2504172 | 55 | Transformer only | Unknown Cause | Patrol - found nothing | 31 | 1705 | 37.5874 | -122.0506 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083778 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1953985 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1108 | 14471108 | TRANSFORMER | T5322 | 20240703 | 1712 | 20240703 | 1756 | 2504171 | 44 | Transformer only | Unknown Cause | Patrol - found nothing | 24 | 1056 | 37.5877 | -122.0513 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083777 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1953984 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | TRANSFORMER | 315806937832 | 20240703 | 1811 | 20240704 | 243 | 2504204 | 512 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 3072 | 37.53 | -121.9471 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0083851 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954033 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DIXON LANDING-2105 | 14722105 | OCB | 2105/2 | 20240703 | 1834 | 20240703 | 1934 | 2504252 | 60 | Distribution Circuit | Equipment Failure/Involved | Underground | 158 | 6708 | 37.457 | -121.9209 | No | Clear-Heat Wave;Above 90 | Elbow | Burned/flashed | 24-0083791 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1953993 | 0 | Non-EPSS | N | 2024 | UNK
MISSION | MISSION | DUMBARTON-1107 | 14471107 | FUSE | 54962 | 20240703 | 1852 | 20240703 | 2052 | 2504267 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 501 | 60120 | 37.5552 | -122.0322 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083855 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954035 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2110 | 14232110 | FUSE | 40976 | 20240703 | 2116 | 20240704 | 1139 | 2504469 | 863 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 14579 | 37.7771 | -121.9608 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0083894 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954072 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 10592 | 20240703 | 2153 | 20240704 | 912 | 2504518 | 679 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 23086 | 37.6297 | -122.0775 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0083898 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | Yes | No | 1954075 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 51382 | 20240704 | 541 | 20240704 | 813 | 2504717 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 269 | 40888 | 37.6919 | -122.1101 | No | Clear;32-90 F |  |  | 24-0083935 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1954103 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1104 | 14471104 | FUSE | 8983 | 20240704 | 1002 | 20240704 | 1102 | 2504895 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 5883 | 37.5362 | -122.0345 | No | Clear-Heat Wave;32-90 F |  |  | 24-0083976 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954126 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 7876 | 20240704 | 1420 | 20240704 | 1950 | 2505097 | 330 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 6270 | 37.6829 | -121.7789 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Leaking | 24-0084041 | UG | Sus | 0 | BAY AREA | JUL | Three Phase Fault | 0 | No | No | No | 1954156 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10648 | 20240704 | 1702 | 20240704 | 1741 | 2505252 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 4836 | 37.5468 | -121.9467 | No | Clear-Heat Wave;32-90 F |  |  | 24-0084083 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1954173 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | TRANSFORMER | 28365 | 20240704 | 1828 | 20240705 | 7 | 2505393 | 339 | Transformer only | Equipment Failure/Involved | Underground | 5 | 1695 | 37.6494 | -121.8992 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084107 | UG | Sus | 0 | BAY AREA | JUL | Three Phase Fault | 0 | No | No | No | 1954191 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | SWITCH | MR663 | 20240704 | 2243 | 20240705 | 530 | 2505547 | 407 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 208 | 49511 | 37.6294 | -122.0475 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0084157 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1954242 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 11082 | 20240705 | 903 | 20240705 | 952 | 2505846 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 9053 | 37.6315 | -122.0745 | No | Clear-Heat Wave;32-90 F |  |  | 24-0084267 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954314 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | TRANSFORMER | 315633638360 | 20240705 | 2258 | 20240705 | 2324 | 2507201 | 26 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 234 | 37.5437 | -122.0072 | No | Clear;32-90 F |  |  | 24-0084491 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954464 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | RECLOSER | 343456 | 20240706 | 656 | 20240706 | 832 | 2507375 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1855 | 178080 | 37.7103 | -122.0738 | No | Clear;32-90 F |  |  | 24-0084528 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1954499 | 0 | EPSS Ckt | Y | 2024 | AB I OC TGT
MISSION | MISSION | SAN RAMON-2111 | 14232111 | FUSE | 11563 | 20240706 | 1416 | 20240706 | 1505 | 2507628 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 588 | 37.7034 | -121.9109 | No | Clear-Heat Wave;Above 90 | Fuse | Failed/Faulted | 24-0084629 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954538 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | FUSE | 73945 | 20240706 | 1442 | 20240706 | 1728 | 2507645 | 166 | Distribution Circuit | Equipment Failure/Involved | Underground | 89 | 14774 | 37.6558 | -121.7857 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Broken | 24-0084642 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954547 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | SWITCH | 3842 | 20240707 | 235 | 20240707 | 241 | 2508638 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 89 | 534 | 37.6578 | -121.7849 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0084642 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1954697 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 12471 | 20240707 | 530 | 20240707 | 643 | 2508717 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 141 | 10293 | 37.7457 | -121.9537 | No | Clear;32-90 F |  |  | 24-0084811 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954710 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 13320 | 20240707 | 1241 | 20240707 | 1338 | 2508922 | 57 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 92 | 5220 | 37.7667 | -121.9803 | No | Clear;32-90 F |  |  | 24-0084870 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954747 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | INTERRUPTER | 981328 | 20240707 | 1607 | 20240708 | 1101 | 2509101 | 1134 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 3266 | 37.7224 | -122.194 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0084939 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954795 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | OCB | 2110/2 | 20240707 | 1910 | 20240708 | 335 | 2509373 | 505 | Distribution Circuit | Equipment Failure/Involved | Underground | 1364 | 132662 | 37.7009 | -121.7335 | No | Clear;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0084946 | UG | Sus | 31698893 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954803 | 0 | EPSS Ckt | N | 2024 | GRD- B/U PH TGT
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | MR190 | 20240708 | 438 | 20240708 | 850 | 2509753 | 252 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3535 | 795540 | 37.6652 | -121.7354 | No | Clear;32-90 F |  |  | 24-0085053 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1954904 | 0 | EPSS Ckt | Y | 2024 | AC AND GRD TGT
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | FUSE | 10556 | 20240708 | 1040 | 20240708 | 1141 | 2510034 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 122 | 37.6563 | -121.7492 | No | Clear;32-90 F |  |  | 24-0085179 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1955038 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | LIVERMORE-1102 | 12141102 | FUSE | 9498 | 20240708 | 1511 | 20240708 | 1702 | 2510531 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 127 | 14097 | 37.673 | -121.7806 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0085268 | OH | Sus | 31699640 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1955082 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2101 | 14232101 | TRANSFORMER | 28862 | 20240710 | 1036 | 20240710 | 1129 | 2512381 | 53 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 583 | 37.7605 | -121.8891 | No | Clear;32-90 F |  |  | 24-0086109 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1955622 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | JUMPER | O/J 1 N/W/OF 14430 | 20240710 | 1359 | 20240710 | 2133 | 2512560 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 22700 | 37.7004 | -122.118 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0086201 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1955636 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | SWITCH | 30440SW | 20240710 | 1415 | 20240711 | 26 | 2512598 | 611 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 5499 | 37.6193 | -122.0551 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0086081 | UG | Sus | 35565477 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1955642 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1113 | 13761113 | TRANSFORMER | 315360341426 | 20240711 | 608 | 20240711 | 922 | 2513151 | 194 | Transformer only | Vegetation | Tree - palm frond fell into line | 19 | 3686 | 37.6268 | -122.1032 | No | Clear;32-90 F | Transformer | Normal | 24-0086529 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1955765 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | FUSE | 73718 | 20240711 | 1047 | 20240711 | 2346 | 2513650 | 779 | Distribution Circuit | Equipment Failure/Involved | Underground | 157 | 55948 | 37.7205 | -121.872 | No | Clear-Heat Wave;32-90 F | Transformer (UG) | Broken | 24-0086732 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1955959 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | FUSE | 12525 | 20240711 | 1452 | 20240712 | 100 | 2513930 | 608 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 608 | 37.5053 | -121.9619 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Leaking | 24-0086832 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1955981 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | RECLOSER | MR172 | 20240711 | 1554 | 20240711 | 2009 | 2514005 | 255 | Distribution Circuit | Equipment Failure/Involved | Underground | 3049 | 562993 | 37.657 | -121.9009 | No | Clear-Heat Wave;Above 90 | Connector or Splice (UG) | Failed/Faulted | 24-0086870 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1955991 | 0 | EPSS Ckt | Y | 2024 | C PHASE TO GRD
MISSION | MISSION | DUMBARTON-1107 | 14471107 | FUSE | 54962 | 20240711 | 1938 | 20240711 | 2025 | 2514334 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 501 | 23547 | 37.5552 | -122.0322 | No | Clear;32-90 F |  |  | 24-0086964 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956042 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | RECLOSER | 806392 | 20240711 | 2028 | 20240712 | 1055 | 2514441 | 867 | Distribution Circuit | Company Initiated | Personnel- company | 244 | 175086 | 37.6386 | -121.8864 | No | Clear;32-90 F | Recloser | Normal | 24-0086974 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956050 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD EVENT
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 40897 | 20240711 | 2259 | 20240712 | 140 | 2514527 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 8531 | 37.7482 | -121.9556 | No | Clear;32-90 F |  |  | 24-0087047 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956116 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1108 | 14471108 | SWITCH | 3082 | 20240711 | 2303 | 20240712 | 156 | 2514519 | 173 | Distribution Circuit | Equipment Failure/Involved | Underground | 55 | 4741 | 37.5862 | -122.0513 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0084002 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1956098 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | T8122 | 20240712 | 512 | 20240712 | 1502 | 2514981 | 590 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 4130 | 37.7493 | -121.9519 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0087185 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956251 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | RECLOSER | 806392 | 20240712 | 1706 | 20240712 | 1853 | 2515388 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 244 | 26108 | 37.6386 | -121.8864 | No | Clear-Heat Wave;Above 90 |  |  | 24-0087414 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1956344 | 0 | EPSS Ckt | Y | 2024 | A & B
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRANSFORMER | 315496544138 | 20240712 | 1930 | 20240713 | 145 | 2515326 | 375 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 5250 | 37.7019 | -122.0577 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087421 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956348 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | FUSE | 9556 | 20240713 | 543 | 20240713 | 715 | 2515765 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 9200 | 37.5276 | -121.9599 | No | Overcast;32-90 F | Secondary | Broken | 24-0087474 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956418 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 51382 | 20240713 | 551 | 20240713 | 924 | 2515875 | 213 | Distribution Circuit | Animal | Bird found | 269 | 57297 | 37.6919 | -122.1101 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0087503 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1956447 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 12113 | 20240713 | 553 | 20240713 | 2133 | 2515770 | 940 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 23316 | 37.6369 | -121.8815 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0087489 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956436 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1108 | 14351108 | FUSE | 60309 | 20240713 | 613 | 20240713 | 919 | 2515783 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 228 | 42408 | 37.5363 | -121.9764 | No | Overcast;32-90 F |  |  | 24-0087502 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956446 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315762837685 | 20240713 | 736 | 20240713 | 1145 | 2515816 | 249 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 5229 | 37.5258 | -121.9622 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0087487 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956434 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | FUSE | 10831 | 20240713 | 2202 | 20240715 | 455 | 2516306 | 1853 | Distribution Circuit | Equipment Failure/Involved | Underground | 48 | 88944 | 37.7017 | -122.1445 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0087651 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956562 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2110 | 14232110 | FUSE | 20061 | 20240714 | 503 | 20240714 | 2059 | 2516440 | 956 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 22939 | 37.7577 | -121.9399 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0087706 | UG | Sus | 35566222 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956617 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316476141907 | 20240714 | 1727 | 20240715 | 357 | 2516800 | 630 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1260 | 37.6444 | -121.7181 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087755 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956664 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | TRANSFORMER | 315119344340 | 20240714 | 2223 | 20240715 | 1 | 2516861 | 98 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 980 | 37.7057 | -122.1886 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0087799 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956710 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | FUSE | 7851 | 20240715 | 750 | 20240715 | 1115 | 2516955 | 205 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 205 | 37.5733 | -122.0871 | No | Partly Cloudy;32-90 F |  |  | 24-0087958 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1956879 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | T88798 | 20240715 | 1043 | 20240715 | 1306 | 2517301 | 143 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 286 | 37.6242 | -122.0861 | No | Overcast;32-90 F |  |  | 24-0088055 | OH | Sus | 0 | BAY AREA | JUL | None | 0 | No | No | No | 1956918 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | MR186 | 20240716 | 532 | 20240716 | 719 | 2517874 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1284 | 37.7324 | -121.7123 | No | Clear;32-90 F |  |  | 24-0088259 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1957017 | 0 | EPSS Ckt | Y | 2024 | A & C
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | FUSE | 11371 | 20240716 | 1037 | 20240716 | 1547 | 2518163 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 139 | 43090 | 37.7072 | -122.113 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0088406 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1957187 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1104 | 14471104 | OCB | 1104/2 | 20240716 | 1059 | 20240716 | 1846 | 2518192 | 467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3057 | 508194 | 37.5571 | -122.0585 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0088425 | OH | Sus | 0 | BAY AREA | JUL | Three Phase Fault | 0 | No | Yes | No | 1957194 | 0 | Non-EPSS | N | 2024 | A- B- C PH
MISSION | MISSION | MT EDEN-1107 | 13761107 | JUMPER | WIRE DOWN | 20240716 | 2032 | 20240717 | 304 | 2518947 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 6555 | 37.6097 | -122.0661 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0088669 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | Yes | Yes | 1957285 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 15428 | 20240716 | 2306 | 20240717 | 225 | 2518987 | 199 | Distribution Circuit | Equipment Failure/Involved | Underground | 43 | 8557 | 37.5695 | -121.9654 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0088692 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1957314 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 9911 | 20240717 | 1113 | 20240717 | 1353 | 2519428 | 160 | Distribution Circuit | 3rd Party | Vehicle | 34 | 5381 | 37.6586 | -121.8893 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0088910 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1957505 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2104 | 14402104 | OCB | 2104/2 | 20240717 | 1538 | 20240718 | 221 | 2519698 | 643 | Distribution Circuit | Equipment Failure/Involved | Underground | 1217 | 127225 | 37.7009 | -121.7336 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0089018 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1957534 | 0 | Non-EPSS | N | 2024 | A & GRD OC
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 10449 | 20240717 | 1820 | 20240717 | 2011 | 2519860 | 111 | Distribution Circuit | Animal | Bird found | 46 | 5106 | 37.6241 | -122.0658 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0089095 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1957564 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | FUSE | 61749 | 20240717 | 1833 | 20240717 | 1917 | 2519861 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 264 | 37.5706 | -122.0773 | No | Clear;32-90 F |  |  | 24-0089086 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1957560 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | TRANSFORMER | 315882135780 | 20240717 | 2325 | 20240718 | 1159 | 2519973 | 754 | Transformer only | Vegetation | Tree - bark fell into line | 10 | 7540 | 37.4741 | -121.9202 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0089208 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1957652 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2102 | 14232102 | TRANSFORMER | T52793 | 20240718 | 237 | 20240718 | 1355 | 2519969 | 678 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 8700 | 37.7656 | -121.9164 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0089173 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1957622 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | RECLOSER | 363116 | 20240718 | 312 | 20240718 | 703 | 2519972 | 231 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 22638 | 37.7726 | -121.9993 | No | Clear;32-90 F |  |  | 24-0089138 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1957605 | 0 | EPSS Ckt | Y | 2024 | A- B 50 INST
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 8790 | 20240718 | 1023 | 20240719 | 642 | 2520167 | 1087 | Distribution Circuit | Equipment Failure/Involved | Underground | 331 | 92955 | 37.6551 | -122.034 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0089292 | UG | Sus | 46281510 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1957683 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | RECLOSER | MR195 | 20240719 | 1035 | 20240719 | 1241 | 2521031 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 7938 | 37.7195 | -121.7004 | No | Clear;32-90 F |  |  | 24-0089691 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1957929 | 0 | EPSS Ckt | Y | 2024 | B- C ABOVE MTT
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | RECLOSER | 132304 | 20240719 | 1816 | 20240719 | 2251 | 2521371 | 275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 186 | 14802 | 37.7077 | -122.0908 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0089874 | OH | Sus | 35567377 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1958004 | 0 | EPSS Ckt | N | 2024 | N/A
MISSION | MISSION | VASCO-1103 | 13751103 | FUSE | 12265 | 20240720 | 1437 | 20240720 | 2100 | 2521864 | 383 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 20 | 7660 | 37.6941 | -121.6757 | No | Clear;Above 90 | Insulator | Broken | 24-0089640 | OH | Sus | 35567367 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1958129 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 13066 | 20240720 | 1443 | 20240720 | 2058 | 2521880 | 353 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 12 | 4108 | 37.6453 | -121.6404 | No | Clear;32-90 F | Fuse | Normal | 24-0089639 | OH | Sus | 35567367 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1958132 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11281 | 20240720 | 1505 | 20240720 | 1521 | 2521910 | 16 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 16 | 37.6855 | -121.6335 | No | Clear;32-90 F | Fuse | Normal | 24-0089639 | OH | Sus | 35567367 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1958141 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 791914 | 20240720 | 2014 | 20240721 | 1442 | 2522176 | 1108 | Distribution Circuit | Equipment Failure/Involved | Underground | 2866 | 315144 | 37.7306 | -121.7357 | No | Clear-Strong Winds;32-90 F | Transformer (UG) | Broken | 24-0090121 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | Yes | No | No | 1958196 | 0 | EPSS Ckt | Y | 2024 | GRD- INST OC
MISSION | MISSION | VINEYARD-2110 | 14502110 | TRANSFORMER | T28781 | 20240721 | 1729 | 20240722 | 238 | 2522604 | 549 | Distribution Circuit | Equipment Failure/Involved | Underground | 92 | 14472 | 37.7128 | -121.8682 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0090221 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1958281 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 884904 | 20240721 | 1927 | 20240722 | 1249 | 2522638 | 1042 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 115910 | 37.752 | -121.7699 | No | Clear;32-90 F |  |  | 24-0090218 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1958278 | 0 | EPSS Ckt | Y | 2024 | A PH AND GRD TGT
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 884904 | 20240722 | 1755 | 20240723 | 1451 | 2523594 | 1256 | Distribution Circuit | Equipment Failure/Involved | Underground | 185 | 46995 | 37.752 | -121.7699 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0090639 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1958537 | 0 | EPSS Ckt | Y | 2024 | A PH AND GRD TGT
MISSION | MISSION | FREMONT-1111 | 14351111 | OTHER | T10532 TWD 11523 | 20240723 | 108 | 20240723 | 436 | 2523829 | 208 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 208 | 37.5491 | -121.9886 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0090684 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1958597 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | JUMPER | 315416044516 | 20240723 | 1509 | 20240723 | 1802 | 2524695 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1449 | 37.7118 | -122.0858 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Deteriorated | 24-0091126 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1958860 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 10382 | 20240723 | 1515 | 20240723 | 1843 | 2524557 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 435 | 90480 | 37.701 | -122.1126 | No | Clear-Heat Wave;Above 90 | Crossarm- Wood | Broken | 24-0091007 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1958850 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | TRANSFORMER | 315385144111 | 20240723 | 1602 | 20240723 | 1753 | 2524700 | 111 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 1998 | 37.7006 | -122.0963 | No | Clear-Heat Wave;Above 90 | Crossarm- Wood | Broken | 24-0091129 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1958861 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | MR297 | 20240723 | 1820 | 20240724 | 1038 | 2524709 | 808 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 157371 | 37.5946 | -121.8882 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Leaking | 24-0091132 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1958863 | 0 | EPSS Ckt | Y | 2024 | C & GRD
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | FUSE | 11172 | 20240724 | 732 | 20240724 | 1055 | 2525245 | 203 | Distribution Circuit | Animal | Other | 2 | 406 | 37.6963 | -122.0486 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0091407 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1959141 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315660638303 | 20240724 | 1943 | 20240725 | 127 | 2526033 | 344 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 4816 | 37.5422 | -121.9978 | No | Clear;32-90 F | Transformer | Normal | 24-0091701 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1959239 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2105 | 14502105 | FUSE | 40221 | 20240725 | 159 | 20240725 | 441 | 2526267 | 162 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 7290 | 37.681 | -121.8958 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0091762 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1959310 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | FUSE | 70822 | 20240725 | 855 | 20240725 | 1155 | 2526462 | 180 | Distribution Circuit | Animal | Squirrel | 13 | 2340 | 37.6569 | -121.9092 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0091930 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1959488 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | TRANSFORMER | 315342043660 | 20240725 | 1116 | 20240725 | 1437 | 2526662 | 201 | Transformer only | Unknown Cause | Patrol - found nothing | 12 | 2412 | 37.688 | -122.111 | No | Clear;32-90 F |  |  | 24-0092071 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1959528 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | 263964 | 20240725 | 1326 | 20240725 | 1608 | 2526752 | 162 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 4212 | 37.6465 | -121.7858 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0092011 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1959516 | 0 | EPSS Ckt | Y | 2024 | B & C INST.
MISSION | MISSION | VINEYARD-2105 | 14502105 | RECLOSER | 855920 | 20240725 | 1849 | 20240725 | 1939 | 2526971 | 30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1838 | 47672 | 37.6749 | -121.8952 | No | Clear;32-90 F |  |  | 24-0092182 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1959555 | 0 | Non-EPSS | N | 2024 | GRD TIMED
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 9607 | 20240726 | 910 | 20240726 | 1000 | 2527358 | 50 | Distribution Circuit | Animal | Squirrel | 68 | 3400 | 37.6409 | -122.0557 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0092363 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1959755 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | T12642 | 20240726 | 1311 | 20240726 | 1401 | 2527633 | 50 | Transformer only | Equipment Failure/Involved | Underground | 12 | 600 | 37.6658 | -121.9064 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0092539 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1959818 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2103 | 14232103 | INTERRUPTER | 93066 | 20240726 | 1630 | 20240726 | 1753 | 2527789 | 83 | Distribution Circuit | Animal | Bird found | 377 | 31291 | 37.7255 | -121.9206 | No | Clear;32-90 F | Interrupter | Failed/Faulted | 24-0092616 | UG | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1959843 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2103 | 14232103 | FUSE | 10474 | 20240726 | 1632 | 20240726 | 1735 | 2527788 | 63 | Distribution Circuit | Animal | Bird found | 133 | 8392 | 37.729 | -121.9231 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0092616 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1959837 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1103 | 13111103 | FUSE | 51719 | 20240727 | 722 | 20240727 | 1145 | 2528142 | 263 | Distribution Circuit | 3rd Party | Vehicle | 31 | 8153 | 37.7103 | -122.1553 | No | Overcast;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0092726 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | Yes | No | 1959938 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MILPITAS-1109 | 82831109 | SWITCH | 92951 | 20240727 | 1405 | 20240729 | 1808 | 2528343 | 3123 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 16 | 288 | 37.515 | -121.8322 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0092765 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 49680 | No | No | No | 1959993 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | RECLOSER | 609690 | 20240727 | 1834 | 20240728 | 825 | 2528445 | 831 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1831 | 277694 | 37.6647 | -121.9162 | No | Clear;32-90 F |  |  | 24-0092802 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1960017 | 0 | EPSS Ckt | Y | 2024 | A GRD
MISSION | MISSION | GRANT-1104 | 14381104 | OCB | 1104/2 | 20240728 | 712 | 20240728 | 909 | 2528567 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 12519 | 37.6718 | -122.1596 | No | Clear-Heat Wave;Above 90 | Crossarm- Wood | Broken | 24-0092846 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1960070 | 0 | Non-EPSS | N | 2024 | A - C - GRD- & TIME OC
MISSION | MISSION | SAN RAMON-2107 | 14232107 | RECLOSER | MR284 | 20240728 | 1953 | 20240729 | 1141 | 2528794 | 948 | Distribution Circuit | Company Initiated | Personnel- company | 1240 | 185050 | 37.6977 | -121.9419 | No | Clear;32-90 F | Fuse | Normal | 24-0092925 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1960124 | 0 | EPSS Ckt | Y | 2024 | B-C GRD ABOVE MTT
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 11789 | 20240728 | 1953 | 20240728 | 2036 | 2528796 | 43 | Distribution Circuit | 3rd Party | Metallic Balloon | 46 | 1990 | 37.7135 | -121.9393 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092927 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1960127 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | RECLOSER | MR195 | 20240728 | 2336 | 20240729 | 1116 | 2528838 | 700 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 42822 | 37.7195 | -121.7004 | No | Clear;32-90 F |  |  | 24-0092955 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1960152 | 0 | EPSS Ckt | Y | 2024 | b & c
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | FUSE | 529586 | 20240729 | 248 | 20240729 | 1445 | 2528837 | 717 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 4845 | 37.5279 | -122.016 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Arcing | 24-0092961 | OH | Sus | 46285682 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1960158 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | FUSE | 10777 | 20240729 | 1246 | 20240729 | 1730 | 2529317 | 284 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 568 | 37.7546 | -121.6776 | No | Clear;32-90 F |  |  | 24-0093408 | OH | Sus | 0 | BAY AREA | JUL | Line to Line | 0 | No | No | No | 1960408 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | OTHER | T93566 TWD 20482 | 20240729 | 1500 | 20240729 | 1707 | 2529443 | 127 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 179 | 37.6953 | -122.0519 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0093202 | UG | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1960389 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 14313 | 20240730 | 843 | 20240730 | 1000 | 2530215 | 77 | Distribution Circuit | 3rd Party | Metallic Balloon | 1 | 77 | 37.6146 | -122.0363 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0093603 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1960643 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 40032 | 20240730 | 907 | 20240731 | 118 | 2530151 | 971 | Distribution Circuit | Equipment Failure/Involved | Underground | 194 | 147206 | 37.783 | -121.9512 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 24-0093643 | UG | Sus | 35569823 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1960670 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRANSFORMER | 315320442406 | 20240730 | 958 | 20240731 | 221 | 2529992 | 983 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 983 | 37.6535 | -122.1176 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0093641 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1960669 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 315855745148 | 20240730 | 1317 | 20240731 | 305 | 2530396 | 828 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1656 | 37.7311 | -121.9343 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0093950 | OH | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1960774 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | JUMPER | FB'S | 20240730 | 1353 | 20240730 | 1806 | 2530417 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 6578 | 37.5424 | -121.9982 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0093788 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1960719 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1101 | 13111101 | INTERRUPTER | 47578 | 20240731 | 652 | 20240814 | 939 | 2530812 | 20327 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 20327 | 37.7079 | -122.1836 | No | Overcast;32-90 F | Customer Equipment | Malfunctioning | 24-0094126 | UG | Sus | 0 | BAY AREA | JUL | Line to Ground | 0 | No | No | No | 1961005 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 8035 | 20240801 | 151 | 20240801 | 1438 | 2531620 | 767 | Distribution Circuit | 3rd Party | Vehicle | 78 | 37430 | 37.7152 | -122.0829 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0094499 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1961143 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | FUSE | 10759 | 20240801 | 1649 | 20240801 | 1920 | 2532185 | 151 | Distribution Circuit | Equipment Failure/Involved | Underground | 96 | 14496 | 37.5104 | -121.9368 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0094855 | UG | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1961358 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | OCB | 2108/2 | 20240801 | 1708 | 20240802 | 435 | 2532399 | 687 | Distribution Circuit | Equipment Failure/Involved | Underground | 3980 | 417215 | 37.7448 | -121.9369 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0094892 | UG | Sus | 35570176 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1961378 | 0 | EPSS Ckt | Y | 2024 | GRD & INST (51)
MISSION | MISSION | MT EDEN-1111 | 13761111 | TRANSFORMER | 315355141376 | 20240803 | 309 | 20240804 | 1247 | 2533433 | 1446 | Distribution Circuit | 3rd Party | Vehicle | 1599 | 62936 | 37.6254 | -122.1049 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0095350 | OH | Sus | 35570561 | BAY AREA | AUG | Three Phase Fault | 0 | No | No | No | 1961693 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 74116 | 20240803 | 728 | 20240803 | 901 | 2533465 | 93 | Distribution Circuit | Animal | Squirrel | 427 | 39711 | 37.6802 | -121.7326 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0095364 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1961711 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | OCB | 2107/2 | 20240803 | 1245 | 20240804 | 1257 | 2533684 | 1224 | Distribution Circuit | Equipment Failure/Involved | Underground | 4262 | 833698 | 37.6697 | -121.8543 | No | Clear;Above 90 | Switch (UG) | Failed/Faulted | 24-0095421 | UG | Sus | 35570494 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1961748 | 0 | EPSS Ckt | Y | 2024 | GRD OC
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | MR243 | 20240803 | 2224 | 20240804 | 2239 | 2533956 | 1455 | Distribution Circuit | 3rd Party | Vehicle | 393 | 97618 | 37.7022 | -122.0452 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0095489 | OH | Sus | 35570700 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1961812 | 0 | EPSS Ckt | Y | 2024 | A & B PH
MISSION | MISSION | NEWARK 21KV-2102 | 12232102 | RECLOSER | MR223 | 20240804 | 1604 | 20240805 | 254 | 2534240 | 650 | Distribution Circuit | Equipment Failure/Involved | Underground | 2974 | 137592 | 37.4875 | -121.9265 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0095563 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1961875 | 0 | Non-EPSS | N | 2024 | A PH & GRD
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 605520 | 20240805 | 705 | 20240805 | 1317 | 2534617 | 372 | Distribution Circuit | 3rd Party | Metallic Balloon | 95 | 25293 | 37.575 | -121.8795 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095658 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | Yes | No | No | 1961947 | 0 | EPSS Ckt | Y | 2024 | A- INST GRD
MISSION | MISSION | JARVIS-1108 | 13501108 | RECLOSER | MR366 | 20240805 | 1247 | 20240805 | 1440 | 2535021 | 113 | Distribution Circuit | 3rd Party | Metallic Balloon | 3220 | 363860 | 37.6093 | -122.0238 | No | Clear;32-90 F | Fuse | Burned Open | 24-0095913 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1962105 | 0 | EPSS Ckt | Y | 2024 | A-B TGTS
MISSION | MISSION | GRANT-1105 | 14381105 | FUSE | 10731 | 20240806 | 1346 | 20240806 | 1447 | 2535929 | 61 | Distribution Circuit | Animal | Bird found | 329 | 20069 | 37.681 | -122.1501 | No | Clear;32-90 F | Fuse | Burned Open | 24-0096431 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1962450 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 639241 | 20240806 | 2146 | 20240806 | 2242 | 2536256 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 1456 | 37.617 | -122.0415 | No | Clear;32-90 F |  |  | 24-0096580 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1962525 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | FUSE | 11079 | 20240807 | 1606 | 20240807 | 1731 | 2536950 | 85 | Distribution Circuit | 3rd Party | Metallic Balloon | 266 | 22610 | 37.6781 | -122.1109 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0096967 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1962786 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1108 | 14351108 | SWITCH | 349931 | 20240807 | 1758 | 20240807 | 2108 | 2537067 | 190 | Distribution Circuit | Vegetation | Other ground vegetation | 697 | 132430 | 37.5404 | -121.9771 | No | Clear;32-90 F | Connector or Splice (OH) | Normal | 24-0096952 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1962794 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | TRANSFORMER | 315907435746 | 20240807 | 1838 | 20240808 | 336 | 2537061 | 538 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 5380 | 37.4733 | -121.9115 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0096995 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1962805 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | TRANSFORMER | 315906335773 | 20240807 | 1935 | 20240808 | 337 | 2537113 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2892 | 37.4741 | -121.9117 | No | Clear;32-90 F | Secondary | Broken | 24-0096990 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1962802 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315562639213 | 20240807 | 1938 | 20240807 | 2120 | 2537112 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 1836 | 37.5669 | -122.0322 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0096987 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1962800 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | TRANSFORMER | 315559539233 | 20240808 | 1 | 20240808 | 48 | 2537235 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 658 | 37.5674 | -122.0333 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0097041 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1962833 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NORTH DUBLIN-2101 | 14052101 | OCB | 2101/2/NORM | 20240808 | 1443 | 20240808 | 1611 | 2538014 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6420 | 391063 | 37.7448 | -121.8576 | No | Clear;32-90 F |  |  | 24-0097342 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1963048 | 0 | EPSS Ckt | Y | 2024 | I OC TGT
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 11475 | 20240808 | 1658 | 20240808 | 2000 | 2538179 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2548 | 37.7179 | -122.0055 | No | Clear;32-90 F |  |  | 24-0097461 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1963094 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | 631066 | 20240809 | 2206 | 20240810 | 1534 | 2539096 | 1048 | Distribution Circuit | 3rd Party | Vehicle | 44 | 46112 | 37.6433 | -121.7674 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0097920 | OH | Sus | 46293513 | BAY AREA | AUG | Line to Ground | 0 | No | Yes | No | 1963378 | 0 | EPSS Ckt | Y | 2024 | A & INT OC
MISSION | MISSION | RADUM-1105 | 13151105 | TRANSFORMER | T1672 | 20240810 | 143 | 20240810 | 1434 | 2539127 | 771 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 3104 | 37.6758 | -121.8752 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0097945 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1963395 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | TRANSFORMER | T6101 | 20240810 | 350 | 20240810 | 2049 | 2539140 | 1019 | Distribution Circuit | Equipment Failure/Involved | Underground | 53 | 37007 | 37.5873 | -122.08 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0097986 | UG | Sus | 35572770 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1963443 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 884904 | 20240810 | 541 | 20240810 | 1103 | 2539156 | 322 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 53790 | 37.752 | -121.7699 | No | Clear;32-90 F |  |  | 24-0097949 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1963398 | 0 | EPSS Ckt | Y | 2024 | C & GRD
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 9273 | 20240810 | 1112 | 20240810 | 1622 | 2539369 | 310 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 7130 | 37.7712 | -121.8105 | No | Clear;32-90 F |  |  | 24-0098019 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1963473 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 9707 | 20240810 | 1140 | 20240810 | 1301 | 2539367 | 81 | Distribution Circuit | 3rd Party | Metallic Balloon | 615 | 49815 | 37.6409 | -122.0808 | No | Clear;32-90 F | Fuse | Normal | 24-0098000 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1963456 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315244842982 | 20240811 | 1540 | 20240812 | 218 | 2539821 | 624 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 19128 | 37.669 | -122.144 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0098096 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1963564 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1109 | 13111109 | TRANSFORMER | 315202245423 | 20240811 | 1640 | 20240812 | 546 | 2539846 | 786 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 25926 | 37.7358 | -122.1603 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0098099 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1963568 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | TASSAJARA-2113 | 14662113 | FUSE | 30849 | 20240811 | 1848 | 20240812 | 846 | 2539895 | 738 | Distribution Circuit | Equipment Failure/Involved | Underground | 90 | 68660 | 37.7651 | -121.9847 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0098110 | UG | Sus | 46297544 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1963574 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 970836 | 20240812 | 825 | 20240812 | 1100 | 2540149 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 775 | 37.5826 | -121.9617 | No | Partly Cloudy;32-90 F |  |  | 24-0098283 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1963763 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | RECLOSER | 72161 | 20240812 | 946 | 20240812 | 1251 | 2540307 | 185 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 185 | 37.6917 | -121.7458 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 24-0098328 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1963781 | 0 | Non-EPSS | N | 2024 | NA
MISSION | MISSION | DUMBARTON-1103 | 14471103 | FUSE | 9047 | 20240814 | 1021 | 20240814 | 2029 | 2542004 | 608 | Distribution Circuit | Equipment Failure/Involved | Underground | 213 | 57735 | 37.5822 | -122.055 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0099289 | UG | Sus | 46299206 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1964379 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | INTERRUPTER | 575542 | 20240815 | 143 | 20240815 | 1825 | 2542666 | 1002 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 6012 | 37.5361 | -122.0606 | No | Partly Cloudy;32-90 F | Elbow | Failed/Faulted | 24-0099542 | UG | Sus | 35574170 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1964479 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2103 | 14232103 | INTERRUPTER | 93066 | 20240815 | 1247 | 20240815 | 1406 | 2542990 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 377 | 29532 | 37.7255 | -121.9206 | No | Clear;32-90 F |  |  | 24-0099730 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1964563 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2103 | 14232103 | FUSE | 10474 | 20240815 | 1248 | 20240815 | 1436 | 2542993 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 133 | 14386 | 37.729 | -121.9231 | No | Clear;32-90 F |  |  | 24-0099731 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1964564 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | FUSE | 7424 | 20240815 | 1249 | 20240815 | 1642 | 2543087 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 466 | 37.7066 | -122.188 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0099774 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1964577 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | FUSE | 11208 | 20240815 | 2238 | 20240816 | 2132 | 2543329 | 1374 | Distribution Circuit | Equipment Failure/Involved | Underground | 108 | 88568 | 37.509 | -121.949 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0099863 | UG | Sus | 35574828 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1964637 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1104 | 14351104 | TRANSFORMER | 315843838148 | 20240816 | 906 | 20240816 | 1030 | 2543563 | 84 | Transformer only | Vegetation | Tree - grew into line | 6 | 504 | 37.5389 | -121.9345 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0099960 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1964785 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 884904 | 20240817 | 1149 | 20240817 | 1523 | 2544327 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 31964 | 37.752 | -121.7699 | No | Partly Cloudy;32-90 F |  |  | 24-0100268 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1964976 | 0 | EPSS Ckt | Y | 2024 | A & GRD
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | SWITCH | 1509 | 20240817 | 1339 | 20240817 | 1810 | 2544388 | 271 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 16576 | 37.5091 | -121.9451 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0100238 | UG | Sus | 35574828 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1964987 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2107 | 14232107 | TRANSFORMER | T5304 | 20240817 | 1752 | 20240817 | 2231 | 2544348 | 279 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2790 | 37.7415 | -121.9434 | No | Partly Cloudy;32-90 F | Other | Broken- wire on ground | 24-0100313 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | Yes | No | 1965006 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | 213524 | 20240817 | 2043 | 20240817 | 2307 | 2544601 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 987 | 142128 | 37.717 | -122.1317 | No | Partly Cloudy;32-90 F |  |  | 24-0100332 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965024 | 0 | EPSS Ckt | Y | 2024 | C PHASE INST.
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | FUSE | 8127 | 20240817 | 2312 | 20240818 | 1759 | 2544635 | 1127 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 12397 | 37.7284 | -122.1364 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0100341 | UG | Sus | 46300804 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965033 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1109 | 13761109 | FUSE | 6025 | 20240818 | 400 | 20240818 | 944 | 2544657 | 344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 53320 | 37.6339 | -122.0939 | No | Overcast;32-90 F | Pothead(Riser Termination) | Broken | 24-0100360 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965060 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | INTERRUPTER | 754322 | 20240818 | 935 | 20240818 | 1035 | 2544733 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 3660 | 37.5622 | -122.0078 | No | Overcast;32-90 F |  |  | 24-0100376 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965075 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 316053642261 | 20240818 | 1313 | 20240818 | 1356 | 2544803 | 43 | Transformer only | 3rd Party | Metallic Balloon | 12 | 516 | 37.6527 | -121.8645 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100402 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965092 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 6039 | 20240818 | 1814 | 20240818 | 1825 | 2544894 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 155 | 1705 | 37.6319 | -122.0932 | No | Clear;32-90 F | Fuse | Normal | 24-0100360 | OH | Sus | 46300883 | BAY AREA | AUG | None | 0 | No | No | No | 1965112 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 11721 | 20240818 | 1926 | 20240818 | 2053 | 2544907 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 10097 | 37.6311 | -122.074 | No | Clear;32-90 F |  |  | 24-0100436 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965126 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 9580 | 20240819 | 603 | 20240819 | 808 | s1965152 | 125 | Distribution Circuit | Animal | Bird found | 225 | 28125 | 37.6314 | -122.0755 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100475 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965152 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 605520 | 20240819 | 1545 | 20240820 | 744 | 2545730 | 959 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 53787 | 37.575 | -121.8795 | No | Clear;32-90 F |  |  | 24-0100726 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965351 | 0 | EPSS Ckt | Y | 2024 | DCD
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | TRANSFORMER | 315382444581 | 20240819 | 1926 | 20240819 | 1939 | 2545677 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 117 | 37.7135 | -122.0975 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0100801 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965376 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | TRANSFORMER | 315382444581 | 20240819 | 2020 | 20240820 | 206 | 2545915 | 346 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3114 | 37.7135 | -122.0975 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0100809 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1965385 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2110 | 14502110 | FUSE | 73757 | 20240820 | 101 | 20240820 | 645 | 2545989 | 344 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 18672 | 37.7083 | -121.8607 | No | Clear;32-90 F |  |  | 24-0100844 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965431 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2110 | 14502110 | TRANSFORMER | 28595 | 20240820 | 702 | 20240821 | 150 | 2546352 | 1128 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 34968 | 37.7085 | -121.8626 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0100973 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965598 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1105 | 13761105 | OCB | 1105/2 | 20240820 | 906 | 20240820 | 916 | 2546234 | 10 | Distribution Circuit | 3rd Party | Vehicle | 1568 | 15680 | 37.6319 | -122.1023 | No | Partly Cloudy;32-90 F | Secondary | Normal | 24-0100916 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1965548 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | JARVIS-1101 | 13501101 | TRANSFORMER | 315502541448 | 20240820 | 1536 | 20240821 | 203 | 2546653 | 627 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1881 | 37.628 | -122.0541 | No | Clear;32-90 F | Other | Failed/Faulted | 24-0101216 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965677 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 292606 | 20240821 | 615 | 20240821 | 726 | 2546903 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 852 | 37.774 | -121.8165 | No | Clear;32-90 F |  |  | 24-0101264 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1965735 | 0 | EPSS Ckt | Y | 2024 | A INST
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315608240710 | 20240821 | 805 | 20240821 | 1217 | 2547196 | 252 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 504 | 37.6082 | -122.0173 | No | Clear;32-90 F |  |  | 24-0101379 | OH | Sus | 0 | BAY AREA | AUG | None | 0 | No | No | No | 1965908 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1101 | 13111101 | OTHER | CAR POLE 1 S/O C223 | 20240821 | 1030 | 20240822 | 48 | 2547215 | 858 | Distribution Circuit | 3rd Party | Vehicle | 480 | 18717 | 37.7147 | -122.1862 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0101395 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | Yes | Yes | 1965917 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 884904 | 20240821 | 1707 | 20240821 | 2008 | 2547534 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 22641 | 37.752 | -121.7699 | No | Clear;32-90 F |  |  | 24-0101642 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | Yes | No | No | 1965975 | 0 | EPSS Ckt | Y | 2024 | A/GRD
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 64737 | 20240822 | 847 | 20240822 | 1030 | 2547932 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 250 | 24490 | 37.5458 | -121.9443 | No | Overcast;32-90 F |  |  | 24-0101869 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1966186 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 10648 | 20240822 | 1230 | 20240822 | 1313 | 2548162 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 5332 | 37.5468 | -121.9467 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0101960 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1966223 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 546328 | 20240822 | 2256 | 20240823 | 745 | 2548722 | 529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 227 | 25133 | 37.6641 | -121.733 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0102205 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1966324 | 0 | EPSS Ckt | Y | 2024 | B-C PH- 50 INST
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 73144 | 20240823 | 1014 | 20240823 | 1224 | 2549098 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 130 | 37.7416 | -121.7374 | No | Partly Cloudy;32-90 F |  |  | 24-0102452 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1966527 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 11787 | 20240823 | 1518 | 20240823 | 1659 | 2549382 | 101 | Distribution Circuit | Animal | Bird found | 97 | 9797 | 37.7083 | -122.061 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0102609 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1966582 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315224644489 | 20240823 | 1837 | 20240824 | 552 | 2549512 | 675 | Transformer only | Animal | Bird found | 1 | 675 | 37.7102 | -122.1519 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0102662 | OH | Sus | 46304763 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1966597 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | FUSE | 12774 | 20240824 | 431 | 20240824 | 936 | 2549618 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 10980 | 37.5632 | -122.0422 | No | Overcast;32-90 F | Fuse | Broken | 24-0102720 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1966666 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | SWITCH | 9314 | 20240824 | 808 | 20240824 | 1053 | 2549922 | 165 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1815 | 37.7619 | -121.7367 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0102712 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1966643 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | BANCROFT-0402 | 13030402 | FUSE | 50705 | 20240824 | 924 | 20240824 | 1808 | 2550095 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 9880 | 37.7346 | -122.1416 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Annealed | 24-0102755 | OH | Sus | 46304729 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1966702 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1104 | 14471104 | FUSE | 7755 | 20240824 | 1556 | 20240825 | 1510 | 2550345 | 1394 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 27090 | 37.5314 | -122.036 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0102841 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1966767 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1103 | 14471103 | SWITCH | 20234 | 20240824 | 1901 | 20240824 | 1935 | 2550575 | 34 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 1224 | 37.566 | -122.0423 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0102720 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1966779 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | 315246143218 | 20240825 | 204 | 20240825 | 850 | 2550623 | 406 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 6090 | 37.6754 | -122.1438 | No | Clear;32-90 F | Fuse | Broken | 24-0102892 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1966849 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1105 | 14351105 | OTHER | J30710 TWD 60078 | 20240825 | 2204 | 20240826 | 102 | 2551037 | 178 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 7832 | 37.5464 | -121.975 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0102953 | UG | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1966904 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2110 | 14232110 | FUSE | 40906 | 20240826 | 734 | 20240826 | 1602 | 2551126 | 508 | Distribution Circuit | Equipment Failure/Involved | Underground | 51 | 12993 | 37.7707 | -121.9553 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0103046 | UG | Sus | 35576854 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1967076 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2110 | 14232110 | FUSE | 71180 | 20240826 | 811 | 20240826 | 1223 | 2551196 | 252 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 252 | 37.7724 | -121.9578 | No | Clear;32-90 F |  |  | 24-0103147 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1967143 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1112 | 13501112 | OCB | 1112/2 | 20240826 | 1411 | 20240826 | 1538 | 2551711 | 87 | Distribution Circuit | 3rd Party | Metallic Balloon | 4893 | 191135 | 37.5953 | -122.0174 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103224 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1967177 | 0 | Non-EPSS | N | 2024 | PHASE- GRD & INST
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | FUSE | 12575 | 20240826 | 2349 | 20240827 | 317 | 2552133 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 208 | 37.5025 | -121.9411 | No | Clear;32-90 F | Fuse | Broken | 24-0103401 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1967257 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1105 | 14351105 | OTHER | J30711 TWD T60117 | 20240827 | 258 | 20240827 | 411 | 2552129 | 73 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 3577 | 37.5458 | -121.9748 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0103368 | UG | Sus | 35576957 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1967255 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 605520 | 20240827 | 1118 | 20240827 | 1615 | 2552683 | 297 | Distribution Circuit | 3rd Party | Metallic Balloon | 95 | 28215 | 37.575 | -121.8795 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0103596 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1967513 | 0 | EPSS Ckt | Y | 2024 | C- INST TGTS
MISSION | MISSION | JARVIS-1110 | 13501110 | TRANSFORMER | 22468 | 20240827 | 1852 | 20240828 | 1048 | 2553018 | 740 | Distribution Circuit | Company Initiated | Personnel- company | 526 | 124763 | 37.5827 | -121.9956 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0103808 | UG | Sus | 31706789 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1967597 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11229 | 20240828 | 457 | 20240828 | 1000 | 2553312 | 303 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 3939 | 37.6534 | -121.6684 | No | Clear;32-90 F |  |  | 24-0103905 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1967708 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2107 | 14402107 | FUSE | 73207 | 20240828 | 619 | 20240828 | 835 | 2553328 | 136 | Distribution Circuit | Animal | Bird found | 29 | 3944 | 37.6519 | -121.8046 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103910 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1967724 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | MR544 | 20240828 | 711 | 20240828 | 833 | 2553362 | 82 | Distribution Circuit | Animal | Squirrel | 2750 | 217103 | 37.7084 | -122.1271 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0103866 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1967651 | 0 | EPSS Ckt | Y | 2024 | B PH & GRD
MISSION | MISSION | MT EDEN-1102 | 13761102 | FUSE | 74807 | 20240828 | 936 | 20240828 | 1534 | 2553654 | 289 | Distribution Circuit | Equipment Failure/Involved | Underground | 433 | 103868 | 37.6285 | -122.0956 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0104022 | UG | Sus | 31706909 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1967839 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 71789 | 20240828 | 1459 | 20240829 | 220 | 2553996 | 681 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 681 | 37.6652 | -121.6968 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0104391 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1967941 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | 213524 | 20240828 | 1915 | 20240828 | 2130 | 2554290 | 135 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 987 | 79551 | 37.717 | -122.1317 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0104426 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1967962 | 0 | EPSS Ckt | Y | 2024 | A- C & 50 INST
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | T7772 | 20240829 | 551 | 20240830 | 339 | 2555312 | 1308 | Transformer only | Equipment Failure/Involved | Underground | 25 | 32700 | 37.6799 | -121.7222 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0104992 | UG | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1968288 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2110 | 14502110 | OCB | 2110/2 | 20240829 | 844 | 20240829 | 1057 | 2554633 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6917 | 919961 | 37.6697 | -121.8542 | No | Partly Cloudy;32-90 F |  |  | 24-0104564 | OH | Sus | 0 | BAY AREA | AUG | Line to Line | 0 | No | No | No | 1968106 | 0 | EPSS Ckt | Y | 2024 | B-C INST- SET A RLY
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315549740916 | 20240829 | 1018 | 20240829 | 1116 | 2554953 | 58 | Transformer only | Company Initiated | Construction Activity/equip- company | 15 | 870 | 37.6136 | -122.0376 | No | Clear;32-90 F | Other | Normal | 24-0104752 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1968252 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | SWITCH | 3122 | 20240829 | 2307 | 20240829 | 2320 | 2555537 | 13 | Distribution Circuit | Equipment Failure/Involved | Underground | 77 | 1001 | 37.6799 | -121.7266 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0104999 | UG | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1968345 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | SWITCH | 3872 | 20240829 | 2307 | 20240830 | 302 | -2555537 | 63 | Distribution Circuit | Equipment Failure/Involved | Underground | 77 | 7469 | 37.6822 | -121.7257 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0104999 | UG | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1968354 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1110 | 14471110 | TRANSFORMER | T56802 | 20240831 | 901 | 20240831 | 1344 | 2556404 | 283 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 5377 | 37.5679 | -122.0622 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0105561 | UG | Sus | 35578034 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1968637 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | FUSE | 73782 | 20240901 | 219 | 20240901 | 809 | 2556967 | 350 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 190 | 66500 | 37.5337 | -121.9509 | No | Partly Cloudy;32-90 F |  |  | 24-0105664 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1968707 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | RECLOSER | MR332 | 20240901 | 735 | 20240902 | 2 | 2557036 | 987 | Distribution Circuit | Equipment Failure/Involved | Underground | 1103 | 193451 | 37.6659 | -121.8416 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0105663 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1968706 | 0 | EPSS Ckt | Y | 2024 | C GRD
MISSION | MISSION | MT EDEN-1109 | 13761109 | TRANSFORMER | 315454441859 | 20240901 | 1018 | 20240901 | 1550 | 2557120 | 332 | Transformer only | Equipment Failure/Involved | Overhead | 26 | 8632 | 37.6392 | -122.0711 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0105698 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1968735 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1104 | 13761104 | FUSE | 10450 | 20240901 | 1806 | 20240901 | 1854 | 2557270 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 7248 | 37.6255 | -122.0657 | No | Clear;32-90 F |  |  | 24-0105737 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1968767 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DIXON LANDING-2111 | 14722111 | TRANSFORMER | 60133 | 20240902 | 437 | 20240902 | 829 | 2557444 | 232 | Transformer only | 3rd Party | Customer Equipment | 4 | 928 | 37.4645 | -121.9177 | No | Clear;32-90 F | Other | Broken | 24-0105781 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1968806 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 298061 | 20240902 | 1004 | 20240902 | 1352 | 2557529 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 202 | 46056 | 37.5958 | -121.8897 | No | Clear;32-90 F |  |  | 24-0105804 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1968816 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316624041904 | 20240902 | 1032 | 20240902 | 2202 | 2557545 | 690 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 690 | 37.6411 | -121.6615 | No | Clear;32-90 F | Transformer | Broken | 24-0105867 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1968863 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 298061 | 20240902 | 1411 | 20240902 | 1444 | 2557654 | 33 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 202 | 6666 | 37.5958 | -121.8897 | No | Clear;32-90 F |  |  | 24-0105843 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1968838 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
MISSION | MISSION | SUNOL-1101 | 14241101 | OCB | 1101/2 | 20240902 | 2116 | 20240903 | 1204 | 2557791 | 888 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 737 | 126040 | 37.5868 | -121.8697 | No | Clear;32-90 F |  |  | 24-0105866 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1968862 | 0 | EPSS Ckt | Y | 2024 | AB INST
MISSION | MISSION | RADUM-1102 | 13151102 | FUSE | 11023 | 20240903 | 722 | 20240903 | 847 | 2557871 | 85 | Distribution Circuit | Animal | Squirrel | 28 | 2380 | 37.6799 | -121.8689 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0105953 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1968975 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316624041904 | 20240903 | 905 | 20240903 | 1508 | 2558057 | 363 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 363 | 37.6411 | -121.6615 | No | Clear;32-90 F |  |  | 24-0106013 | OH | Sus | 0 | BAY AREA | SEP | None | 0 | No | No | No | 1969045 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | SWITCH | 1581 | 20240903 | 1802 | 20240903 | 1836 | 2558667 | 34 | Distribution Circuit | Company Initiated | Return Circuit Normal | 281 | 3914 | 37.6275 | -122.0985 | No | Clear;32-90 F | Connector or Splice (UG) | Normal | 24-0104022 | UG | Sus | 31706909 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1969160 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2105 | 14402105 | INTERRUPTER | 979276 | 20240904 | 1514 | 20240904 | 1607 | 2559550 | 53 | Distribution Circuit | Company Initiated | Improper Construction | 14 | 742 | 37.68 | -121.7214 | No | Clear;Above 90 | Conductor- Underground | Normal | 24-0099717 | UG | Sus | 35345730 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1969489 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 36224 | 20240905 | 329 | 20240905 | 715 | 2559797 | 226 | Distribution Circuit | Equipment Failure/Involved | Underground | 103 | 23278 | 37.6813 | -121.7764 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0107030 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1969553 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1102 | 14381102 | TRANSFORMER | 315308442146 | 20240905 | 1206 | 20240905 | 1429 | 2560303 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1144 | 37.6463 | -122.1216 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0107309 | OH | Sus | 31707586 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1969762 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | SWITCH | 36334 | 20240905 | 1332 | 20240905 | 1340 | 2560361 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 5 | 40 | 37.6812 | -121.7762 | No | Clear;Above 90 | Switch (UG) | Normal | 24-0107030 | UG | Sus | 35579242 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1969771 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 36224 | 20240905 | 1340 | 20240905 | 1543 | s1969786 | 123 | Distribution Circuit | Company Initiated | Improper Construction | 5 | 615 | 37.6813 | -121.7764 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0107030 | UG | Sus | 35579242 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1969786 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2103 | 14232103 | FUSE | 30481 | 20240905 | 1615 | 20240906 | 1250 | 2560522 | 1010 | Distribution Circuit | Equipment Failure/Involved | Underground | 73 | 38865 | 37.7234 | -121.92 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0107593 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1969824 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | SWITCH | 36334 | 20240905 | 1758 | 20240905 | 1807 | 2560598 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 5 | 45 | 37.6812 | -121.7762 | No | Clear;Above 90 | Switch (UG) | Normal | 24-0107030 | UG | Sus | 35579242 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1969815 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 25134 | 20240906 | 857 | 20240906 | 916 | 2560934 | 19 | Transformer only | Equipment Failure/Involved | Underground | 14 | 266 | 37.6686 | -121.8646 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 24-0107761 | UG | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1969986 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | TRANSFORMER | 315367444091 | 20240906 | 1319 | 20240906 | 1409 | 2561275 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 450 | 37.7 | -122.1023 | No | Clear;32-90 F | Fuse | Broken | 24-0108034 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1970116 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1103 | 13751103 | RECLOSER | 964102 | 20240906 | 2100 | 20240907 | 539 | 2561642 | 519 | Distribution Circuit | 3rd Party | Vehicle | 35 | 18165 | 37.6944 | -121.6953 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0108140 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1970162 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | SWITCH | 14835 | 20240906 | 2139 | 20240906 | 2340 | 2561648 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 121 | 37.6886 | -122.1565 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0108144 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1970164 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 10383 | 20240907 | 1713 | 20240907 | 1945 | 2562150 | 152 | Distribution Circuit | Equipment Failure/Involved | Underground | 187 | 27704 | 37.5378 | -122.0598 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0108293 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1970307 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315308643566 | 20240908 | 922 | 20240908 | 1248 | 2562446 | 206 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2678 | 37.6853 | -122.1223 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0108353 | OH | Sus | 0 | BAY AREA | SEP | Open Circuit | 0 | No | No | No | 1970368 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 36224 | 20240908 | 1016 | 20240908 | 1553 | 2562500 | 337 | Distribution Circuit | Equipment Failure/Involved | Underground | 103 | 34706 | 37.6813 | -121.7764 | No | Clear;32-90 F | Switch (UG) | Leaking | 24-0108363 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1970375 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 36344 | 20240908 | 1017 | 20240908 | 1514 | 2562501 | 297 | Distribution Circuit | Equipment Failure/Involved | Underground | 123 | 15256 | 37.6822 | -121.7727 | No | Clear;32-90 F | Switch (UG) | Leaking | 24-0108366 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1970379 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 14095 | 20240908 | 1755 | 20240908 | 1848 | 2562800 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 219 | 11607 | 37.6948 | -122.1061 | No | Clear;32-90 F |  |  | 24-0108418 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1970419 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | SWITCH | 70595 | 20240909 | 124 | 20240909 | 146 | 2562925 | 22 | Distribution Circuit | Equipment Failure/Involved | Underground | 128 | 2419 | 37.6825 | -121.775 | No | Clear;32-90 F | Switch (UG) | Broken | 24-0108363 | UG | Sus | 35579829 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1970447 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | TRANSFORMER | 16169 | 20240909 | 1300 | 20240909 | 1337 | 2563178 | 37 | Transformer only | Equipment Failure/Involved | Underground | 21 | 777 | 37.52 | -121.938 | No | Clear;32-90 F | Secondary | Broken | 24-0108793 | UG | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1970690 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1106 | 12221106 | JUMPER | FB'S 39493 SEASCAPE RD, FREMONT | 20240909 | 1612 | 20240909 | 1821 | 2563668 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 3225 | 37.5301 | -121.9935 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0108874 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1970701 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | FUSE | 12608 | 20240909 | 2205 | 20240909 | 2335 | 2563969 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 3782 | 37.5194 | -121.9636 | No | Partly Cloudy;32-90 F |  |  | 24-0108956 | OH | Sus | 0 | BAY AREA | SEP | Open Circuit | 0 | No | No | No | 1970744 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2102 | 12232102 | FUSE | 10413 | 20240910 | 900 | 20240910 | 1722 | 2564255 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 11419 | 37.4893 | -121.9213 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 24-0109129 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1970980 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | 315280744002 | 20240910 | 1051 | 20240910 | 1410 | 2564438 | 199 | Transformer only | Equipment Failure/Involved | Overhead | 38 | 7562 | 37.6971 | -122.1322 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0109139 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1970986 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1104 | 14351104 | FUSE | 64737 | 20240910 | 1355 | 20240910 | 1645 | 2564659 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 250 | 28262 | 37.5458 | -121.9443 | No | Clear;32-90 F |  |  | 24-0109279 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1971039 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | 263964 | 20240910 | 1411 | 20240910 | 1506 | 2564677 | 55 | Distribution Circuit | Animal | Bird found | 26 | 1355 | 37.6465 | -121.7858 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109259 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1971032 | 0 | EPSS Ckt | Y | 2024 | A PHASE & GRD
MISSION | MISSION | NEWARK 21KV-2102 | 12232102 | FUSE | 11957 | 20240911 | 321 | 20240911 | 836 | 2564986 | 315 | Distribution Circuit | Equipment Failure/Involved | Underground | 70 | 21810 | 37.4879 | -121.9251 | No | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Broken | 24-0109473 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1971124 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 14409 | 20240911 | 1000 | 20240911 | 1358 | 2565205 | 238 | Distribution Circuit | 3rd Party | Vehicle | 38 | 9044 | 37.6569 | -122.0491 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0109754 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1971343 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1102 | 13111102 | FUSE | 14436 | 20240911 | 1459 | 20240911 | 1547 | 2565691 | 48 | Distribution Circuit | 3rd Party | Metallic Balloon | 110 | 5280 | 37.7325 | -122.1574 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0109869 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1971383 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | 315278144596 | 20240911 | 1602 | 20240911 | 1844 | 2565791 | 162 | Transformer only | Animal | Squirrel | 30 | 4860 | 37.7135 | -122.1335 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0109950 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1971421 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | TRANSFORMER | T7005 | 20240912 | 210 | 20240912 | 1339 | 2566115 | 689 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 7645 | 37.6547 | -121.772 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0110037 | UG | Sus | 35580657 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1971482 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315211244180 | 20240912 | 1341 | 20240912 | 1530 | 2566687 | 109 | Transformer only | Equipment Failure/Involved | Electrical Overload | 16 | 1744 | 37.7017 | -122.1563 | No | Clear;32-90 F | Transformer | Normal | 24-0110422 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1971712 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1101 | 13111101 | TRANSFORMER | 315133744506 | 20240914 | 820 | 20240914 | 1530 | 2568032 | 430 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 860 | 37.7103 | -122.1835 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0110980 | OH | Sus | 35581358 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1972080 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1101 | 13111101 | TRANSFORMER | 315132744380 | 20240914 | 1058 | 20240914 | 1623 | 2568170 | 325 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 2600 | 37.7069 | -122.1837 | No | Clear;32-90 F |  |  | 24-0111043 | OH | Sus | 0 | BAY AREA | SEP | None | 0 | No | No | No | 1972137 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | 315249243213 | 20240914 | 2006 | 20240914 | 2230 | 2568435 | 144 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 864 | 37.6753 | -122.1427 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0111103 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1972191 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2110 | 14502110 | RECLOSER | 472595 | 20240915 | 551 | 20240915 | 805 | 2568512 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 4020 | 37.7051 | -121.8234 | No | Partly Cloudy;32-90 F |  |  | 24-0111138 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1972215 | 0 | EPSS Ckt | Y | 2024 | A PHASE
MISSION | MISSION | MT EDEN-1112 | 13761112 | FUSE | 12756 | 20240915 | 1824 | 20240915 | 1935 | 2568997 | 71 | Distribution Circuit | 3rd Party | Metallic Balloon | 526 | 37346 | 37.6535 | -122.0884 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0111220 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1972296 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2105 | 14502105 | FUSE | 11304 | 20240915 | 1846 | 20240915 | 2159 | 2569002 | 193 | Distribution Circuit | Equipment Failure/Involved | Underground | 101 | 19493 | 37.6679 | -121.884 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0111223 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1972300 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | RECLOSER | 840916 | 20240915 | 2001 | 20240915 | 2213 | 2569049 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1096 | 144672 | 37.6592 | -122.0516 | No | Overcast;32-90 F |  |  | 24-0111230 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1972309 | 0 | EPSS Ckt | Y | 2024 | B GRD
MISSION | MISSION | GRANT-1105 | 14381105 | FUSE | 8467 | 20240915 | 2135 | 20240916 | 408 | 2569126 | 393 | Distribution Circuit | 3rd Party | Vehicle | 1 | 393 | 37.6832 | -122.1587 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0111244 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1972321 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | OCB | 1102/2/NORM | 20240916 | 808 | 20240916 | 1014 | 2569243 | 126 | Distribution Circuit | Equipment Failure/Involved | Underground | 2286 | 109147 | 37.5014 | -121.9891 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 24-0111361 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1972463 | 0 | Non-EPSS | N | 2024 | C & GRD
MISSION | MISSION | CAYETANO-2109 | 14422109 | SWITCH | 335934 | 20240916 | 1115 | 20240916 | 1315 | 2569308 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 1680 | 37.7518 | -121.7318 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0111498 | OH | Sus | 46321938 | BAY AREA | SEP | None | 0 | No | No | No | 1972563 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1103 | 13501103 | OCB | MR366 | 20240916 | 1806 | 20240917 | 515 | 2570018 | 669 | Distribution Circuit | 3rd Party | Vehicle | 4639 | 544642 | 37.6093 | -122.0238 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0111739 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1972647 | 0 | Non-EPSS | N | 2024 | A GRD
MISSION | MISSION | MT EDEN-1107 | 13761107 | TRANSFORMER | T5609 | 20240917 | 820 | 20240918 | 111 | 2570366 | 1011 | Distribution Circuit | Equipment Failure/Involved | Underground | 92 | 21676 | 37.6258 | -122.0978 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0112007 | UG | Sus | 35582016 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1972932 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | JUMPER | NEW SW 387939 | 20240917 | 832 | 20240917 | 1003 | 2570628 | 91 | Distribution Circuit | Company Initiated | Improper Construction | 1057 | 96187 | 37.6806 | -122.0938 | No | Overcast;32-90 F | Switch (OH) | Normal | 24-0103984 | OH | Sus | 35224841 | BAY AREA | SEP | None | 0 | No | No | No | 1972892 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2105 | 14502105 | FUSE | 11358 | 20240917 | 1548 | 20240917 | 1555 | 2570891 | 7 | Distribution Circuit | Equipment Failure/Involved | Underground | 101 | 707 | 37.6662 | -121.8787 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0111223 | UG | Sus | 31708885 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1972970 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 298061 | 20240918 | 546 | 20240918 | 848 | 2571167 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 203 | 36946 | 37.5958 | -121.8897 | No | Overcast;32-90 F |  |  | 24-0112226 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1973029 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 604267 | 20240918 | 856 | 20240918 | 1711 | 2571414 | 495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1980 | 37.7634 | -121.7513 | No | Clear;32-90 F | Insulator | Broken- wire on ground | 24-0112413 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | Yes | No | 1973271 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2109 | 14402109 | FUSE | 10751 | 20240918 | 1757 | 20240919 | 511 | 2572013 | 669 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 26 | 2319 | 37.6864 | -121.766 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 24-0112754 | UG | Sus | 46323474 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1973368 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315229643739 | 20240919 | 1237 | 20240919 | 1419 | 2572577 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1122 | 37.6897 | -122.1497 | No | Clear;32-90 F | Secondary | Broken | 24-0113161 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1973594 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315223743891 | 20240919 | 1500 | 20240919 | 1634 | 2572708 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 846 | 37.6938 | -122.1519 | No | Clear;32-90 F | Secondary | Broken | 24-0113183 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1973597 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315233243901 | 20240919 | 1500 | 20240919 | 1608 | 2572712 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 1088 | 37.6941 | -122.1487 | No | Clear;32-90 F | Secondary | Broken | 24-0113188 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1973599 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | RECLOSER | MR243 | 20240920 | 1635 | 20240920 | 1825 | 2573683 | 110 | Distribution Circuit | Company Initiated | Personnel- company | 393 | 43230 | 37.7022 | -122.0452 | No | Clear;32-90 F | Recloser | Normal | 24-0113861 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | Yes | No | No | 1973942 | 0 | EPSS Ckt | Y | 2024 | SGF TRGT
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 298061 | 20240921 | 1132 | 20240921 | 1409 | 2574032 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 202 | 31714 | 37.5958 | -121.8897 | No | Clear;32-90 F |  |  | 24-0113968 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | Yes | No | No | 1974074 | 0 | EPSS Ckt | Y | 2024 | SGF
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 12812 | 20240921 | 1600 | 20240921 | 1620 | 2574140 | 20 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 40 | 37.7549 | -121.7287 | No | Clear;32-90 F | Fuse | Burned Open | 24-0114053 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1974120 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 36400 | 20240921 | 2125 | 20240923 | 108 | 2574277 | 1663 | Distribution Circuit | Equipment Failure/Involved | Underground | 774 | 331890 | 37.7542 | -121.9503 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0114084 | UG | Sus | 46325043 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1974147 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | OCB | 1107/2 | 20240922 | 455 | 20240922 | 1021 | 2574350 | 170 | Distribution Circuit | Equipment Failure/Involved | Underground | 5737 | 1401843 | 37.5418 | -121.962 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0114093 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1974159 | 0 | Non-EPSS | N | 2024 | C PHASE
MISSION | MISSION | DUMBARTON-1107 | 14471107 | JUMPER | WIRE DOWN 1 SPANS LD SIDE CGC#315621638713 | 20240922 | 845 | 20240922 | 1530 | 2574440 | 405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 41621 | 37.5531 | -122.0116 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0114115 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | Yes | Yes | 1974211 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | MR650 | 20240922 | 1513 | 20240922 | 1836 | 2574596 | 203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 500 | 44716 | 37.5934 | -121.8844 | No | Clear;32-90 F |  |  | 24-0114139 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | Yes | No | No | 1974253 | 0 | EPSS Ckt | Y | 2024 | A-B TGTS
MISSION | MISSION | SAN LEANDRO-1102 | 13111102 | TRANSFORMER | 315217445273 | 20240922 | 2021 | 20240923 | 426 | 2574784 | 485 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 10670 | 37.7317 | -122.1549 | No | Clear;32-90 F | Transformer | Leaking | 24-0114165 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1974278 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1112 | 14471112 | OCB | 1112/2 | 20240923 | 926 | 20240923 | 1231 | 2575180 | 185 | Distribution Circuit | Equipment Failure/Involved | Underground | 34 | 4818 | 37.5571 | -122.0582 | No | Clear;32-90 F | Other | Broken | 24-0114267 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1974483 | 0 | Non-EPSS | N | 2024 | PH & GRD INST
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | RECLOSER | 343456 | 20240923 | 1312 | 20240923 | 1400 | 2575424 | 48 | Distribution Circuit | Animal | Squirrel | 1857 | 89136 | 37.7103 | -122.0738 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0114401 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1974546 | 0 | EPSS Ckt | Y | 2024 | B/C PHASE
MISSION | MISSION | GRANT-1108 | 14381108 | FUSE | 8876 | 20240923 | 1737 | 20240924 | 710 | 2575628 | 813 | Distribution Circuit | 3rd Party | Vehicle | 12 | 9761 | 37.6728 | -122.1225 | No | Clear;Above 90 | Pole - Tower- steel | Bent or Twisted | 24-0114566 | OH | Sus | 35583290 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1974592 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315282042856 | 20240923 | 2142 | 20240924 | 303 | 2575814 | 321 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 5136 | 37.6656 | -122.1311 | No | Clear;32-90 F |  |  | 24-0114617 | OH | Sus | 0 | BAY AREA | SEP | None | 0 | No | No | No | 1974626 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315235742947 | 20240924 | 1227 | 20240925 | 0 | 2576452 | 693 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 11088 | 37.668 | -122.1471 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0114953 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1974933 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1102 | 14471102 | RECLOSER | 205046 | 20240924 | 1633 | 20240925 | 35 | 2576665 | 482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 682 | 92774 | 37.5594 | -122.0256 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0115109 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | Yes | No | 1974972 | 0 | Non-EPSS | N | 2024 | A-G- 50 INST
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 886522 | 20240925 | 942 | 20240925 | 1027 | 2577263 | 45 | Distribution Circuit | Animal | Bird found | 153 | 6885 | 37.6634 | -121.6803 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115338 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1975235 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE OC
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | TRANSFORMER | 315258143668 | 20240925 | 1005 | 20240925 | 1157 | 2577289 | 112 | Transformer only | Company Initiated | Coordination failure | 14 | 1568 | 37.6878 | -122.1399 | No | Overcast;32-90 F | Other | Malfunctioning | 24-0115434 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1975279 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 61573 | 20240925 | 1320 | 20240925 | 1542 | s1975323 | 72 | Distribution Circuit | Equipment Failure/Involved | Underground | 605 | 70090 | 37.5271 | -122.0375 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0115537 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1975323 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315254942926 | 20240925 | 1335 | 20240925 | 1455 | 2577552 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 1200 | 37.6675 | -122.1405 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0115508 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1975311 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1112 | 13111112 | TRANSFORMER | 315195444614 | 20240926 | 1126 | 20240926 | 1212 | 2578319 | 46 | Transformer only | Company Initiated | Coordination failure | 17 | 782 | 37.7135 | -122.1621 | No | Overcast;32-90 F | Other | Normal | 24-0115981 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1975607 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | RECLOSER | 343456 | 20240926 | 1132 | 20240926 | 1322 | 2578333 | 110 | Distribution Circuit | Animal | Bird found | 1855 | 204050 | 37.7103 | -122.0738 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0115959 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | Yes | No | No | 1975597 | 0 | EPSS Ckt | Y | 2024 | G- SGF TGTS
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | 415780 | 20240926 | 1400 | 20240926 | 1410 | 2578467 | 10 | Distribution Circuit | Company Initiated | Personnel- company | 731 | 7310 | 37.7033 | -122.1035 | No | Clear;32-90 F | Jumper | Normal | 24-0116081 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | Yes | No | No | 1975639 | 0 | EPSS Ckt | Y | 2024 | BC GRD
MISSION | MISSION | DUMBARTON-1104 | 14471104 | OCB | 1104/2 | 20240926 | 2331 | 20240927 | 1932 | 2578872 | 1201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3076 | 565925 | 37.5571 | -122.0585 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0116291 | OH | Sus | 31710226 | BAY AREA | SEP | Line to Ground | 0 | No | Yes | No | 1975728 | 0 | Non-EPSS | N | 2024 | A - B & GRD
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315236943775 | 20240927 | 939 | 20240927 | 1458 | 2579309 | 319 | Transformer only | Company Initiated | Coordination failure | 13 | 4147 | 37.6908 | -122.1473 | No | Clear;32-90 F | Other | Normal | 24-0116538 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1975938 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315236943727 | 20240927 | 944 | 20240927 | 1508 | 2579349 | 324 | Transformer only | Company Initiated | Coordination failure | 18 | 5832 | 37.6894 | -122.1472 | No | Clear;32-90 F | Other | Normal | 24-0116537 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1975937 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 10412 | 20240928 | 1148 | 20240928 | 1702 | 2579979 | 314 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 16014 | 37.6912 | -122.1106 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0116874 | OH | Sus | 0 | BAY AREA | SEP | Force Out | 0 | No | No | No | 1976149 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2101 | 14232101 | OCB | 2101/2 | 20240928 | 1519 | 20240929 | 1340 | 2580207 | 1286 | Distribution Circuit | 3rd Party | Vehicle | 6093 | 1107778 | 37.745 | -121.9369 | No | Clear;32-90 F | Switch (UG) | Broken | 24-0116933 | UG | Sus | 35584326 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1976217 | 0 | EPSS Ckt | Y | 2024 | c phase to grd (time)
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 36400 | 20240929 | 1210 | 20240930 | 544 | 2580701 | 729 | Distribution Circuit | Equipment Failure/Involved | Underground | 774 | 222953 | 37.7542 | -121.9503 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0117105 | UG | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1976367 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1111 | 13501111 | RECLOSER | 306824 | 20240930 | 631 | 20240930 | 844 | 2580987 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1998 | 116882 | 37.5782 | -121.9845 | No | Clear;32-90 F |  |  | 24-0117170 | OH | Sus | 0 | BAY AREA | SEP | Line to Line | 0 | No | No | No | 1976432 | 0 | EPSS Ckt | Y | 2024 | A/B PHASE INST
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315234343756 | 20240930 | 812 | 20240930 | 1224 | 2581416 | 252 | Transformer only | Company Initiated | Coordination failure | 23 | 5796 | 37.6902 | -122.1481 | No | Clear;32-90 F | Other | Normal | 24-0117403 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1976624 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1112 | 13111112 | TRANSFORMER | 315194444693 | 20241001 | 1450 | 20241001 | 1720 | 2582532 | 150 | Transformer only | Company Initiated | Coordination failure | 8 | 1200 | 37.7157 | -122.1626 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0117982 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977022 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2119 | 14232119 | TRANSFORMER | 28100 | 20241002 | 1018 | 20241002 | 1650 | 2583377 | 392 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 784 | 37.7034 | -121.904 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0118338 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977315 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1104 | 14351104 | JUMPER | OJ 1 SP/E/O 10739 | 20241002 | 1029 | 20241002 | 1521 | 2583380 | 292 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 2336 | 37.545 | -121.9528 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0118257 | UG | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1977285 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1112 | 13111112 | TRANSFORMER | 315205844675 | 20241002 | 1030 | 20241002 | 1351 | 2583391 | 201 | Transformer only | Company Initiated | Coordination failure | 18 | 3618 | 37.7153 | -122.1586 | No | Clear;32-90 F | Other | Normal | 24-0118273 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977292 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 10873 | 20241002 | 1449 | 20241002 | 1512 | 2583695 | 23 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 920 | 37.6974 | -122.114 | No | Clear;Above 90 | Other | Burned/flashed | 24-0118495 | UG | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1977360 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 315806045669 | 20241002 | 1545 | 20241002 | 2332 | 2583744 | 467 | Transformer only | Equipment Failure/Involved | Underground | 15 | 7005 | 37.7453 | -121.9517 | No | Clear;Above 90 | Connector or Splice (UG) | Burned/flashed | 24-0118586 | UG | Sus | 46330502 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977377 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LAS POSITAS-2110 | 14402110 | RECLOSER | MR195 | 20241002 | 1607 | 20241003 | 115 | 2583772 | 548 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 14476 | 37.7195 | -121.7004 | No | Clear;Above 90 | Fuse | Broken | 24-0118554 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977367 | 0 | EPSS Ckt | Y | 2024 | C PHASE / GRD
MISSION | MISSION | NORTH DUBLIN-2101 | 14052101 | RECLOSER | MR765 | 20241002 | 1626 | 20241003 | 207 | 2583797 | 581 | Distribution Circuit | Equipment Failure/Involved | Underground | 1406 | 93535 | 37.7482 | -121.8719 | No | Clear;Above 90 | Transformer (UG) | Burned/flashed | 24-0118573 | UG | Sus | 2055305 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977374 | 0 | EPSS Ckt | Y | 2024 | B PHASE- GRD- INST
MISSION | MISSION | BANCROFT-0402 | 13030402 | FUSE | 10403 | 20241002 | 1756 | 20241002 | 1900 | 2583946 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 162 | 10368 | 37.7345 | -122.1457 | No | Clear;Above 90 |  |  | 24-0118618 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977397 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | BANCROFT-0402 | 13030402 | FUSE | 10403 | 20241002 | 1909 | 20241002 | 1948 | 2584106 | 39 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 162 | 6318 | 37.7345 | -122.1457 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0118618 | OH | Sus | 0 | BAY AREA | OCT | Open Circuit | 0 | No | No | No | 1977405 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | TASSAJARA-2113 | 14662113 | TRANSFORMER | 20701 | 20241002 | 1927 | 20241002 | 2302 | 2584119 | 215 | Transformer only | Equipment Failure/Involved | Underground | 13 | 2795 | 37.7868 | -121.9456 | No | Clear;32-90 F | Fuse | Normal | 24-0118677 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977434 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 11983 | 20241002 | 2124 | 20241004 | 46 | 2584184 | 1642 | Distribution Circuit | Equipment Failure/Involved | Underground | 147 | 70549 | 37.6856 | -122.0509 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0118672 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977430 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 61683 | 20241002 | 2344 | 20241003 | 1430 | 2584180 | 886 | Distribution Circuit | Equipment Failure/Involved | Underground | 124 | 46114 | 37.5654 | -121.9886 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0118685 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977438 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1114 | 13761114 | FUSE | 10664 | 20241003 | 1103 | 20241004 | 204 | s1977684 | 901 | Distribution Circuit | 3rd Party | Vandalism | 2 | 1802 | 37.6295 | -122.1158 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0119221 | OH | Sus | 31710865 | BAY AREA | OCT | Multi-Fault | 0 | No | No | No | 1977684 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | TRANSFORMER | 315457243965 | 20241003 | 1415 | 20241003 | 1726 | 2584903 | 191 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1719 | 37.6969 | -122.0712 | No | Clear;Above 90 | Transformer (OH) | Leaking | 24-0119057 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1977635 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1108 | 12221108 | FUSE | 60701 | 20241003 | 1804 | 20241004 | 627 | 2585185 | 743 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 743 | 37.5123 | -121.9799 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0119227 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977686 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DIXON LANDING-2109 | 14722109 | FUSE | 11311 | 20241003 | 1805 | 20241003 | 1845 | 2585126 | 40 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 214 | 8560 | 37.494 | -121.9103 | No | Clear;32-90 F | Fuse | Burned Open | 24-0119209 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977679 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1107 | 12221107 | INTERRUPTER | 23900 | 20241003 | 1918 | 20241004 | 624 | 2585173 | 666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1332 | 37.5228 | -121.9671 | No | Clear;32-90 F | Other | Normal | 24-0119230 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1977689 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | TRANSFORMER | 315520042963 | 20241003 | 2122 | 20241004 | 620 | 2585254 | 538 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3228 | 37.6697 | -122.049 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0119252 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977716 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | TRANSFORMER | 315517742970 | 20241003 | 2127 | 20241004 | 630 | 2585255 | 543 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2172 | 37.6698 | -122.0496 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0119265 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977725 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 12KV-1108 | 12221108 | SWITCH | 60702SW | 20241004 | 813 | 20241004 | 1508 | 2585505 | 415 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 415 | 37.5123 | -121.9799 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0119386 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977859 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 10412 | 20241004 | 1016 | 20241004 | 1427 | 2585691 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 12801 | 37.6912 | -122.1106 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0119431 | OH | Sus | 0 | BAY AREA | OCT | None | 0 | No | No | No | 1977885 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | FUSE | 7906 | 20241004 | 1135 | 20241004 | 1214 | 2585773 | 39 | Distribution Circuit | Animal | Squirrel | 1 | 39 | 37.724 | -122.1885 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0119540 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1977916 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | RECLOSER | 298074 | 20241004 | 1747 | 20241004 | 1806 | 2586084 | 19 | Distribution Circuit | Company Initiated | Coordination failure | 951 | 18069 | 37.6865 | -122.1021 | No | Clear;32-90 F | Recloser | Normal | 24-0112255 | OH | Sus | 35272615 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1977950 | 0 | Non-EPSS | N | 2024 | B PH TGT
MISSION | MISSION | MT EDEN-1103 | 13761103 | RECLOSER | MR808 | 20241005 | 1138 | 20241006 | 5 | 2586751 | 729 | Distribution Circuit | Equipment Failure/Involved | Underground | 3120 | 326554 | 37.6431 | -122.0915 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0119795 | UG | Sus | 46332113 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1978070 | 0 | Non-EPSS | N | 2024 | C & INT
MISSION | MISSION | MT EDEN-1104 | 13761104 | OCB | 1104/2 | 20241005 | 1422 | 20241006 | 703 | 2586834 | 1001 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3544 | 259326 | 37.6319 | -122.1025 | No | Clear;Above 90 | Switch (OH) | Burned/flashed | 24-0119826 | OH | Sus | 31710875 | BAY AREA | OCT | Three Phase Fault | 0 | No | No | No | 1978090 | 0 | Non-EPSS | N | 2024 | ABC TGT
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | OTHER | 5004 | 20241005 | 1553 | 20241005 | 1709 | 2586906 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 5776 | 37.5171 | -121.9992 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0114812 | UG | Sus | 35581708 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978103 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1102 | 12221102 | SWITCH | 4415 | 20241005 | 1748 | 20241006 | 1 | 2586969 | 373 | Distribution Circuit | Equipment Failure/Involved | Underground | 37 | 9361 | 37.5186 | -121.9987 | No | Clear;Above 90 | Switch (UG) | Burned/flashed | 24-0114812 | UG | Sus | 35581708 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1978106 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1108 | 14351108 | TRANSFORMER | 315752438269 | 20241005 | 1844 | 20241006 | 524 | 2587016 | 640 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 5120 | 37.5417 | -121.9662 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0119880 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978121 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 11721 | 20241005 | 2041 | 20241005 | 2130 | 2587053 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 5687 | 37.6311 | -122.074 | No | Clear;32-90 F |  |  | 24-0119887 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1978124 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | FUSE | 10831 | 20241006 | 35 | 20241007 | 337 | 2587107 | 1622 | Distribution Circuit | Equipment Failure/Involved | Underground | 48 | 77856 | 37.7017 | -122.1445 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0119922 | UG | Sus | 31711241 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1978177 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1108 | 14351108 | TRANSFORMER | 315752438269 | 20241006 | 650 | 20241006 | 1651 | 2587154 | 601 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 4808 | 37.5417 | -121.9662 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0119912 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978164 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | FUSE | 14372 | 20241006 | 816 | 20241006 | 1146 | 2587281 | 210 | Distribution Circuit | Animal | Squirrel | 5 | 1050 | 37.6768 | -122.059 | No | Clear;32-90 F | Fuse | Normal | 24-0119941 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978192 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | FUSE | 7650 | 20241006 | 1024 | 20241006 | 1107 | 2587349 | 43 | Distribution Circuit | Animal | Squirrel | 88 | 3784 | 37.7056 | -122.1523 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0119934 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1978187 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1105 | 13111105 | TRANSFORMER | 315279244448 | 20241006 | 1507 | 20241007 | 612 | 2587539 | 905 | Transformer only | Equipment Failure/Involved | Electrical Overload | 14 | 12670 | 37.7094 | -122.133 | No | Clear;Above 90 | Transformer | Broken | 24-0119973 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978223 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1101 | 13111101 | FUSE | 10677 | 20241006 | 1521 | 20241006 | 1707 | 2587460 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 10494 | 37.7055 | -122.181 | No | Partly Cloudy;Above 90 | Cutout- fuse holder | Broken | 24-0119974 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978224 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | RECLOSER | MR219 | 20241006 | 1740 | 20241007 | 405 | 2587545 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 10625 | 37.6816 | -122.0927 | No | Clear;Above 90 | Transformer (OH) | Leaking | 24-0119986 | OH | Sus | 35585884 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1978234 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | TRANSFORMER | 24722 | 20241006 | 1828 | 20241007 | 1103 | 2587705 | 995 | Distribution Circuit | Equipment Failure/Involved | Underground | 37 | 20615 | 37.6866 | -122.0387 | No | Clear;Above 90 | Transformer (UG) | Broken | 24-0120009 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978260 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | 315346343395 | 20241006 | 2012 | 20241007 | 304 | 2587769 | 408 | Transformer only | Equipment Failure/Involved | Overhead | 30 | 12240 | 37.6808 | -122.1091 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 24-0120022 | OH | Sus | 46332330 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978272 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1105 | 13111105 | TRANSFORMER | 315276844470 | 20241006 | 2031 | 20241007 | 613 | 2587776 | 582 | Transformer only | Equipment Failure/Involved | Electrical Overload | 10 | 5820 | 37.71 | -122.1339 | No | Heat Wave-Clear;32-90 F | Transformer | Failed/Faulted | 24-0120040 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978292 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 13204 | 20241006 | 2341 | 20241007 | 705 | 2587534 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 13059 | 37.6721 | -121.8863 | No | Clear;Above 90 | Other | Deteriorated | 24-0120029 | OH | Sus | 0 | BAY AREA | OCT | Open Circuit | 0 | No | No | No | 1978280 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | TRANSFORMER | 315739038152 | 20241007 | 214 | 20241007 | 931 | 2587883 | 437 | Transformer only | Equipment Failure/Involved | Electrical Overload | 17 | 7429 | 37.5384 | -121.9707 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0120044 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978296 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315333443085 | 20241007 | 402 | 20241007 | 1044 | 2587902 | 402 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 4422 | 37.6721 | -122.1135 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0120105 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978393 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | INTERRUPTER | 269364 | 20241007 | 508 | 20241007 | 1945 | 2587910 | 565 | Distribution Circuit | Equipment Failure/Involved | Underground | 71 | 34020 | 37.5186 | -122.0532 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0120167 | UG | Sus | 35586046 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978486 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | FUSE | 97507 | 20241007 | 1051 | 20241007 | 1325 | 2588279 | 154 | Distribution Circuit | Animal | Bird found | 12 | 1848 | 37.6961 | -122.0865 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0120269 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978551 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315330742764 | 20241007 | 1338 | 20241007 | 1441 | 2588423 | 63 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 1260 | 37.6634 | -122.1142 | No | Clear;Above 90 | Conductor- Overhead | Burned/flashed | 24-0120284 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978564 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315351243268 | 20241007 | 1824 | 20241008 | 256 | 2588843 | 512 | Transformer only | 3rd Party | Metallic Balloon | 29 | 14848 | 37.6773 | -122.1074 | No | Clear;32-90 F | Transformer | Normal | 24-0120421 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978626 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | TRANSFORMER | 315208444310 | 20241008 | 445 | 20241008 | 756 | 2589056 | 191 | Transformer only | 3rd Party | Customer Equipment | 6 | 1146 | 37.7053 | -122.1575 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0120525 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1978689 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 7274 | 20241008 | 649 | 20241008 | 915 | 2589106 | 146 | Distribution Circuit | Animal | Bird found | 1 | 146 | 37.6468 | -121.7195 | No | Clear;32-90 F | Fuse | Burned Open | 24-0120585 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1978843 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DIXON LANDING-2111 | 14722111 | TRANSFORMER | 22502 | 20241008 | 1330 | 20241009 | 553 | 2589732 | 983 | Transformer only | 3rd Party | Customer Equipment | 1 | 983 | 37.4636 | -121.9213 | No | Clear;Above 90 | Transformer | Broken | 24-0120820 | OH | Sus | 0 | BAY AREA | OCT | None | 0 | No | No | No | 1978940 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | TRANSFORMER | 315578645302 | 20241008 | 1350 | 20241008 | 1853 | 2589709 | 303 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 909 | 37.7341 | -122.03 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0120794 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1978934 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | 315349943410 | 20241008 | 2216 | 20241009 | 545 | 2590083 | 449 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 7633 | 37.6812 | -122.108 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0120951 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1978990 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2107 | 12232107 | FUSE | 10993 | 20241009 | 623 | 20241009 | 1000 | 2590186 | 217 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 10976 | 37.5065 | -121.9241 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0121044 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1979035 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | OTHER | J62140 TWD T8964 | 20241009 | 1622 | 20241010 | 457 | 2591142 | 444 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 70 | 16282 | 37.5324 | -122.0123 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0121356 | UG | Sus | 31712176 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1979333 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1112 | 13501112 | RECLOSER | 999908 | 20241010 | 1635 | 20241011 | 539 | 2591792 | 784 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2091 | 99143 | 37.5748 | -122.0407 | No | Partly Cloudy;32-90 F | Pothead/Riser Termination | Burned/flashed | 24-0121993 | OH | Sus | 0 | BAY AREA | OCT | Open Circuit | 0 | No | No | No | 1979582 | 0 | Non-EPSS | N | 2024 | 50 INST- 51 TIME
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315594340632 | 20241011 | 1006 | 20241012 | 452 | 2592270 | 1126 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 9008 | 37.6059 | -122.022 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0122194 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1979803 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | 315373543354 | 20241011 | 1241 | 20241012 | 453 | 2592371 | 972 | Transformer only | Equipment Failure/Involved | Electrical Overload | 94 | 91368 | 37.6797 | -122.0998 | No | Clear;32-90 F | Transformer | Normal | 24-0122319 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1979830 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | MR650 | 20241012 | 657 | 20241012 | 2021 | 2592717 | 804 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 500 | 124762 | 37.5934 | -121.8844 | No | Clear;32-90 F |  |  | 24-0122494 | OH | Sus | 46338238 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1979912 | 0 | EPSS Ckt | Y | 2024 | B & C
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 604267 | 20241012 | 1047 | 20241013 | 15 | 2592916 | 808 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 3232 | 37.7634 | -121.7513 | No | Clear;32-90 F |  |  | 24-0122644 | OH | Sus | 0 | BAY AREA | OCT | Open Circuit | 0 | No | No | No | 1980076 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2110 | 14502110 | OCB | 2110/2 | 20241012 | 1052 | 20241012 | 1351 | 2592921 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6917 | 1233145 | 37.6697 | -121.8542 | No | Clear;32-90 F |  |  | 24-0122549 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1979993 | 0 | EPSS Ckt | Y | 2024 | A & B
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 6154 | 20241012 | 1459 | 20241012 | 1936 | 2593264 | 277 | Transformer only | Equipment Failure/Involved | Underground | 4 | 1108 | 37.7272 | -121.9352 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 24-0122628 | UG | Sus | 46338631 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1980060 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 134120 | 20241013 | 654 | 20241013 | 929 | 2593418 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 8525 | 37.7899 | -121.8435 | No | Clear;32-90 F |  |  | 24-0122663 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1980096 | 0 | EPSS Ckt | Y | 2024 | A GRD
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRANSFORMER | 315296542425 | 20241013 | 1121 | 20241013 | 1229 | 2593524 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 408 | 37.654 | -122.1259 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0122683 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1980128 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | WARD-0401 | 12980401 | TRANSFORMER | M1244 | 20241013 | 2202 | 20241014 | 1138 | 2593765 | 816 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 5712 | 37.7263 | -122.1572 | No | Partly Cloudy;32-90 F |  |  | 24-0122737 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1980168 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | FUSE | 9095 | 20241014 | 627 | 20241015 | 1453 | 2593856 | 1946 | Distribution Circuit | Equipment Failure/Involved | Underground | 261 | 377655 | 37.5485 | -121.9905 | No | Overcast;32-90 F | Transformer (UG) | Arcing | 24-0122800 | UG | Sus | 35587528 | BAY AREA | OCT | Multi-Fault | 0 | No | No | No | 1980294 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2109 | 14502109 | FUSE | 12226 | 20241015 | 13 | 20241015 | 1702 | 2594745 | 1009 | Distribution Circuit | Equipment Failure/Involved | Underground | 180 | 52656 | 37.6712 | -121.8893 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0123152 | UG | Sus | 46339328 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1980515 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | 315235643220 | 20241015 | 1316 | 20241015 | 1410 | 2595374 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 864 | 37.6755 | -122.1473 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0123408 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1980782 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1105 | 14381105 | TRANSFORMER | 315222043310 | 20241015 | 1708 | 20241015 | 2114 | 2595601 | 246 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 4182 | 37.6778 | -122.152 | No | Clear;32-90 F | Jumper | Broken | 24-0123577 | OH | Sus | 46339796 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1980834 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1105 | 14381105 | TRANSFORMER | 315224743340 | 20241015 | 1708 | 20241015 | 2114 | 2595599 | 246 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 3444 | 37.6786 | -122.1511 | No | Clear;32-90 F | Transformer | Broken | 24-0123583 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1980838 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | TRANSFORMER | 315412243957 | 20241015 | 2145 | 20241016 | 2020 | 2595702 | 1355 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 6775 | 37.6965 | -122.0868 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0123625 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1980870 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | SWITCH | 8932 | 20241015 | 2239 | 20241015 | 2254 | 2595712 | 15 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 405 | 37.6705 | -121.8918 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0123152 | UG | Sus | 46339328 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1980866 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | FUSE | 60273 | 20241016 | 1037 | 20241016 | 2154 | 2596103 | 531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 25561 | 37.5733 | -122.0792 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0123998 | OH | Sus | 35589942 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981089 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | JUMPER | JUMPERS LD SIDE OF CGC# 315257243643 | 20241016 | 1105 | 20241016 | 1241 | 2596288 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 2688 | 37.6871 | -122.1402 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 24-0124033 | OH | Sus | 0 | BAY AREA | OCT | None | 0 | No | No | No | 1981105 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2105 | 14502105 | RECLOSER | MR172 | 20241016 | 1237 | 20241016 | 1438 | 2596256 | 121 | Distribution Circuit | Equipment Failure/Involved | Underground | 3049 | 353233 | 37.657 | -121.9009 | No | Partly Cloudy;32-90 F | Stepdown | Failed/Faulted | 24-0124029 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981104 | 0 | Non-EPSS | Y | 2024 | A B GRD
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | 315222543141 | 20241016 | 1356 | 20241016 | 2003 | 2596351 | 367 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 4771 | 37.6732 | -122.1518 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0124080 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981136 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1112 | 13501112 | RECLOSER | 1105/2 | 20241016 | 1511 | 0 0 0 | 0 0 | 2596415 | 166 | Distribution Circuit | Equipment Failure/Involved | Underground | 8328 | 233885 | 37.5953 | -122.0176 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0124131 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981152 | 0 | Non-EPSS | N | 2024 | 50 INST
MISSION | MISSION | VINEYARD-2105 | 14502105 | TRANSFORMER | 30123 | 20241016 | 1746 | 20241017 | 157 | 2596539 | 491 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 491 | 37.6581 | -121.8938 | No | Clear;32-90 F | Transformer | Broken | 24-0124223 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981168 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1107 | 14471107 | TRANSFORMER | 315646338694 | 20241016 | 2145 | 20241017 | 556 | 2596664 | 491 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 12275 | 37.553 | -122.003 | No | Clear;32-90 F | Transformer | Broken | 24-0124287 | OH | Sus | 31712982 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981203 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2110 | 14502110 | OCB | 2110/2 | 20241017 | 1052 | 20241017 | 1331 | 2597044 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6917 | 743827 | 37.6697 | -121.8542 | Yes | Partly Cloudy;32-90 F |  |  | 24-0124478 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981296 | 0 | EPSS Ckt | Y | 2024 | A- B PH- GRD- INST OC
MISSION | MISSION | VINEYARD-2110 | 14502110 | OCB | 2110/2 | 20241017 | 1521 | 20241017 | 1721 | 2597417 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6917 | 788544 | 37.6697 | -121.8542 | Yes | Clear;32-90 F |  |  | 24-0124688 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981410 | 0 | EPSS Ckt | Y | 2024 | A-B- GRD TGT- INST
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | 263964 | 20241017 | 1636 | 20241017 | 1758 | 2597504 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2132 | 37.6465 | -121.7858 | Yes | Clear;32-90 F |  |  | 24-0124726 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981429 | 0 | EPSS Ckt | Y | 2024 | GRD- INST TGTS
MISSION | MISSION | MILPITAS-1109 | 82831109 | RECLOSER | 62157 | 20241017 | 1947 | 20241019 | 1739 | 2598599 | 2752 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 5504 | 37.4939 | -121.8244 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125054 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981786 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | VINEYARD-2105 | 14502105 | SWITCH | 73419 | 20241017 | 1948 | 20241019 | 744 | 2597875 | 2156 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 7 | 15092 | 37.6608 | -121.9272 | Yes | Clear;32-90 F | Other | Normal | 24-0124397 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981522 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | TRIP-SAVER | 8971 | 20241017 | 1958 | 20241019 | 1039 | 2597885 | 2315 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 81 | 186735 | 37.7112 | -122.0551 | Yes | Clear;32-90 F | Other | Normal | 24-0124371 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981532 | 0 | EPSS Ckt | N | 2024 | N/A
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | MR387 | 20241017 | 2004 | 20241019 | 1720 | 2597888 | 2716 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 72 | 180741 | 37.5738 | -121.8643 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123811 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981526 | 0 | EPSS Ckt | N | 2024 | N/A
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 48180 | 20241017 | 2004 | 20241019 | 1743 | 2597942 | 2739 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 2739 | 37.5711 | -121.864 | Yes | Clear;32-90 F |  |  | 24-0123811 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981541 | 0 | EPSS Ckt | N | 2024 | N/A
MISSION | MISSION | SUNOL-1101 | 14241101 | SWITCH | 97999 | 20241017 | 2004 | 20241019 | 1735 | 2597997 | 2731 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 2731 | 37.5681 | -121.8631 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123811 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981567 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | SWITCH | 630224 | 20241017 | 2039 | 20241019 | 1436 | 2597976 | 2517 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 62 | 156054 | 37.7886 | -121.77 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123714 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981557 | 0 | EPSS Ckt | Y | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 745511 | 20241017 | 2040 | 20241019 | 1353 | 2597964 | 2473 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 55 | 136015 | 37.7526 | -121.7791 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123714 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981550 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 915615 | 20241017 | 2040 | 20241019 | 1353 | s1981560 | 2473 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 4946 | 37.775 | -121.733 | Yes | Clear;32-90 F | Other | Normal | 24-0123714 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981560 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 292606 | 20241017 | 2041 | 20241019 | 1430 | 2597959 | 2497 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 67 | 167189 | 37.774 | -121.8165 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123777 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | Yes | No | No | 1981551 | 0 | EPSS Ckt | N | 2024 | N/A
MISSION | MISSION | CAYETANO-2109 | 14422109 | SWITCH | 148900 | 20241017 | 2045 | 20241019 | 1409 | 2597984 | 2484 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 7 | 17388 | 37.7811 | -121.7989 | Yes | Clear;32-90 F | Other | Normal | 24-0123714 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981561 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 11775 | 20241017 | 2046 | 20241019 | 1345 | s1981562 | 2459 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 16 | 39344 | 37.7685 | -121.7986 | Yes | Clear;32-90 F | Other | Normal | 24-0123714 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981562 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 546328 | 20241017 | 2120 | 20241019 | 1106 | 2598008 | 2266 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 115 | 260590 | 37.6641 | -121.733 | Yes | Clear;32-90 F | Other | Normal | 24-0123917 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981573 | 0 | EPSS Ckt | N | 2024 | N/A
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 530878 | 20241017 | 2120 | 20241019 | 1144 | 2598014 | 2304 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 111 | 255744 | 37.6114 | -121.6831 | Yes | Clear-Strong Winds;32-90 F | Other | Normal | 24-0123917 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981576 | 0 | EPSS Ckt | N | 2024 | N/A
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10633 | 20241017 | 2120 | 20241019 | 1540 | 2598023 | 2540 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 2540 | 37.5786 | -121.5877 | Yes | Clear;32-90 F |  |  | 24-0123917 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981582 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | FUSE | 11287 | 20241018 | 243 | 20241018 | 853 | 2598124 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 250 | 92500 | 37.7332 | -121.9379 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0124847 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | Yes | No | 1981631 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | TRANSFORMER | 315735837909 | 20241018 | 1212 | 20241018 | 1848 | 2598639 | 396 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 5148 | 37.5317 | -121.9716 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0125077 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981794 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2105 | 14502105 | FUSE | 11304 | 20241018 | 1221 | 20241018 | 1411 | 2598618 | 110 | Distribution Circuit | Animal | Bird found | 34 | 3700 | 37.6679 | -121.884 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0125100 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981801 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1108 | 14351108 | FUSE | 60309 | 20241018 | 2208 | 20241019 | 117 | 2599037 | 189 | Distribution Circuit | Equipment Failure/Involved | Underground | 228 | 43092 | 37.5363 | -121.9764 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0125282 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1981880 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | FUSE | 14584 | 20241019 | 1836 | 20241020 | 1928 | 2599579 | 1492 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 4440 | 37.6965 | -122.0462 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0125483 | UG | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1982042 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 107664 | 20241020 | 329 | 20241020 | 835 | 2599631 | 306 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 16218 | 37.74 | -121.7469 | No | Clear;32-90 F |  |  | 24-0125491 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1982055 | 0 | EPSS Ckt | Y | 2024 | B PHASE
MISSION | MISSION | LAS POSITAS-2108 | 14402108 | RECLOSER | MR190 | 20241022 | 1459 | 20241022 | 1725 | 2601451 | 146 | Distribution Circuit | 3rd Party | Vehicle | 3538 | 37556 | 37.6652 | -121.7354 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0126456 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1982711 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | SWITCH | 9253 | 20241022 | 2255 | 20241022 | 2333 | 2601702 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5536 | 210368 | 37.5008 | -121.9899 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0126606 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1982757 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 9449 | 20241022 | 2333 | 20241023 | 841 | 2601698 | 548 | Distribution Circuit | Equipment Failure/Involved | Overhead | 113 | 16553 | 37.6216 | -122.0846 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0126620 | OH | Sus | 35592179 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1982759 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2103 | 14232103 | SWITCH | 20099 | 20241023 | 602 | 20241023 | 615 | 2601769 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2 | 26 | 37.7005 | -121.9194 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0117208 | UG | Sus | 35437717 | BAY AREA | OCT | None | 0 | No | No | No | 1982778 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2110 | 12232110 | SWITCH | 70858 | 20241023 | 1316 | 20241023 | 1343 | 2602270 | 27 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5536 | 149472 | 37.5091 | -122.0029 | No | Clear;32-90 F | Switch (OH) | Broken | 24-0126606 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1983018 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2110 | 14502110 | OCB | 2110/2 | 20241023 | 1730 | 20241023 | 1855 | 2602450 | 85 | Distribution Circuit | Animal | Bird found | 5858 | 497930 | 37.6697 | -121.8542 | No | Clear;32-90 F | PT/CCVT | Burned/flashed | 24-0127071 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1983056 | 0 | EPSS Ckt | Y | 2024 | A-B- GRD- ISNT OC
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 12274 | 20241024 | 455 | 20241024 | 712 | 2602665 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 7261 | 37.5346 | -121.9409 | No | Clear;32-90 F |  |  | 24-0127143 | OH | Sus | 0 | BAY AREA | OCT | None | 0 | No | No | No | 1983097 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 12274 | 20241024 | 731 | 20241024 | 830 | 2602698 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 3127 | 37.5346 | -121.9409 | No | Clear;32-90 F |  |  | 24-0127158 | OH | Sus | 0 | BAY AREA | OCT | None | 0 | No | No | No | 1983105 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 12274 | 20241024 | 1007 | 20241024 | 1639 | 2602974 | 392 | Distribution Circuit | Vegetation | Tree - grew into line | 53 | 20776 | 37.5346 | -121.9409 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127295 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1983275 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | TRANSFORMER | 315415543990 | 20241024 | 1020 | 20241024 | 1043 | 2602938 | 23 | Transformer only | Company Initiated | Coordination failure | 39 | 897 | 37.6974 | -122.0857 | No | Clear;32-90 F | Other | Normal | 24-0127262 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1983262 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | 315421043537 | 20241024 | 1047 | 20241024 | 1249 | 2603021 | 122 | Transformer only | Company Initiated | Coordination failure | 15 | 1830 | 37.6851 | -122.0835 | No | Clear;32-90 F | Other | Normal | 24-0127332 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1983299 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 11162 | 20241024 | 1736 | 20241024 | 1922 | 2603305 | 106 | Distribution Circuit | Animal | Squirrel | 6 | 636 | 37.5717 | -121.9655 | No | Clear;32-90 F | Fuse | Burned Open | 24-0127630 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1983365 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | RECLOSER | MR354 | 20241024 | 1943 | 20241024 | 1949 | 2603347 | 6 | Distribution Circuit | Company Initiated | Other Circuits | 2676 | 16056 | 37.6726 | -122.1055 | No | Clear;32-90 F | Recloser | Normal | 24-0127629 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1983364 | 0 | Non-EPSS | N | 2024 | A/B/C
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | TRANSFORMER | T908555 | 20241025 | 1317 | 20241025 | 1401 | 2603942 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 31 | 1364 | 37.6939 | -122.0838 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0127958 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1983588 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | FUSE | 50028 | 20241025 | 1706 | 20241025 | 2123 | 2604168 | 257 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 13107 | 37.6868 | -122.1338 | No | Clear;32-90 F |  |  | 24-0128074 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1983623 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | TRANSFORMER | 315382043450 | 20241026 | 520 | 20241026 | 653 | 2604475 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 93 | 37.6827 | -122.0973 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0128109 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1983659 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11007 | 20241027 | 908 | 20241027 | 1016 | 2605317 | 68 | Distribution Circuit | Animal | Bird found | 1 | 68 | 37.6676 | -121.6744 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128283 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1983912 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | JUMPER | 12KV OJ @ 22206 PROSPECT ST | 20241027 | 1347 | 20241027 | 2010 | 2605430 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 14171 | 37.6771 | -122.0877 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0128301 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1983929 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1112 | 13501112 | TRANSFORMER | 315563639345 | 20241027 | 1521 | 20241027 | 2011 | 2605460 | 290 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1160 | 37.5705 | -122.0319 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0128324 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1983947 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRANSFORMER | 100000107412 | 20241027 | 2000 | 20241028 | 8 | s1983961 | 248 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1736 | 37.6553 | -122.1075 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0128340 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1983961 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-2111 | 14472111 | FUSE | 7377 | 20241028 | 714 | 20241028 | 910 | 2605671 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 116 | 37.5288 | -122.0633 | No | Partly Cloudy;32-90 F |  |  | 24-0128437 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1984095 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | RECLOSER | MR366 | 20241028 | 850 | 20241028 | 929 | 2605935 | 39 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3215 | 125385 | 37.6093 | -122.0238 | No | Partly Cloudy;32-90 F |  |  | 24-0128448 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1984122 | 0 | EPSS Ckt | N | 2024 | B & C
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 11295 | 20241028 | 942 | 20241028 | 1025 | 2606048 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 660 | 37.6236 | -122.0397 | No | Partly Cloudy;32-90 F |  |  | 24-0128480 | OH | Sus | 0 | BAY AREA | OCT | Line to Line | 0 | No | No | No | 1984147 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1109 | 14091109 | OCB | 1109/22 | 20241028 | 1126 | 20241028 | 2348 | 2606159 | 742 | Distribution Circuit | 3rd Party | Vehicle | 5039 | 409636 | 37.6917 | -122.0611 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0128533 | OH | Sus | 35593130 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1984167 | 0 | Non-EPSS | N | 2024 | A- C- GRD & 51
MISSION | MISSION | CAYETANO-2109 | 14422109 | OCB | 2109/2/NORM | 20241028 | 1335 | 20241028 | 1603 | 2606335 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3151 | 363915 | 37.7383 | -121.7706 | No | Partly Cloudy;32-90 F |  |  | 24-0128610 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1984208 | 0 | EPSS Ckt | Y | 2024 | PH- GRD INST- BU RLY
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | RECLOSER | MR235 | 20241028 | 2222 | 20241028 | 2243 | 2606657 | 21 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5225 | 109725 | 37.6704 | -122.0726 | No | Clear;32-90 F |  |  | 24-0128783 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1984268 | 0 | EPSS Ckt | N | 2024 | SGF
MISSION | MISSION | DUMBARTON-1102 | 14471102 | FUSE | 30291 | 20241029 | 738 | 20241029 | 2035 | 2606882 | 777 | Distribution Circuit | Equipment Failure/Involved | Underground | 146 | 44282 | 37.5556 | -122.0153 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0128927 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1984497 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | OCB | 1104/2 | 20241029 | 1155 | 20241029 | 1756 | 2607283 | 225 | Distribution Circuit | Equipment Failure/Involved | Underground | 5311 | 877372 | 37.6718 | -122.1596 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0128998 | UG | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1984544 | 0 | Non-EPSS | N | 2024 | B- GRD &
MISSION | MISSION | FREMONT-1104 | 14351104 | RECLOSER | 645342 | 20241030 | 1021 | 20241030 | 1207 | 2608275 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2650 | 37.5586 | -121.9197 | No | Partly Cloudy;32-90 F |  |  | 24-0129512 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | No | No | No | 1984856 | 0 | EPSS Ckt | Y | 2024 | A & INST
MISSION | MISSION | VINEYARD-2105 | 14502105 | SWITCH | 70361 | 20241030 | 1418 | 20241030 | 1520 | 2608583 | 62 | Distribution Circuit | Company Initiated | Return Circuit Normal | 82 | 5084 | 37.6745 | -121.8665 | No | Partly Cloudy;32-90 F | Switch (UG) | Normal | 24-0126130 | UG | Sus | 45034135 | BAY AREA | OCT | None | 0 | No | No | No | 1984951 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | RECLOSER | MR203 | 20241031 | 210 | 20241031 | 1344 | 2608942 | 694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 694 | 37.7169 | -122.1807 | No | Overcast-Rain;32-90 F | Switch (OH) | Failed/Faulted | 24-0129829 | OH | Sus | 35593737 | BAY AREA | OCT | Three Phase Fault | 0 | No | No | No | 1985025 | 0 | Non-EPSS | N | 2024 | A-B-C PH
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 884904 | 20241031 | 739 | 20241031 | 935 | 2609127 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 21280 | 37.752 | -121.7699 | No | Overcast;32-90 F |  |  | 24-0129905 | OH | Sus | 0 | BAY AREA | OCT | Line to Ground | 0 | Yes | No | No | 1985075 | 0 | EPSS Ckt | Y | 2024 | A- GRD TGTS
MISSION | MISSION | MT EDEN-1102 | 13761102 | TRANSFORMER | 315291842394 | 20241031 | 909 | 20241031 | 946 | 2609308 | 37 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 333 | 37.6531 | -122.1274 | No | Partly Cloudy;32-90 F |  |  | 24-0129995 | OH | Sus | 0 | BAY AREA | OCT | None | 0 | No | No | No | 1985209 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1103 | 14471103 | SWITCH | 4316 | 20241101 | 1721 | 20241101 | 2005 | 2610716 | 164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2546 | 184078 | 37.5724 | -122.0553 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 24-0130734 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1985613 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1107 | 14471107 | FUSE | 9027 | 20241102 | 16 | 20241102 | 1011 | 2611002 | 595 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 129 | 76755 | 37.5425 | -122.0207 | No | Overcast;32-90 F | Crossarm- Wood | Burned/flashed | 24-0130801 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1985667 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1109 | 13761109 | FUSE | 10454 | 20241102 | 249 | 20241102 | 1747 | 2611149 | 898 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 120 | 40080 | 37.6321 | -122.0687 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0130820 | OH | Sus | 31715606 | BAY AREA | NOV | Line to Ground | 0 | No | Yes | No | 1985681 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | JUMPER | 12KV JUMPERS 1/N CGC#315428243549 | 20241102 | 909 | 20241102 | 1228 | 2611494 | 199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2587 | 37.6857 | -122.081 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0130873 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1985778 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1103 | 14091103 | JUMPER | 12KV JUMPERS 4/N CGC#315419843678 | 20241102 | 1013 | 20241102 | 1815 | 2611526 | 482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 32294 | 37.6902 | -122.0842 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0130895 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1985803 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1103 | 14471103 | FUSE | 5564 | 20241102 | 1920 | 20241102 | 2109 | s1985913 | 109 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1162 | 126658 | 37.5663 | -122.0511 | No | Clear;32-90 F | Fuse | Burned Open | 24-0131048 | OH | Sus | 0 | BAY AREA | NOV | Open Circuit | 0 | No | No | No | 1985913 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1102 | 13111102 | FUSE | 9316 | 20241103 | 711 | 20241103 | 945 | 2612183 | 154 | Distribution Circuit | Animal | Squirrel | 58 | 8936 | 37.7272 | -122.1404 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0131097 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1985964 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1109 | 14471109 | FUSE | 7123 | 20241103 | 720 | 20241103 | 1008 | 2612187 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 544 | 89856 | 37.604 | -122.0594 | No | Clear;32-90 F |  |  | 24-0131101 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1985969 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | RECLOSER | 363116 | 20241103 | 1321 | 20241103 | 1558 | 2612524 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 13538 | 37.7726 | -121.9993 | No | Clear;32-90 F |  |  | 24-0131139 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1986009 | 0 | EPSS Ckt | Y | 2024 | A - C - & INT
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 12607 | 20241103 | 1615 | 20241103 | 1649 | 2612636 | 34 | Distribution Circuit | Animal | Squirrel | 1 | 23 | 37.7022 | -121.939 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0131173 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1986026 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2118 | 14232118 | SWITCH | 72177 | 20241103 | 2101 | 20241104 | 38 | 2612728 | 217 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 2387 | 37.6904 | -121.9144 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0127689 | UG | Sus | 35088214 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986045 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1104 | 13111104 | FUSE | 7844 | 20241104 | 434 | 20241104 | 450 | 2612806 | 16 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 304 | 37.7114 | -122.1752 | No | Clear;32-90 F |  |  | 24-0131224 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1986059 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | TRANSFORMER | T6237 | 20241104 | 1243 | 20241104 | 1639 | 2613340 | 236 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 472 | 37.6879 | -122.1257 | No | Clear;32-90 F |  |  | 24-0131451 | UG | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1986309 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 8917 | 20241104 | 1316 | 20241104 | 1643 | 2613453 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 5382 | 37.5848 | -121.6 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0131538 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986330 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1103 | 13501103 | OCB | 1103/2 | 20241104 | 2151 | 20241105 | 1645 | 2613813 | 354 | Distribution Circuit | 3rd Party | Vehicle | 94 | 33276 | 37.5953 | -122.0177 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0131732 | OH | Sus | 35595757 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1986408 | 0 | Non-EPSS | N | 2024 | G
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | T6661 | 20241105 | 231 | 20241105 | 1027 | 2613833 | 476 | Transformer only | 3rd Party | Vandalism | 8 | 3808 | 37.6276 | -122.098 | Yes | Clear;32-90 F | Circuit Breaker | Normal | 24-0131945 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1986567 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | RECLOSER | 467034 | 20241105 | 443 | 20241105 | 843 | 2613853 | 240 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4234 | 1016160 | 37.6189 | -122.0448 | Yes | Partly Cloudy;32-90 F |  |  | 24-0131799 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1986417 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | JUMPER | FB'S 5 S/O CGC 315503247212 | 20241105 | 950 | 20241105 | 1516 | 2614064 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 5542 | 37.786 | -122.0598 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0131922 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986522 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316625039970 | 20241105 | 1501 | 20241105 | 1643 | 2614496 | 102 | Transformer only | Company Initiated | Personnel- company | 1 | 102 | 37.5914 | -121.6661 | Yes | Strong Winds-Partly Cloudy;32-90 F | Transformer | Broken | 24-0132178 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986672 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 605520 | 20241105 | 1559 | 20241107 | 832 | 2614553 | 2433 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 160213 | 37.575 | -121.8795 | Yes | Partly Cloudy;32-90 F |  |  | 24-0132230 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1986681 | 0 | EPSS Ckt | Y | 2024 | GRD INST
MISSION | MISSION | VINEYARD-2105 | 14502105 | SWITCH | 2108/2 | 20241105 | 1713 | 20241105 | 1843 | 2614696 | 90 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4085 | 367496 | 37.6697 | -121.8543 | Yes | Clear;32-90 F |  |  | 24-0118503 | OH | Sus | 46330412 | BAY AREA | NOV | Open Circuit | 0 | No | No | No | 1986693 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | RECLOSER | 609690 | 20241105 | 1843 | 20241105 | 1856 | -2614699 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1831 | 23803 | 37.6647 | -121.9162 | Yes | Clear;32-90 F |  |  | 24-0118503 | OH | Sus | 46330412 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1986698 | 0 | EPSS Ckt | N | 2024 | A&C GRD
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 546328 | 20241105 | 1926 | 20241106 | 1440 | 2614754 | 1154 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 114 | 131556 | 37.6641 | -121.733 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131971 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986716 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 530878 | 20241105 | 1926 | 20241106 | 1522 | 2614964 | 1196 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 111 | 132756 | 37.6114 | -121.6831 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131971 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986796 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10633 | 20241105 | 1926 | 20241106 | 1721 | 2615013 | 1315 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 1315 | 37.5786 | -121.5877 | Yes | Clear;32-90 F |  |  | 24-0131971 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986808 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 134120 | 20241105 | 1949 | 20241106 | 2101 | 2614844 | 1512 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 93 | 139628 | 37.7899 | -121.8435 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131932 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986764 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 915615 | 20241105 | 1959 | 20241106 | 2037 | 2614881 | 1478 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 108 | 152385 | 37.775 | -121.733 | Yes | Clear;32-90 F |  |  | 24-0131842 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986768 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2111 | 14422111 | FUSE | 383645 | 20241105 | 2004 | 20241106 | 2046 | 2614883 | 1482 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 26 | 38532 | 37.7114 | -121.8059 | Yes | Clear;32-90 F |  |  | 24-0131944 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986770 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | SWITCH | 148900 | 20241105 | 2009 | 20241107 | 935 | 2614929 | 2246 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 7 | 15722 | 37.7811 | -121.7989 | Yes | Clear;32-90 F |  |  | 24-0131842 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986781 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 292606 | 20241105 | 2009 | 20241106 | 2202 | 2617179 | 1553 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 12 | 18636 | 37.774 | -121.8165 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131932 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987320 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | NEWARK 21KV-2108 | 12232108 | OCB | 2108/2 | 20241105 | 2017 | 20241106 | 1521 | 2614911 | 1144 | Distribution Circuit | Equipment Failure/Involved | Underground | 1618 | 396024 | 37.5029 | -121.9816 | Yes | Clear;32-90 F | Connector or Splice (UG) | Broken | 24-0132290 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1986790 | 0 | Non-EPSS | N | 2024 | A & GRD
MISSION | MISSION | CAYETANO-2109 | 14422109 | SWITCH | 630224 | 20241105 | 2025 | 20241107 | 908 | 2617253 | 2203 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 48 | 76818 | 37.7886 | -121.77 | Yes | Clear;32-90 F |  |  | 24-0131842 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987329 | 0 | EPSS Ckt | Y | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 72173 | 20241105 | 2026 | 20241107 | 927 | 2617261 | 2221 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 14 | 31094 | 37.8155 | -121.7953 | Yes | Clear;32-90 F |  |  | 24-0131842 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987331 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MILPITAS-1109 | 82831109 | SWITCH | 34342 | 20241106 | 18 | 20241107 | 1138 | 2616885 | 2120 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 4240 | 37.4939 | -121.8243 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131786 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987276 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2107 | 14232107 | FUSE | 11464 | 20241106 | 19 | 20241106 | 1413 | 2615333 | 834 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7506 | 37.7171 | -122.0077 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0132478 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1987100 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | MR544 | 20241106 | 29 | 20241106 | 325 | 2615321 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2750 | 484000 | 37.7084 | -122.1271 | No | Clear;32-90 F |  |  | 24-0132318 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1986881 | 0 | EPSS Ckt | Y | 2024 | C
MISSION | MISSION | VINEYARD-2108 | 14502108 | SWITCH | 73419 | 20241106 | 30 | 20241106 | 1742 | 2615323 | 1032 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 7 | 7224 | 37.6608 | -121.9272 | No | Clear-Strong Winds;32-90 F |  |  | 24-0132072 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986884 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 48180 | 20241106 | 35 | 20241107 | 911 | 2615331 | 1956 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 1956 | 37.5711 | -121.864 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131980 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986890 | 0 | EPSS Ckt | N | 2024 | NONE
MISSION | MISSION | SUNOL-1101 | 14241101 | SWITCH | 97999 | 20241106 | 35 | 20241107 | 930 | 2615337 | 1975 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 1975 | 37.5681 | -121.8631 | No | Clear;32-90 F |  |  | 24-0131980 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986891 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 13102 | 20241106 | 37 | 20241107 | 944 | 2615326 | 1987 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 8 | 15434 | 37.6196 | -121.9226 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131980 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986886 | 0 | EPSS Ckt | N | 2024 | NONE
MISSION | MISSION | SUNOL-1101 | 14241101 | JUMPER | 491853 SBCO | 20241106 | 37 | 20241107 | 916 | 2615339 | 1959 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 1959 | 37.559 | -121.86 | No | Clear;32-90 F |  |  | 24-0131980 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986892 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | FUSE | 611309 | 20241106 | 59 | 20241106 | 1252 | 2615335 | 713 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 47771 | 37.6937 | -122.0995 | No | Clear;32-90 F |  |  | 24-0132666 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1987259 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2108 | 14232108 | RECLOSER | 363116 | 20241106 | 148 | 20241107 | 947 | 2615360 | 1919 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 98 | 188062 | 37.7726 | -121.9993 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0132331 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1986902 | 0 | EPSS Ckt | N | 2024 | A - C & INT
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 12704 | 20241106 | 753 | 20241106 | 1640 | s1987037 | 527 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 1581 | 37.727 | -122.0795 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132036 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987037 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | RECLOSER | 8971 | 20241106 | 758 | 20241106 | 1635 | 2615848 | 517 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 78 | 40326 | 37.7112 | -122.0551 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132036 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987009 | 0 | EPSS Ckt | N | 2024 | NONE
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | RECLOSER | MR544 | 20241106 | 806 | 20241106 | 1029 | 2615407 | 143 | Distribution Circuit | 3rd Party | Other | 2750 | 376870 | 37.7084 | -122.1271 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132447 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1987044 | 0 | EPSS Ckt | Y | 2024 | C
MISSION | MISSION | SAN RAMON-2108 | 14232108 | SWITCH | 916526BP | 20241106 | 822 | 20241107 | 954 | 2616065 | 1532 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 70 | 107240 | 37.7949 | -122.0183 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132055 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987072 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | OCB | UO-1/2 | 20241106 | 903 | 20241106 | 2326 | 2616222 | 863 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7575 | 1296385 | 37.7107 | -122.1488 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132505 | OH | Sus | 46382365 | BAY AREA | NOV | Line to Line | 0 | No | Yes | No | 1987148 | 0 | Non-EPSS | N | 2024 | OC
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | JUMPER | 2076 STRANG AVE, SAN LEANDRO | 20241106 | 1047 | 20241106 | 1637 | 2616612 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 14000 | 37.7036 | -122.1098 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0132583 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1987215 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1104 | 14471104 | JUMPER | FB'S LD SIDE OF CGC 315555438179 | 20241107 | 1314 | 20241107 | 1819 | 2618004 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2745 | 37.5386 | -122.034 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0133162 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987585 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315223743891 | 20241108 | 15 | 20241108 | 1049 | 2618319 | 634 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 5706 | 37.6938 | -122.1519 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0133362 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1987664 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | TRANSFORMER | 315401043975 | 20241108 | 910 | 20241108 | 1113 | 2618654 | 123 | Transformer only | 3rd Party | Other | 10 | 1230 | 37.697 | -122.0907 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0133547 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1987873 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DIXON LANDING-2101 | 14722101 | OCB | 2101/2 | 20241108 | 1701 | 20241110 | 1100 | 2619318 | 2286 | Distribution Circuit | Equipment Failure/Involved | Underground | 4068 | 722457 | 37.457 | -121.921 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0133724 | UG | Sus | 46383981 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1987942 | 0 | EPSS Ckt | N | 2024 | B PH & GRD
MISSION | MISSION | SAN LEANDRO-1116 | 13111116 | OCB | 1116/2 | 20241110 | 746 | 20241110 | 848 | 2620055 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3340 | 73920 | 37.7106 | -122.1485 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0133891 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1988167 | 0 | Non-EPSS | N | 2024 | A & B
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | TRANSFORMER | 315349643952 | 20241110 | 1346 | 20241110 | 1540 | 2620244 | 114 | Transformer only | Unknown Cause | Patrol - found nothing | 24 | 2736 | 37.696 | -122.1085 | No | Clear;32-90 F |  |  | 24-0133956 | OH | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1988228 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2109 | 14502109 | INTERRUPTER | 408134 | 20241110 | 1346 | 20241111 | 15 | 2620241 | 629 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 34117 | 37.6763 | -121.8611 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0133950 | UG | Sus | 35597140 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1988223 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 14038 | 20241110 | 1516 | 20241110 | 1619 | 2620267 | 63 | Distribution Circuit | Animal | Squirrel | 101 | 6363 | 37.6508 | -122.0783 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0133963 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1988231 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | OCB | 1106/2 | 20241111 | 629 | 20241111 | 1144 | 2620459 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5203 | 1126620 | 37.6718 | -122.1596 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0134009 | OH | Sus | 46386987 | BAY AREA | NOV | Line to Ground | 0 | No | Yes | No | 1988287 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 11893 | 20241111 | 736 | 20241111 | 1024 | 2620508 | 168 | Distribution Circuit | Animal | Squirrel | 28 | 4704 | 37.6621 | -122.0559 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 24-0134078 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1988386 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1110 | 14471110 | TRANSFORMER | 7250 | 20241111 | 911 | 20241111 | 1800 | 2620616 | 529 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 1409 | 37.5581 | -122.065 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0134094 | UG | Sus | 35597113 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1988402 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | OCB | 2109/2/NORM | 20241111 | 944 | 20241111 | 1220 | 2620740 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3151 | 470795 | 37.7383 | -121.7706 | No | Overcast;32-90 F |  |  | 24-0134068 | OH | Sus | 0 | BAY AREA | NOV | Multi-Fault | 0 | No | No | No | 1988376 | 0 | EPSS Ckt | Y | 2024 | PH OR GRD INST OC
MISSION | MISSION | FREMONT-1108 | 14351108 | INTERRUPTER | 44766 | 20241111 | 945 | 20241111 | 1125 | 2620721 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1224 | 122400 | 37.5414 | -121.9747 | No | Overcast;32-90 F |  |  | 24-0134107 | UG | Sus | 0 | BAY AREA | NOV | None | 0 | No | No | No | 1988415 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1106 | 13761106 | RECLOSER | MR222 | 20241111 | 957 | 20241111 | 1632 | 2620788 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 14388 | 37.6332 | -122.1212 | No | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 24-0134073 | OH | Sus | 46387460 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1988382 | 0 | Non-EPSS | N | 2024 | B/GRD
MISSION | MISSION | FREMONT-1108 | 14351108 | FUSE | 60309 | 20241111 | 1054 | 20241111 | 1856 | 2620865 | 482 | Distribution Circuit | Equipment Failure/Involved | Underground | 634 | 121960 | 37.5363 | -121.9764 | No | Overcast-Rain;32-90 F | Conductor- Underground | Deteriorated | 24-0134148 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1988458 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1105 | 13501105 | FUSE | 15070 | 20241112 | 856 | 20241113 | 350 | 2622631 | 1134 | Distribution Circuit | Equipment Failure/Involved | Underground | 3348 | 298789 | 37.5642 | -122.0075 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0134548 | UG | Sus | 35597461 | BAY AREA | NOV | Multi-Fault | 0 | No | No | No | 1988961 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 884904 | 20241113 | 651 | 20241113 | 858 | 2623586 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 23495 | 37.752 | -121.7699 | No | Partly Cloudy;32-90 F |  |  | 24-0134922 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1989174 | 0 | EPSS Ckt | N | 2024 | A & GRD
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | FUSE | 10558 | 20241113 | 2141 | 20241114 | 151 | 2624529 | 250 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 250 | 37.5307 | -122.0163 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0135315 | UG | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1989495 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1105 | 12221105 | JUMPER | OVERARM OJ 2 SPANS W/ O CGC# 315583937602 | 20241114 | 1803 | 20241115 | 348 | 2625378 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 585 | 37.5231 | -122.0251 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0135715 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1989818 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1103 | 13501103 | OCB | 1103/2 | 20241114 | 2111 | 20241115 | 404 | 2625462 | 413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 704 | 43353 | 37.5953 | -122.0177 | No | Partly Cloudy;32-90 F | Capacitor | Failed/Faulted | 24-0135742 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1989831 | 0 | Non-EPSS | N | 2024 | A-B- GRD
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 12793 | 20241116 | 1344 | 20241116 | 1435 | 2627061 | 51 | Distribution Circuit | Animal | Squirrel | 15 | 782 | 37.7077 | -122.0738 | No | Clear;32-90 F | Fuse | Burned Open | 24-0136247 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1990287 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2111 | 14232111 | FUSE | 7553 | 20241116 | 1517 | 20241116 | 1630 | 2627106 | 73 | Distribution Circuit | Animal | Squirrel | 23 | 1677 | 37.7086 | -121.9166 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0136268 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1990296 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315336742941 | 20241117 | 314 | 20241117 | 1004 | 2627239 | 410 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 6560 | 37.6682 | -122.1122 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0136290 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1990333 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 9877 | 20241117 | 2246 | 20241118 | 521 | 2627694 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 15577 | 37.5342 | -121.9454 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0136369 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1990431 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NEWARK 21KV-2110 | 12232110 | TRANSFORMER | 315631536565 | 20241118 | 944 | 20241118 | 1054 | 2628123 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 70 | 37.4943 | -122.0072 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0136525 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1990648 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315245243163 | 20241118 | 1024 | 20241118 | 2027 | 2628194 | 603 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 15075 | 37.6739 | -122.144 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0136674 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1990701 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 12KV-1103 | 12221103 | SWITCH | 20441 | 20241118 | 1326 | 20241118 | 1356 | 2628374 | 30 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 70 | 2100 | 37.5309 | -122.0138 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0136551 | UG | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1990685 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315240343119 | 20241118 | 1718 | 20241118 | 2028 | 2628627 | 190 | Transformer only | Equipment Failure/Involved | Electrical Overload | 23 | 4370 | 37.6727 | -122.1457 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0136783 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1990741 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1107 | 14471107 | RECLOSER | MR242 | 20241119 | 252 | 20241119 | 1021 | 2628744 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5249 | 314963 | 37.5439 | -122.0196 | No | Partly Cloudy;32-90 F | Switch (OH) | Arcing | 24-0136821 | OH | Sus | 46391372 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1990769 | 0 | Non-EPSS | N | 2024 | NO TARGETS
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | TRANSFORMER | 315174644875 | 20241119 | 907 | 20241119 | 1419 | 2628972 | 312 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 3432 | 37.7206 | -122.1695 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0137000 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1990981 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1101 | 13111101 | TRANSFORMER | T7286 | 20241119 | 1203 | 20241119 | 1324 | 2629293 | 81 | Transformer only | 3rd Party | Customer Equipment | 3 | 243 | 37.7135 | -122.1877 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0137131 | UG | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1991029 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | FUSE | 9790 | 20241119 | 1417 | 20241119 | 1436 | 2629386 | 19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 263 | 4997 | 37.6206 | -122.037 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0137246 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1991065 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1101 | 13501101 | FUSE | 9803 | 20241119 | 1749 | 20241119 | 1757 | 2629713 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 263 | 2104 | 37.617 | -122.042 | No | Overcast;32-90 F | Fuse | Normal | 24-0137337 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1991091 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 847902 | 20241120 | 616 | 20241120 | 808 | 2630083 | 112 | Distribution Circuit | Equipment Failure/Involved | Underground | 2006 | 191210 | 37.7128 | -121.8719 | No | Overcast;32-90 F | Switch (UG) | Broken | 24-0137432 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1991174 | 0 | EPSS Ckt | N | 2024 | A PH- GRD- INST
MISSION | MISSION | VINEYARD-2110 | 14502110 | TRANSFORMER | T78747 | 20241120 | 741 | 20241120 | 1247 | 2630197 | 306 | Distribution Circuit | Equipment Failure/Involved | Underground | 79 | 8486 | 37.7086 | -121.843 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0137548 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1991268 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | FUSE | 14069 | 20241120 | 932 | 20241120 | 1204 | 2630461 | 152 | Distribution Circuit | 3rd Party | Customer Equipment | 38 | 5776 | 37.6809 | -122.0858 | No | Overcast;32-90 F | Other | Burned/flashed | 24-0137711 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1991406 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | OTHER | WIRE DOWN @ CGC# 315318243646 | 20241120 | 937 | 20241120 | 1745 | 2630485 | 488 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2576 | 31168 | 37.6872 | -122.1191 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0137617 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | Yes | Yes | 1991346 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1107 | 13111107 | OTHER | OJ N/OF 8196 | 20241120 | 1019 | 20241120 | 1218 | 2630660 | 80 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2572 | 203824 | 37.6994 | -122.1396 | No | Overcast;32-90 F | Conductor- Overhead | Arcing | 24-0137667 | OH | Sus | 0 | BAY AREA | NOV | Open Circuit | 0 | No | No | No | 1991382 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1105 | 14381105 | TRANSFORMER | 315318243646 | 20241120 | 1438 | 20241120 | 1848 | 2631385 | 250 | Transformer only | Equipment Failure/Involved | Electrical Overload | 7 | 1750 | 37.6875 | -122.1191 | No | Rain-Overcast;32-90 F | Transformer | Broken | 24-0137896 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1991516 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2104 | 14232104 | TRANSFORMER | 315855144728 | 20241120 | 1550 | 20241120 | 1638 | 2631517 | 48 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 288 | 37.7197 | -121.9341 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0137975 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1991557 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1107 | 14351107 | TRANSFORMER | 315724537861 | 20241120 | 1627 | 20241120 | 2324 | 2631521 | 417 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 7506 | 37.5303 | -121.9755 | No | Overcast;32-90 F | Transformer | Broken- wire on ground | 24-0137998 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | Yes | No | 1991572 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1105 | 14381105 | SWITCH | 4680 | 20241120 | 1706 | 20241120 | 1713 | 2631664 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2441 | 17087 | 37.6867 | -122.1385 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0137667 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1991583 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | FUSE | 8570 | 20241120 | 1859 | 20241120 | 2149 | 2631799 | 170 | Distribution Circuit | 3rd Party | Vehicle | 192 | 32640 | 37.6628 | -122.0276 | No | Overcast;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0138099 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1991646 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | MR418 | 20241120 | 2121 | 20241121 | 351 | 2631962 | 390 | Distribution Circuit | 3rd Party | Vehicle | 310 | 26994 | 37.6799 | -121.7168 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0138101 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1991648 | 0 | EPSS Ckt | N | 2024 | A & C PHASE
MISSION | MISSION | GRANT-1105 | 14381105 | TRANSFORMER | 315246543553 | 20241121 | 133 | 20241121 | 1216 | 2632294 | 643 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 3215 | 37.6847 | -122.1439 | No | Overcast-Rain;32-90 F | Secondary | Normal | 24-0138406 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1991837 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | TRANSFORMER | 315306644614 | 20241121 | 454 | 20241121 | 1242 | 2632236 | 468 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 9360 | 37.7141 | -122.1236 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0138274 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | Yes | No | 1991764 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1103 | 13761103 | RECLOSER | MR643 | 20241121 | 515 | 20241121 | 1122 | 2632146 | 367 | Distribution Circuit | 3rd Party | Metallic Balloon | 2211 | 60353 | 37.6564 | -122.0987 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0138180 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1991722 | 0 | Non-EPSS | N | 2024 | NA
MISSION | MISSION | GRANT-1102 | 14381102 | OCB | 1102/2 | 20241121 | 711 | 20241121 | 808 | 2632307 | 57 | Distribution Circuit | Vegetation | Tree - branch fell on line | 484 | 27588 | 37.6718 | -122.1597 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0138206 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1991726 | 0 | Non-EPSS | N | 2024 | B-C PH- TIME OC- SET A
MISSION | MISSION | SAN LEANDRO-1109 | 13111109 | TRANSFORMER | 315194445127 | 20241121 | 1040 | 20241121 | 1058 | 2632288 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 414 | 37.7277 | -122.1627 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Arcing | 24-0138354 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1991815 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 11228 | 20241121 | 1456 | 20241121 | 1606 | 2633030 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 420 | 37.6551 | -121.6688 | No | Clear;32-90 F |  |  | 24-0138583 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1991912 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | FUSE | 9235 | 20241121 | 2045 | 20241122 | 1420 | 2633312 | 1055 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 7553 | 37.5257 | -121.9495 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0138691 | UG | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1991949 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | TRANSFORMER | 315493543701 | 20241122 | 1412 | 20241122 | 2103 | 2634805 | 411 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2055 | 37.6898 | -122.0585 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 24-0139147 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1992218 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1112 | 13761112 | FUSE | 12756 | 20241122 | 1600 | 20241122 | 1954 | 2634983 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 526 | 123084 | 37.6535 | -122.0884 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Together | 24-0139208 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1992240 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 546328 | 20241122 | 1853 | 20241122 | 2002 | 2635293 | 69 | Distribution Circuit | Equipment Failure/Involved | Overhead | 226 | 15480 | 37.6641 | -121.733 | No | Overcast-Heavy Rain;32-90 F | Lightning Arrestor | Burned/flashed | 24-0139261 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1992278 | 0 | EPSS Ckt | N | 2024 | C- SGF & 50
MISSION | MISSION | JARVIS-1111 | 13501111 | FUSE | 6444 | 20241123 | 858 | 20241123 | 1924 | 2636051 | 74 | Distribution Circuit | Equipment Failure/Involved | Underground | 73 | 5906 | 37.5742 | -121.9896 | No | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Broken | 24-0139481 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1992480 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315312343142 | 20241123 | 951 | 20241123 | 1302 | 2636192 | 191 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 3438 | 37.6736 | -122.1208 | No | Partly Cloudy-Drizzle;32-90 F | Secondary | Broken | 24-0139493 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1992487 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1104 | 14381104 | FUSE | 51033 | 20241123 | 1129 | 20241123 | 1357 | 2636296 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 9620 | 37.6908 | -122.1233 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0139519 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1992510 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | RECLOSER | 457996 | 20241124 | 827 | 20241124 | 1610 | 2636886 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 6487 | 37.5243 | -122.0425 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139660 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | Yes | No | 1992622 | 0 | Non-EPSS | N | 2024 | A - C & GRD
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | TRANSFORMER | 315564542428 | 20241124 | 1007 | 20241124 | 1236 | 2636953 | 149 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 298 | 37.6551 | -122.0333 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0139711 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1992650 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1111 | 13111111 | OCB | 1111/2 | 20241125 | 119 | 20241126 | 1417 | 2637287 | 2218 | Distribution Circuit | Equipment Failure/Involved | Underground | 1283 | 433982 | 37.7107 | -122.1489 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Broken | 24-0139805 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1992702 | 0 | Non-EPSS | N | 2024 | GRD- PH OC
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 9376 | 20241125 | 1014 | 20241125 | 1550 | 2637526 | 336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 35616 | 37.6536 | -122.0736 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Deteriorated | 24-0139989 | OH | Sus | 31718579 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1992774 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2119 | 14232119 | FUSE | 670549 | 20241125 | 1207 | 20241125 | 1230 | 2637697 | 23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 23 | 37.7159 | -121.8988 | No | Overcast-Drizzle;32-90 F |  |  | 24-0139988 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1992773 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1105 | 14381105 | TRANSFORMER | 315202542984 | 20241125 | 1239 | 20241125 | 1446 | 2637739 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 127 | 37.6688 | -122.1587 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Burned Open | 24-0140082 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1992804 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2111 | 14232111 | OCB | 2111/2 | 20241126 | 706 | 20241126 | 1139 | 2638282 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2285 | 282591 | 37.7448 | -121.9369 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0140259 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | Yes | No | 1992898 | 0 | Non-EPSS | N | 2024 | PH OC TARGET B-C
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | FUSE | 10589 | 20241126 | 1122 | 20241126 | 1251 | s1993014 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 120 | 10685 | 37.5285 | -122.0435 | No | Clear;32-90 F |  |  | 24-0140486 |  | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1993014 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | TRANSFORMER | 315982538667 | 20241128 | 1112 | 20241128 | 1717 | 2639847 | 365 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 365 | 37.5538 | -121.8864 | No | Clear;32-90 F | Transformer | On Ground | 24-0141230 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1993276 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | RECLOSER | 546328 | 20241128 | 1217 | 20241128 | 1448 | 2639854 | 151 | Distribution Circuit | 3rd Party | Vehicle | 226 | 34126 | 37.6641 | -121.733 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0141207 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1993250 | 0 | EPSS Ckt | N | 2024 | N/A
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 298061 | 20241128 | 1258 | 20241129 | 935 | 2639883 | 1119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 203 | 247977 | 37.5958 | -121.8897 | No | Clear;32-90 F |  |  | 24-0141211 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1993255 | 0 | EPSS Ckt | N | 2024 | SGF & OC
MISSION | MISSION | SAN RAMON-2117 | 14232117 | FUSE | 70049 | 20241129 | 1413 | 20241130 | 937 | 2640269 | 1164 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 5236 | 37.714 | -121.8846 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0141303 | UG | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1993336 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | DUMBARTON-1110 | 14471110 | TRANSFORMER | T94917 | 20241130 | 1650 | 20241201 | 359 | 2640842 | 669 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 9973 | 37.5688 | -122.0604 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0141447 | UG | Sus | 35601706 | BAY AREA | NOV | None | 0 | No | No | No | 1993435 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10882 | 20241130 | 1920 | 20241130 | 2216 | 2640922 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 352 | 37.5977 | -121.6341 | No | Clear;32-90 F |  |  | 24-0141467 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1993445 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | TRANSFORMER | 315224644489 | 20241203 | 1147 | 20241204 | 115 | 2643151 | 808 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 808 | 37.7102 | -122.1519 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0142279 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1994145 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1110 | 13111110 | OCB | 1110/2 | 20241203 | 1149 | 20241204 | 217 | 2642906 | 868 | Distribution Circuit | 3rd Party | Vehicle | 3663 | 447347 | 37.7107 | -122.1486 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0142133 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1994078 | 0 | Non-EPSS | N | 2024 | ABC PH OC
MISSION | MISSION | FREMONT-1110 | 14351110 | FUSE | 15289 | 20241203 | 1355 | 20241204 | 418 | 2643047 | 863 | Distribution Circuit | 3rd Party | Vehicle | 111 | 87433 | 37.5362 | -121.9655 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0142211 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1994113 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | LIVERMORE-1102 | 12141102 | FUSE | 9498 | 20241204 | 836 | 20241204 | 1341 | 2643551 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 127 | 38735 | 37.673 | -121.7806 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0142389 | OH | Sus | 35601816 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1994280 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | FUSE | 74146 | 20241204 | 1317 | 20241204 | 1447 | 2644034 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 8190 | 37.6619 | -121.8707 | No | Clear;32-90 F |  |  | 24-0142602 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1994509 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | TRANSFORMER | 315167344786 | 20241204 | 1420 | 20241204 | 1724 | 2644082 | 184 | Transformer only | Equipment Failure/Involved | Electrical Overload | 17 | 3128 | 37.7181 | -122.1719 | No | Clear;32-90 F | Transformer | Broken | 24-0142613 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1994511 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2106 | 14502106 | TRANSFORMER | 316032842537 | 20241204 | 1732 | 20241205 | 609 | 2644211 | 757 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 6056 | 37.6602 | -121.8718 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0142752 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1994553 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1101 | 13761101 | TRANSFORMER | 315353241779 | 20241205 | 44 | 20241205 | 350 | 2644323 | 186 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 2604 | 37.6365 | -122.1059 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0142756 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1994557 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1103 | 13761103 | TRANSFORMER | 315365342595 | 20241205 | 1739 | 20241205 | 2157 | 2645370 | 258 | Transformer only | Equipment Failure/Involved | Electrical Overload | 16 | 4128 | 37.6588 | -122.1022 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0143134 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1994904 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 11575 | 20241205 | 2139 | 20241206 | 940 | 2645452 | 721 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 721 | 37.636 | -121.8792 | No | Clear;32-90 F |  |  | 24-0143176 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1994938 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | RADUM-1102 | 13151102 | FUSE | 11023 | 20241206 | 915 | 20241206 | 1100 | 2645747 | 105 | Distribution Circuit | Animal | Squirrel | 28 | 2940 | 37.6799 | -121.8689 | No | Clear;32-90 F | Insulator | Normal | 24-0143287 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1995139 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 14329 | 20241208 | 213 | 20241208 | 2227 | 2646766 | 1214 | Distribution Circuit | Equipment Failure/Involved | Underground | 188 | 169094 | 37.6569 | -122.0419 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0143660 | UG | Sus | 46407782 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1995414 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2108 | 14502108 | RECLOSER | 609690 | 20241208 | 913 | 20241208 | 1257 | 2646879 | 224 | Distribution Circuit | Equipment Failure/Involved | Underground | 1831 | 202520 | 37.6647 | -121.9162 | No | Partly Cloudy;32-90 F | Switch (UG) | Leaking | 24-0143692 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1995464 | 0 | EPSS Ckt | N | 2024 | B AND GRD
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316504042736 | 20241208 | 1152 | 20241209 | 425 | 2646937 | 993 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 993 | 37.6674 | -121.7091 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143725 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1995499 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 73258 | 20241209 | 342 | 20241209 | 412 | 2647202 | 30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 270 | 37.6652 | -121.7323 | No | Clear;32-90 F |  |  | 24-0143791 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1995545 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 12274 | 20241209 | 554 | 20241209 | 807 | 2647230 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 7049 | 37.5346 | -121.9409 | No | Clear;32-90 F |  |  | 24-0143822 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1995580 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | RECLOSER | 884904 | 20241209 | 640 | 20241210 | 146 | 2647241 | 1146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 212010 | 37.752 | -121.7699 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0143807 | OH | Sus | 35604115 | BAY AREA | DEC | Line to Line | 0 | No | Yes | No | 1995564 | 0 | EPSS Ckt | N | 2024 | B-C TGTS
MISSION | MISSION | FREMONT-1109 | 14351109 | FUSE | 12274 | 20241209 | 850 | 20241209 | 939 | 2647483 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 2597 | 37.5346 | -121.9409 | No | Clear;32-90 F |  |  | 24-0143866 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1995712 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1103 | 13501103 | FUSE | 11713 | 20241209 | 938 | 20241209 | 1048 | 2647599 | 70 | Distribution Circuit | Animal | Squirrel | 9 | 630 | 37.6051 | -122.0589 | No | Clear;32-90 F | Fuse | Burned Open | 24-0143895 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1995753 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | FREMONT-1110 | 14351110 | TRANSFORMER | 315730037902 | 20241209 | 2018 | 20241210 | 214 | 2648138 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 4959 | 37.5315 | -121.9736 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0144043 | OH | Sus | 35604298 | BAY AREA | DEC | None | 0 | No | No | No | 1995863 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315424741704 | 20241209 | 2154 | 20241210 | 102 | 2648178 | 188 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 3760 | 37.6348 | -122.0811 | No | Clear;32-90 F | Transformer | Broken | 24-0144055 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1995881 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 71413 | 20241210 | 220 | 20241210 | 527 | 2648283 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 935 | 37.7619 | -121.7811 | No | Clear;32-90 F |  |  | 24-0144071 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1995901 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 9901 | 20241210 | 627 | 20241210 | 1001 | 2648310 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 5350 | 37.6627 | -121.8635 | No | Clear;32-90 F |  |  | 24-0144134 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1996125 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | TRANSFORMER | 100000130370 | 20241210 | 627 | 20241210 | 1017 | 2648311 | 230 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 920 | 37.6628 | -121.8635 | No | Clear;32-90 F |  |  | 24-0144147 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 1996143 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1114 | 13111114 | FUSE | 8459 | 20241210 | 751 | 20241210 | 2232 | 2648368 | 881 | Distribution Circuit | Animal | Bird found | 356 | 32481 | 37.7078 | -122.1263 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0144104 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1995944 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1104 | 14091104 | OCB | 1104/12 | 20241210 | 1346 | 20241211 | 200 | 2648976 | 734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3216 | 412426 | 37.6917 | -122.0611 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0144235 | OH | Sus | 46415083 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | No | 1996223 | 0 | Non-EPSS | N | 2024 | SEL-351 TIME OC
MISSION | MISSION | CAYETANO-2109 | 14422109 | SWITCH | 148900 | 20241210 | 2320 | 20241211 | 246 | 2649258 | 206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1442 | 37.7811 | -121.7989 | No | Overcast;32-90 F | Other | Broken | 24-0144315 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1996286 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | TRANSFORMER | 315410841434 | 20241211 | 1012 | 20241212 | 210 | 2649663 | 958 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 958 | 37.6274 | -122.0857 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0144480 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1996620 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LIVERMORE-1101 | 12141101 | FUSE | 10907 | 20241211 | 1225 | 20241211 | 1605 | 2650052 | 220 | Distribution Circuit | Animal | Squirrel | 1 | 220 | 37.673 | -121.7859 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0144466 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1996613 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CAYETANO-2109 | 14422109 | TRANSFORMER | 316208045865 | 20241211 | 1435 | 20241211 | 1451 | 2649968 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 32 | 37.7523 | -121.8124 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0144448 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1996601 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 9411 | 20241212 | 45 | 20241212 | 455 | 2650371 | 250 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 82 | 20500 | 37.6527 | -122.0725 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0144529 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1996674 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | JUMPER | WIRE DOWN C/O KEYS PL & CALAROGA AVE | 20241212 | 713 | 20241212 | 1028 | 2650517 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6295 | 192659 | 37.6256 | -122.0889 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0144554 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | Yes | 1996704 | 1 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 13066 | 20241212 | 1306 | 20241213 | 1141 | 2650988 | 1355 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 10840 | 37.6453 | -121.6404 | No | Overcast;32-90 F |  |  | 24-0144712 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1996938 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | BANCROFT-0402 | 13030402 | FUSE | 50693 | 20241212 | 2200 | 20241212 | 2225 | 2651324 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 4275 | 37.7342 | -122.143 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 24-0144740 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1996968 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | MT EDEN-1108 | 13761108 | FUSE | 9411 | 20241213 | 319 | 20241214 | 200 | 2651394 | 1361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 69756 | 37.6527 | -122.0725 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0144796 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1997057 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | OCB | 1111/2 | 20241213 | 353 | 20241214 | 1846 | 2651402 | 2333 | Distribution Circuit | 3rd Party | Vehicle | 2530 | 540226 | 37.7388 | -122.1941 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0144752 | OH | Sus | 35605664 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | No | 1996988 | 0 | Non-EPSS | N | 2024 | A/B/C TIME
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 8260 | 20241213 | 454 | 20241213 | 1407 | 2651423 | 553 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 29811 | 37.6707 | -122.1455 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 24-0144754 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1996992 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | VASCO-1102 | 13751102 | TRANSFORMER | 316712042580 | 20241213 | 1323 | 20241213 | 1754 | 2651958 | 271 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 271 | 37.6637 | -121.6398 | No | Overcast;32-90 F |  |  | 24-0144943 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 1997235 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1111 | 14091111 | FUSE | 8570 | 20241213 | 2309 | 20241214 | 732 | 2652455 | 503 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 192 | 96576 | 37.6628 | -122.0276 | No | Overcast-Rain;32-90 F |  |  | 24-0145169 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1997475 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | LAS POSITAS-2106 | 14402106 | RECLOSER | MR180 | 20241213 | 2311 | 20241214 | 545 | 2652490 | 390 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9959 | 1329083 | 37.6751 | -121.7617 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Burned Open | 24-0144987 | OH | Sus | 0 | BAY AREA | DEC | Multi-Fault | 0 | No | No | No | 1997292 | 0 | Non-EPSS | N | 2024 | ABC
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 8873 | 20241213 | 2315 | 20241214 | 800 | 2652545 | 525 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 26613 | 37.6381 | -121.8943 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0145208 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1997516 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | RADUM-1105 | 13151105 | FUSE | 71831 | 20241214 | 8 | 20241214 | 719 | 2652691 | 431 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 105 | 45255 | 37.6632 | -121.871 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0145157 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1997463 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | CASTRO VALLEY-1107 | 14091107 | FUSE | 607 | 20241214 | 914 | 20241214 | 1117 | 2656268 | 123 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 623 | 76497 | 37.6773 | -122.0674 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0145430 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1997752 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN LEANDRO-1151 | 13111151 | OCB | UO-1/2 | 20241214 | 1003 | 20241214 | 1256 | 2657577 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6834 | 1176218 | 37.7107 | -122.1488 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145560 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1997882 | 0 | Non-EPSS | N | 2024 | GRD TARGET
MISSION | MISSION | CASTRO VALLEY-1102 | 14091102 | FUSE | 88026 | 20241214 | 1007 | 20241214 | 1942 | 2657251 | 575 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 6325 | 37.6825 | -122.0531 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Burned/flashed | 24-0145936 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998265 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | WARD-0401 | 12980401 | TRANSFORMER | 315188845191 | 20241214 | 1013 | 20241214 | 1448 | 2656700 | 275 | Transformer only | Equipment Failure/Involved | Electrical Overload | 15 | 4125 | 37.7294 | -122.1647 | Yes | Strong Winds-Overcast-Heavy Rain;32-90 F | Transformer | Broken- wire on ground | 24-0145484 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | No | 1997807 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1110 | 14471110 | FUSE | 8644 | 20241214 | 1028 | 20241214 | 1110 | 2657525 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 437 | 18354 | 37.5446 | -122.0342 | Yes | Overcast;32-90 F |  |  | 24-0145521 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1997846 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315414743210 | 20241214 | 1130 | 20241214 | 1331 | 2658357 | 121 | Transformer only | Unknown Cause | Patrol - found nothing | 24 | 2904 | 37.6761 | -122.0855 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0145750 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 1998082 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1108 | 13111108 | TRANSFORMER | 315208444310 | 20241214 | 1216 | 20241214 | 1414 | 2658790 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 708 | 37.7053 | -122.1575 | Yes | Overcast-Drizzle;32-90 F | Fuse | Burned Open | 24-0145856 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998191 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 2101/2/NORM | 20241214 | 1233 | 20241214 | 2257 | 2658952 | 548 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7522 | 369029 | 37.7448 | -121.8576 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0145675 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1998001 | 0 | EPSS Ckt | N | 2024 | NA
MISSION | MISSION | MT EDEN-1109 | 13761109 | TRANSFORMER | 315446641792 | 20241214 | 1531 | 20241214 | 1849 | 2658377 | 198 | Transformer only | Vegetation | Tree - grew into line | 34 | 6732 | 37.6374 | -122.0736 | Yes | Overcast;32-90 F | Transformer | Normal | 24-0145877 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998211 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | FUSE | 51336 | 20241214 | 1833 | 20241215 | 1141 | 2660433 | 1028 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 33924 | 37.6651 | -122.131 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0146096 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1998440 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1106 | 13761106 | FUSE | 97172 | 20241215 | 601 | 20241215 | 1541 | 2660913 | 580 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 10318 | 37.6471 | -122.1185 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0146167 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998515 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315593840394 | 20241215 | 1526 | 20241215 | 1840 | 2661800 | 194 | Transformer only | Equipment Failure/Involved | Overhead | 43 | 8342 | 37.5995 | -122.022 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0146356 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1998727 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | JARVIS-1108 | 13501108 | TRANSFORMER | 315590240695 | 20241215 | 2044 | 20241216 | 37 | 2662145 | 233 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 4194 | 37.6078 | -122.0235 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0146455 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1998820 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315303343019 | 20241216 | 857 | 20241216 | 1138 | 2662527 | 161 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1610 | 37.6702 | -122.1238 | No | Overcast-Rain;32-90 F | Fuse | Broken | 24-0146583 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998962 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | LIVERMORE-1103 | 12141103 | TRANSFORMER | 316365343220 | 20241216 | 1315 | 20241216 | 1430 | 2662549 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 75 | 37.6801 | -121.757 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0146615 | OH | Sus | 46419194 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998997 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | MT EDEN-1109 | 13761109 | TRANSFORMER | 315483641761 | 20241216 | 2141 | 20241216 | 2305 | 2663707 | 84 | Transformer only | Unknown Cause | Patrol - not conducted | 24 | 2016 | 37.6366 | -122.0609 | No | Fog;32-90 F |  |  | 24-0146711 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 1999094 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SUNOL-1101 | 14241101 | RECLOSER | 298061 | 20241217 | 1716 | 20241218 | 1338 | 2664526 | 1222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 203 | 243152 | 37.5958 | -121.8897 | No | Clear;32-90 F | Capacitor | Broken | 24-0146855 | OH | Sus | 0 | BAY AREA | DEC | Three Phase Fault | 0 | No | No | No | 1999347 | 0 | EPSS Ckt | N | 2024 | ABC- SGF -TIME- INST
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | 315535037750 | 20241218 | 2105 | 20241218 | 2150 | 2665570 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 900 | 37.5266 | -122.0408 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0147055 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1999699 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1110 | 14091110 | TRIP-SAVER | 10315 | 20241219 | 1103 | 20241219 | 2132 | 2665912 | 629 | Distribution Circuit | 3rd Party | Vehicle | 73 | 12725 | 37.6519 | -121.9824 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0147112 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1999834 | 0 | EPSS Ckt | N | 2024 | BC
MISSION | MISSION | GRANT-1107 | 14381107 | TRANSFORMER | 315192543882 | 20241219 | 1232 | 20241219 | 1950 | 2666004 | 438 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3066 | 37.6934 | -122.1625 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0147137 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1999869 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | DUMBARTON-1106 | 14471106 | SWITCH | 973 | 20241220 | 906 | 20241220 | 1543 | 2666534 | 397 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 15227 | 37.5906 | -122.0772 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 24-0146661 | UG | Sus | 35605650 | BAY AREA | DEC | None | 0 | No | No | No | 2000082 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2103 | 12232103 | TRANSFORMER | T157710 | 20241221 | 57 | 20241221 | 1256 | 2667143 | 719 | Distribution Circuit | Equipment Failure/Involved | Underground | 64 | 9108 | 37.5197 | -122.0522 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0147293 | UG | Sus | 35606963 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000208 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1105 | 14381105 | FUSE | 12308 | 20241221 | 800 | 20241221 | 1344 | 2667230 | 344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 9976 | 37.6863 | -122.1528 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 24-0147311 | OH | Sus | 31720532 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000257 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1106 | 13111106 | TRANSFORMER | 315149643910 | 20241224 | 436 | 20241224 | 957 | 2668793 | 321 | Transformer only | Vegetation | Tree - palm frond fell into line | 28 | 8988 | 37.694 | -122.1776 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0147589 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000645 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN LEANDRO-1113 | 13111113 | OCB | 1113/2 | 20241224 | 605 | 20241224 | 1327 | 2668833 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2405 | 87268 | 37.7106 | -122.1486 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147561 | OH | Sus | 46438454 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | No | 2000614 | 0 | Non-EPSS | N | 2024 | A & GRD
MISSION | MISSION | FREMONT-1110 | 14351110 | FUSE | 48889 | 20241224 | 846 | 20241224 | 1729 | 2668983 | 523 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 19351 | 37.5352 | -121.968 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken | 24-0147631 | OH | Sus | 31720907 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 2000689 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2111 | 14232111 | OCB | 2111/2 | 20241225 | 1048 | 20241225 | 1405 | 2669623 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2285 | 300903 | 37.7448 | -121.9369 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0147721 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | No | 2000782 | 0 | Non-EPSS | N | 2024 | PHASE OC
MISSION | MISSION | NORTH DUBLIN-2103 | 14052103 | RECLOSER | 134120 | 20241226 | 710 | 20241226 | 1043 | 2669863 | 213 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 11411 | 37.7899 | -121.8435 | No | Overcast;32-90 F |  |  | 24-0147777 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000837 | 0 | EPSS Ckt | N | 2024 | A PH GRD INST
MISSION | MISSION | VINEYARD-2109 | 14502109 | RECLOSER | MR170 | 20241227 | 511 | 20241227 | 1024 | 2670501 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1480 | 205576 | 37.6722 | -121.8732 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147886 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | No | 2000982 | 0 | Non-EPSS | N | 2024 | ABC & GRD
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | TRANSFORMER | 26931 | 20241227 | 828 | 20241227 | 1354 | 2670591 | 326 | Transformer only | 3rd Party | Customer Equipment | 15 | 4890 | 37.4971 | -121.9356 | No | Overcast-Fog;32-90 F | Transformer | Normal | 24-0147909 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001028 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1103 | 14381103 | TRANSFORMER | 315292442268 | 20241227 | 1008 | 20241227 | 1355 | 2670706 | 227 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 227 | 37.6496 | -122.1273 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147956 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001087 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | CASTRO VALLEY-1105 | 14091105 | JUMPER | 132304 | 20241227 | 1902 | 20241227 | 2359 | 2671020 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 8019 | 37.7077 | -122.0908 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0147981 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 2001112 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | VINEYARD-2107 | 14502107 | FUSE | 13191 | 20241229 | 742 | 20241229 | 927 | 2671632 | 105 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 21 | 2205 | 37.6536 | -121.8667 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0148102 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001248 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1105 | 14381105 | RECLOSER | MR363 | 20241229 | 755 | 20241229 | 1005 | 2671635 | 130 | Distribution Circuit | 3rd Party | Other | 1779 | 77816 | 37.6811 | -122.1511 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0148089 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 2001233 | 0 | Non-EPSS | N | 2024 | NONE
MISSION | MISSION | CASTRO VALLEY-1108 | 14091108 | FUSE | 14209 | 20241229 | 852 | 20241229 | 1037 | 2671669 | 105 | Distribution Circuit | Animal | Squirrel | 78 | 8190 | 37.698 | -122.0613 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0148109 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 2001256 | 0 | EPSS Ckt | N | 2024
MISSION | MISSION | SAN RAMON-2117 | 14232117 | FUSE | 70049 | 20241229 | 2238 | 20241230 | 200 | 2672108 | 202 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 1616 | 37.714 | -121.8846 | No | Fog;32-90 F | Customer Equipment | Failed/Faulted | 24-0148169 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001320 | 1 | EPSS Ckt | N | 2024
MISSION | MISSION | GRANT-1106 | 14381106 | TRANSFORMER | 315261642760 | 20241230 | 944 | 20241230 | 1536 | 2672391 | 352 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 5280 | 37.6629 | -122.1381 | No | Clear;32-90 F | Transformer | Broken | 24-0148211 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001448 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1102 | 14381102 | TRANSFORMER | T6080 | 20241230 | 1048 | 20241230 | 1405 | 2672456 | 197 | Transformer only | 3rd Party | Customer Equipment | 1 | 197 | 37.6458 | -122.1355 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0148205 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 2001437 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | GRANT-1108 | 14381108 | TRANSFORMER | 315316543154 | 20241231 | 1150 | 20241231 | 1308 | 2673200 | 78 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 780 | 37.674 | -122.1193 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0148299 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 2001591 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | NEWARK 21KV-2105 | 12232105 | TRANSFORMER | 315844836557 | 20241231 | 1230 | 20250101 | 700 | 2673227 | 1110 | Transformer only | Equipment Failure/Involved | Fire- pole | 5 | 5550 | 37.4953 | -121.9333 | No | Clear;32-90 F | Transformer | Broken | 24-0148305 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001598 | 0 | Non-EPSS | N | 2024
MISSION | MISSION | SAN RAMON-2117 | 14232117 | FUSE | 70049 | 20241231 | 1503 | 20241231 | 1520 | 2673354 | 17 | Distribution Circuit | Company Initiated | Return Circuit Normal | 7 | 119 | 37.714 | -121.8846 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0148315 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001613 | 0 | EPSS Ckt | N | 2024
NORTH BAY | SILVERADO | CARQUINEZ-1103 | 43281103 | FUSE | 3413 | 20230101 | 2 | 20230101 | 1017 | 1907556 | 615 | Distribution Circuit | 3rd Party | Gun Shot | 37 | 22755 | 38.1204 | -122.2546 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004245 | OH | Sus | 31634140 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1794838 | 0 | Non-EPSS | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL 1109 | 42011109 | FUSE | 5363 | 20230101 | 601 | 20230101 | 933 | 1907843 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3677 | 37.9722 | -122.5206 | No | Clear;32-90F |  |  | 23-0004327 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1794923 | 1 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | NAPA 1105 | 42021105 | TRANSFORMER | 219179823295 | 20230101 | 958 | 20230101 | 1327 | 1906487 | 209 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2508 | 38.3058 | -122.2871 | No | Clear;32-90F | Secondary | Broken | 23-0004344 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1794938 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | PUEBLO 2103 | 43292103 | TRANSFORMER | 218684526500 | 20230101 | 1128 | 20230101 | 1238 | 1908349 | 70 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 140 | 38.3933 | -122.4598 | No | Clear;32-90F |  |  | 23-0004399 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1794995 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | MONTICELLO 1101 | 43051101 | RECLOSER | 718 | 20230101 | 1224 | 20230101 | 1345 | 1908471 | 81 | Distribution Circuit | Vegetation | Tree - branch fell on line | 211 | 17091 | 38.3768 | -122.1841 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0004388 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1794983 | 0 | EPSS Ckt | N | 2023 | B & C
NORTH BAY | NORTH BAY | SAN RAFAEL-1107 | 42011107 | TRANSFORMER | 314134453657 | 20230101 | 1409 | 20230101 | 1553 | 2049699 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 728 | 37.9562 | -122.5357 | No | Partly Cloudy;32-90 F | Bus | Deteriorated | 23-0047440 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1826833 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | NORTH TOWER-1108 | 42041108 | JUMPER | 6557 | 20230101 | 1608 | 20230101 | 2355 | 1908683 | 467 | Distribution Circuit | 3rd Party | Vehicle | 102 | 47634 | 38.0842 | -122.1982 | No | Clear;32-90F | Pole-Wood | Broken | 23-0004442 | OH | Sus | 35419622 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1795041 | 0 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | HIGHWAY-1106 | 42651106 | FUSE | 7377 | 20230102 | 218 | 20230102 | 315 | 1909455 | 57 | Distribution Circuit | 3rd Party | Vehicle | 26 | 1482 | 38.1403 | -122.2525 | No | Clear;32-90F | Pole-Wood | Normal | 23-0004642 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1795260 | 0 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | SILVERADO 2102 | 43432102 | FUSE | 663 | 20230102 | 824 | 20230102 | 1152 | 1909610 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 416 | 38.5027 | -122.4527 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0004672 | OH | Sus | 31634143 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1795283 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | BASALT 1106 | 42461106 | TRANSFORMER | 219119019710 | 20230102 | 900 | 20230102 | 1510 | 1909661 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 10806 | 38.2075 | -122.3076 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0004695 | OH | Sus | 31634220 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1795298 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | SILVERADO 2104 | 43432104 | FUSE | 2221 | 20230102 | 1114 | 20230102 | 1833 | 1909895 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 878 | 38.5183 | -122.4717 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004719 | OH | Sus | 31634221 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795325 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | IGNACIO 1104 | 42481104 | FUSE | 2563 | 20230102 | 1121 | 20230102 | 1729 | 1909911 | 368 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2944 | 38.1726 | -122.4563 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0004778 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1795380 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL 1105 | 42011105 | FUSE | 4487 | 20230102 | 1648 | 20230103 | 713 | 1910360 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 2760 | 96500 | 37.9704 | -122.5026 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004826 | OH | Sus | 31634146 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795429 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | WOODACRE 1101 | 43021101 | FUSE | 5639 | 20230102 | 1747 | 20230103 | 1015 | 1910471 | 821 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2328 | 38.0773 | -122.6754 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004861 | OH | Sus | 45615346 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795466 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 3423 | 20230103 | 112 | 20230112 | 1612 | 1910867 | 13860 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 130404 | 38.6801 | -122.2606 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004962 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1795566 | 1 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL 1107 | 42011107 | TRANSFORMER | T4562 | 20230103 | 1026 | 20230103 | 1638 | 1911299 | 372 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 824 | 37.9556 | -122.5693 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0005100 | UG | Sus | 35419670 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1795662 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | IGNACIO-1104 | 42481104 | TRANSFORMER | 314163460848 | 20230103 | 1219 | 20230103 | 1552 | 1911300 | 213 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 213 | 38.1534 | -122.535 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0005122 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1795673 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | NOVATO 1104 | 42211104 | FUSE | 6389 | 20230103 | 1358 | 20230103 | 1843 | 1911636 | 285 | Distribution Circuit | Animal | Squirrel | 212 | 19420 | 38.1145 | -122.5641 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0005225 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1795728 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL-1109 | 42011109 | FUSE | 5363 | 20230104 | 215 | 20230104 | 757 | 1912203 | 342 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 5931 | 37.9722 | -122.5206 | Yes | Clear;32-90F |  |  | 23-0005573 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796032 | 1 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | HIGHWAY 1102 | 42651102 | FUSE | 3079 | 20230104 | 515 | 20230104 | 817 | 1912240 | 182 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 12 | 2184 | 38.1971 | -122.2889 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0005569 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796027 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | SILVERADO 2105 | 43432105 | FUSE | 170035 | 20230104 | 526 | 20230104 | 1633 | 1913370 | 356 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 17789 | 38.4947 | -122.494 | Yes | Clear;32-90F |  |  | 23-0005778 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796178 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | BASALT-1106 | 42461106 | FUSE | 388255 | 20230104 | 638 | 20230104 | 912 | 1912383 | 154 | Distribution Circuit | Animal | Bird found | 5 | 770 | 38.2551 | -122.3485 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0005647 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796077 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | NAPA-1110 | 42021110 | FUSE | 170759 | 20230104 | 918 | 20230104 | 1003 | 1912911 | 45 | Distribution Circuit | Animal | Squirrel | 132 | 5940 | 38.3044 | -122.3262 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0005697 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796113 | 1 | Non-EPSS | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL-1109 | 42011109 | FUSE | 5363 | 20230104 | 1017 | 20230104 | 1138 | 1913176 | 81 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 2106 | 37.9722 | -122.5206 | Yes | Clear;32-90F | Conductor- Underground | Broken | 23-0005821 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796216 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | OLEMA 1101 | 42291101 | FUSE | 3211 | 20230104 | 1107 | 20230108 | 1514 | 1912490 | 6007 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 210245 | 38.0182 | -122.9878 | Yes | Clear;32-90F | Conductor- Overhead | Deteriorated | 23-0005787 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1796190 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL-1109 | 42011109 | FUSE | 5363 | 20230104 | 1241 | 20230105 | 1654 | 1914039 | 1582 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 44018 | 37.9722 | -122.5206 | Yes | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0005972 | UG | Sus | 35419669 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796320 | 1 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | OLEMA-1101 | 42291101 | SWITCH | 6053 | 20230104 | 1315 | 20230106 | 2125 | 1914031 | 3370 | Distribution Circuit | Vegetation | Tree - fell into line | 373 | 281710 | 38.0983 | -122.8529 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0005969 | OH | Sus | 0 | NORTH COAST | JAN | Three Phase Fault | 0 | No | No | No | 1796318 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | OLEMA-1101 | 42291101 | FUSE | 311 | 20230104 | 1324 | 20230109 | 2353 | 1914346 | 7599 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 181 | 669098 | 38.0438 | -122.7465 | Yes | Clear;32-90F |  |  | 23-0006074 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796403 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | WOODACRE-1101 | 43021101 | FUSE | 5821 | 20230104 | 1421 | 20230106 | 1144 | 1914420 | 2723 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 76244 | 38.0179 | -122.6911 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0006090 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796416 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | OLEMA-1101 | 42291101 | FUSE | 5147 | 20230104 | 1443 | 20230104 | 1740 | 1914587 | 177 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 4956 | 38.0682 | -122.8253 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0006197 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796510 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | SILVERADO-2102 | 43432102 | RECLOSER | 636 | 20230104 | 1542 | 20230104 | 1702 | 1914904 | 80 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 131 | 10480 | 38.5089 | -122.4472 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006149 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796468 | 0 | EPSS Ckt | N | 2023 | A & C
NORTH BAY | NORTH BAY | WOODACRE-1101 | 43021101 | FUSE | 2619 | 20230104 | 1604 | 20230105 | 1900 | 1915087 | 1616 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 185840 | 38.0151 | -122.6931 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006275 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796580 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | WOODACRE-1101 | 43021101 | FUSE | 2623 | 20230104 | 1616 | 20230105 | 2228 | 1918458 | 1812 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 30804 | 38.0138 | -122.6989 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007668 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797864 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20230104 | 1635 | 20230108 | 1514 | 1915600 | 5679 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 607653 | 38.1094 | -122.8698 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006263 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796567 | 0 | EPSS Ckt | N | 2023 | C PHASE & GRD
NORTH BAY | NORTH BAY | WOODACRE-1101 | 43021101 | TRANSFORMER | 186957 | 20230104 | 1653 | 20230106 | 1626 | 1917671 | 2853 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5706 | 38.0344 | -122.6761 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0006482 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1796781 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | BOLINAS 1101 | 42261101 | RECLOSER | 1236 | 20230104 | 1655 | 20230107 | 1700 | 1915548 | 3888 | Distribution Circuit | Vegetation | Tree - fell into line | 323 | 531339 | 37.9315 | -122.6977 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006254 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796558 | 0 | EPSS Ckt | N | 2023 | SGF
NORTH BAY | NORTH BAY | WOODACRE-1101 | 43021101 | FUSE | 754427 | 20230104 | 1657 | 20230106 | 1145 | 1915551 | 2568 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 25680 | 38.0125 | -122.6672 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0007405 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797649 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | BOLINAS-1101 | 42261101 | RECLOSER | 806 | 20230104 | 1658 | 20230107 | 1609 | 1915645 | 4271 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25626 | 37.9558 | -122.6188 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006271 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796576 | 0 | EPSS Ckt | N | 2023 | GRD & SGF
NORTH BAY | NORTH BAY | OLEMA-1101 | 42291101 | RECLOSER | 1252 | 20230104 | 1658 | 20230108 | 1540 | 1915624 | 5682 | Distribution Circuit | Vegetation | Tree - branch fell on line | 126 | 200379 | 38.078 | -122.8329 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006267 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796572 | 0 | EPSS Ckt | N | 2023 | A PHASE & GRD
NORTH BAY | NORTH BAY | ALTO 1125 | 42031125 | RECLOSER | 1226 | 20230104 | 1701 | 20230106 | 1245 | 1915615 | 2624 | Distribution Circuit | Vegetation | Tree - fell into line | 829 | 294168 | 37.8966 | -122.5394 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006265 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796570 | 0 | EPSS Ckt | N | 2023 | ABC
NORTH BAY | NORTH BAY | BOLINAS-1101 | 42261101 | FUSE | 389437 | 20230104 | 1705 | 20230105 | 1405 | 1915661 | 1260 | Distribution Circuit | Vegetation | Tree - bark fell into line | 305 | 384300 | 37.9041 | -122.6975 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007517 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797735 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | BOLINAS-1101 | 42261101 | RECLOSER | 530 | 20230104 | 1706 | 20230109 | 2030 | 1915711 | 7404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 37020 | 37.9427 | -122.7025 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006284 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796589 | 0 | EPSS Ckt | N | 2023 | A/C PHASE
NORTH BAY | NORTH BAY | ALTO-1125 | 42031125 | TRANSFORMER | 314014451937 | 20230104 | 1707 | 20230105 | 1831 | 1915592 | 1524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 12192 | 37.9085 | -122.5759 | Yes | Clear;32-90 F | Secondary | Bent or Twisted | 23-0007725 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797906 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | ALTO-1125 | 42031125 | RECLOSER | 902 | 20230104 | 1709 | 20230106 | 1740 | 1915710 | 2911 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 522228 | 37.8893 | -122.5549 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006285 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796590 | 0 | EPSS Ckt | N | 2023 | AB GRD
NORTH BAY | NORTH BAY | ALTO-1120 | 42031120 | TRANSFORMER | 314132150940 | 20230104 | 1712 | 20230106 | 843 | 1915726 | 2371 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 21339 | 37.8816 | -122.5346 | Yes | Clear;32-90F |  |  | 23-0008119 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1798218 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL 1108 | 42011108 | OTHER | WIRE DOWN 3 SPANS LD SIDE 3177 | 20230104 | 1712 | 20230105 | 1224 | 1915764 | 1152 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 117923 | 37.9823 | -122.5791 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006392 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796689 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | WOODACRE-1101 | 43021101 | FUSE | 5853 | 20230104 | 1712 | 20230106 | 1712 | 1915852 | 2880 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 72000 | 38.015 | -122.7023 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007746 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1797923 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | ALTO 1124 | 42031124 | RECLOSER | 432 | 20230104 | 1716 | 20230105 | 1421 | 1915890 | 1193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 687 | 791922 | 37.9087 | -122.5475 | Yes | Clear;32-90F | Jumper | Broken | 23-0006332 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1796630 | 0 | EPSS Ckt | N | 2023 | NA
NORTH BAY | NORTH BAY | OLEMA-1101 | 42291101 | RECLOSER | 50396 | 20230104 | 1716 | 20230107 | 1404 | 1915740 | 3999 | Distribution Circuit | Vegetation | Tree - fell into line | 580 | 1437765 | 38.0772 | -122.8316 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0006299 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796602 | 0 | EPSS Ckt | N | 2023 | A/C PHASE
NORTH BAY | NORTH BAY | SAUSALITO 1102 | 42491102 | TRIP-SAVER | 2033 | 20230104 | 1717 | 20230105 | 1215 | 1915827 | 1138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 192322 | 37.8525 | -122.483 | Yes | Clear;32-90 F |  |  | 23-0007385 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797634 | 0 | EPSS Ckt | N | 2023 | N/A
NORTH BAY | NORTH BAY | SAN RAFAEL-1102 | 42011102 | TRANSFORMER | 314223053975 | 20230104 | 1727 | 20230104 | 2111 | 1917332 | 224 | Transformer only | Equipment Failure/Involved | Overhead | 73 | 16352 | 37.9655 | -122.5051 | Yes | Clear;32-90F | Secondary | Burned Open | 23-0006446 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1796744 | 0 | Non-EPSS | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL-1102 | 42011102 | TRANSFORMER | 314226353953 | 20230104 | 1727 | 20230107 | 1435 | 1917334 | 4148 | Transformer only | Unknown Cause | Patrol - found nothing | 90 | 373320 | 37.9648 | -122.504 | Yes | Clear;32-90 F |  |  | 23-0007638 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797842 | 0 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | SILVERADO-2105 | 43432105 | RECLOSER | 658898 | 20230104 | 1728 | 20230108 | 1835 | 1916079 | 5687 | Distribution Circuit | Vegetation | Tree - branch fell on line | 238 | 549792 | 38.5071 | -122.4907 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0006320 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796620 | 0 | EPSS Ckt | N | 2023 | B/C PHASE
NORTH BAY | SILVERADO | SILVERADO-2105 | 43432105 | RECLOSER | 394844 | 20230104 | 1728 | 20230104 | 1816 | 1916083 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 5232 | 38.5061 | -122.4788 | Yes | Clear;32-90F |  |  | 23-0006324 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796624 | 0 | EPSS Ckt | N | 2023 | AB TIME
NORTH BAY | NORTH BAY | WOODACRE 1102 | 43021102 | RECLOSER | 1280 | 20230104 | 1739 | 20230104 | 1753 | 1916226 | 14 | Distribution Circuit | 3rd Party | Other | 791 | 11074 | 37.9963 | -122.5956 | Yes | Clear;32-90F | Other | Normal | 23-0006335 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1796633 | 0 | EPSS Ckt | N | 2023 | NONE
NORTH BAY | SILVERADO | VALLEJO B-0414 | 42450414 | FUSE | 1379 | 20230104 | 1744 | 20230104 | 2321 | 1916278 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 191 | 64367 | 38.1015 | -122.2437 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0006809 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797111 | 0 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | VALLEJO B-0414 | 42450414 | FUSE | 1697 | 20230104 | 1746 | 20230105 | 925 | 1916305 | 939 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 30048 | 38.1053 | -122.2435 | Yes | Clear;32-90 F |  |  | 23-0007129 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797415 | 0 | Non-EPSS | N | 2023
NORTH BAY | NORTH BAY | ALTO-1125 | 42031125 | FUSE | 5191 | 20230104 | 1747 | 20230106 | 1450 | 1916310 | 2703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 121 | 191981 | 37.8826 | -122.546 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0006832 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797136 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | ALTO-1124 | 42031124 | RECLOSER | 994213 | 20230104 | 1749 | 20230107 | 955 | 1915637 | 3846 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 250254 | 37.9036 | -122.5361 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0006348 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1796646 | 0 | EPSS Ckt | N | 2023 | NA
NORTH BAY | SILVERADO | HIGHWAY-1102 | 42651102 | FUSE | 5067 | 20230104 | 1753 | 20230104 | 2135 | 1916386 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 3552 | 38.1689 | -122.2527 | Yes | Clear;32-90F | Conductor- Overhead | Deteriorated | 23-0006545 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796843 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | VALLEJO B-0411 | 42450411 | FUSE | 981 | 20230104 | 1753 | 20230105 | 1732 | 1916390 | 1419 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 43472 | 38.1065 | -122.2536 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0006773 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797075 | 1 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | PARKWAY-1103 | 42051103 | TRANSFORMER | MTR#1008593914 | 20230104 | 1755 | 20230107 | 1046 | 1916424 | 3891 | Transformer only | Vegetation | Tree - fell into line | 15 | 58365 | 38.1241 | -122.2334 | Yes | Clear;32-90 F | Service conductor | Broken- wire on object | 23-0007324 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797582 | 0 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | BAHIA-1104 | 43251104 | SWITCH | 7118 | 20230104 | 1756 | 20230104 | 1905 | 1916551 | 69 | Distribution Circuit | Vegetation | Tree - fell into line | 1947 | 54543 | 38.1128 | -122.1975 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006371 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796669 | 0 | Non-EPSS | N | 2023
NORTH BAY | NORTH BAY | ALTO 1120 | 42031120 | FUSE | 3005 | 20230104 | 1758 | 20230106 | 1803 | 1916583 | 2885 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 634700 | 37.8972 | -122.507 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006752 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1797054 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | PUEBLO 1104 | 43291104 | FUSE | 363 | 20230104 | 1758 | 20230105 | 1315 | 1916543 | 1157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 63635 | 38.3174 | -122.256 | Yes | Clear;32-90 F |  |  | 23-0007431 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1797672 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | PUEBLO 1105 | 43291105 | RECLOSER | 348368 | 20230104 | 1810 | 20230107 | 940 | 1916726 | 3620 | Distribution Circuit | Equipment Failure/Involved | Overhead | 203 | 133482 | 38.323 | -122.2411 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006388 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796685 | 0 | EPSS Ckt | N | 2023 | B & C PHASE GRD
NORTH BAY | NORTH BAY | SAN RAFAEL-1107 | 42011107 | OCB | 1107/2 | 20230104 | 1812 | 20230105 | 1032 | 1918124 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 4654 | 4356360 | 37.9703 | -122.5268 | Yes | Clear;32-90F | Conductor- Overhead | Arcing | 23-0006551 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796848 | 0 | EPSS Ckt | N | 2023 | AB GRD TIME & SET A PHASE OC
NORTH BAY | NORTH BAY | IGNACIO-1102 | 42481102 | OCB | 1102/2 | 20230104 | 1815 | 20230104 | 2002 | 1916781 | 107 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1864 | 199448 | 38.0757 | -122.5396 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006395 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796692 | 0 | Non-EPSS | N | 2023 | A/B/C PHASE INST/TIME
NORTH BAY | SILVERADO | NORTH TOWER 2101 | 42042101 | RECLOSER | 158556/2 | 20230104 | 1815 | 20230104 | 2049 | 1915507 | 154 | Distribution Circuit | Environmental/External | Flood/Erosion | 3289 | 506506 | 38.0676 | -122.1956 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on object | 23-0006450 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796748 | 0 | EPSS Ckt | N | 2023 | ABC
NORTH BAY | SILVERADO | HIGHWAY-1102 | 42651102 | FUSE | 3079 | 20230104 | 1821 | 20230105 | 2155 | 1921274 | 1654 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 12 | 19848 | 38.1971 | -122.2889 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007930 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798068 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | NAPA 1112 | 42021112 | FUSE | 347 | 20230104 | 1824 | 20230105 | 1341 | 1916855 | 1157 | Distribution Circuit | Vegetation | Tree - branch fell on line | 125 | 144625 | 38.2942 | -122.2417 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007472 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797698 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | IGNACIO-1104 | 42481104 | RECLOSER | 469764 | 20230104 | 1825 | 20230105 | 1000 | 1915450 | 935 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 294 | 274890 | 38.1187 | -122.5022 | Yes | Clear;32-90F |  |  | 23-0006407 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796705 | 0 | EPSS Ckt | N | 2023 | ABC PHASE OC
NORTH BAY | SILVERADO | CALISTOGA-1101 | 42711101 | FUSE | 729 | 20230104 | 1826 | 20230106 | 2132 | 1916927 | 3066 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 27594 | 38.5951 | -122.6025 | Yes | Clear;32-90 F | Insulator | Broken | 23-0007848 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798010 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | PUEBLO-1105 | 43291105 | FUSE | 4853 | 20230104 | 1827 | 20230106 | 1413 | 1916849 | 2626 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 84032 | 38.3241 | -122.2736 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006454 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796752 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | VALLEJO B-0411 | 42450411 | FUSE | 1053 | 20230104 | 1833 | 20230105 | 1257 | 1916916 | 1104 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 188 | 207552 | 38.1026 | -122.2527 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007376 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797626 | 0 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | PUEBLO-1105 | 43291105 | FUSE | 6379 | 20230104 | 1847 | 20230106 | 1040 | 1917219 | 2393 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 100 | 239300 | 38.4256 | -122.3002 | Yes | Clear;32-90F |  |  | 23-0008167 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798253 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | PUEBLO-2103 | 43292103 | TRANSFORMER | 219024823190 | 20230104 | 1849 | 20230105 | 1652 | 1917394 | 1323 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 7938 | 38.3031 | -122.3407 | Yes | Clear;32-90 F |  |  | 23-0007741 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1797919 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | NAPA-1105 | 42021105 | FUSE | 2412 | 20230104 | 1855 | 20230105 | 955 | 1920859 | 900 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 13500 | 38.3044 | -122.2846 | Yes | Clear;32-90 F |  |  | 23-0007072 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1797367 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | CALISTOGA 1101 | 42711101 | RECLOSER | 886282 | 20230104 | 1919 | 20230105 | 1401 | 1916842 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 118932 | 38.5599 | -122.6285 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006475 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796772 | 0 | EPSS Ckt | N | 2023 | B&C PHASE OC INST
NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 7511 | 20230104 | 1921 | 20230106 | 1715 | 1917589 | 2754 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 33048 | 38.468 | -122.2295 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007087 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797381 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | NOVATO-1104 | 42211104 | RECLOSER | 1282 | 20230104 | 1932 | 20230107 | 1320 | 1917726 | 2500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 725 | 1320703 | 38.1164 | -122.5632 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006493 | OH | Sus | 0 | NORTH COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1796792 | 0 | EPSS Ckt | N | 2023 | ABC GRD
NORTH BAY | NORTH BAY | BOLINAS-1101 | 42261101 | RECLOSER | 37034 | 20230104 | 1958 | 20230108 | 1635 | 1917925 | 5557 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 111140 | 37.9443 | -122.7033 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006529 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796827 | 0 | EPSS Ckt | N | 2023 | A/B/C PHASE
NORTH BAY | NORTH BAY | WOODACRE-1101 | 43021101 | RECLOSER | 96844 | 20230104 | 2040 | 20230106 | 2202 | 1916291 | 2962 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 712774 | 38.0193 | -122.663 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006586 | OH | Sus | 0 | NORTH COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1796885 | 0 | EPSS Ckt | N | 2023 | ABC
NORTH BAY | SILVERADO | VALLEJO B-0411 | 42450411 | TRANSFORMER | 219262515918 | 20230104 | 2043 | 20230106 | 1407 | 1921823 | 2484 | Transformer only | Vegetation | Tree - fell into line | 34 | 84456 | 38.1036 | -122.2574 | Yes | Clear;32-90 F | Transformer | Broken | 23-0007683 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797873 | 0 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | SILVERADO-2102 | 43432102 | RECLOSER | 98998 | 20230104 | 2106 | 20230105 | 1002 | 1921029 | 776 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 54320 | 38.4714 | -122.3993 | Yes | Clear;32-90 F |  |  | 23-0007207 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797482 | 0 | EPSS Ckt | N | 2023 | A&C PHASE
NORTH BAY | SILVERADO | SILVERADO-2102 | 43432102 | RECLOSER | 942170 | 20230104 | 2108 | 20230105 | 1002 | 1918775 | 774 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 207 | 160218 | 38.4631 | -122.3704 | Yes | Clear;32-90F |  |  | 23-0006712 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797014 | 0 | EPSS Ckt | N | 2023 | C PHASE GRD
NORTH BAY | NORTH BAY | SAN RAFAEL 1101 | 42011101 | FUSE | 7255 | 20230104 | 2112 | 20230106 | 1903 | 1918299 | 2751 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 60522 | 37.9717 | -122.555 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007878 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798041 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | PUEBLO-2104 | 43292104 | RECLOSER | 656 | 20230104 | 2134 | 20230105 | 1804 | 1919034 | 1230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 334 | 124300 | 38.3886 | -122.318 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0006700 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797001 | 0 | Non-EPSS | N | 2023 | ABC PHASE OC
NORTH BAY | NORTH BAY | SAN RAFAEL-1104 | 42011104 | TRANSFORMER | 314033354798 | 20230104 | 2137 | 20230106 | 1753 | 1918946 | 2656 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 13280 | 37.9869 | -122.5715 | Yes | Clear;32-90 F |  |  | 23-0007938 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1798076 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL-1108 | 42011108 | RECLOSER | 516 | 20230104 | 2140 | 20230106 | 1329 | 1916801 | 2389 | Distribution Circuit | Vegetation | Tree - fell into line | 1553 | 3342556 | 37.9861 | -122.5875 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006698 | OH | Sus | 0 | NORTH COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1796999 | 0 | EPSS Ckt | N | 2023 | ABC
NORTH BAY | NORTH BAY | WOODACRE-1102 | 43021102 | OCB | 1102/2 | 20230104 | 2145 | 20230106 | 1030 | 1915598 | 2205 | Distribution Circuit | Vegetation | Tree - fell into line | 3037 | 2291552 | 38.0125 | -122.654 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006710 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797012 | 0 | EPSS Ckt | N | 2023 | AB- TIME- SET A
NORTH BAY | NORTH BAY | IGNACIO-1102 | 42481102 | OCB | 1102/2 | 20230104 | 2146 | 20230105 | 859 | 1919072 | 673 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1864 | 1254472 | 38.0757 | -122.5396 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0006711 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797013 | 0 | Non-EPSS | N | 2023 | A/C PHASE TIME
NORTH BAY | NORTH BAY | SAN RAFAEL-1101 | 42011101 | FUSE | 723 | 20230104 | 2146 | 20230105 | 2006 | 1919087 | 1340 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 17420 | 37.9626 | -122.5572 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007912 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798058 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | CARQUINEZ-1103 | 43281103 | TRANSFORMER | 219229616367 | 20230104 | 2153 | 20230106 | 1634 | 1921670 | 2548 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 161002 | 38.1159 | -122.2689 | Yes | Clear;32-90 F | Secondary | Broken | 23-0007241 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797512 | 0 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | SILVERADO-2105 | 43432105 | RECLOSER | 337226 | 20230104 | 2155 | 20230105 | 2225 | 1922338 | 914 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 63210 | 38.5057 | -122.4845 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007474 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797700 | 0 | EPSS Ckt | N | 2023 | TARGETS
NORTH BAY | SILVERADO | VALLEJO STA C-0401 | 42550401 | FUSE | 1059 | 20230104 | 2156 | 20230104 | 2206 | 1917808 | 10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 121 | 1210 | 38.1005 | -122.2486 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006727 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1797029 | 0 | Non-EPSS | N | 2023
NORTH BAY | SILVERADO | PUEBLO-1105 | 43291105 | RECLOSER | 642 | 20230104 | 2158 | 20230107 | 1257 | 1916911 | 3779 | Distribution Circuit | Vegetation | Tree - branch fell on line | 792 | 610139 | 38.3252 | -122.2762 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0006739 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797040 | 0 | EPSS Ckt | N | 2023 | SGF
NORTH BAY | NORTH BAY | SAN RAFAEL-1105 | 42011105 | SWITCH | 1271 | 20230104 | 2219 | 20230106 | 1915 | 1918264 | 2696 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 61919 | 37.9879 | -122.486 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0006761 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1797063 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | PUEBLO-1105 | 43291105 | FUSE | 879039 | 20230104 | 2222 | 20230106 | 1730 | 1919375 | 2588 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 7764 | 38.3845 | -122.2986 | Yes | Clear;32-90F | Transformer (UG) | Burned/flashed | 23-0008533 | UG | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1798462 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL-1109 | 42011109 | FUSE | 5723 | 20230104 | 2232 | 20230105 | 1511 | 1919445 | 999 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 24975 | 37.9702 | -122.5083 | Yes | Clear;32-90 F |  |  | 23-0007592 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797802 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL-1108 | 42011108 | FUSE | 5343 | 20230105 | 31 | 20230105 | 1733 | 1920051 | 1022 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 34748 | 37.9759 | -122.5772 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007786 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797954 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | SAN RAFAEL 1104 | 42011104 | FUSE | 2889 | 20230105 | 215 | 20230107 | 1245 | 1920346 | 3510 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 231660 | 37.9719 | -122.5365 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006977 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797280 | 0 | EPSS Ckt | N | 2023
NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 632 | 20230105 | 646 | 20230106 | 1906 | 1920767 | 2180 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 77204 | 38.574 | -122.4444 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007018 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797321 | 0 | EPSS Ckt | N | 2023 | NONE
NORTH BAY | NORTH BAY | WOODACRE-1101 | 43021101 | TRANSFORMER | 313725755825 | 20230105 | 712 | 20230107 | 1910 | 1920843 | 3598 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 7196 | 38.013 | -122.679 | Yes | Clear;32-90F | Pole-Wood | Normal | 23-0008481 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798413 | 0 | EPSS Ckt | N | 2023
NORTH BAY | NORTH BAY | IGNACIO-1101 | 42481101 | FUSE | 7303 | 20230105 | 714 | 20230106 | 939 | 1920849 | 1585 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 57060 | 38.0657 | -122.5575 | Yes | Clear;32-90F |  |  | 23-0008109 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798209 | 0 | EPSS Ckt | N | 2023