YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 6024 | 20230306 | 158 | 20230306 | 434 | 2024204 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1560 | 37.1496 | -120.2929 | No | Clear;32-90F |  |  | 23-0040538 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822273 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320439616355 | 20230306 | 902 | 20230306 | 948 | 2024402 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 46 | 36.9494 | -120.3503 | No | Clear;32-90 F | Fuse | Broken | 23-0040621 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822324 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 673480 | 20230306 | 910 | 20230306 | 1140 | 2024444 | 150 | Distribution Circuit | Environmental/External | Ice or snow | 231 | 10588 | 37.288 | -119.5203 | No | Partly Cloudy-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0034562 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822315 | 0 | EPSS Ckt | N | 2023 | A & B PH
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320539155534 | 20230306 | 1007 | 20230306 | 1253 | 2024502 | 166 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 166 | 38.025 | -120.3146 | No | Clear;32-90F |  |  | 23-0040744 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1822380 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | TRANSFORMER | 319907317485 | 20230306 | 1113 | 20230306 | 1247 | 2024592 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 94 | 36.9809 | -120.5332 | No | Clear;32-90 F | Fuse | Broken | 23-0040769 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822389 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320176550063 | 20230306 | 1217 | 20230306 | 1234 | 2024671 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 34 | 37.8747 | -120.4387 | No | Snow-Clear;32-90F | Service conductor | Deteriorated | 23-0040709 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822364 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320717055835 | 20230306 | 1221 | 20230306 | 1357 | 2024677 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 192 | 38.0311 | -120.2526 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0040828 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822415 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320168450081 | 20230306 | 1223 | 20230306 | 1636 | 2024692 | 253 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 253 | 37.8737 | -120.4417 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0040721 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822367 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318710944937 | 20230306 | 1228 | 20230306 | 1305 | 2024660 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 111 | 37.7334 | -120.9466 | No | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0040704 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822361 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321121544300 | 20230306 | 1240 | 20230308 | 955 | 2023788 | 2715 | Transformer only | Vegetation | Tree - fell into line | 2 | 5430 | 37.7182 | -120.1139 | No | Clear;32-90 F | Service conductor | Broken | 23-0040749 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822382 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20230306 | 1241 | 20230306 | 1635 | 2024707 | 234 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 17 | 3978 | 37.1863 | -120.6348 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0040884 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822441 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10494 | 20230306 | 1305 | 20230306 | 1315 | 2024730 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 20 | 37.5858 | -119.8517 | No | Clear;32-90F |  |  | 23-0040751 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822383 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 4569 | 20230306 | 1422 | 20230306 | 1436 | 2024804 | 14 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 196 | 37.4791 | -119.8688 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0040806 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822399 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 39105 | 20230306 | 1522 | 20230306 | 1700 | s1822420 | 98 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 2646 | 37.3188 | -119.5555 | No | Clear;32-90 F | Service conductor | Broken | 23-0034562 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822420 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | TRANSFORMER | 318798429744 | 20230306 | 1600 | 20230306 | 1618 | 2024799 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 18 | 37.3138 | -120.9151 | No | Clear;32-90 F | Fuse | Broken | 23-0040872 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822433 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10353 | 20230306 | 1758 | 20230308 | 950 | 2025026 | 2392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 43056 | 37.576 | -119.8535 | No | Clear;32-90 F | Jumper | Burned Open | 23-0041509 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1822817 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320770353257 | 20230306 | 2302 | 20230306 | 2340 | 2025179 | 38 | Transformer only | 3rd Party | Fire- house or bldg. | 13 | 494 | 37.9623 | -120.2339 | No | Partly Cloudy-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0041000 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822535 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321529518563 | 20230307 | 631 | 20230307 | 1333 | 2025241 | 422 | Transformer only | Equipment Failure/Involved | Underground | 1 | 422 | 37.0085 | -119.9769 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0041087 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822583 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 5562 | 20230307 | 653 | 20230307 | 902 | 2025249 | 129 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 67 | 8643 | 37.2492 | -119.5134 | No | Clear;32-90F |  |  | 23-0041077 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822573 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11624 | 20230307 | 806 | 20230307 | 1155 | 2025288 | 229 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1603 | 37.2075 | -120.3295 | No | Clear;32-90F |  |  | 23-0041176 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822620 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | TRANSFORMER | 415257653273 | 20230307 | 815 | 20230307 | 1059 | 2025300 | 164 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 328 | 36.7856 | -120.6208 | No | Clear;32-90F | Connector or Splice (OH) | Burned Open | 23-0041134 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822609 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322782825543 | 20230307 | 1048 | 20230307 | 1209 | 2025482 | 81 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 81 | 37.1985 | -119.5451 | No | Clear;32-90F |  |  | 23-0041177 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1822621 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 2199 | 20230307 | 1142 | 20230307 | 1810 | 2025553 | 388 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2328 | 37.151 | -120.6376 | No | Clear;32-90F |  |  | 23-0041357 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822687 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321086745454 | 20230307 | 1148 | 20230307 | 1737 | 2025556 | 349 | Transformer only | Vegetation | Tree - fell into line | 1 | 349 | 37.7501 | -120.1255 | No | Clear;32-90F | Pole-Wood | Broken | 23-0041345 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822678 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 6103 | 20230307 | 1148 | 20230307 | 2139 | 2025557 | 565 | Distribution Circuit | Equipment Failure/Involved | Underground | 283 | 113704 | 36.9603 | -120.0836 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0041185 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822625 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 20775 | 20230307 | 1337 | 20230307 | 1410 | 2025619 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 66 | 38.0166 | -120.3559 | No | Clear;32-90F | Cutout- fuse holder | Failed/Faulted | 23-0041196 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822627 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321522234037 | 20230307 | 1356 | 20230307 | 1650 | 2025696 | 174 | Transformer only | Vegetation | Tree - fell into line | 1 | 174 | 37.4325 | -119.9764 | No | Clear;32-90F | Other | Broken | 23-0041251 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822646 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320762055953 | 20230307 | 1418 | 20230307 | 1715 | 2025723 | 177 | Transformer only | Environmental/External | Ice or snow | 4 | 708 | 38.0363 | -120.2367 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0041346 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822679 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321926336130 | 20230307 | 1546 | 20230307 | 2139 | 2025812 | 353 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 353 | 37.4904 | -119.8371 | No | Clear;32-90F |  |  | 23-0041432 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1822761 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 100000005930 | 20230307 | 1855 | 20230308 | 653 | 2025797 | 718 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 718 | 36.9487 | -120.3183 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0041384 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822711 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 27390 | 20230307 | 2045 | 20230308 | 155 | s1822782 | 310 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 310 | 36.7564 | -120.3891 | No | Clear;32-90 F |  |  | 23-0041452 |  | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822782 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BONITA-1103 | 255391103 | FUSE | 6836 | 20230307 | 2117 | 20230307 | 2240 | 2026055 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1384 | 37.0101 | -120.2294 | No | Clear;32-90F |  |  | 23-0041438 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822768 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320490153508 | 20230307 | 2235 | 20230307 | 2330 | 2026086 | 55 | Transformer only | 3rd Party | Fire- house or bldg. | 3 | 165 | 37.9698 | -120.3311 | No | Clear;32-90F | Service conductor | Burned/flashed | 23-0041445 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822775 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | FUSE | 6534 | 20230307 | 2350 | 20230308 | 650 | 2026105 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 420 | 36.952 | -120.0555 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0041439 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822769 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 20155 | 20230308 | 536 | 20230308 | 634 | 2026216 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1044 | 37.8055 | -120.9236 | No | Clear;32-90 F |  |  | 23-0041483 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822807 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 23483 | 20230308 | 956 | 20230308 | 1038 | 2026503 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 126 | 37.0435 | -120.7018 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0041594 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822871 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 25876 | 20230308 | 1105 | 20230308 | 1305 | 2026596 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 840 | 37.7776 | -120.1738 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0041637 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822897 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20230308 | 1125 | 20230309 | 1100 | 2026617 | 1415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 24055 | 37.1863 | -120.6348 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041716 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1822923 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322788727315 | 20230308 | 1126 | 20230308 | 1455 | 2026618 | 209 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 209 | 37.2483 | -119.5432 | No | Clear;32-90 F |  |  | 23-0041773 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1822951 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4672 | 20230308 | 1222 | 20230308 | 1405 | 2026672 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 309 | 37.186 | -120.6097 | No | Clear;32-90 F |  |  | 23-0041746 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822944 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 25892 | 20230308 | 1258 | 20230308 | 1613 | 2026840 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 195 | 37.1198 | -120.1788 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041776 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1822952 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 6009 | 20230308 | 1302 | 20230308 | 1610 | 2026699 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 884 | 37.0398 | -120.4736 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0041744 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822943 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320657154036 | 20230308 | 1755 | 20230309 | 1051 | 2026983 | 1016 | Transformer only | Vegetation | Tree - fell into line | 1 | 1016 | 37.9853 | -120.2733 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0041832 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1822973 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1102 | 252261102 | FUSE | 7749 | 20230308 | 1852 | 20230308 | 2030 | 2027021 | 98 | Distribution Circuit | Animal | Bird found | 20 | 1960 | 37.3643 | -120.7916 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0041856 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822997 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10753 | 20230309 | 54 | 20230309 | 1039 | 2027145 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 19890 | 37.3669 | -119.6576 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041906 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | Yes | Yes | 1823044 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 5592 | 20230309 | 612 | 20230309 | 838 | 2027180 | 146 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 53 | 7738 | 37.0934 | -119.7181 | Yes | Partly Cloudy;32-90 F |  |  | 23-0041961 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823063 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10798 | 20230309 | 758 | 20230309 | 920 | 2027218 | 82 | Distribution Circuit | Animal | Other | 60 | 3268 | 37.2612 | -119.8623 | Yes | Overcast;32-90 F | Transformer (OH) | Normal | 23-0041971 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823065 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319711531024 | 20230309 | 835 | 20230309 | 1011 | 2027224 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 768 | 37.3523 | -120.6002 | Yes | Clear;32-90F | Secondary | Broken | 23-0041951 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823061 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 12315 | 20230309 | 942 | 20230309 | 1042 | 2027320 | 60 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 180 | 36.8798 | -120.2303 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042055 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823095 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320758455800 | 20230309 | 1034 | 20230309 | 1113 | 2027381 | 39 | Transformer only | 3rd Party | Other | 3 | 117 | 38.0324 | -120.2378 | Yes | Clear;32-90F | Other | Broken | 23-0042091 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823103 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | TRANSFORMER | 415111656039 | 20230309 | 1126 | 20230309 | 1430 | 2027411 | 184 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 184 | 36.8607 | -120.6717 | Yes | Clear;32-90F | Other | Burned Open | 23-0042100 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823107 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 90550 | 20230309 | 1143 | 20230310 | 1053 | 2027583 | 1390 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 52518 | 37.5151 | -120.052 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0042106 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823128 | 0 | EPSS Ckt | N | 2023 | A/GRD
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | T718450 | 20230309 | 1338 | 20230309 | 1658 | 2027584 | 200 | Transformer only | Equipment Failure/Involved | Underground | 12 | 2400 | 36.872 | -120.4642 | Yes | Clear;32-90 F | Transformer (UG) | Broken | 23-0042199 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823141 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | RECLOSER | 9020 | 20230309 | 1508 | 20230309 | 2005 | 2027873 | 297 | Distribution Circuit | 3rd Party | Vehicle | 1141 | 53594 | 37.7627 | -120.9789 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042267 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1823159 | 0 | Non-EPSS | N | 2023 | ABC
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | FUSE | 9613 | 20230309 | 1523 | 20230310 | 55 | 2027911 | 572 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 763 | 36.7493 | -120.4595 | Yes | Clear;32-90F |  |  | 23-0042672 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823480 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | INTERRUPTER | 948442 | 20230309 | 1622 | 20230309 | 1653 | 2028049 | 31 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 1550 | 36.8722 | -120.4636 | Yes | Clear;32-90 F | Transformer (UG) | Leaking | 23-0042183 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823181 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 447617 | 20230309 | 1637 | 20230309 | 2222 | 2028111 | 345 | Distribution Circuit | 3rd Party | Vehicle | 307 | 53915 | 37.2094 | -121.0139 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0042429 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823262 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L881 | 20230309 | 1658 | 20230310 | 1013 | 2028148 | 1035 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12420 | 38.0418 | -120.3472 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042503 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823326 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 40283 | 20230309 | 1809 | 20230309 | 2135 | 2028474 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 122 | 25132 | 38.0375 | -120.427 | Yes | Clear;32-90F |  |  | 23-0042438 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823271 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | OTHER | WIRE DOWN 1/W/OF 5049 | 20230309 | 1909 | 20230310 | 1936 | 2028896 | 1467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 187454 | 37.0325 | -120.3102 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042453 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1823281 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 318903017806 | 20230309 | 1917 | 20230310 | 206 | 2028207 | 409 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 818 | 36.9884 | -120.8765 | Yes | Clear;32-90F | Fuse | Broken | 23-0042712 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823524 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20230309 | 1958 | 20230309 | 2119 | 2027938 | 81 | Distribution Circuit | Environmental/External | Water | 144 | 11664 | 37.0679 | -119.9091 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Deteriorated | 23-0042490 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823313 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | JUMPER | OPEN JMPR | 20230309 | 2016 | 20230309 | 2116 | 2029217 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 5234 | 37.3269 | -120.8603 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0042571 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1823390 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | JUMPER | 19854 | 20230309 | 2048 | 20230310 | 800 | 2029331 | 672 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1344 | 37.3278 | -120.8821 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0042581 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1823398 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L885 | 20230309 | 2246 | 20230310 | 1616 | 2029632 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 11550 | 38.0459 | -120.3415 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042642 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823452 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 913 | 20230310 | 129 | 20230310 | 359 | 2029875 | 150 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 91 | 13607 | 37.6579 | -120.559 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0042727 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823540 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3518 | 20230310 | 216 | 20230310 | 1005 | 2030674 | 469 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 4690 | 36.96 | -120.6581 | No | Clear;32-90F |  |  | 23-0042924 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823660 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 20777 | 20230310 | 411 | 20230310 | 519 | 2030046 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1134 | 37.9934 | -120.3366 | No | Clear;32-90F |  |  | 23-0042746 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823560 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | S2125 | 20230310 | 525 | 20230316 | 1517 | 2030161 | 9232 | Distribution Circuit | Environmental/External | Flood/Erosion | 12 | 10266 | 38.006 | -120.2668 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0042748 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823566 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 9270 | 20230310 | 526 | 20230310 | 611 | 2030112 | 45 | Distribution Circuit | Environmental/External | Flood/Erosion | 513 | 16795 | 38.026 | -120.2543 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0042748 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823562 | 0 | EPSS Ckt | N | 2023 | B & C
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 19684 | 20230310 | 605 | 20230310 | 831 | 2030159 | 146 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 3796 | 37.9526 | -120.3906 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0042807 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823594 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318594145972 | 20230310 | 633 | 20230310 | 734 | 2030182 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 122 | 37.7615 | -120.9874 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0042777 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823579 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318856030256 | 20230310 | 704 | 20230310 | 826 | 2030264 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 82 | 37.3279 | -120.8953 | No | Clear;32-90 F | Fuse | Broken | 23-0042825 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823603 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322237026265 | 20230310 | 729 | 20230310 | 1419 | 2030173 | 410 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1230 | 37.2179 | -119.7317 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0042789 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823584 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | JUMPER | OJ @ CGC# 320711356150 | 20230310 | 940 | 20230310 | 1339 | 2030512 | 239 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 956 | 38.0419 | -120.2532 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0042849 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823614 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320208026781 | 20230310 | 1042 | 20230310 | 1424 | 2030638 | 222 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 222 | 37.2364 | -120.43 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0042959 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823677 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | RECLOSER | 275318 | 20230310 | 1052 | 20230310 | 1223 | 2030738 | 91 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 6370 | 37.1268 | -120.1275 | No | Overcast-Rain;32-90 F | Jumper | Burned Open | 23-0042970 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | No | No | 1823683 | 0 | Non-EPSS | N | 2023 | A- B- C
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | S2613 | 20230310 | 1108 | 20230310 | 1212 | 2030783 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1024 | 37.7036 | -120.818 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0043020 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823697 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1101 | 162671101 | TRANSFORMER | 317908839598 | 20230310 | 1154 | 20230310 | 1537 | 2030891 | 223 | Transformer only | Animal | Other | 2 | 446 | 37.5851 | -121.2233 | No | Overcast;32-90 F | Transformer (OH) | Normal | 23-0043182 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1823780 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | TRANSFORMER | T2054 | 20230310 | 1322 | 20230310 | 1328 | 2029375 | 6 | Transformer only | Equipment Failure/Involved | Underground | 26 | 156 | 36.9671 | -120.0507 | No | Overcast-Fog-Rain;32-90 F | Secondary | Broken | 23-0043099 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1823735 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6636 | 20230310 | 1724 | 20230311 | 1422 | 2031479 | 1258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 5035 | 37.0399 | -120.0293 | No | Clear;32-90F | Pole-Wood | Broken | 23-0043402 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823968 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10813 | 20230310 | 2152 | 20230311 | 1106 | 2031697 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 110366 | 37.4044 | -119.6248 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043312 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1823897 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 8717 | 20230311 | 351 | 20230311 | 511 | 2031856 | 80 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 480 | 37.3121 | -120.4828 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0043332 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823917 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | S719 | 20230311 | 623 | 20230311 | 727 | 2031911 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 320 | 37.7255 | -120.7744 | No | Clear;32-90F |  |  | 23-0043354 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1823934 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 322062017031 | 20230311 | 1058 | 20230311 | 1246 | 2032284 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 540 | 36.9654 | -119.7962 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0043454 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824011 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318925452707 | 20230311 | 1435 | 20230311 | 1608 | 2032512 | 93 | Transformer only | Environmental/External | Lightning | 2 | 186 | 37.9477 | -120.8731 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0043513 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824058 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | TRANSFORMER | 321292717933 | 20230311 | 1438 | 20230311 | 1550 | 2032637 | 72 | Transformer only | Animal | Bird found | 4 | 288 | 36.992 | -120.0588 | No | Clear;32-90 F | Fuse | Normal | 23-0043511 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | No | No | 1824056 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 87222 | 20230311 | 1503 | 20230312 | 1704 | 2032575 | 1561 | Distribution Circuit | Environmental/External | Flood/Erosion | 208 | 40516 | 37.9608 | -120.4062 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043492 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1824039 | 0 | EPSS Ckt | N | 2023 | C & GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 10580 | 20230311 | 1503 | 20230312 | 1611 | 2032569 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 351 | 529308 | 37.9489 | -120.4255 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043493 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1824040 | 0 | EPSS Ckt | N | 2023 | A & GRD
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 19684 | 20230311 | 1509 | 20230312 | 1547 | 2032577 | 1478 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 16252 | 37.9526 | -120.3906 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0043557 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824097 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320430655825 | 20230311 | 1514 | 20230313 | 1110 | 2032587 | 2636 | Distribution Circuit | Environmental/External | Lightning | 6 | 15816 | 38.0311 | -120.352 | No | Strong Winds; | Transformer (OH) | Failed/Faulted | 23-0043633 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824174 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | L1167 | 20230311 | 1515 | 20230311 | 2309 | 2032585 | 474 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 23 | 10749 | 38.0091 | -120.2316 | No | Strong Winds; |  |  | 23-0043607 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824147 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L2155 | 20230311 | 1519 | 20230311 | 1943 | 2032586 | 264 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 4224 | 37.9492 | -120.2562 | No | Strong Winds; |  |  | 23-0043570 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824109 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 21485 | 20230311 | 1520 | 20230312 | 1929 | 2032588 | 1689 | Distribution Circuit | Environmental/External | Flood/Erosion | 25 | 26704 | 37.9588 | -120.4039 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043529 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1824070 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23239 | 20230311 | 1530 | 20230311 | 1731 | 2032601 | 121 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 41 | 4961 | 37.9859 | -120.2825 | No | Strong Winds; |  |  | 23-0043531 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824073 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319067446274 | 20230311 | 1531 | 20230312 | 1032 | 2032602 | 1141 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1141 | 37.77 | -120.8237 | No | Strong Winds; | Jumper | Burned Open | 23-0043537 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824077 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320502654931 | 20230311 | 1545 | 20230312 | 1252 | 2032841 | 1267 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 6335 | 38.0084 | -120.3264 | No | Strong Winds; | Transformer (OH) | Failed/Faulted | 23-0043547 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824102 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | S1491 | 20230311 | 1551 | 20230311 | 1835 | 2032628 | 164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4100 | 38.0177 | -120.3276 | No | Clear-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0043547 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824087 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 100000033262 | 20230311 | 1554 | 20230312 | 1622 | 2032836 | 1468 | Transformer only | Environmental/External | Lightning | 1 | 1468 | 37.9747 | -120.2517 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043610 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824151 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 52899 | 20230311 | 1611 | 20230312 | 1601 | 2032648 | 1430 | Distribution Circuit | Environmental/External | Lightning | 6 | 8580 | 37.9763 | -120.2694 | No | Strong Winds; | Crossarm- Wood | Broken | 23-0043573 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824112 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320718052741 | 20230311 | 1713 | 20230313 | 1023 | 2032732 | 2470 | Transformer only | Environmental/External | Lightning | 3 | 7410 | 37.9487 | -120.2514 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043617 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824158 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 238071 | 20230311 | 1728 | 20230312 | 1532 | 2032830 | 1324 | Distribution Circuit | Environmental/External | Lightning | 1 | 1324 | 37.9345 | -120.8719 | No | Strong Winds; | Transformer (UG) | Failed/Faulted | 23-0043555 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824095 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 100000028125 | 20230311 | 1728 | 20230312 | 1532 | 2032740 | 1324 | Distribution Circuit | Environmental/External | Lightning | 1 | 1324 | 37.9303 | -120.8725 | No | Strong Winds; | Transformer (OH) | Failed/Faulted | 23-0043569 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824108 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 320140912931 | 20230311 | 1731 | 20230311 | 1831 | 2032680 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 24 | 1440 | 36.855 | -120.4534 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0043553 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824093 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1949 | 20230311 | 1744 | 20230312 | 1814 | 2032772 | 1470 | Distribution Circuit | Environmental/External | Lightning | 155 | 227746 | 37.8529 | -120.1659 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043624 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1824164 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320496254937 | 20230311 | 1815 | 20230312 | 1351 | 2032844 | 1176 | Transformer only | Environmental/External | Lightning | 1 | 1176 | 38.0085 | -120.3284 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043547 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824104 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320715856007 | 20230311 | 1847 | 20230312 | 1722 | 2032797 | 1355 | Transformer only | Environmental/External | Lightning | 2 | 2710 | 38.0376 | -120.2519 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043629 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824171 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320498054978 | 20230311 | 1941 | 20230312 | 1356 | 2032868 | 1095 | Transformer only | Environmental/External | Lightning | 2 | 2190 | 38.0098 | -120.3281 | No | Strong Winds; | Transformer (OH) | Failed/Faulted | 23-0043621 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824161 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | RECLOSER | 4940 | 20230311 | 2020 | 20230312 | 1 | 2032888 | 180 | Distribution Circuit | 3rd Party | Vehicle | 84 | 18396 | 37.1347 | -120.4929 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0043506 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1824114 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320560250460 | 20230311 | 2046 | 20230313 | 1042 | 2032899 | 2276 | Transformer only | Environmental/External | Lightning | 2 | 4552 | 37.8858 | -120.3061 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043619 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824159 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320243052618 | 20230311 | 2215 | 20230312 | 1903 | 2032946 | 1248 | Transformer only | Environmental/External | Lightning | 5 | 6240 | 37.9451 | -120.4167 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043606 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824146 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 100000033263 | 20230312 | 23 | 20230312 | 1725 | 2032975 | 1022 | Transformer only | Environmental/External | Lightning | 1 | 1022 | 37.9739 | -120.2507 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043614 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824155 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320560450512 | 20230312 | 313 | 20230313 | 1044 | 2033001 | 1891 | Transformer only | Environmental/External | Lightning | 1 | 1891 | 37.8872 | -120.3063 | No | Strong Winds;32-90 F | Transformer | Broken | 23-0043620 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824160 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | JUMPER | OJS 1 S/OF CGC 319146550005 | 20230312 | 719 | 20230312 | 1058 | 2033068 | 219 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 219 | 37.8722 | -120.7969 | No | Strong Winds; | Conductor- Overhead | Normal | 23-0043676 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1824207 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320764054981 | 20230312 | 720 | 20230312 | 1432 | 2033108 | 432 | Transformer only | Environmental/External | Lightning | 2 | 864 | 38.0071 | -120.235 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043644 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824180 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 318031638878 | 20230312 | 836 | 20230312 | 1115 | 2033119 | 159 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1272 | 37.5657 | -121.1804 | No | Overcast;32-90 F | Fuse | Broken | 23-0043708 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824224 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320759354946 | 20230312 | 848 | 20230312 | 1737 | 2033107 | 529 | Transformer only | Environmental/External | Lightning | 1 | 529 | 38.0087 | -120.2377 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043658 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824193 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320764054960 | 20230312 | 905 | 20230312 | 1542 | 2033137 | 397 | Transformer only | Environmental/External | Lightning | 1 | 397 | 38.009 | -120.2359 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043659 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824194 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 907060 | 20230312 | 945 | 20230312 | 1036 | 2033185 | 51 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 51 | 37.276 | -120.6331 | No | Partly Cloudy;32-90 F | Recloser | Normal | 23-0043678 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1824209 | 0 | Non-EPSS | N | 2023 | A-B-C TIME OC
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320644754103 | 20230312 | 954 | 20230312 | 1939 | 2033183 | 585 | Transformer only | Environmental/External | Lightning | 2 | 1170 | 37.9859 | -120.2769 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043690 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824216 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23247 | 20230312 | 1137 | 20230313 | 1252 | 2033226 | 1515 | Distribution Circuit | Environmental/External | Flood/Erosion | 4426 | 120742 | 37.979 | -120.2763 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043720 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1824236 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321058946059 | 20230312 | 1458 | 20230313 | 1345 | 2033544 | 1367 | Transformer only | Environmental/External | Lightning | 1 | 1367 | 37.7666 | -120.1358 | No | Heavy Rain;32-90 F | Transformer | Failed/Faulted | 23-0043785 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824298 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | T7751 | 20230312 | 1622 | 20230312 | 2221 | 2033447 | 359 | Transformer only | Equipment Failure/Involved | Underground | 10 | 3590 | 37.9845 | -120.3659 | No | Heavy Rain | Secondary | Broken | 23-0043761 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1824276 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 319978116733 | 20230312 | 1632 | 20230312 | 1734 | 2033468 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 124 | 36.9602 | -120.5092 | No | Heavy Rain; | Fuse | Broken | 23-0043772 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824285 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321512037676 | 20230312 | 1742 | 20230313 | 1326 | 2033521 | 1184 | Distribution Circuit | Environmental/External | Lightning | 1 | 1184 | 37.5323 | -119.9791 | No | Heavy Rain; | Transformer (OH) | Failed/Faulted | 23-0043797 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824310 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 13446 | 20230312 | 1800 | 20230313 | 1328 | 2033566 | 1168 | Distribution Circuit | Environmental/External | Lightning | 111 | 129648 | 37.5353 | -119.9833 | No | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 23-0043922 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824436 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6642 | 20230312 | 1811 | 20230312 | 1931 | 2033671 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 320 | 37.0056 | -120.0287 | No | Heavy Rain; |  |  | 23-0043796 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824309 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320702052655 | 20230312 | 1855 | 20230313 | 1040 | 2033588 | 945 | Transformer only | Environmental/External | Lightning | 1 | 945 | 37.946 | -120.2577 | No | Heavy Rain;32-90 F | Transformer | Failed/Faulted | 23-0043804 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824318 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320275053215 | 20230312 | 1918 | 20230313 | 1214 | 2033640 | 1016 | Transformer only | Environmental/External | Lightning | 20 | 20320 | 37.9613 | -120.4057 | No | Overcast-Drizzle;32-90 F | Transformer | Broken | 23-0043800 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824313 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321515837648 | 20230312 | 2023 | 20230313 | 1326 | 2033703 | 1023 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2046 | 37.5318 | -119.9779 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Broken | 23-0043815 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824329 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | FUSE | 493933 | 20230312 | 2024 | 20230313 | 1058 | 2033705 | 874 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4370 | 37.0907 | -120.1302 | No | Heavy Rain; | Conductor- Overhead | Broken- wire on ground | 23-0043817 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1824334 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | RECLOSER | 9830 | 20230312 | 2132 | 20230313 | 1420 | 2033855 | 1008 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 48770 | 37.0019 | -120.3101 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0043921 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824435 | 1 | Non-EPSS | N | 2023 | UNK
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20230313 | 308 | 20230313 | 1421 | 2033882 | 673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3074 | 237044 | 37.8473 | -120.2023 | No | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0043929 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1824443 | 0 | EPSS Ckt | N | 2023 | SGF
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | SECTIONALIZER | 11240 | 20230313 | 339 | 20230313 | 818 | 2033890 | 279 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 12834 | 36.785 | -120.3741 | No | Clear;32-90 F |  |  | 23-0043971 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1824462 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 7713 | 20230313 | 654 | 20230313 | 807 | 2033985 | 73 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 12 | 876 | 37.2287 | -120.2254 | No | Clear;32-90F |  |  | 23-0043970 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824461 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 320025023237 | 20230313 | 801 | 20230313 | 1106 | 2034297 | 185 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 740 | 37.1381 | -120.4921 | No | Clear;32-90F | Fuse | Broken | 23-0044080 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824512 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 20065 | 20230313 | 808 | 20230313 | 852 | 2034077 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 44 | 37.2546 | -120.9875 | No | Clear;32-90F |  |  | 23-0043997 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824472 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321391018451 | 20230313 | 836 | 20230313 | 1234 | 2034117 | 238 | Transformer only | Environmental/External | Lightning | 1 | 238 | 37.0058 | -120.0246 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0043991 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824468 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320948211515 | 20230313 | 926 | 20230313 | 1123 | 2034202 | 117 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 117 | 36.815 | -120.1779 | No | Clear;32-90F | Fuse | Broken | 23-0044092 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824515 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | TRANSFORMER | 320043927275 | 20230313 | 933 | 20230313 | 1324 | 2034211 | 231 | Transformer only | Environmental/External | Lightning | 3 | 693 | 37.2498 | -120.485 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0044057 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824506 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 10606 | 20230313 | 1248 | 20230313 | 1416 | 2034497 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 88 | 37.2108 | -119.5031 | No | Partly Cloudy;32-90 F |  |  | 23-0044199 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824559 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | FUSE | 9627 | 20230313 | 1426 | 20230313 | 1613 | 2034685 | 107 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 357 | 37.0708 | -120.9982 | No | Clear;32-90F |  |  | 23-0044283 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824586 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321508137632 | 20230313 | 1519 | 20230314 | 1129 | 2034766 | 1210 | Transformer only | Environmental/External | Lightning | 1 | 1210 | 37.5306 | -119.9807 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0044323 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824608 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | T9123 | 20230313 | 1641 | 20230314 | 1441 | 2034858 | 1320 | Transformer only | Environmental/External | Lightning | 1 | 1320 | 37.8125 | -119.951 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0044300 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824593 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320607054521 | 20230313 | 1643 | 20230313 | 1810 | 2034868 | 87 | Transformer only | Equipment Failure/Involved | Underground | 2 | 174 | 37.9969 | -120.2908 | No | Clear;32-90F | Other | Broken | 23-0044307 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1824596 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | FUSE | 9627 | 20230313 | 1718 | 20230313 | 2045 | 2034968 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 690 | 37.0708 | -120.9982 | No | Clear;32-90F |  |  | 23-0044375 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824640 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 20363 | 20230313 | 1925 | 20230313 | 2040 | 2035038 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2400 | 38.0159 | -120.3105 | No | Clear;32-90F |  |  | 23-0044369 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824635 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318917552564 | 20230313 | 2034 | 20230314 | 1210 | 2035064 | 936 | Transformer only | Environmental/External | Lightning | 1 | 936 | 37.943 | -120.8763 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0044397 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824664 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322014136067 | 20230313 | 2117 | 20230314 | 1214 | 2035085 | 897 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1794 | 37.4887 | -119.8073 | No | Overcast-Fog;32-90 F | Transformer (OH) | Broken | 23-0044379 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824645 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4642 | 20230314 | 717 | 20230314 | 816 | 2035217 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1475 | 37.5583 | -119.9304 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0044540 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824758 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321511038218 | 20230314 | 816 | 20230314 | 1044 | 2035310 | 148 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 444 | 37.5473 | -119.9802 | Yes | Clear;32-90F |  |  | 23-0044718 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1824859 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 8674 | 20230314 | 829 | 20230314 | 930 | 2035334 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1220 | 37.3592 | -120.6685 | Yes | Clear;32-90 F |  |  | 23-0044620 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824795 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | JUMPER | OJ 1 POLE N/OF CGC#319501131197 | 20230314 | 829 | 20230314 | 1552 | 2036655 | 443 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 886 | 37.3567 | -120.6722 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0045044 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1825115 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10813 | 20230314 | 840 | 20230314 | 1458 | 2035346 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 35046 | 37.4044 | -119.6248 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0044697 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824844 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 20018 | 20230314 | 920 | 20230314 | 1055 | 2035444 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 570 | 37.1975 | -121.0127 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0044739 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824876 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 21059 | 20230314 | 929 | 20230316 | 1721 | 2046240 | 3352 | Distribution Circuit | Environmental/External | Flood/Erosion | 40 | 107752 | 37.5103 | -121.3234 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | On Ground | 23-0046359 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1826172 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 7318 | 20230314 | 938 | 20230314 | 1020 | 2035516 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 378 | 37.4041 | -120.7116 | Yes | Clear;32-90F |  |  | 23-0044707 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824850 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | RECLOSER | 49704 | 20230314 | 1009 | 20230314 | 1045 | 2035765 | 36 | Distribution Circuit | Vegetation | Tree - branch fell on line | 258 | 9288 | 37.7769 | -120.817 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0044657 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824817 | 0 | EPSS Ckt | N | 2023 | B & C
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 20601 | 20230314 | 1028 | 20230315 | 1916 | 2035883 | 1968 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2020 | 37.7765 | -120.7962 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Deteriorated | 23-0044681 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1824834 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | S2065 | 20230314 | 1031 | 20230314 | 1140 | 2035929 | 69 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 345 | 37.2967 | -121.0066 | Yes | Clear;32-90F | Anchor or Guy | Normal | 23-0044878 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824984 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 913 | 20230314 | 1040 | 20230314 | 1205 | 2036067 | 85 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 7711 | 37.6579 | -120.559 | Yes | Clear;32-90F | Fuse | Broken | 23-0044956 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825041 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 39660 | 20230314 | 1100 | 20230315 | 1215 | 2036304 | 1515 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 14691 | 37.8894 | -120.8403 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0044780 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824907 | 0 | EPSS Ckt | N | 2023 | A & C
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | TRANSFORMER | 318942346102 | 20230314 | 1123 | 20230314 | 1702 | 2036510 | 339 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 1695 | 37.7655 | -120.8669 | Yes | Clear;32-90 F | Transformer | Arcing | 23-0044856 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824965 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1105 | 254101105 | TRANSFORMER | 320740022106 | 20230314 | 1131 | 20230314 | 1326 | 2037123 | 115 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 460 | 37.1072 | -120.2479 | Yes | Clear;32-90F | Secondary | Normal | 23-0045171 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825219 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | 20959 | 20230314 | 1131 | 20230314 | 1330 | 2037113 | 119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 10003 | 37.7272 | -120.9267 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0044919 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825012 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | JUMPER | OJ WEST PH OF CGC# 320394518862 | 20230314 | 1135 | 20230314 | 1442 | 2041664 | 187 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 748 | 37.0179 | -120.3656 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0045275 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1825292 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | SECTIONALIZER | 10810 | 20230314 | 1141 | 20230314 | 1326 | 2037607 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 4725 | 37.5363 | -120.5166 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0045444 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1825421 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | JUMPER | 5841 | 20230314 | 1150 | 20230314 | 1230 | 2037696 | 40 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 360 | 37.7762 | -120.7898 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0044981 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1825063 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 2391 | 20230314 | 1150 | 20230314 | 1312 | 2037700 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 2461 | 37.7946 | -120.9508 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0045157 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825206 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319187346911 | 20230314 | 1154 | 20230314 | 1453 | 2037763 | 179 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 179 | 37.7882 | -120.7825 | Yes | Clear;32-90F | Fuse | Broken | 23-0045387 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825374 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319254644044 | 20230314 | 1200 | 20230314 | 1319 | 2037882 | 79 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 79 | 37.709 | -120.7591 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0045144 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825195 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | 20905 | 20230314 | 1202 | 20230314 | 1410 | 2037971 | 128 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2176 | 37.7278 | -120.9079 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0045119 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1825173 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | JUMPER | OJ SS OF 21036 | 20230314 | 1217 | 20230314 | 1739 | 2043770 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 6416 | 37.4038 | -120.5765 | Yes | Clear;32-90F | Jumper | Broken | 23-0045659 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1825601 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 4191 | 20230314 | 1217 | 20230314 | 1538 | 2039589 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1743 | 37.8195 | -120.8685 | Yes | Clear;32-90F | Fuse | Broken | 23-0045496 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1825466 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | S1807 | 20230314 | 1224 | 20230314 | 1734 | 2038611 | 310 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 5890 | 37.7597 | -120.8925 | Yes | Clear;32-90F |  |  | 23-0045640 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825583 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | RECLOSER | 8160 | 20230314 | 1225 | 20230314 | 1841 | 2038697 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 113 | 12568 | 37.7985 | -121.0021 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044996 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1825076 | 0 | Non-EPSS | N | 2023 | A-B-C
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 7054 | 20230314 | 1227 | 20230314 | 1500 | 2038788 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 9486 | 37.346 | -120.7245 | Yes | Clear;32-90 F |  |  | 23-0045480 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825452 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | RECLOSER | 2350 | 20230314 | 1231 | 20230314 | 2007 | 2039012 | 456 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2085 | 158032 | 37.308 | -120.5052 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045028 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1825100 | 0 | Non-EPSS | N | 2023 | A-B & GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319994551125 | 20230314 | 1240 | 20230314 | 1923 | 2039918 | 403 | Transformer only | Vegetation | Tree - fell into line | 1 | 403 | 37.9039 | -120.5015 | Yes | Clear;32-90 F | Transformer | Broken | 23-0045456 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825429 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 7318 | 20230314 | 1245 | 20230314 | 1534 | 2039307 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1521 | 37.4041 | -120.7116 | Yes | Clear;32-90F |  |  | 23-0045469 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825442 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 12315 | 20230314 | 1247 | 20230315 | 1045 | 2039361 | 1318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 3954 | 36.8798 | -120.2303 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0045361 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825349 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11624 | 20230314 | 1250 | 20230314 | 1635 | 2039456 | 225 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1575 | 37.2075 | -120.3295 | Yes | Clear;32-90F |  |  | 23-0045590 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825542 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | RECLOSER | 11670 | 20230314 | 1252 | 20230315 | 128 | 2039615 | 756 | Distribution Circuit | Equipment Failure/Involved | Overhead | 315 | 27898 | 37.3614 | -120.4686 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045091 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1825153 | 0 | Non-EPSS | N | 2023 | A-B-C
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | JUMPER | OJ @ CGC# 318602531135 | 20230314 | 1309 | 20230515 | 1345 | 2039843 | 89316 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 535896 | 37.3541 | -120.982 | Yes | Clear;32-90 F | Other | Normal | 23-0045101 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1825159 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 2391 | 20230314 | 1322 | 20230314 | 1604 | 2040786 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 7290 | 37.7946 | -120.9508 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0045224 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825255 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | RECLOSER | 246168 | 20230314 | 1337 | 20230314 | 1630 | 2041107 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 523 | 90479 | 37.787 | -120.7632 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0045439 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825416 | 0 | EPSS Ckt | N | 2023 | AB
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 6285 | 20230314 | 1439 | 20230314 | 1634 | 2042323 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 228 | 26220 | 37.191 | -119.7891 | Yes | Overcast-Rain;32-90 F |  |  | 23-0045537 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825499 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | OCB | 1111/2 | 20230314 | 1505 | 20230314 | 1742 | 2042630 | 157 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2892 | 132956 | 36.9832 | -120.0334 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0045422 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1825401 | 0 | Non-EPSS | N | 2023 | C & GRD TIME
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | TRANSFORMER | 319038245918 | 20230314 | 1510 | 20230315 | 1427 | 2040770 | 1397 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1397 | 37.7605 | -120.8337 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045489 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1825460 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | OCB | 1703/2 | 20230314 | 1527 | 20230314 | 1825 | 2042778 | 178 | Distribution Circuit | 3rd Party | Vehicle | 3105 | 342827 | 37.9799 | -120.4136 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045455 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1825428 | 0 | EPSS Ckt | N | 2023 | A C GRD
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 87260 | 20230314 | 1548 | 20230314 | 1915 | 2043321 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2484 | 36.9646 | -120.0742 | Yes | Overcast-Drizzle;32-90 F | Secondary | Broken | 23-0045608 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1825557 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1647 | 20230314 | 1659 | 20230314 | 2057 | 2043624 | 238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 6664 | 37.8209 | -120.7041 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0045847 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825769 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320287153339 | 20230314 | 1730 | 20230314 | 1917 | 2043800 | 107 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 526 | 37.965 | -120.4012 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Normal | 23-0045663 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1825605 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 4712 | 20230314 | 1737 | 20230314 | 2144 | 2043851 | 247 | Distribution Circuit | Equipment Failure/Involved | Underground | 234 | 50742 | 37.3122 | -120.4693 | Yes | Overcast-Heavy Rain;32-90 F | Elbow | Failed/Faulted | 23-0045705 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825643 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 87563 | 20230314 | 1846 | 20230315 | 1020 | 2044217 | 934 | Distribution Circuit | Environmental/External | Lightning | 7 | 1588 | 37.472 | -120.1048 | Yes | Overcast-Fog-Heavy Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0045857 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825780 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7887 | 20230314 | 1918 | 20230314 | 2110 | 2044436 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1120 | 37.3267 | -120.2518 | Yes | Clear;32-90F |  |  | 23-0045859 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825782 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 26506 | 20230314 | 1940 | 20230314 | 2048 | 2044507 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 340 | 37.7254 | -120.7901 | Yes | Clear;32-90F |  |  | 23-0045873 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825797 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 6885 | 20230314 | 2005 | 20230314 | 2028 | 2044397 | 23 | Distribution Circuit | Animal | Other | 106 | 2438 | 36.9959 | -119.8707 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0045834 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1825756 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | JUMPER | OJ @ CGC# 318459648035 | 20230314 | 2111 | 20230314 | 2312 | 2044799 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 241 | 37.8184 | -121.0344 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0045890 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1825813 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 12236 | 20230314 | 2206 | 20230315 | 1513 | 2045036 | 1027 | Distribution Circuit | Environmental/External | Flood/Erosion | 204 | 209508 | 37.5334 | -119.835 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken | 23-0046032 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1825948 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321669838319 | 20230314 | 2336 | 20230314 | 2345 | 2044861 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 36 | 37.5514 | -119.9249 | Yes | Overcast-Fog-Drizzle;32-90 F | Customer Equipment | Deteriorated | 23-0046006 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1825930 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 667248 | 20230315 | 158 | 20230315 | 304 | 2045073 | 66 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2889 | 190674 | 38.049 | -120.2357 | No | Clear;32-90 F |  |  | 23-0046040 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1825958 | 0 | EPSS Ckt | N | 2023 | A B C
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318701346137 | 20230315 | 301 | 20230315 | 1336 | 2045263 | 635 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1270 | 37.7658 | -120.9502 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0046068 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825990 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | S1577 | 20230315 | 308 | 20230315 | 1041 | 2045144 | 453 | Distribution Circuit | Environmental/External | Flood/Erosion | 94 | 20022 | 38.0269 | -120.2468 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046057 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 22080 | No | Yes | No | 1825976 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 20007 | 20230315 | 522 | 20230315 | 544 | 2045251 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 147 | 37.7623 | -120.9502 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0046075 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1825996 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | S727 | 20230315 | 706 | 20230315 | 805 | 2045505 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 59 | 37.8037 | -120.9518 | No | Clear;32-90F |  |  | 23-0046117 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826017 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320090229401 | 20230315 | 920 | 20230315 | 1017 | 2045616 | 57 | Transformer only | Vegetation | Tree - fell into line | 8 | 456 | 37.308 | -120.4687 | No | Clear;32-90 F | Secondary | Broken | 23-0046147 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1826040 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 21548 | 20230315 | 1101 | 20230315 | 1532 | 2045918 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 813 | 38.0448 | -120.2076 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0046236 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1826102 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319565530206 | 20230315 | 1345 | 20230315 | 1530 | 2046286 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 315 | 37.3293 | -120.6508 | No | Overcast;32-90 F | Secondary | Broken | 23-0046377 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1826184 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | TRANSFORMER | 321320216574 | 20230315 | 1440 | 20230315 | 1542 | 2046393 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 1178 | 36.9544 | -120.0491 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0046417 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1826206 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7013 | 20230315 | 2136 | 20230315 | 2219 | 2047374 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 3327 | 37.3301 | -120.6872 | No | Overcast-Fog;32-90 F |  |  | 23-0046783 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826431 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | 20619 | 20230315 | 2300 | 20230316 | 1114 | 2047650 | 734 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 734 | 37.7494 | -120.7573 | No | Clear;32-90 F | Elbow | Broken | 23-0046846 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826469 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7314 | 20230316 | 49 | 20230316 | 151 | 2047524 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 620 | 37.4826 | -120.649 | No | Overcast-Fog;32-90 F |  |  | 23-0046829 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1826455 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | 6221 | 20230316 | 319 | 20230316 | 512 | 2047588 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 4294 | 37.7619 | -120.8071 | No | Clear;32-90 F |  |  | 23-0046844 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1826466 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 5676 | 20230316 | 651 | 20230316 | 818 | 2047687 | 87 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 54 | 4698 | 37.2412 | -119.7369 | No | Clear;32-90 F |  |  | 23-0046878 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1826478 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | OTHER | T14385 TWD T14687 | 20230316 | 1155 | 20230316 | 1624 | 2048284 | 269 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 269 | 37.0575 | -120.02 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0046980 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1826538 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | TRANSFORMER | 322854528983 | 20230316 | 1238 | 20230316 | 1613 | 2048916 | 215 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1075 | 37.2926 | -119.5199 | No | Clear;32-90 F | Secondary | Broken | 23-0047158 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1826642 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322023634596 | 20230316 | 1342 | 20230317 | 1308 | 2048566 | 1406 | Transformer only | Environmental/External | Ice or snow | 1 | 1406 | 37.448 | -119.8049 | No | Overcast;32-90 F | Transformer | Broken | 23-0047315 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826775 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | 213845 | 20230316 | 1350 | 20230316 | 1358 | 2048594 | 8 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 8 | 38.0592 | -120.2144 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0047065 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1826593 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 447617 | 20230316 | 1451 | 20230316 | 1655 | 2048737 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 204 | 25309 | 37.2094 | -121.0139 | No | Clear;32-90 F |  |  | 23-0047200 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826668 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321552512860 | 20230316 | 1649 | 20230317 | 1550 | 2048519 | 1381 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1381 | 36.8518 | -119.9709 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047183 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826659 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | TRANSFORMER | 320614528696 | 20230316 | 2011 | 20230317 | 930 | 2049165 | 799 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3196 | 37.2869 | -120.2885 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047254 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826715 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5140 | 20230316 | 2026 | 20230317 | 102 | 2049292 | 276 | Distribution Circuit | 3rd Party | Vehicle | 10 | 2760 | 37.0542 | -120.0308 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0047236 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1826718 | 0 | EPSS Ckt | N | 2023 | N/A
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320498854917 | 20230316 | 2056 | 20230317 | 1422 | 2049319 | 1046 | Transformer only | Environmental/External | Lightning | 1 | 1046 | 38.0081 | -120.3278 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0047302 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826763 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 142739 | 20230317 | 33 | 20230317 | 152 | 2049404 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 105 | 37.8865 | -120.8805 | No | Clear;32-90 F |  |  | 23-0047341 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826781 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322121135381 | 20230317 | 405 | 20230317 | 1310 | 2049439 | 545 | Transformer only | Environmental/External | Ice or snow | 1 | 545 | 37.4684 | -119.7701 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0047353 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826788 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | S957 | 20230317 | 1031 | 20230317 | 1218 | 2049829 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1819 | 37.7111 | -120.7919 | No | Clear;32-90 F |  |  | 23-0047525 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1826872 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | TRANSFORMER | 322838527225 | 20230317 | 1158 | 20230317 | 1607 | 2050002 | 249 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 249 | 37.2464 | -119.5249 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047583 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826897 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 390615 | 20230317 | 1315 | 20230317 | 1750 | 2050146 | 275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 275 | 36.6615 | -120.3881 | No | Clear;32-90 F | Fuse | Broken | 23-0047735 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1826979 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320691612522 | 20230317 | 1405 | 20230317 | 1657 | 2050227 | 172 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 172 | 36.8437 | -120.2625 | No | Clear;32-90 F | Fuse | Broken | 23-0047716 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826962 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | TRANSFORMER | 322831527187 | 20230317 | 1425 | 20230317 | 1720 | 2050260 | 175 | Transformer only | Environmental/External | Ice or snow | 1 | 175 | 37.2448 | -119.5286 | No | Clear;32-90 F | Fuse | Normal | 23-0047722 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1826966 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 19495 | 20230317 | 2044 | 20230317 | 2210 | 2050751 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 4386 | 37.4113 | -120.0898 | No | Partly Cloudy;32-90 F |  |  | 23-0047772 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827004 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | RECLOSER | 59150 | 20230318 | 152 | 20230318 | 1645 | 2050847 | 893 | Distribution Circuit | 3rd Party | Vehicle | 2336 | 645054 | 37.281 | -120.4881 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0048232 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1827463 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6555 | 20230318 | 655 | 20230318 | 837 | 2050892 | 102 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 1429 | 36.8794 | -120.0196 | No | Clear;32-90 F |  |  | 23-0048257 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827482 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 21992 | 20230318 | 709 | 20230318 | 1240 | 2051196 | 329 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2632 | 36.749 | -120.3535 | No | Fog;32-90 F |  |  | 23-0048311 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1827526 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | T9317 | 20230318 | 940 | 20230318 | 952 | 2050997 | 12 | Transformer only | Equipment Failure/Involved | Underground | 15 | 180 | 37.7714 | -120.826 | No | Clear;32-90 F | Secondary | Broken | 23-0048270 | UG | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1827492 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20230318 | 1026 | 20230318 | 1228 | 2051038 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2074 | 37.1863 | -120.6348 | No | Clear;32-90 F |  |  | 23-0048310 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827525 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | FUSE | 6088 | 20230318 | 1308 | 20230318 | 1441 | 2051295 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 93 | 36.93 | -120.0269 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0048327 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827534 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | S285 | 20230318 | 1559 | 20230320 | 1318 | 2051403 | 2719 | Distribution Circuit | 3rd Party | Other | 1 | 2719 | 37.4931 | -121.3034 | No | Overcast;32-90 F | Anchor or Guy | Broken | 23-0048521 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827727 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 25439 | 20230319 | 645 | 20230319 | 1422 | 2051720 | 457 | Distribution Circuit | 3rd Party | Vehicle | 93 | 42501 | 37.3241 | -120.5875 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0048433 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1827641 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319771025999 | 20230319 | 1224 | 20230319 | 1300 | 2051919 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 72 | 37.2147 | -120.5791 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0048497 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827705 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | T9256 | 20230319 | 1320 | 20230319 | 1418 | 2051940 | 58 | Transformer only | Equipment Failure/Involved | Underground | 19 | 1102 | 37.9802 | -120.3642 | No | Overcast-Drizzle;32-90 F | Bus | Failed/Faulted | 23-0048482 | UG | Sus | 45702866 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1827692 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 21059 | 20230319 | 1322 | 20230320 | 1019 | 2051692 | 1257 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 36792 | 37.5102 | -121.3237 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0048499 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1827707 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319585031080 | 20230319 | 1326 | 20230319 | 1805 | 2052068 | 279 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 558 | 37.3534 | -120.644 | No | Overcast;32-90 F | Secondary | Deteriorated | 23-0048513 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827720 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7392 | 20230319 | 1452 | 20230319 | 1550 | 2052137 | 58 | Distribution Circuit | Animal | Bird found | 20 | 1160 | 37.411 | -120.5961 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0048526 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827732 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23256 | 20230319 | 2221 | 20230319 | 2348 | 2052486 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1740 | 38.0108 | -120.3057 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0048590 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827798 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10284 | 20230319 | 2333 | 20230320 | 56 | 2052495 | 83 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 20 | 1660 | 37.3877 | -119.6326 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0048592 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827799 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322507532160 | 20230320 | 119 | 20230320 | 1051 | 2052529 | 572 | Transformer only | Environmental/External | Lightning | 2 | 1144 | 37.3808 | -119.6387 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 23-0048599 | OH | Sus | 35432749 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827805 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 4621 | 20230320 | 1252 | 20230320 | 1505 | 2053146 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 976 | 37.2567 | -121.097 | No | Partly Cloudy;32-90 F |  |  | 23-0048917 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827928 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320624613044 | 20230320 | 1337 | 20230320 | 1537 | 2053125 | 120 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 120 | 36.858 | -120.2866 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0048974 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827952 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 3736 | 20230320 | 1526 | 20230320 | 1621 | 2053245 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 367 | 36.792 | -120.2592 | No | Partly Cloudy;32-90 F |  |  | 23-0048984 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1827956 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | RECLOSER | 4760 | 20230320 | 1554 | 20230323 | 1232 | 2053280 | 4118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 83044 | 37.0986 | -120.4938 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049008 | OH | Sus | 45703906 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1827966 | 0 | Non-EPSS | N | 2023 | A- B- GRD
YOSEMITE | YOSEMITE | PANOCHE-1102 | 253671102 | OCB | 1102/2 | 20230320 | 2226 | 20230321 | 149 | 2053492 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 21964 | 36.6512 | -120.5803 | No | Overcast;32-90 F | Regulator | Failed/Faulted | 23-0049048 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828005 | 0 | Non-EPSS | N | 2023 | A & GRD
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | TRANSFORMER | 416223251247 | 20230321 | 15 | 20230321 | 310 | 2053505 | 175 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 175 | 36.7342 | -120.29 | Yes | Overcast;32-90 F | Fuse | Broken | 23-0049065 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828022 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 10776 | 20230321 | 744 | 20230321 | 1018 | 2053630 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 201 | 30954 | 37.207 | -119.6803 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0049154 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828063 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 6887 | 20230321 | 825 | 20230322 | 1309 | 2053666 | 1724 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 7932 | 36.9592 | -119.9121 | Yes | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049144 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828056 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | RECLOSER | 315398 | 20230321 | 826 | 20230321 | 1620 | 2053668 | 474 | Distribution Circuit | 3rd Party | Vehicle | 201 | 42242 | 36.9714 | -120.0668 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049122 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1828043 | 0 | Non-EPSS | N | 2023 | A-B-C & GRD
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318501829489 | 20230321 | 843 | 20230321 | 1028 | 2053706 | 105 | Transformer only | 3rd Party | Vehicle | 5 | 525 | 37.3087 | -121.017 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0049248 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828102 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10498 | 20230321 | 1045 | 20230321 | 1824 | 2054004 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 19278 | 37.4644 | -119.7603 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049375 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1828159 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321417061507 | 20230321 | 1105 | 20230321 | 1354 | 2055439 | 169 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 169 | 38.1889 | -120.008 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0049539 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828299 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 26538 | 20230321 | 1129 | 20230321 | 1554 | 2054117 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 795 | 37.3483 | -120.9795 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049407 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1828184 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 6936 | 20230321 | 1130 | 20230321 | 2335 | 2056755 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5876 | 37.0985 | -120.4748 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049691 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1828417 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11624 | 20230321 | 1131 | 20230321 | 2205 | 2054132 | 634 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4438 | 37.2075 | -120.3295 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049881 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1828574 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 4000 | 20230321 | 1139 | 20230321 | 1757 | 2054165 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 37220 | 37.5266 | -120.442 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0049351 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828144 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | SECTIONALIZER | 10810 | 20230321 | 1145 | 20230321 | 1605 | 2056476 | 260 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 11700 | 37.5363 | -120.5166 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0049809 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1828513 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | OCB | 1116/2 | 20230321 | 1150 | 20230321 | 1541 | 2054199 | 231 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2053 | 239025 | 37.2732 | -120.4872 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0049360 | OH | Sus | 35433026 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828150 | 0 | Non-EPSS | N | 2023 | B & C & INST
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 25276 | 20230321 | 1152 | 20230321 | 1314 | 2054185 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 6888 | 37.5393 | -120.1792 | Yes | Clear;32-90 F |  |  | 23-0049441 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828210 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | RECLOSER | 9770 | 20230321 | 1154 | 20230321 | 2326 | 2054226 | 692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 259 | 34540 | 36.8941 | -120.6523 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049367 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1828155 | 0 | Non-EPSS | N | 2023 | A & B PHASE
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20230321 | 1158 | 20230321 | 1424 | 2054222 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1655 | 37.1863 | -120.6348 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049662 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828392 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320219936526 | 20230321 | 1158 | 20230321 | 1936 | 2054223 | 458 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 458 | 37.5031 | -120.4252 | Yes | Overcast;32-90 F | Fuse | Broken | 23-0050098 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828769 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | RECLOSER | 12100 | 20230321 | 1214 | 20230321 | 1640 | 2054299 | 266 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 59 | 15694 | 36.7379 | -120.6934 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049395 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828173 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | RECLOSER | 3160 | 20230321 | 1218 | 20230321 | 1948 | 2054318 | 450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 27027 | 36.7225 | -120.3811 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049398 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1828176 | 0 | Non-EPSS | N | 2023 | B PHASE & GRD
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | RECLOSER | 421930 | 20230321 | 1221 | 20230321 | 1648 | 2054323 | 267 | Distribution Circuit | 3rd Party | Thrown Object | 50 | 13350 | 37.4937 | -120.5004 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049401 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828179 | 0 | Non-EPSS | N | 2023 | B&C
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | OCB | 1106/2 | 20230321 | 1223 | 20230321 | 1715 | 2054373 | 292 | Distribution Circuit | Vegetation | Tree - fell into line | 4330 | 165048 | 36.9233 | -120.0551 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049415 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1828189 | 0 | Non-EPSS | N | 2023 | A & C- INST OC
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | RECLOSER | 11870 | 20230321 | 1233 | 20230321 | 2038 | 2054431 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 768 | 142790 | 36.9658 | -120.1284 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049425 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1828200 | 0 | Non-EPSS | N | 2023 | A & B PHASE
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 23314 | 20230321 | 1237 | 20230321 | 1430 | 2055473 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 113 | 37.7109 | -120.7611 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049713 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828436 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 81061 | 20230321 | 1242 | 20230321 | 1710 | 2055438 | 268 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 268 | 36.9963 | -120.2027 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0049551 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828307 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | RECLOSER | 620474 | 20230321 | 1244 | 20230321 | 2020 | 2054549 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 972 | 62805 | 36.9967 | -120.0994 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049449 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1828216 | 0 | Non-EPSS | N | 2023 | C & GRD
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 22893 | 20230321 | 1323 | 20230321 | 1632 | 2055465 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 5979 | 36.8957 | -119.7943 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0049839 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828541 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320404052938 | 20230321 | 1344 | 20230321 | 2100 | 2055721 | 436 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 872 | 37.9541 | -120.361 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049654 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828383 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321249113079 | 20230321 | 1423 | 20230321 | 1547 | 2056463 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 336 | 36.8591 | -120.074 | Yes | Clear-Strong Winds;32-90 F | Fuse | Failed/Faulted | 23-0049785 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828493 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321754235327 | 20230321 | 1429 | 20230321 | 1510 | 2057025 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 123 | 37.4663 | -119.8957 | Yes | Overcast-Rain;32-90 F | Secondary | Broken- wire on ground | 23-0049729 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1828448 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 10376 | 20230321 | 1435 | 20230321 | 1549 | 2056572 | 74 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 56 | 4144 | 37.4552 | -119.9603 | Yes | Overcast-Rain;32-90 F |  |  | 23-0049775 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828484 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 7423 | 20230321 | 1437 | 20230321 | 1516 | 2056590 | 39 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 74 | 2886 | 37.4218 | -119.9717 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0049722 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828444 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321707233247 | 20230321 | 1451 | 20230322 | 1609 | 2056714 | 1518 | Transformer only | Environmental/External | Lightning | 2 | 3036 | 37.4124 | -119.9131 | Yes | Rain-Overcast;32-90 F | Transformer | Broken | 23-0050057 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828735 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 4714 | 20230321 | 1507 | 20230321 | 1850 | 2056898 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1784 | 37.3332 | -120.3785 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0050042 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828725 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 1590 | 20230321 | 1513 | 20230321 | 2057 | 2056975 | 344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 344 | 36.9874 | -120.1044 | Yes | Partly Cloudy-Strong Winds;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0049812 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828517 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 933811 | 20230321 | 1600 | 20230322 | 906 | 2057631 | 1026 | Distribution Circuit | Environmental/External | Lightning | 20 | 2755 | 37.4783 | -119.8232 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049918 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828606 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321958035678 | 20230321 | 1604 | 20230322 | 1045 | 2057735 | 1121 | Transformer only | Environmental/External | Lightning | 1 | 1121 | 37.4783 | -119.8257 | Yes | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049999 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828684 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320421142269 | 20230321 | 1609 | 20230322 | 1105 | 2057951 | 1136 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2272 | 37.6616 | -120.3549 | Yes | Clear-Strong Winds;32-90 F | Cutout- fuse holder | Arcing | 23-0050150 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828814 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321926336130 | 20230321 | 1614 | 20230322 | 1413 | 2057941 | 1319 | Transformer only | Environmental/External | Lightning | 1 | 1319 | 37.4904 | -119.8371 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050167 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828830 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | FUSE | 22396 | 20230321 | 1617 | 20230321 | 2024 | 2057662 | 247 | Distribution Circuit | 3rd Party | Vehicle | 23 | 5681 | 37.3496 | -120.5751 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0049808 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828512 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 4393 | 20230321 | 1622 | 20230321 | 2100 | 2058108 | 278 | Distribution Circuit | Environmental/External | Lightning | 67 | 7958 | 37.794 | -120.9416 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Burned/flashed | 23-0049968 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1828654 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321543034199 | 20230321 | 1629 | 20230322 | 1328 | 2058247 | 1259 | Transformer only | Environmental/External | Lightning | 1 | 1259 | 37.4373 | -119.9694 | Yes | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 23-0050039 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828722 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321576534395 | 20230321 | 1631 | 20230322 | 1330 | 2058276 | 1259 | Transformer only | Environmental/External | Lightning | 2 | 2518 | 37.4431 | -119.958 | Yes | Overcast;32-90 F | Transformer | Broken | 23-0050088 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828760 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318652350518 | 20230321 | 1638 | 20230322 | 841 | 2060265 | 963 | Transformer only | Environmental/External | Lightning | 2 | 1926 | 37.8864 | -120.9684 | Yes | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0050071 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828749 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 20151 | 20230321 | 1638 | 20230321 | 2258 | 2060828 | 380 | Distribution Circuit | Environmental/External | Lightning | 1 | 380 | 37.8837 | -120.988 | Yes | Overcast;32-90 F | Transformer (UG) | Normal | 23-0050168 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828831 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 4185 | 20230321 | 1644 | 20230321 | 1859 | 2058574 | 135 | Distribution Circuit | Environmental/External | Lightning | 71 | 9585 | 37.8868 | -120.9457 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049976 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1828662 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318666050530 | 20230321 | 1644 | 20230322 | 948 | 2060249 | 1024 | Transformer only | Environmental/External | Lightning | 3 | 3072 | 37.8866 | -120.9629 | Yes | Strong Winds-Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 23-0050067 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828745 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318649050390 | 20230321 | 1644 | 20230322 | 947 | 2060291 | 1023 | Transformer only | Environmental/External | Lightning | 2 | 2046 | 37.8829 | -120.9692 | Yes | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0050080 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828755 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 6107 | 20230321 | 1732 | 20230321 | 1806 | 2059498 | 34 | Distribution Circuit | 3rd Party | Kite | 57 | 1938 | 37.1041 | -120.2768 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0049969 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828655 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319515430679 | 20230321 | 1733 | 20230322 | 1332 | 2056314 | 1199 | Transformer only | Animal | Other | 1 | 1199 | 37.3423 | -120.6678 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049980 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828667 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | TRANSFORMER | 321313315903 | 20230321 | 1800 | 20230321 | 1902 | 2059419 | 62 | Transformer only | Vegetation | Tree - fell into line | 6 | 372 | 36.936 | -120.0516 | Yes | Overcast;32-90 F | Secondary | Normal | 23-0049992 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828679 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 6196 | 20230321 | 1822 | 20230322 | 1209 | 2059831 | 1067 | Distribution Circuit | Equipment Failure/Involved | Overhead | 186 | 15947 | 37.2936 | -119.6478 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0050001 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828686 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 10855 | 20230321 | 1833 | 20230321 | 1900 | 2059954 | 27 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 297 | 36.9984 | -120.8643 | Yes | Overcast;32-90 F |  |  | 23-0050069 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1828747 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318567547722 | 20230321 | 1859 | 20230322 | 1301 | 2058306 | 1082 | Transformer only | Environmental/External | Lightning | 3 | 3246 | 37.8097 | -120.9969 | Yes | Overcast-Drizzle;32-90 F | Transformer | Burned/flashed | 23-0050054 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828732 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 320139236748 | 20230321 | 1904 | 20230322 | 1211 | 2059194 | 1027 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2054 | 37.5087 | -120.4527 | Yes | Overcast-Strong Winds;32-90 F | Secondary | Broken | 23-0050601 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1829124 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321947533830 | 20230321 | 1913 | 20230322 | 1251 | 2060263 | 1058 | Transformer only | Environmental/External | Lightning | 1 | 1058 | 37.4283 | -119.8314 | Yes | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050145 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828808 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | JUMPER | BURNED OPEN JUMPER AT 20997 | 20230321 | 1924 | 20230321 | 2236 | 2060331 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 11904 | 37.8867 | -120.9586 | Yes | Overcast-Heavy Rain;32-90 F | Jumper | Burned Open | 23-0050230 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1828890 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318726047570 | 20230321 | 1959 | 20230321 | 2100 | 2060523 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 122 | 37.8056 | -120.9419 | Yes | Overcast-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050121 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828789 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | OCB | 1701/2 | 20230322 | 20 | 20230322 | 1518 | 2061383 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 2324 | 137093 | 37.7729 | -120.8261 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050273 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1828934 | 0 | EPSS Ckt | N | 2023 | A B GRD
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318657550485 | 20230322 | 359 | 20230322 | 1553 | 2061786 | 714 | Transformer only | Environmental/External | Lightning | 1 | 714 | 37.8855 | -120.9664 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 23-0050435 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829044 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | S1301 | 20230322 | 847 | 20230322 | 935 | 2061989 | 48 | Distribution Circuit | Animal | Squirrel | 35 | 1680 | 37.9907 | -120.4117 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0050425 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829036 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | TRANSFORMER | 321133813653 | 20230322 | 909 | 20230322 | 950 | 2062062 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 82 | 36.8749 | -120.1128 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0050412 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1829029 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318657550487 | 20230322 | 919 | 20230322 | 1627 | 2062090 | 428 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 428 | 37.8859 | -120.9664 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0050429 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829039 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321598534415 | 20230322 | 1035 | 20230322 | 1606 | 2062289 | 331 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 331 | 37.4437 | -119.9501 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050625 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829138 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | JUMPER | 7032 | 20230322 | 1159 | 20230322 | 1419 | 2062520 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 4620 | 37.2662 | -120.6561 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0050646 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829152 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | TRANSFORMER | 319138019480 | 20230322 | 1500 | 20230323 | 820 | 2063073 | 1040 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1040 | 37.0343 | -120.796 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050914 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829317 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | OCB | 1704/2 | 20230322 | 1647 | 20230322 | 2027 | 2063210 | 220 | Distribution Circuit | Animal | Other | 3345 | 714515 | 37.9035 | -120.4971 | No | Overcast;32-90 F | Insulator | Burned/flashed | 23-0050908 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1829314 | 0 | EPSS Ckt | N | 2023 | A&B TIME
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 10776 | 20230323 | 223 | 20230323 | 328 | 2063999 | 65 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 67 | 4329 | 37.207 | -119.6803 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0051137 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829514 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 21066 | 20230323 | 736 | 20230323 | 856 | 2064121 | 80 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 240 | 37.5067 | -120.4212 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0051193 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829534 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | JUMPER | FB 4 SPANS W/OF MTR#1010129217 | 20230323 | 738 | 20230324 | 1342 | 2064108 | 1804 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1804 | 37.8986 | -120.9397 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0051172 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1829526 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318565728360 | 20230323 | 805 | 20230323 | 1812 | 2064156 | 607 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 607 | 37.2778 | -120.9942 | No | Clear;32-90 F | Fuse | Broken | 23-0051574 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829742 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | 318564127531 | 20230323 | 813 | 20230323 | 1110 | 2064135 | 177 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 177 | 37.255 | -120.9943 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0051200 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829536 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321690233254 | 20230323 | 910 | 20230323 | 1616 | 2064276 | 426 | Transformer only | Environmental/External | Lightning | 2 | 852 | 37.4132 | -119.9185 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0051329 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829611 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 983543 | 20230323 | 1036 | 20230323 | 1203 | 2064447 | 87 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 1218 | 37.3176 | -120.3606 | No | Overcast-Rain;32-90 F |  |  | 23-0051358 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1829628 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318720047570 | 20230323 | 1235 | 20230323 | 1917 | 2064672 | 402 | Transformer only | Environmental/External | Lightning | 1 | 402 | 37.8055 | -120.9438 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0051411 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829658 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 10776 | 20230323 | 1325 | 20230323 | 1440 | 2064759 | 75 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 67 | 4995 | 37.207 | -119.6803 | No | Overcast-Rain;32-90 F |  |  | 23-0051462 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829683 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 3337 | 20230323 | 1521 | 20230323 | 1745 | 2064970 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1728 | 37.8577 | -120.9055 | No | Clear;32-90 F |  |  | 23-0051563 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1829735 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317530435792 | 20230323 | 1730 | 20230323 | 2332 | 2065181 | 362 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 362 | 37.4793 | -121.3521 | No | Clear;32-90 F | Transformer (OH) |  | 23-0051566 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829737 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20230323 | 1929 | 20230323 | 2053 | 2065324 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 144 | 12096 | 37.0679 | -119.9091 | No | Partly Cloudy;32-90 F |  |  | 23-0051622 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1829776 | 0 | EPSS Ckt | N | 2023 | A AND C PHASE
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | RECLOSER | 11500 | 20230324 | 657 | 20230324 | 1458 | 2065596 | 397 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1257 | 131631 | 37.3859 | -120.7258 | No | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051720 | OH | Sus | 45707949 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1829842 | 0 | Non-EPSS | N | 2023 | SGF
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 1590 | 20230324 | 758 | 20230324 | 857 | 2065645 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 59 | 36.9874 | -120.1044 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0051705 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1829833 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 322462130579 | 20230324 | 958 | 20230324 | 1109 | 2065814 | 71 | Transformer only | Equipment Failure/Involved | Underground | 2 | 142 | 37.3368 | -119.654 | No | Clear;32-90 F | Secondary | Broken | 23-0051779 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1829867 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | RECLOSER | 75582 | 20230324 | 1500 | 20230324 | 2304 | 2066261 | 484 | Distribution Circuit | 3rd Party | Vehicle | 588 | 58975 | 37.7621 | -120.9958 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051966 | OH | Sus | 31640444 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1829948 | 0 | Non-EPSS | N | 2023 | AC & GRD
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320683653938 | 20230325 | 121 | 20230325 | 757 | 2066697 | 396 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 792 | 37.981 | -120.2639 | No | Overcast;32-90 F | Transformer | Broken | 23-0052420 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830381 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | SECTIONALIZER | 11240 | 20230325 | 159 | 20230325 | 507 | 2066701 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 8648 | 36.785 | -120.3741 | No | Partly Cloudy;32-90 F |  |  | 23-0052422 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1830384 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L879 | 20230325 | 644 | 20230325 | 854 | 2066751 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1690 | 38.0394 | -120.3454 | No | Partly Cloudy;Below 32 F |  |  | 23-0052451 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1830409 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321529312759 | 20230325 | 1423 | 20230325 | 2204 | 2067098 | 461 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 922 | 36.849 | -119.9786 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052528 | OH | Sus | 31640357 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830479 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320946949936 | 20230325 | 1612 | 20230325 | 1825 | 2067175 | 133 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 399 | 37.8708 | -120.172 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0052543 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830492 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 21237 | 20230325 | 1727 | 20230325 | 2029 | 2067204 | 182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 897 | 37.7186 | -120.8667 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052537 | OH | Sus | 31640451 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1830486 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | RECLOSER | 11680 | 20230326 | 125 | 20230326 | 1015 | 2067448 | 530 | Distribution Circuit | Equipment Failure/Involved | Overhead | 557 | 168526 | 37.0982 | -120.2011 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052621 | OH | Sus | 45709061 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1830563 | 0 | Non-EPSS | N | 2023 | A&C PHASE
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 21581 | 20230326 | 643 | 20230326 | 1347 | 2067483 | 424 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 3392 | 36.9193 | -119.7647 | No | Clear;32-90 F |  |  | 23-0052671 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1830613 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 5519 | 20230326 | 839 | 20230326 | 857 | 2067531 | 18 | Distribution Circuit | Company Initiated | Return Circuit Normal | 120 | 2160 | 37.1415 | -119.6791 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037696 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | Yes | No | 1830580 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 20923 | 20230327 | 717 | 20230327 | 758 | 2068201 | 41 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 140 | 5740 | 37.728 | -120.9405 | No | Clear;32-90 F |  |  | 23-0052793 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1830709 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318715944738 | 20230327 | 823 | 20230327 | 1200 | 2068286 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 868 | 37.728 | -120.9447 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052832 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830744 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 321962615998 | 20230327 | 825 | 20230327 | 939 | 2068289 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 74 | 36.9373 | -119.8308 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0052853 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830768 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 319095847580 | 20230327 | 922 | 20230327 | 1354 | 2068417 | 272 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 272 | 37.8062 | -120.8137 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052886 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830785 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319375532802 | 20230327 | 1143 | 20230327 | 1412 | 2068682 | 149 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 298 | 37.4004 | -120.7155 | No | Clear;32-90 F |  |  | 23-0052960 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830814 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321460513071 | 20230327 | 1211 | 20230327 | 1323 | 2068723 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 72 | 36.8577 | -120.001 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0053003 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830832 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7025 | 20230327 | 1445 | 20230328 | 1215 | 2068958 | 1290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 3762 | 37.3456 | -120.6454 | No | Clear;32-90 F | Jumper | Broken | 23-0053076 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1830860 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRANSFORMER | 320552822352 | 20230327 | 1556 | 20230328 | 1148 | 2068965 | 1192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1192 | 37.1139 | -120.311 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0053091 | OH | Sus | 35434179 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830870 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 778665 | 20230327 | 1826 | 20230328 | 1025 | 2069257 | 959 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 8631 | 37.2299 | -120.7025 | No | Partly Cloudy;32-90 F |  |  | 23-0053396 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831086 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | SWITCH | 957737 | 20230328 | 1223 | 20230328 | 1535 | 2070531 | 192 | Distribution Circuit | 3rd Party | Vehicle | 14 | 2688 | 36.8459 | -120.1103 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0053553 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1831181 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2447 | 20230328 | 1329 | 20230328 | 1409 | 2070659 | 40 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 102 | 4080 | 38.0531 | -120.2027 | No | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0053650 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831233 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 78277 | 20230328 | 1330 | 20230328 | 1503 | 2070669 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 10974 | 37.9599 | -120.4517 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0053721 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831276 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20230328 | 1331 | 20230328 | 1710 | 2070672 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 367 | 41639 | 37.9754 | -120.4464 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0053641 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831228 | 0 | EPSS Ckt | N | 2023 | A&C
YOSEMITE | YOSEMITE | GALLO-1101 | 254901101 | TRANSFORMER | 319102631775 | 20230328 | 1345 | 20230328 | 1500 | 2070711 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 75 | 37.371 | -120.8096 | No | Overcast;32-90 F | Jumper | Broken | 23-0053631 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831218 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 21066 | 20230328 | 1355 | 20230328 | 1751 | 2071017 | 236 | Distribution Circuit | Animal | Other | 9 | 2124 | 37.5067 | -120.4212 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer (OH) | Normal | 23-0053822 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831331 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 823548 | 20230328 | 1401 | 20230328 | 1506 | 2070761 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 841 | 54665 | 38.0441 | -120.248 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0053692 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831260 | 0 | EPSS Ckt | N | 2023 | B&C INSTANT
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230328 | 1413 | 20230328 | 1441 | 2070780 | 28 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 259 | 7252 | 37.0552 | -120.0295 | No | Overcast;32-90 F |  |  | 23-0053709 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831271 | 0 | EPSS Ckt | N | 2023 | AC
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 48691 | 20230328 | 1418 | 20230328 | 2243 | 2070801 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 37370 | 37.991 | -120.2788 | No | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053777 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1831298 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | JUMPER | OJS 1 S/OF CGC 415950247590 | 20230328 | 1454 | 20230328 | 1840 | 2070854 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 678 | 36.6325 | -120.3812 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 23-0053726 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1831277 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | 20323 | 20230328 | 1512 | 20230328 | 1852 | 2071036 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 5576 | 38.144 | -120.0646 | No | Overcast-Snow-Strong Winds;Below 32 F |  |  | 23-0053885 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831368 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321501919934 | 20230328 | 1535 | 20230328 | 1751 | 2070947 | 136 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 272 | 37.0468 | -119.9866 | No | Rain-Overcast;32-90 F |  |  | 23-0053774 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1831297 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | KERCKHOFF-1101 | 252561101 | FUSE | 10233 | 20230328 | 1741 | 20230328 | 1847 | 2071211 | 66 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 330 | 37.1021 | -119.5773 | No | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken | 23-0053820 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1831329 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 12315 | 20230328 | 1755 | 20230329 | 1033 | 2071334 | 998 | Distribution Circuit | Vegetation | Other ground vegetation | 3 | 2994 | 36.8798 | -120.2303 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 23-0053982 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831460 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 847947 | 20230328 | 1756 | 20230329 | 1600 | 2071320 | 1324 | Distribution Circuit | Animal | Bird found | 4 | 4606 | 36.9143 | -120.3183 | No | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 23-0054327 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831616 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 6504 | 20230328 | 1809 | 20230328 | 1930 | 2071382 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 4860 | 36.9531 | -120.0861 | No | Overcast-Rain;32-90 F |  |  | 23-0053884 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831367 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 23043 | 20230328 | 2032 | 20230328 | 2140 | 2072040 | 68 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 204 | 37.0729 | -120.4735 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0053928 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831409 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 979289 | 20230328 | 2217 | 20230328 | 2355 | 2072141 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 196 | 36.8873 | -120.3139 | No | Overcast-Drizzle;32-90 F |  |  | 23-0053976 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831454 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 5502 | 20230328 | 2219 | 20230329 | 915 | 2072150 | 656 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 81 | 53136 | 37.2961 | -119.5213 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0054110 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831529 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 559473 | 20230328 | 2325 | 20230329 | 1130 | 2072174 | 725 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 725 | 36.8874 | -120.3096 | No | Overcast-Drizzle;32-90 F |  |  | 23-0053973 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831450 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | S21255 | 20230328 | 2339 | 20230329 | 750 | 2072184 | 491 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1473 | 37.7448 | -120.849 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Normal | 23-0053979 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831456 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | FUSE | 267963 | 20230329 | 1324 | 20230329 | 1658 | 2073111 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 214 | 37.0327 | -120.3194 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054524 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831682 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 6504 | 20230329 | 1334 | 20230329 | 1430 | 2073135 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 3360 | 36.9531 | -120.0861 | No | Partly Cloudy;32-90 F |  |  | 23-0054443 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831661 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | FUSE | 24071 | 20230329 | 1400 | 20230329 | 1620 | 2073474 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 140 | 36.5632 | -120.461 | No | Overcast-Drizzle;32-90 F |  |  | 23-0054569 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831697 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 194413 | 20230329 | 1504 | 20230329 | 1614 | 2073331 | 70 | Distribution Circuit | Animal | Bird found | 1 | 70 | 36.8658 | -120.0336 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Normal | 23-0054554 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831694 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 318339330456 | 20230329 | 1527 | 20230330 | 728 | 2073799 | 961 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 961 | 37.3322 | -121.0493 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0054711 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831800 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 26922 | 20230329 | 1530 | 20230329 | 2150 | 2073415 | 380 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 7980 | 37.3473 | -121.0359 | No | Clear;32-90 F |  |  | 23-0054646 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831747 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 318405530236 | 20230329 | 1530 | 20230330 | 729 | 2073800 | 959 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 959 | 37.3296 | -121.0493 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0054712 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831801 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | FUSE | 25547 | 20230329 | 1558 | 20230330 | 741 | 2073457 | 943 | Distribution Circuit | Environmental/External | Lightning | 8 | 5711 | 37.3165 | -121.0493 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054614 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831718 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 318931719067 | 20230329 | 1646 | 20230329 | 2208 | 2073507 | 322 | Transformer only | 3rd Party | Vehicle | 2 | 644 | 37.0226 | -120.8664 | No | Overcast;32-90 F | Pole-Wood | On Ground | 23-0054615 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831719 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | TRANSFORMER | 318405429807 | 20230329 | 1654 | 20230330 | 124 | 2073511 | 510 | Transformer only | Environmental/External | Lightning | 2 | 1020 | 37.3175 | -121.0493 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054619 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831723 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319657229740 | 20230329 | 1704 | 20230330 | 815 | 2073681 | 911 | Transformer only | Environmental/External | Lightning | 1 | 911 | 37.3165 | -120.6191 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054715 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831804 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 69153 | 20230329 | 1725 | 20230329 | 2250 | 2073735 | 325 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 650 | 37.3603 | -120.6728 | No | Overcast;32-90 F |  |  | 23-0054667 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831762 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320177229524 | 20230329 | 1726 | 20230330 | 1441 | 2073543 | 1275 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 5100 | 37.3113 | -120.4388 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 23-0054658 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831754 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | RECLOSER | 783470 | 20230329 | 1729 | 20230329 | 2206 | 2073541 | 277 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 6648 | 37.3602 | -120.6695 | No | Overcast;32-90 F |  |  | 23-0054607 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1831712 | 0 | Non-EPSS | N | 2023 | MANUAL OPEN
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7026 | 20230329 | 1732 | 20230329 | 2330 | 2073545 | 358 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3938 | 37.3023 | -120.6448 | No | Overcast-Rain;32-90 F |  |  | 23-0054709 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831798 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319539531222 | 20230329 | 1822 | 20230330 | 1100 | 2073586 | 998 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 998 | 37.3573 | -120.6592 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054707 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831796 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | RECLOSER | 10960 | 20230329 | 1916 | 20230329 | 2335 | 2073655 | 259 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3185 | 95739 | 37.3307 | -120.4693 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0054621 | OH | Sus | 31641010 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1831740 | 0 | Non-EPSS | N | 2023 | MANUAL OPEN
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319536531321 | 20230329 | 1934 | 20230330 | 903 | 2073664 | 809 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 809 | 37.3603 | -120.66 | No | Overcast-Fog;32-90 F |  |  | 23-0054710 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831799 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 5841 | 20230329 | 1948 | 20230329 | 2128 | 2073677 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 900 | 37.7762 | -120.7898 | No | Clear;32-90 F |  |  | 23-0054669 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831763 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 76694 | 20230329 | 2203 | 20230330 | 16 | 2073757 | 133 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 4389 | 37.7405 | -120.1279 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0054700 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831790 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | RECLOSER | 1584 | 20230329 | 2220 | 20230330 | 12 | 2073769 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 304 | 32888 | 37.3316 | -121.0264 | No | Clear;32-90 F | Jumper | Broken | 23-0054702 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831792 | 0 | Non-EPSS | N | 2023 | A PHASE & GRD
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4597 | 20230329 | 2233 | 20230330 | 114 | 2073818 | 161 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 19 | 3059 | 37.7329 | -120.0816 | No | Overcast-Fog-Snow;32-90 F |  |  | 23-0054717 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831806 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 20230329 | 2352 | 20230330 | 301 | 2073798 | 189 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 36 | 6804 | 37.5512 | -119.9231 | No | Overcast-Fog;32-90 F |  |  | 23-0054725 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831813 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 767890 | 20230330 | 19 | 20230330 | 238 | 2073806 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1238 | 163689 | 38.0568 | -120.203 | No | Overcast-Fog;Below 32 F |  |  | 23-0054716 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831805 | 0 | EPSS Ckt | N | 2023 | GRD & TIME OC TARGETS
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | S2243 | 20230330 | 31 | 20230330 | 249 | 2073814 | 138 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 241 | 33258 | 38.0383 | -120.2477 | No | Overcast-Fog;Below 32 F |  |  | 23-0054724 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831812 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 27337 | 20230330 | 108 | 20230330 | 418 | 2073824 | 190 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 1710 | 37.8143 | -120.0619 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0054728 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831816 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 13485 | 20230330 | 227 | 20230330 | 1355 | 2073837 | 688 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 916 | 37.5335 | -120.0516 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Deteriorated | 23-0054731 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831819 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 20230330 | 347 | 20230330 | 1251 | 2073843 | 544 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 36 | 19584 | 37.5512 | -119.9231 | No | Overcast-Fog;32-90 F |  |  | 23-0055016 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831969 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4601 | 20230330 | 447 | 20230330 | 1614 | 2073861 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 23358 | 37.757 | -120.1145 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0055186 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1832008 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 2272 | 20230330 | 713 | 20230330 | 1154 | 2073885 | 275 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 30 | 8250 | 37.4915 | -119.8272 | No | Overcast;32-90 F |  |  | 23-0054972 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831953 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 9590 | 20230330 | 714 | 20230330 | 1501 | 2073888 | 467 | Distribution Circuit | Environmental/External | Ice or snow | 523 | 77481 | 37.4593 | -119.8997 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken | 23-0054760 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831828 | 0 | EPSS Ckt | N | 2023 | B & GRD
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 22075 | 20230330 | 746 | 20230330 | 1018 | 2073937 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 13224 | 37.4973 | -119.8338 | No | Overcast-Fog;32-90 F |  |  | 23-0054891 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831918 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | RECLOSER | 661820 | 20230330 | 839 | 20230330 | 1354 | 2074012 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 25917 | 37.1421 | -120.4949 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0054808 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1831858 | 0 | Non-EPSS | N | 2023 | B&GRD
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L883 | 20230330 | 859 | 20230330 | 1045 | 2074068 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2120 | 38.0449 | -120.3423 | No | Partly Cloudy;32-90 F |  |  | 23-0054889 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831917 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2485 | 20230330 | 902 | 20230330 | 940 | 2074050 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 3496 | 38.0519 | -120.2027 | No | Partly Cloudy;32-90 F |  |  | 23-0054857 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831895 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10070 | 20230330 | 903 | 20230330 | 1120 | 2073977 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 297 | 40689 | 37.5079 | -119.9962 | No | Overcast-Fog;32-90 F |  |  | 23-0054832 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831872 | 0 | EPSS Ckt | N | 2023 | B & GRD
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319509631522 | 20230330 | 925 | 20230330 | 1521 | 2074115 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 712 | 37.3657 | -120.6693 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Broken | 23-0055019 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831971 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319394628974 | 20230330 | 1024 | 20230330 | 1505 | 2074215 | 281 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 281 | 37.2953 | -120.7097 | No | Partly Cloudy;32-90 F |  |  | 23-0055141 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831995 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 953336 | 20230330 | 1029 | 20230330 | 1906 | 2074257 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 922 | 190072 | 38.0678 | -120.1869 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0054912 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1831930 | 0 | EPSS Ckt | N | 2023 | SGF
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 90550 | 20230330 | 1039 | 20230330 | 1322 | 2074285 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 7721 | 37.5151 | -120.052 | No | Overcast;32-90 F |  |  | 23-0054922 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831935 | 0 | EPSS Ckt | N | 2023 | A & GRD
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318282029365 | 20230330 | 1550 | 20230330 | 1615 | 2074565 | 25 | Transformer only | Animal | Other | 1 | 25 | 37.3051 | -121.0923 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0055168 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1832005 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | WIRE DOWN 1 SPAN W/O MTR 1010269803 | 20230330 | 1601 | 20230330 | 1930 | 2074649 | 209 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 418 | 37.7344 | -120.07 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0055219 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | Yes | Yes | 1832020 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | TRANSFORMER | 319331614217 | 20230330 | 1635 | 20230330 | 1705 | 2074297 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 90 | 36.8901 | -120.7298 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0055183 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1832006 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319536531321 | 20230330 | 1758 | 20230331 | 315 | 2074730 | 557 | Transformer only | Environmental/External | Lightning | 1 | 557 | 37.3603 | -120.66 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055238 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1832036 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 1834 | 20230330 | 2025 | 20230330 | 2041 | 2074819 | 16 | Distribution Circuit | Company Initiated | Coordination failure | 907 | 14512 | 37.948 | -120.4201 | No | Clear;32-90 F | Relay | Normal | 23-0055250 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1832040 | 0 | EPSS Ckt | N | 2023 | SGF
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319460031259 | 20230331 | 724 | 20230331 | 812 | 2075108 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 48 | 37.3582 | -120.6868 | No | Fog;32-90 F | Fuse | Broken | 23-0055373 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1832134 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 13336 | 20230331 | 752 | 20230331 | 850 | 2075130 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 58 | 37.4515 | -120.6253 | No | Fog;32-90 F |  |  | 23-0055413 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1832163 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319510020187 | 20230331 | 814 | 20230331 | 942 | 2075155 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 88 | 37.054 | -120.6691 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0055443 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1832189 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 20823 | 20230331 | 850 | 20230331 | 956 | 2075220 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 924 | 37.938 | -120.421 | No | Clear-Drizzle;32-90 F |  |  | 23-0055435 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1832183 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 320139236748 | 20230331 | 1455 | 20230331 | 1755 | 2075607 | 180 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 360 | 37.5087 | -120.4527 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0055630 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1832247 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | RECLOSER | 4220 | 20230331 | 1722 | 20230401 | 106 | 2075715 | 464 | Distribution Circuit | 3rd Party | Vehicle | 633 | 47672 | 37.4226 | -120.6127 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0055668 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1832265 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7952 | 20230331 | 2005 | 20230331 | 2219 | 2076232 | 134 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 19 | 2546 | 37.2665 | -120.6704 | No | Clear;32-90 F |  |  | 23-0055710 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1832309 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | 319682732304 | 20230401 | 654 | 20230401 | 1518 | 2076467 | 504 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 5544 | 37.3873 | -120.6101 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055821 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832414 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 19598 | 20230401 | 751 | 20230401 | 845 | 2076496 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 2700 | 37.948 | -120.3621 | No | Clear;32-90 F |  |  | 23-0055819 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832413 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | SWITCH | 749 | 20230401 | 1216 | 20230401 | 1338 | 2076706 | 82 | Distribution Circuit | 3rd Party | Vehicle | 108 | 8856 | 37.838 | -120.9237 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0055800 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1832464 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 8882 | 20230402 | 5 | 20230402 | 152 | 2077103 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1605 | 37.3005 | -120.8333 | No | Clear;32-90 F |  |  | 23-0055989 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832582 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 452601 | 20230402 | 742 | 20230402 | 901 | 2077284 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 79 | 37.5177 | -120.4469 | No | Clear;32-90 F |  |  | 23-0056005 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832601 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3518 | 20230402 | 937 | 20230402 | 1200 | 2077444 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3146 | 36.96 | -120.6581 | No | Partly Cloudy;32-90 F |  |  | 23-0056030 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832623 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 2984 | 20230402 | 1103 | 20230402 | 1522 | 2077540 | 259 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 518 | 37.1861 | -120.6235 | No | Partly Cloudy;32-90 F |  |  | 23-0056045 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832637 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | SWITCH | 5009 | 20230402 | 1120 | 20230402 | 1329 | 2077376 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1161 | 37.1382 | -120.2758 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0056025 | OH | Sus | 45713925 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1832619 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | RECLOSER | 5550 | 20230402 | 2219 | 20230403 | 437 | 2077712 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 271 | 18801 | 37.0838 | -120.2866 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0056090 | OH | Sus | 45714011 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1832682 | 0 | Non-EPSS | N | 2023 | A B C
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 6764 | 20230403 | 644 | 20230403 | 858 | 2077847 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 938 | 37.0101 | -120.147 | No | Clear;32-90 F |  |  | 23-0056198 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832761 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320898711782 | 20230403 | 806 | 20230403 | 1100 | 2077924 | 174 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 174 | 36.8222 | -120.1934 | No | Clear;32-90 F |  |  | 23-0056283 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1832839 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 100000001266 | 20230403 | 913 | 20230403 | 1413 | 2078051 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 300 | 36.9252 | -120.5004 | No | Clear;32-90 F | Fuse | Burned Open | 23-0056405 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832879 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | RECLOSER | 3650 | 20230403 | 1137 | 20230403 | 1534 | 2078256 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 9270 | 36.926 | -120.8187 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0056321 | OH | Sus | 31641285 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1832849 | 0 | EPSS Ckt | N | 2023 | B- GRD- SGF
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 4749 | 20230403 | 1312 | 20230403 | 1428 | 2078368 | 76 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 380 | 37.3946 | -120.0854 | No | Clear;32-90 F |  |  | 23-0056416 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832885 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321402717863 | 20230403 | 1333 | 20230403 | 1555 | 2078406 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 284 | 36.99 | -120.0203 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0056381 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832871 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | TRANSFORMER | 318374247493 | 20230403 | 1344 | 20230403 | 1442 | 2078423 | 58 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 58 | 37.803 | -121.0636 | No | Clear;32-90 F |  |  | 23-0056472 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1832915 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20687 | 20230403 | 1432 | 20230403 | 1619 | 2078517 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 856 | 37.7401 | -120.7918 | No | Clear;32-90 F |  |  | 23-0056502 | OH | Sus | 45714850 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832930 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | OCB | 1103/2 | 20230403 | 1438 | 20230403 | 2143 | 2078331 | 425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 850 | 37.0663 | -120.836 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0056432 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1832890 | 0 | Non-EPSS | N | 2023 | na
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 4749 | 20230403 | 1445 | 20230403 | 2236 | 2078699 | 471 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 2355 | 37.3946 | -120.0854 | No | Clear;32-90 F |  |  | 23-0056476 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832917 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318517029041 | 20230403 | 1520 | 20230403 | 1914 | 2078650 | 234 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 936 | 37.2966 | -121.0107 | No | Clear;32-90 F |  |  | 23-0056618 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1833002 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318751645868 | 20230403 | 1538 | 20230403 | 2350 | 2078720 | 492 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 984 | 37.7589 | -120.933 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0056574 | OH | Sus | 45714788 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1832974 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 11509 | 20230403 | 1557 | 20230403 | 1918 | 2078790 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 6030 | 37.3103 | -120.4445 | No | Clear;32-90 F |  |  | 23-0056616 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833000 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 482838 | 20230403 | 1600 | 20230403 | 1815 | 2078850 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1424 | 191889 | 37.5247 | -120.3293 | No | Clear;32-90 F |  |  | 23-0056498 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1832927 | 0 | EPSS Ckt | N | 2023 | A- B- INST
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | TRANSFORMER | 322054514728 | 20230403 | 1700 | 20230403 | 1915 | 2078985 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 540 | 36.9021 | -119.799 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0056617 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833001 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 7896 | 20230403 | 2116 | 20230403 | 2338 | 2079394 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1562 | 37.2099 | -120.4556 | No | Overcast-Drizzle;32-90 F |  |  | 23-0056701 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1833065 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | RECLOSER | 3160 | 20230403 | 2238 | 20230404 | 702 | 2079439 | 504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 34521 | 36.7225 | -120.3811 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0056697 | OH | Sus | 31641292 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1833061 | 0 | Non-EPSS | N | 2023 | C GRD
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 4621 | 20230404 | 112 | 20230404 | 428 | 2079474 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1438 | 37.2567 | -121.0971 | No | Clear;32-90 F |  |  | 23-0056710 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833075 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 426421 | 20230404 | 710 | 20230404 | 825 | 2079554 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 150 | 36.9229 | -119.849 | No | Clear;32-90 F |  |  | 23-0056793 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1833131 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 319017329681 | 20230404 | 830 | 20230404 | 902 | 2079575 | 32 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 32 | 37.3132 | -120.8389 | No | Clear;32-90 F |  |  | 23-0056822 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1833160 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 320692011470 | 20230404 | 938 | 20230404 | 1634 | 2079798 | 416 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 416 | 36.8143 | -120.2641 | No | Clear;32-90 F |  |  | 23-0056940 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1833225 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 319095847580 | 20230404 | 1225 | 20230404 | 2040 | 2079963 | 495 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 495 | 37.8062 | -120.8137 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0057101 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833261 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 4969 | 20230404 | 1342 | 20230404 | 1810 | 2080039 | 268 | Distribution Circuit | Vegetation | Tree - bark fell into line | 62 | 16616 | 37.4335 | -119.8958 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0057169 | OH | Sus | 45715581 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1833279 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 34123 | 20230404 | 1430 | 20230404 | 2148 | 2080088 | 423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 757 | 37.5366 | -120.603 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0057177 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833281 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | TRANSFORMER | 321265815404 | 20230404 | 1548 | 20230404 | 1825 | 2080060 | 157 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 157 | 36.9222 | -120.0677 | No | Clear;32-90 F | Jumper | Broken | 23-0057175 | OH | Sus | 45715663 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833280 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319184745430 | 20230404 | 1726 | 20230405 | 220 | 2080131 | 534 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 534 | 37.7473 | -120.7806 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0057199 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833288 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | RECLOSER | 335302 | 20230404 | 2139 | 20230405 | 554 | 2080322 | 495 | Distribution Circuit | 3rd Party | Vehicle | 449 | 82898 | 37.7547 | -120.8877 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0057222 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1833306 | 0 | Non-EPSS | N | 2023 | A C & GRD
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321773217202 | 20230404 | 2309 | 20230405 | 108 | 2080336 | 119 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 357 | 36.9707 | -119.8937 | No | Clear;32-90 F | Jumper | Broken | 23-0057240 | OH | Sus | 45715778 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833324 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 13165 | 20230405 | 340 | 20230405 | 513 | 2080362 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 341 | 37.0069 | -119.9917 | No | Clear;32-90 F |  |  | 23-0057248 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833333 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | RECLOSER | 5850 | 20230405 | 1133 | 20230405 | 1317 | 2080772 | 104 | Distribution Circuit | Company Initiated | Coordination failure | 956 | 99424 | 36.8513 | -120 | No | Clear;32-90 F | Recloser | Normal | 23-0057485 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833498 | 0 | Non-EPSS | N | 2023 | SGF
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | T0340 | 20230405 | 1455 | 20230405 | 1511 | 2080990 | 16 | Transformer only | Equipment Failure/Involved | Underground | 7 | 112 | 37.3724 | -120.6074 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0057638 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1833544 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321512034056 | 20230405 | 1710 | 20230406 | 930 | 2081094 | 980 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 980 | 37.4332 | -119.9797 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0057742 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833604 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4673 | 20230405 | 2000 | 20230405 | 2051 | 2081158 | 51 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 408 | 37.1857 | -120.6325 | No | Clear;32-90 F |  |  | 23-0057708 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1833571 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 3337 | 20230406 | 112 | 20230406 | 248 | 2081282 | 96 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 12 | 1152 | 37.8577 | -120.9055 | No | Clear;32-90 F |  |  | 23-0057748 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1833613 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318694447892 | 20230406 | 845 | 20230406 | 1750 | 2081457 | 545 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 545 | 37.8144 | -120.9527 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0057871 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833776 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 100000004939 | 20230406 | 859 | 20230406 | 1150 | 2081364 | 171 | Transformer only | Environmental/External | Lightning | 2 | 342 | 37.9458 | -120.8865 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0057836 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833721 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321599235120 | 20230406 | 1334 | 20230406 | 1401 | 2081876 | 27 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 81 | 37.4617 | -119.9489 | No | Clear;32-90 F |  |  | 23-0058052 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833830 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321049718833 | 20230406 | 1429 | 20230406 | 1700 | 2081932 | 151 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 151 | 37.0168 | -120.1414 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0058068 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833834 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 5817 | 20230406 | 1626 | 20230406 | 1925 | 2082040 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1790 | 37.0238 | -119.947 | No | Clear;32-90 F |  |  | 23-0058183 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1833869 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 26484 | 20230406 | 2233 | 20230407 | 105 | 2082191 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 304 | 37.821 | -120.6991 | No | Overcast;32-90 F |  |  | 23-0058277 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833965 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 24003 | 20230407 | 303 | 20230407 | 601 | 2082256 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 948 | 37.5054 | -120.0424 | No | Overcast;32-90 F |  |  | 23-0058291 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833980 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | TRANSFORMER | 415026650242 | 20230407 | 709 | 20230407 | 1256 | 2082443 | 347 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 347 | 36.7016 | -120.6975 | No | Overcast;32-90 F | Fuse | Broken | 23-0058549 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834093 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320624455170 | 20230407 | 749 | 20230407 | 1103 | 2082391 | 194 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 194 | 38.0149 | -120.284 | No | Overcast;32-90 F | Fuse | Broken | 23-0058382 | OH | Sus | 31641359 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834037 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 318508632190 | 20230407 | 829 | 20230407 | 1125 | 2082376 | 176 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 176 | 37.3832 | -121.0148 | No | Overcast;32-90 F |  |  | 23-0058359 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834014 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 24003 | 20230407 | 849 | 20230407 | 917 | 2082463 | 28 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 149 | 37.5054 | -120.0424 | No | Overcast;32-90 F |  |  | 23-0058390 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834041 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | RECLOSER | 3520 | 20230407 | 924 | 20230407 | 1730 | 2082515 | 486 | Distribution Circuit | 3rd Party | Vehicle | 94 | 2996 | 37.0547 | -120.5489 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0058396 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | Yes | No | 1834051 | 0 | Non-EPSS | N | 2023 | FORCE OUT
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319592134916 | 20230407 | 931 | 20230407 | 1036 | 2082526 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 65 | 37.4586 | -120.641 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0058443 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834069 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321823517659 | 20230407 | 1022 | 20230407 | 1521 | 2082567 | 299 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 299 | 36.9835 | -119.8762 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0058464 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834074 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | FUSE | 13048 | 20230407 | 1024 | 20230407 | 1604 | 2082536 | 340 | Distribution Circuit | 3rd Party | Vehicle | 20 | 6800 | 36.9816 | -120.038 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0058440 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834066 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319758337740 | 20230407 | 1218 | 20230407 | 1228 | 2082590 | 10 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 10 | 37.5365 | -120.5845 | No | Overcast;32-90 F | Transformer (OH) |  | 23-0058534 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834089 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | 21217 | 20230407 | 2040 | 20230407 | 2113 | 2082924 | 33 | Distribution Circuit | Animal | Bird found | 23 | 759 | 37.7383 | -120.8586 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0058700 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834135 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | L573 | 20230407 | 2249 | 20230408 | 1324 | 2082941 | 875 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 3500 | 38.0081 | -120.2639 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 23-0058717 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834158 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10315 | 20230408 | 622 | 20230408 | 820 | 2083032 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1888 | 37.4684 | -119.7375 | No | Clear;32-90 F |  |  | 23-0058740 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834185 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319877428680 | 20230408 | 818 | 20230408 | 1050 | 2083080 | 152 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 304 | 37.2881 | -120.5421 | No | Clear;32-90 F |  |  | 23-0058761 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1834220 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | TRANSFORMER | 321340117117 | 20230408 | 1404 | 20230408 | 2234 | 2083294 | 510 | Distribution Circuit | Animal | Bird found | 666 | 10980 | 36.9691 | -120.0419 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0058797 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834250 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 5675 | 20230409 | 631 | 20230409 | 936 | 2083544 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 6845 | 37.2321 | -119.7418 | No | Clear;32-90 F |  |  | 23-0058852 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834301 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 24856 | 20230409 | 1035 | 20230409 | 1052 | 2083640 | 17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 17 | 37.1567 | -120.4148 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0058863 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834312 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | 900759 | 20230409 | 1433 | 20230409 | 1520 | 2083727 | 47 | Distribution Circuit | 3rd Party | Vehicle | 1 | 47 | 37.8567 | -120.9466 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0058886 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834334 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 2381 | 20230409 | 1821 | 20230409 | 1937 | 2083861 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1444 | 37.8293 | -121.0249 | No | Clear;32-90 F |  |  | 23-0058899 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834348 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 11585 | 20230409 | 1830 | 20230409 | 1945 | 2083864 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 150 | 37.2051 | -120.2708 | No | Clear;32-90 F |  |  | 23-0058904 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834353 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318752521894 | 20230409 | 1935 | 20230410 | 330 | 2083925 | 475 | Transformer only | 3rd Party | Vehicle | 4 | 1900 | 37.1 | -120.9292 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0058905 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834355 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 2297 | 20230410 | 42 | 20230410 | 201 | 2083981 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 527 | 37.7123 | -120.6917 | No | Clear;32-90 F |  |  | 23-0058924 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834375 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 322230933342 | 20230410 | 503 | 20230410 | 1248 | 2084012 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 465 | 37.4131 | -119.7335 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059014 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834483 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 20829 | 20230410 | 612 | 20230410 | 710 | 2084036 | 58 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 102 | 5916 | 37.905 | -120.4131 | No | Clear;32-90 F |  |  | 23-0058938 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834388 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4601 | 20230410 | 617 | 20230410 | 2207 | 2084041 | 950 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 34 | 32300 | 37.757 | -120.1145 | No | Clear;32-90 F |  |  | 23-0059350 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834677 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318784319249 | 20230410 | 811 | 20230410 | 1920 | 2084118 | 669 | Transformer only | Animal | Other | 1 | 669 | 37.0272 | -120.9173 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059046 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834518 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 6335 | 20230410 | 857 | 20230410 | 1428 | 2084219 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1655 | 36.9534 | -119.7845 | No | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0059044 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1834515 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | TRANSFORMER | 415639947893 | 20230410 | 1004 | 20230410 | 1030 | 2084218 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 52 | 36.6396 | -120.4878 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0059082 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834542 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319552529014 | 20230410 | 1006 | 20230410 | 2345 | 2084112 | 819 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 819 | 37.2963 | -120.6558 | No | Clear;32-90 F |  |  | 23-0059058 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834522 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319537429020 | 20230410 | 1020 | 20230410 | 2345 | 2084359 | 805 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 805 | 37.2966 | -120.6599 | No | Clear;32-90 F |  |  | 23-0059070 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834534 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | FUSE 365009 | 20230410 | 1259 | 20230410 | 1401 | s1834600 | 62 | Distribution Circuit | Animal | Other | 2 | 124 | 37.1333 | -119.7186 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0059212 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834600 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 21045 | 20230410 | 1309 | 20230410 | 1832 | 2084544 | 323 | Distribution Circuit | 3rd Party | Vehicle | 72 | 10965 | 37.372 | -120.6774 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0059153 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1834586 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 320868049146 | 20230410 | 1328 | 20230410 | 1850 | 2084565 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 1802 | 37.8494 | -120.2014 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059223 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834606 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321737935613 | 20230410 | 1525 | 20230411 | 403 | 2084695 | 758 | Transformer only | Animal | Bird found | 2 | 1516 | 37.4752 | -119.9013 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0059384 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834694 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319511831390 | 20230410 | 1609 | 20230411 | 515 | 2084730 | 786 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1572 | 37.362 | -120.6685 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059351 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834678 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319486030281 | 20230410 | 1641 | 20230410 | 1730 | 2084679 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 147 | 37.3312 | -120.678 | No | Clear;32-90 F | Service conductor | Deteriorated | 23-0059262 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834627 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | TRANSFORMER | T0279 | 20230411 | 108 | 20230411 | 1311 | 2084978 | 723 | Transformer only | Equipment Failure/Involved | Underground | 32 | 23136 | 37.3166 | -120.4686 | No | Clear;32-90 F | Secondary | Burned/flashed | 23-0059382 | UG | Sus | 45726170 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834690 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320330113658 | 20230411 | 732 | 20230411 | 1125 | 2085046 | 233 | Transformer only | Animal | Other | 1 | 233 | 36.8752 | -120.3884 | No | Overcast;32-90 F | Transformer (OH) |  | 23-0059572 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834885 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318282029365 | 20230411 | 808 | 20230411 | 1519 | 2085086 | 431 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 431 | 37.3051 | -121.0923 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059519 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834857 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321799617739 | 20230411 | 816 | 20230411 | 909 | 2085108 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 53 | 36.9857 | -119.8843 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0059464 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834814 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1104 | 253401104 | FUSE | 83171 | 20230411 | 849 | 20230411 | 1010 | 2085195 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 108 | 36.72 | -120.5496 | No | Partly Cloudy;32-90 F |  |  | 23-0059511 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834853 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | TRANSFORMER | T1554 | 20230411 | 914 | 20230411 | 951 | 2085258 | 37 | Transformer only | Equipment Failure/Involved | Underground | 10 | 370 | 36.966 | -120.0912 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0059466 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834820 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 778665 | 20230411 | 1003 | 20230411 | 1250 | 2085335 | 167 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 1003 | 37.2299 | -120.7025 | No | Clear;32-90 F |  |  | 23-0059629 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834912 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | STEPDOWN | MIWOK_SD1 | 20230411 | 1004 | 20230411 | 1111 | s1834875 | 67 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 67 | 0 | 0 | No | Clear;32-90 F |  |  | 23-0059557 |  | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834875 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321241519157 | 20230411 | 1130 | 20230411 | 1323 | 2085570 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 226 | 37.0253 | -120.0761 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0059574 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834887 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320617054014 | 20230411 | 1405 | 20230411 | 1501 | 2085739 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 168 | 37.9842 | -120.2857 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0059721 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834928 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 993215 | 20230411 | 1422 | 20230411 | 1453 | 2085752 | 31 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 155 | 37.3459 | -120.6908 | No | Partly Cloudy;32-90 F |  |  | 23-0059727 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834929 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319952729204 | 20230411 | 1516 | 20230411 | 1553 | 2085775 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 296 | 37.3028 | -120.5157 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0059748 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834933 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | TRANSFORMER | 318387125038 | 20230411 | 1614 | 20230411 | 1725 | 2085704 | 71 | Transformer only | Animal | Other | 1 | 71 | 37.186 | -121.054 | No | Partly Cloudy;32-90 F | Transformer (OH) |  | 23-0059783 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834945 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230411 | 1759 | 20230411 | 1942 | 2085956 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 259 | 26677 | 37.0552 | -120.0295 | No | Partly Cloudy;32-90 F |  |  | 23-0059793 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834955 | 0 | EPSS Ckt | N | 2023 | C PH & GRD
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 2075 | 20230411 | 1837 | 20230412 | 253 | 2085985 | 496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 5456 | 37.2731 | -119.6892 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0059794 | OH | Sus | 31641978 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834958 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10240 | 20230412 | 619 | 20230412 | 845 | 2086162 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 469 | 68474 | 37.5251 | -119.9181 | No | Partly Cloudy;32-90 F |  |  | 23-0059871 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835022 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3757 | 20230412 | 706 | 20230412 | 922 | 2086187 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 454 | 36.9241 | -120.6889 | No | Clear;32-90 F | Fuse | Broken | 23-0060019 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835178 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230412 | 801 | 20230412 | 908 | 2086226 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 259 | 17353 | 37.0552 | -120.0295 | No | Clear;32-90 F |  |  | 23-0059990 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835137 | 0 | EPSS Ckt | N | 2023 | C & GRD
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | FUSE | 2341 | 20230412 | 853 | 20230412 | 930 | 2086290 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 111 | 36.9963 | -119.7174 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0059958 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1835074 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320509029753 | 20230412 | 917 | 20230412 | 928 | 2086369 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 11 | 37.3167 | -120.3247 | No | Clear;32-90 F | Fuse | Broken | 23-0060014 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835172 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318587346874 | 20230412 | 1241 | 20230412 | 1256 | 2086581 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 15 | 37.7863 | -120.99 | No | Clear;32-90 F | Fuse | Broken | 23-0060177 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835236 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | TRANSFORMER | 319067621928 | 20230412 | 1324 | 20230412 | 1411 | 2086628 | 47 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 94 | 37.1013 | -120.8213 | No | Clear;32-90 F |  |  | 23-0060237 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835252 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 142739 | 20230412 | 1418 | 20230412 | 1613 | 2086794 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 230 | 37.8865 | -120.8805 | No | Clear;32-90 F |  |  | 23-0060284 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835267 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | FUSE | 20555 | 20230412 | 1707 | 20230412 | 1854 | 2086987 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 357 | 37.8131 | -121.0525 | No | Clear;32-90 F | Fuse | Broken | 23-0060382 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835299 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20230412 | 1906 | 20230412 | 1951 | 2087088 | 45 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 145 | 6525 | 37.0679 | -119.9091 | No | Clear;32-90 F |  |  | 23-0060389 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835305 | 0 | EPSS Ckt | N | 2023 | B- GRD
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319299330887 | 20230412 | 2245 | 20230413 | 410 | 2087163 | 325 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 650 | 37.3473 | -120.7422 | No | Clear;32-90F |  |  | 23-0060441 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835348 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 13083 | 20230413 | 602 | 20230413 | 747 | 2087231 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 4305 | 36.9963 | -120.0847 | No | Clear;32-90F |  |  | 23-0060501 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835385 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | FUSE | 493933 | 20230413 | 644 | 20230413 | 842 | 2087255 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 394 | 37.0907 | -120.1302 | No | Clear;32-90 F |  |  | 23-0060534 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835453 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 319021729535 | 20230413 | 907 | 20230413 | 1225 | 2087470 | 198 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 198 | 37.3093 | -120.8378 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0060670 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835567 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 78031 | 20230413 | 912 | 20230413 | 1110 | 2087483 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 315 | 37.9145 | -120.4604 | No | Clear;32-90 F |  |  | 23-0060584 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835533 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | FUSE | 10852 | 20230413 | 1032 | 20230413 | 1122 | 2087588 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 133 | 36.994 | -120.837 | No | Clear;32-90 F | Fuse | Broken | 23-0060635 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835556 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | TRANSFORMER | 321344821798 | 20230413 | 1201 | 20230413 | 1508 | 2087671 | 187 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 187 | 37.0978 | -120.0407 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0060658 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835561 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | JUMPER | OJ @ FUCO 12145 | 20230413 | 2342 | 20230414 | 410 | 2088154 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1007 | 45604 | 37.091 | -121.0161 | No | Clear;32-90 F | Jumper | Burned Open | 23-0060939 | OH | Sus | 45729925 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1835694 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 7293 | 20230414 | 802 | 20230414 | 1006 | 2088323 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 868 | 37.541 | -119.9184 | No | Clear;32-90 F |  |  | 23-0061069 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835847 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 26374 | 20230414 | 824 | 20230414 | 1010 | 2088336 | 106 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 21 | 2226 | 38.0291 | -120.4066 | No | Clear;32-90 F |  |  | 23-0061066 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835842 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318403728487 | 20230414 | 916 | 20230414 | 1224 | 2088456 | 188 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 376 | 37.2811 | -121.0495 | No | Clear;32-90 F |  |  | 23-0061109 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1835871 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320200419958 | 20230414 | 1058 | 20230414 | 1249 | 2088576 | 111 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 222 | 37.048 | -120.4324 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0061164 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835891 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | TRANSFORMER | 318799848540 | 20230414 | 1115 | 20230414 | 1140 | 2088582 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 25 | 37.8321 | -120.9167 | No | Clear;32-90 F | Service conductor | Normal | 23-0061113 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1835873 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230414 | 1356 | 20230414 | 1445 | 2088770 | 48 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 259 | 12432 | 37.0552 | -120.0295 | No | Clear;32-90 F |  |  | 23-0061214 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835908 | 0 | EPSS Ckt | N | 2023 | GRD
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 25416 | 20230414 | 1406 | 20230414 | 1523 | 2088784 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2387 | 37.2946 | -119.5211 | No | Partly Cloudy;32-90 F |  |  | 23-0061220 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835910 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | TRANSFORMER | 415281051965 | 20230414 | 1509 | 20230414 | 2128 | 2088826 | 379 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 379 | 36.7495 | -120.6121 | No | Clear;32-90 F |  |  | 23-0061276 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1835932 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 20829 | 20230414 | 1908 | 20230414 | 2055 | 2088955 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 7280 | 37.905 | -120.4131 | No | Clear;32-90 F | Fuse | Broken | 23-0061274 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835930 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 3736 | 20230414 | 2009 | 20230415 | 930 | 2088971 | 801 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 8010 | 36.792 | -120.2592 | No | Clear;32-90 F |  |  | 23-0061289 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835946 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 731 | 20230415 | 219 | 20230415 | 501 | 2089017 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 486 | 37.8824 | -120.401 | No | Clear;32-90 F |  |  | 23-0061302 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835959 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 8895 | 20230415 | 515 | 20230415 | 1041 | 2089040 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2282 | 37.4039 | -120.6677 | No | Fog;32-90 F | Pole-Wood | Broken | 23-0061303 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1835960 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 6263 | 20230415 | 954 | 20230415 | 1138 | 2089190 | 104 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 61 | 6344 | 37.1678 | -119.7555 | No | Clear;32-90 F |  |  | 23-0061338 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836036 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 20617 | 20230415 | 1025 | 20230415 | 1415 | 2089204 | 230 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3910 | 37.9983 | -120.3154 | No | Clear;32-90 F |  |  | 23-0061371 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836055 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320966514666 | 20230415 | 1026 | 20230415 | 1258 | 2089205 | 152 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 152 | 36.9028 | -120.1701 | No | Clear;32-90 F | Fuse | Broken | 23-0061358 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836044 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | FUSE | 21093 | 20230415 | 1036 | 20230415 | 1733 | 2089211 | 417 | Distribution Circuit | 3rd Party | Vehicle | 23 | 9591 | 37.0181 | -120.3073 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0061335 | OH | Sus | 31642383 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1836033 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4675 | 20230415 | 1058 | 20230415 | 1438 | 2089214 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 880 | 37.1862 | -120.6536 | No | Clear;32-90 F |  |  | 23-0061375 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836059 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | RECLOSER | 12020 | 20230415 | 1121 | 20230415 | 1159 | 2089222 | 38 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 417 | 15846 | 37.2009 | -120.3249 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0061337 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836035 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | 319712018209 | 20230415 | 1236 | 20230415 | 1305 | 2089216 | 29 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 29 | 36.9995 | -120.5995 | No | Clear;32-90 F |  |  | 23-0061360 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1836046 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | TRANSFORMER | 321039012021 | 20230415 | 1538 | 20230415 | 1900 | 2089305 | 202 | Transformer only | Vegetation | Other ground vegetation | 1 | 202 | 36.8293 | -120.1463 | No | Clear;32-90 F | Jumper | Burned/flashed | 23-0061380 | OH | Sus | 45731681 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836064 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11625 | 20230415 | 1947 | 20230416 | 32 | 2089401 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 1584 | 37.2074 | -120.3248 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0061390 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836077 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRIP-SAVER | 596130 | 20230415 | 2211 | 20230415 | 2322 | 2089469 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 3905 | 37.4308 | -120.5411 | No | Clear;32-90 F |  |  | 23-0061420 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836111 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | FUSE | 19673 | 20230416 | 22 | 20230416 | 355 | 2089512 | 213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 213 | 36.9947 | -120.2781 | No | Clear;32-90 F | Fuse | Broken | 23-0061424 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836117 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 4562 | 20230416 | 610 | 20230416 | 937 | 2089528 | 207 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 73 | 15111 | 37.4515 | -119.8524 | No | Clear;32-90 F |  |  | 23-0061445 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836149 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | TRANSFORMER | 100000012702 | 20230416 | 1204 | 20230416 | 1332 | 2089667 | 88 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 88 | 37.1879 | -121.0683 | No | Clear;32-90 F |  |  | 23-0061464 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1836167 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | JUMPER | WIRE DOWN HOT AT CGC #321285317387 | 20230416 | 1730 | 20230417 | 250 | 2089768 | 560 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3175 | 100618 | 36.9761 | -120.0615 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0061493 | OH | Sus | 31642445 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | Yes | 1836181 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | L467 | 20230416 | 1902 | 20230416 | 2150 | 2089800 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 137 | 23016 | 37.8868 | -120.5956 | No | Clear;32-90 F |  |  | 23-0061504 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836194 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10315 | 20230416 | 1948 | 20230416 | 2131 | 2089806 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1648 | 37.4684 | -119.7375 | No | Clear;32-90 F |  |  | 23-0061502 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836192 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 3998 | 20230417 | 144 | 20230417 | 1542 | 2089924 | 838 | Distribution Circuit | 3rd Party | Vehicle | 23 | 16308 | 37.1836 | -120.9589 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0061528 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836220 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | RECLOSER | 11500 | 20230417 | 624 | 20230417 | 1043 | 2089944 | 259 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1190 | 99693 | 37.3859 | -120.7258 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0061545 | OH | Sus | 45732161 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1836241 | 0 | Non-EPSS | N | 2023 | SGF
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320208323193 | 20230417 | 831 | 20230417 | 1430 | 2090085 | 359 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 718 | 37.1376 | -120.4293 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0061665 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836412 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | FUSE | 10852 | 20230417 | 924 | 20230417 | 1235 | 2090229 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 510 | 36.994 | -120.837 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0061689 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836428 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | TRANSFORMER | 320271028675 | 20230417 | 927 | 20230417 | 1233 | 2090231 | 186 | Transformer only | 3rd Party | Customer Equipment | 1 | 186 | 37.2876 | -120.4064 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0061587 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836370 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6089 | 20230417 | 1146 | 20230417 | 2150 | 2090446 | 604 | Distribution Circuit | Equipment Failure/Involved | Underground | 145 | 5500 | 37.1219 | -119.8651 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 23-0061687 | UG | Sus | 31642407 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836426 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 19398 | 20230417 | 1447 | 20230417 | 1510 | 2090651 | 23 | Distribution Circuit | 3rd Party | Metallic Balloon | 17 | 391 | 37.3535 | -120.6163 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0061747 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836467 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | FUSE | 55511 | 20230417 | 1509 | 20230417 | 1743 | 2090676 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1848 | 36.988 | -120.3704 | No | Overcast;32-90 F |  |  | 23-0061812 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836492 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318356046795 | 20230417 | 1526 | 20230418 | 200 | 2090686 | 634 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1268 | 37.7836 | -121.07 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0061787 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836482 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321089116482 | 20230417 | 1534 | 20230417 | 1901 | 2090694 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 207 | 36.9526 | -120.1276 | No | Clear;32-90 F | Fuse | Broken | 23-0061822 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836503 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | FUSE | 6657 | 20230417 | 2017 | 20230417 | 2328 | 2090923 | 191 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 573 | 36.9688 | -120.1288 | No | Clear;32-90 F |  |  | 23-0061854 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836531 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 320130435214 | 20230418 | 756 | 20230418 | 820 | 2091060 | 24 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 24 | 37.4693 | -120.457 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0061912 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1836587 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 97147 | 20230418 | 849 | 20230418 | 946 | 2091365 | 57 | Distribution Circuit | 3rd Party | Vehicle | 1 | 57 | 37.3457 | -120.6124 | No | Clear;32-90 F | Anchor or Guy | Normal | 23-0061949 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836693 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318773430539 | 20230418 | 1145 | 20230418 | 1155 | 2091311 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 10 | 37.3355 | -120.924 | No | Clear;32-90 F | Fuse | Broken | 23-0062053 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836736 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1105 | 254101105 | TRANSFORMER | 320694622793 | 20230418 | 1156 | 20230418 | 1348 | 2091514 | 112 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1344 | 37.1259 | -120.2629 | No | Clear;32-90 F | Secondary | Broken | 23-0062104 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836759 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320650254220 | 20230418 | 1209 | 20230418 | 1615 | 2091511 | 246 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 492 | 37.9885 | -120.2751 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0062050 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836735 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320547513859 | 20230418 | 1308 | 20230418 | 1700 | 2091570 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 275 | 36.8804 | -120.3138 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0062172 | OH | Sus | 45735134 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836774 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 320555913571 | 20230418 | 1515 | 20230418 | 2058 | 2091598 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 343 | 36.8728 | -120.3097 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0062214 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836783 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 22749 | 20230418 | 2000 | 20230419 | 48 | 2091877 | 288 | Distribution Circuit | Animal | Bird found | 22 | 6336 | 38.001 | -120.2664 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0062275 | OH | Sus | 45735309 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1836828 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 97147 | 20230418 | 2019 | 20230419 | 103 | 2091882 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 284 | 37.3457 | -120.6124 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0062248 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1836804 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | RECLOSER | 10510 | 20230419 | 536 | 20230419 | 657 | 2091969 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 306 | 24786 | 37.3472 | -120.6112 | No | Fog;32-90 F |  |  | 23-0062292 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836841 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 320132024007 | 20230419 | 714 | 20230419 | 848 | 2091996 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 94 | 37.1604 | -120.4558 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0062360 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836949 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | SWITCH | 5995 | 20230419 | 841 | 20230419 | 1735 | 2092289 | 534 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 534 | 38.1039 | -120.1218 | No | Clear;32-90 F | Elbow | Burned/flashed | 23-0062444 | UG | Sus | 45735725 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1837031 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 6009 | 20230419 | 922 | 20230419 | 1318 | 2092418 | 236 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2046 | 37.0398 | -120.4736 | No | Clear;32-90 F |  |  | 23-0062548 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837058 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | S1949 | 20230419 | 927 | 20230419 | 1015 | 2092426 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 336 | 37.7326 | -120.8895 | No | Clear;32-90 F |  |  | 23-0062432 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837021 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 559149 | 20230419 | 1010 | 20230419 | 1805 | 2092484 | 475 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 475 | 37.5395 | -120.5323 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0062427 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1837018 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319143045195 | 20230419 | 1050 | 20230419 | 1810 | 2092523 | 440 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 880 | 37.7407 | -120.7975 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0062512 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837050 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320854549236 | 20230419 | 1323 | 20230420 | 10 | 2092621 | 647 | Transformer only | Vegetation | Tree - fell into line | 9 | 5823 | 37.852 | -120.2052 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0062562 | OH | Sus | 35438902 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837061 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | TRANSFORMER | 320510426397 | 20230419 | 1356 | 20230419 | 1459 | 2092649 | 63 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 63 | 37.2253 | -120.3249 | No | Clear;32-90 F |  |  | 23-0062620 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1837070 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321167119158 | 20230419 | 1529 | 20230419 | 2046 | 2092660 | 317 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 317 | 37.0255 | -120.1014 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0062652 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837077 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320263254397 | 20230420 | 0 | 20230420 | 233 | 2092853 | 153 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 918 | 37.9942 | -120.41 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0062754 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1837126 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 796291 | 20230420 | 543 | 20230420 | 659 | 2092874 | 76 | Distribution Circuit | Animal | Bird found | 136 | 10336 | 37.9509 | -120.3669 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0062790 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837135 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | OCB | 1708/2 | 20230420 | 717 | 20230420 | 1547 | s1837267 | 510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2235 | 204089 | 37.7729 | -120.8258 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0062795 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1837267 | 0 | EPSS Ckt | N | 2023 | A/B/C
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 10293 | 20230420 | 835 | 20230420 | 1023 | 2092990 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2484 | 37.3237 | -119.6037 | No | Clear;32-90 F |  |  | 23-0062878 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837223 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 11509 | 20230420 | 919 | 20230420 | 1002 | 2093041 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 1290 | 37.3103 | -120.4445 | No | Clear;32-90 F |  |  | 23-0062867 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837218 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | TRANSFORMER | T4497 | 20230420 | 1006 | 20230420 | 1145 | 2093063 | 99 | Transformer only | Equipment Failure/Involved | Underground | 2 | 198 | 36.7664 | -120.3836 | No | Clear;32-90 F | Fuse | Broken | 23-0062976 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837260 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 3698 | 20230420 | 1011 | 20230420 | 1041 | 2093069 | 30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 40 | 36.6884 | -120.4417 | No | Clear;32-90 F |  |  | 23-0062885 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837226 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | TRANSFORMER | 320369016875 | 20230420 | 1356 | 20230421 | 21 | 2093236 | 625 | Transformer only | 3rd Party | Vehicle | 1 | 625 | 36.9633 | -120.3741 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0063180 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1837292 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | MTR#T8191 | 20230420 | 1514 | 20230420 | 1845 | 2093401 | 211 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 633 | 37.8595 | -120.8911 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 23-0063223 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837310 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | RECLOSER | 10910 | 20230420 | 2002 | 20230421 | 359 | 2093413 | 477 | Distribution Circuit | Animal | Bird found | 126 | 18832 | 37.3609 | -120.5188 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0063229 | OH | Sus | 45737394 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1837314 | 0 | Non-EPSS | N | 2023 | B- GRD
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320830412023 | 20230420 | 2014 | 20230420 | 2135 | 2093415 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 81 | 36.8292 | -120.2175 | No | Clear;32-90 F | Fuse | Broken | 23-0063233 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837320 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 13344 | 20230421 | 144 | 20230421 | 320 | 2093457 | 96 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 288 | 37.4424 | -120.6304 | No | Clear;32-90 F |  |  | 23-0063260 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837350 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | RECLOSER | 90140 | 20230421 | 409 | 20230421 | 858 | 2093472 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 204 | 47145 | 37.8277 | -120.999 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0063262 | OH | Sus | 45737395 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1837352 | 0 | Non-EPSS | N | 2023 | C- GRD
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6574 | 20230421 | 414 | 20230421 | 521 | 2093473 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 402 | 36.8583 | -120.057 | No | Clear;32-90 F |  |  | 23-0063265 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837356 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 5675 | 20230421 | 601 | 20230421 | 722 | 2093482 | 81 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 37 | 2997 | 37.2321 | -119.7418 | No | Clear;32-90 F |  |  | 23-0063297 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837364 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321292112123 | 20230421 | 602 | 20230421 | 730 | 2093475 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 88 | 36.8332 | -120.06 | No | Clear;32-90 F | Jumper | Broken | 23-0063270 | OH | Sus | 45737581 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837357 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | TRANSFORMER | 415330851156 | 20230421 | 1055 | 20230421 | 1343 | 2093855 | 168 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 168 | 36.728 | -120.5942 | No | Clear;32-90 F | Fuse | Broken | 23-0063559 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837575 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | T2008 | 20230421 | 1327 | 20230421 | 2055 | 2093985 | 448 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 4928 | 36.9538 | -120.0866 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0063601 | UG | Sus | 35439193 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837589 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 11634 | 20230421 | 1338 | 20230421 | 1544 | 2094006 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 420 | 37.1854 | -120.3379 | No | Clear;32-90 F |  |  | 23-0063618 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837597 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318744245012 | 20230421 | 1443 | 20230421 | 1701 | 2094035 | 138 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 2484 | 37.7355 | -120.9351 | No | Clear;32-90 F | Jumper | Burned/flashed | 23-0063595 | OH | Sus | 31642865 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837587 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | TRANSFORMER | 320886316712 | 20230421 | 1508 | 20230421 | 1637 | 2094079 | 89 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 89 | 36.9591 | -120.1975 | No | Clear;32-90 F |  |  | 23-0063627 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1837602 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | T7378 | 20230421 | 1533 | 20230422 | 200 | 2094098 | 627 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1254 | 36.9314 | -120.25 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0063614 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837596 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 23099 | 20230421 | 1708 | 20230421 | 2301 | 2094187 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 13061 | 37.0472 | -120.6178 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0063644 | OH | Sus | 45738577 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | Yes | 1837612 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1116 | 252761116 | FUSE | 5845 | 20230421 | 1954 | 20230421 | 2037 | 2094308 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 179 | 7697 | 36.9242 | -120.045 | No | Clear;32-90 F |  |  | 23-0063650 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837620 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 5837 | 20230421 | 2026 | 20230421 | 2215 | 2094328 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1853 | 37.7578 | -121.0649 | No | Clear;32-90 F |  |  | 23-0063694 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837663 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | TRANSFORMER | 100000005906 | 20230421 | 2108 | 20230422 | 1120 | 2094215 | 852 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 852 | 36.5965 | -120.4606 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0063657 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837627 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319716232702 | 20230422 | 648 | 20230422 | 745 | 2094433 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 57 | 37.3983 | -120.5986 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0063722 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837698 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 21997 | 20230422 | 1019 | 20230422 | 1213 | 2094588 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1482 | 37.0179 | -120.411 | No | Partly Cloudy;32-90 F |  |  | 23-0063761 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837778 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319573027317 | 20230422 | 1054 | 20230422 | 1225 | 2094603 | 91 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 182 | 37.2499 | -120.647 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0063762 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837780 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 659827 | 20230422 | 1142 | 20230422 | 1955 | 2094624 | 493 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1972 | 37.154 | -120.2744 | No | Clear;32-90 F | Other | Broken | 23-0063767 | OH | Sus | 45738585 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837786 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 87125 | 20230422 | 1209 | 20230422 | 1506 | 2094638 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 236 | 37.1273 | -120.4595 | No | Clear;32-90 F |  |  | 23-0063774 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837792 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | RECLOSER | 3290 | 20230422 | 1955 | 20230423 | 858 | 2094816 | 783 | Distribution Circuit | 3rd Party | Vehicle | 347 | 72422 | 37.7466 | -120.8398 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0063795 | OH | Sus | 31643000 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1837809 | 0 | Non-EPSS | N | 2023 | A-B-C TIME
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | TRANSFORMER | 318757530260 | 20230423 | 435 | 20230423 | 933 | 2094957 | 298 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 298 | 37.3281 | -120.9279 | No | Clear;32-90 F | Fuse | Broken | 23-0063834 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837864 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6086 | 20230423 | 656 | 20230423 | 1213 | 2095037 | 317 | Distribution Circuit | Animal | Other | 1 | 211 | 37.1242 | -119.8975 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0063848 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837875 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20230423 | 659 | 20230423 | 831 | 2094930 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 145 | 13195 | 37.0679 | -119.9091 | No | Clear;32-90 F |  |  | 23-0063822 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837851 | 0 | EPSS Ckt | N | 2023 | B & GRD
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 6589 | 20230423 | 701 | 20230423 | 920 | 2094929 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2363 | 36.9527 | -120.1818 | No | Clear;32-90 F |  |  | 23-0063826 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837859 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 7948 | 20230423 | 847 | 20230423 | 1012 | 2094970 | 85 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 16 | 1361 | 37.3457 | -120.6563 | No | Clear;32-90 F |  |  | 23-0063838 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1837867 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 7948 | 20230423 | 1119 | 20230423 | 1212 | 2095020 | 53 | Distribution Circuit | 3rd Party | Metallic Balloon | 24 | 1272 | 37.3457 | -120.6563 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0063846 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837873 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | FUSE | 3752 | 20230423 | 2237 | 20230424 | 52 | 2095218 | 135 | Distribution Circuit | 3rd Party | Metallic Balloon | 53 | 7155 | 37.0984 | -120.747 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0063897 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837920 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 8515 | 20230424 | 107 | 20230424 | 225 | 2095229 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 624 | 37.793 | -120.96 | No | Clear;32-90 F |  |  | 23-0063901 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837923 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 77985 | 20230424 | 220 | 20230424 | 318 | 2095230 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 232 | 37.1418 | -120.4749 | No | Partly Cloudy;32-90 F |  |  | 23-0063903 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837925 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 19495 | 20230424 | 551 | 20230424 | 702 | 2095241 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 3621 | 37.4113 | -120.0898 | No | Partly Cloudy;32-90 F |  |  | 23-0063931 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837941 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 11507 | 20230424 | 609 | 20230424 | 708 | 2095249 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 649 | 37.4939 | -120.517 | No | Clear;32-90 F |  |  | 23-0063932 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1837944 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 13169 | 20230424 | 741 | 20230424 | 950 | 2095306 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 129 | 37.0635 | -119.9095 | No | Clear;32-90 F |  |  | 23-0064012 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838092 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | RECLOSER | 9090 | 20230424 | 857 | 20230424 | 1547 | 2095444 | 410 | Distribution Circuit | 3rd Party | Vehicle | 348 | 23729 | 37.096 | -120.9254 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0063984 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1838026 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 922015 | 20230424 | 922 | 20230424 | 1331 | 2095676 | 249 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 249 | 37.3366 | -119.5798 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0064085 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838128 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | RECLOSER | 9170 | 20230424 | 1024 | 20230424 | 1113 | 2095604 | 49 | Distribution Circuit | Vegetation | Tree - fell into line | 570 | 27930 | 37.732 | -120.9495 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0064038 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1838103 | 0 | Non-EPSS | N | 2023 | A & GRD
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322678830604 | 20230424 | 1101 | 20230424 | 1359 | 2095636 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 178 | 37.3388 | -119.5786 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0064108 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838145 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | OCB | 1704/2 | 20230424 | 1110 | 20230424 | 1200 | 2095643 | 50 | Distribution Circuit | Animal | Other | 3346 | 167300 | 37.9035 | -120.4971 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0064061 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1838118 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | L1123 | 20230424 | 1130 | 20230424 | 1326 | 2095663 | 116 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 17864 | 38.1975 | -120.0126 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0064131 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838156 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318398429582 | 20230424 | 1240 | 20230424 | 1628 | 2095750 | 228 | Transformer only | Environmental/External | Lightning | 1 | 228 | 37.3113 | -121.0519 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0064127 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838154 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | SWITCH | 3456 | 20230424 | 1555 | 20230424 | 1603 | -2095444 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 35 | 280 | 37.1219 | -120.9476 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0063984 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1838183 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | S1249 | 20230424 | 2344 | 20230425 | 115 | 2096121 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2246 | 37.7834 | -120.8622 | No | Clear;32-90 F |  |  | 23-0064298 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838231 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 20737 | 20230425 | 257 | 20230425 | 425 | 2096140 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 4050 | 37.8098 | -120.7212 | No | Clear;32-90 F |  |  | 23-0064302 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838235 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 22085 | 20230425 | 627 | 20230425 | 1933 | 2096216 | 786 | Distribution Circuit | 3rd Party | Vehicle | 1 | 786 | 37.4315 | -120.0988 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0064342 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838259 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 535839 | 20230425 | 644 | 20230425 | 930 | 2096217 | 166 | Distribution Circuit | 3rd Party | Vehicle | 4 | 664 | 37.3747 | -120.6682 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0064333 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838254 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | OCB | 2101/2 | 20230425 | 817 | 20230425 | 845 | 2096306 | 28 | Distribution Circuit | 3rd Party | Metallic Balloon | 406 | 11368 | 37.2731 | -120.4872 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0064354 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | No | No | 1838287 | 0 | Non-EPSS | N | 2023 | AB&GRD
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | RECLOSER | 90270 | 20230425 | 849 | 20230425 | 1420 | 2096364 | 331 | Distribution Circuit | 3rd Party | Metallic Balloon | 406 | 99110 | 37.2846 | -120.4869 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0064354 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838323 | 0 | Non-EPSS | N | 2023 | AC PH
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | T7378 | 20230425 | 1138 | 20230425 | 1304 | 2096626 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 172 | 36.9314 | -120.25 | No | Clear;32-90 F |  |  | 23-0064530 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838439 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 319125931250 | 20230425 | 1310 | 20230425 | 1616 | 2096748 | 186 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 186 | 37.3585 | -120.8012 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0064678 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838494 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321582115931 | 20230425 | 1451 | 20230425 | 1608 | 2096848 | 77 | Transformer only | Animal | Other | 1 | 77 | 36.9359 | -119.9605 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0064673 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838491 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | 6415 | 20230425 | 1542 | 20230426 | 123 | 2096895 | 581 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 18769 | 37.746 | -120.9081 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0064677 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838493 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | JUMPER | 5707BP | 20230425 | 1657 | 20230425 | 1813 | 2096974 | 76 | Distribution Circuit | Equipment Failure/Involved | Overhead | 248 | 18848 | 37.7731 | -120.9956 | No | Clear;32-90 F | Jumper | Burned Open | 23-0064695 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1838499 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | 321190116522 | 20230425 | 1839 | 20230425 | 1937 | 2097003 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 406 | 36.9535 | -120.094 | No | Clear;32-90 F | Fuse | Broken | 23-0064711 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1838510 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10372 | 20230426 | 33 | 20230426 | 154 | 2097122 | 81 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 5427 | 37.5222 | -119.9398 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0064746 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1838546 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | JUMPER | 6906 | 20230426 | 501 | 20230426 | 1032 | 2097135 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 4177 | 37.0971 | -120.2805 | No | Clear;32-90 F | Jumper | Burned Open | 23-0064768 | OH | Sus | 45741096 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1838562 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 472863 | 20230426 | 511 | 20230426 | 1000 | 2097136 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 578 | 37.8232 | -120.9056 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0064756 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838555 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 11893 | 20230426 | 1020 | 20230426 | 1306 | 2097373 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 166 | 36.8868 | -120.0016 | No | Clear;32-90 F | Jumper | Broken | 23-0064918 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1838725 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 5517 | 20230426 | 1124 | 20230426 | 1335 | 2097520 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3406 | 37.241 | -119.494 | No | Clear;32-90 F |  |  | 23-0065042 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838761 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | RECLOSER | 738194 | 20230426 | 1210 | 20230427 | 305 | 2097550 | 895 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 76075 | 36.7785 | -120.3907 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0064979 | OH | Sus | 45741961 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1838747 | 0 | Non-EPSS | N | 2023 | A&C PHASE
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 21045 | 20230426 | 1417 | 20230426 | 1509 | 2097669 | 52 | Distribution Circuit | 3rd Party | Vehicle | 73 | 3796 | 37.3721 | -120.6774 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0065123 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1838784 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1719 | 20230426 | 1701 | 20230426 | 1850 | 2097517 | 109 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1090 | 37.9038 | -120.3637 | No | Clear;32-90 F | Circuit Breaker | Normal | 23-0065173 | OH | Sus | 45741474 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1838796 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321595013545 | 20230427 | 840 | 20230427 | 1503 | 2098177 | 383 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 766 | 36.8706 | -119.9561 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0065619 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839053 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | TRANSFORMER | 321261817051 | 20230427 | 1539 | 20230427 | 1558 | 2098632 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 209 | 36.9677 | -120.0696 | No | Clear;Above 90 | Secondary | Broken | 23-0065678 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839065 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 319872524695 | 20230427 | 1604 | 20230427 | 2310 | 2098591 | 426 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 426 | 37.1784 | -120.5447 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0065709 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839074 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 24514 | 20230427 | 1625 | 20230428 | 247 | 2098832 | 622 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1244 | 36.7138 | -120.6923 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0065742 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839104 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 3612 | 20230427 | 1625 | 20230427 | 2012 | 2098830 | 225 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1350 | 36.7091 | -120.6938 | No | Clear;32-90 F |  |  | 23-0065744 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839106 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 4193 | 20230427 | 1701 | 20230427 | 1815 | 2098734 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 296 | 37.8311 | -120.8692 | No | Clear;32-90 F |  |  | 23-0065725 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839086 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | TRANSFORMER | 320157229932 | 20230427 | 2251 | 20230427 | 2315 | 2098900 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 120 | 37.3228 | -120.4458 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0065802 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839153 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | RECLOSER | 5450 | 20230427 | 2351 | 20230428 | 611 | 2098925 | 380 | Distribution Circuit | 3rd Party | Vehicle | 715 | 25002 | 37.0401 | -120.2544 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0065808 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1839154 | 0 | Non-EPSS | N | 2023 | ABC
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | JUMPER | VERT JUMPS 1 POLES E/OF CGC 318506624579 | 20230428 | 32 | 20230428 | 239 | 2098938 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 254 | 37.1738 | -121.0132 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0065813 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839158 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 6649 | 20230428 | 226 | 20230428 | 512 | 2098972 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1328 | 36.8509 | -119.9925 | No | Clear;32-90 F |  |  | 23-0065832 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839174 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | TRANSFORMER | T0913 | 20230428 | 350 | 20230428 | 510 | 2098979 | 80 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 1040 | 37.3504 | -120.5983 | No | Clear;32-90 F |  |  | 23-0065830 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1839172 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 6493 | 20230428 | 705 | 20230428 | 953 | 2099025 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 784 | 36.8354 | -120.2731 | No | Clear;32-90 F | Fuse | Burned Open | 23-0065947 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839289 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 7958 | 20230428 | 710 | 20230428 | 928 | 2099248 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 138 | 37.5399 | -120.3577 | No | Clear;32-90 F |  |  | 23-0065959 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839297 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | S255 | 20230428 | 1256 | 20230428 | 1336 | 2099410 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 143 | 5720 | 37.7699 | -120.9412 | No | Clear;32-90 F |  |  | 23-0066085 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839337 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | OTHER | J24573 TWD T8294 | 20230428 | 1336 | 20230428 | 1433 | 2099447 | 57 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 57 | 37.12 | -120.285 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0066078 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839338 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | TRANSFORMER | 320172428916 | 20230428 | 1352 | 20230429 | 110 | 2099473 | 678 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1356 | 37.2946 | -120.4401 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066122 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839351 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20230428 | 1517 | 20230428 | 1742 | 2099531 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1307 | 65621 | 38.0063 | -120.3474 | No | Clear;32-90 F |  |  | 23-0066135 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839354 | 0 | EPSS Ckt | Y | 2023 | A&B PHASE
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318710846388 | 20230428 | 1555 | 20230428 | 2051 | 2099563 | 296 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 296 | 37.773 | -120.9471 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0066156 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839367 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6379 | 20230428 | 1719 | 20230429 | 2100 | 2099639 | 1661 | Distribution Circuit | 3rd Party | Vehicle | 18 | 29898 | 36.8404 | -120.0557 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0066171 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1839379 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319741130365 | 20230428 | 1845 | 20230428 | 2220 | 2099683 | 215 | Transformer only | 3rd Party | Vehicle | 4 | 860 | 37.3342 | -120.589 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0066169 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839378 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 21145 | 20230428 | 1916 | 20230429 | 15 | 2099698 | 299 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 897 | 36.8931 | -119.9388 | No | Clear;32-90 F |  |  | 23-0066218 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839417 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318378026830 | 20230428 | 1921 | 20230429 | 38 | 2099700 | 317 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 317 | 37.2355 | -121.0579 | No | Partly Cloudy;32-90 F |  |  | 23-0066219 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1839418 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 11608 | 20230429 | 557 | 20230429 | 1019 | 2099848 | 262 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 12838 | 37.2328 | -120.3899 | No | Clear;32-90 F |  |  | 23-0066265 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839493 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 20018 | 20230429 | 750 | 20230429 | 901 | 2099903 | 71 | Distribution Circuit | Animal | Bird found | 4 | 284 | 37.1975 | -121.0127 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0066258 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839488 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320778256077 | 20230429 | 1122 | 20230429 | 1938 | 2100048 | 496 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 7936 | 38.0401 | -120.2309 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066305 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839526 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | OCB | 1105/2 | 20230429 | 1146 | 20230429 | 1158 | 2100054 | 12 | Distribution Circuit | 3rd Party | Vehicle | 921 | 11052 | 37.3635 | -120.7606 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0066288 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839515 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321697437852 | 20230429 | 1847 | 20230430 | 9 | s1839550 | 322 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 644 | 37.5384 | -119.9162 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066331 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839550 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 2493 | 20230429 | 1856 | 20230430 | 9 | s1839551 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1252 | 37.5386 | -119.9184 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0066332 | OH | Sus | 45745152 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839551 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1102 | 253881102 | RECLOSER | 605060 | 20230430 | 403 | 20230430 | 858 | 2100367 | 295 | Distribution Circuit | 3rd Party | Vehicle | 54 | 15107 | 37.3446 | -120.4691 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0066373 | OH | Sus | 31643720 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839592 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321679234380 | 20230430 | 818 | 20230430 | 1407 | 2100411 | 349 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1047 | 37.4447 | -119.9222 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066402 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839630 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318753817963 | 20230430 | 1032 | 20230430 | 1533 | 2100504 | 301 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 301 | 36.9926 | -120.927 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0066416 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839643 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | TRANSFORMER | 320132228881 | 20230430 | 1329 | 20230430 | 1840 | 2100582 | 311 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1866 | 37.2938 | -120.4543 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066448 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839665 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | TRANSFORMER | T1020 | 20230430 | 1958 | 20230501 | 210 | 2100907 | 372 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 5208 | 37.8179 | -120.8672 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066486 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1839695 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 4155 | 20230501 | 435 | 20230501 | 600 | 2101083 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 454 | 37.7913 | -120.7821 | No | Clear;32-90 F |  |  | 23-0066526 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1839734 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320130021988 | 20230501 | 723 | 20230501 | 939 | 2101167 | 136 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 136 | 37.1055 | -120.4553 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0066597 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1839851 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | JUMPER | OJ 1 SPAN NORTH OF CGC 322786227251 | 20230501 | 909 | 20230501 | 1246 | 2101238 | 217 | Distribution Circuit | Vegetation | Tree - grew into line | 3 | 651 | 37.2469 | -119.5441 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0066564 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1839779 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PINECREST 0401 | 163160401 | OTHER | WIRE DOWN 8/LD/SIDE CGC 321519161927 | 20230501 | 1147 | 20230502 | 1424 | 2101540 | 1597 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 49494 | 38.1996 | -119.9725 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0066656 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1839897 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | TRANSFORMER | 322091842979 | 20230501 | 1307 | 20230502 | 653 | 2101628 | 1066 | Transformer only | Vegetation | Tree - fell into line | 7 | 7462 | 37.6777 | -119.778 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0066771 | OH | Sus | 45745946 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1839941 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | S987 | 20230501 | 1412 | 20230501 | 1432 | 2101703 | 20 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 360 | 37.7774 | -120.8495 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0066735 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1839933 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 22993 | 20230501 | 1521 | 20230501 | 1652 | 2101798 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 243 | 37.1711 | -120.4919 | No | Overcast;32-90 F |  |  | 23-0066822 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1839956 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 196877 | 20230501 | 1708 | 20230502 | 10 | 2101902 | 422 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 844 | 36.8498 | -120.0007 | No | Clear;32-90 F |  |  | 23-0066876 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840006 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | SWITCH | 6356 | 20230501 | 1913 | 20230501 | 1931 | 2101962 | 18 | Distribution Circuit | Company Initiated | Return Circuit Normal | 18 | 324 | 37.7785 | -120.8471 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0066735 | UG | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1839965 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | TRANSFORMER | T8402 | 20230501 | 2119 | 20230502 | 157 | 2101994 | 278 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 4170 | 37.08 | -120.8334 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0066845 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1839977 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | FUSE | 6225 | 20230502 | 511 | 20230502 | 613 | 2102105 | 62 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 248 | 37.2408 | -120.9399 | No | Partly Cloudy;32-90 F |  |  | 23-0066891 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840024 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321274813856 | 20230502 | 635 | 20230502 | 909 | 2102137 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 462 | 36.8798 | -120.0659 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066987 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840127 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 6757 | 20230502 | 647 | 20230502 | 1043 | 2102153 | 236 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 1652 | 37.808 | -120.7218 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0066944 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840060 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | TRANSFORMER | 320701023955 | 20230502 | 944 | 20230502 | 1351 | 2102611 | 247 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 247 | 37.1579 | -120.2603 | No | Overcast-Drizzle;32-90 F |  |  | 23-0067206 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1840233 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | RECLOSER | 11820 | 20230502 | 1008 | 20230502 | 1624 | 2102663 | 376 | Distribution Circuit | 3rd Party | Vehicle | 106 | 15547 | 37.3643 | -120.5032 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0067038 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1840170 | 0 | Non-EPSS | N | 2023 | A PH & GRD
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 9572 | 20230502 | 1031 | 20230502 | 1220 | 2102681 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 327 | 37.086 | -120.9258 | No | Partly Cloudy;32-90 F |  |  | 23-0067135 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840210 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | TRANSFORMER | 319206919660 | 20230502 | 1110 | 20230502 | 2147 | 2102712 | 637 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 637 | 37.0393 | -120.7722 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0067404 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840292 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | TRANSFORMER | 318423022455 | 20230502 | 1152 | 20230503 | 119 | 2102988 | 807 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 807 | 37.1154 | -121.0438 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0067372 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840280 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1103 | 253671103 | FUSE | 965555 | 20230502 | 1214 | 20230502 | 1604 | 2102766 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 920 | 36.6337 | -120.639 | No | Clear;32-90 F | Other | Annealed | 23-0067205 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840232 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 9616 | 20230502 | 1239 | 20230502 | 2305 | 2102801 | 626 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 4382 | 36.7638 | -120.6031 | No | Overcast;32-90 F |  |  | 23-0067428 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840312 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318255031213 | 20230502 | 1258 | 20230503 | 833 | 2103061 | 1175 | Transformer only | Animal | Other | 1 | 1175 | 37.3557 | -121.101 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067323 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840254 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318254531130 | 20230502 | 1258 | 20230503 | 852 | 2103062 | 1194 | Transformer only | Environmental/External | Flood/Erosion | 1 | 1194 | 37.3535 | -121.1014 | No | Rain-Overcast;32-90 F | Fuse | Burned Open | 23-0067330 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1840258 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | RECLOSER | 9920 | 20230502 | 1318 | 20230502 | 2113 | 2102897 | 475 | Distribution Circuit | Equipment Failure/Involved | Overhead | 95 | 12281 | 37.1151 | -120.6384 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0067174 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1840223 | 0 | Non-EPSS | N | 2023 | A PHASE- GROUND
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | TRANSFORMER | 318453122975 | 20230502 | 1320 | 20230502 | 1741 | 2102900 | 261 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 261 | 37.1298 | -121.0314 | No | Partly Cloudy;32-90 F |  |  | 23-0067358 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1840270 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 25385 | 20230502 | 1532 | 20230502 | 1747 | 2103044 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1755 | 37.9453 | -120.8992 | No | Partly Cloudy-Lightning;32-90 F |  |  | 23-0067356 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840268 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | RECLOSER | 56332 | 20230502 | 1650 | 20230502 | 2346 | 2103110 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 310 | 31934 | 37.1858 | -120.494 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0067352 | OH | Sus | 31643891 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1840267 | 0 | Non-EPSS | N | 2023 | SGF
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 319823525970 | 20230502 | 1945 | 20230503 | 51 | 2103231 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 306 | 37.2136 | -120.5609 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067383 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840285 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322492030823 | 20230502 | 2235 | 20230503 | 507 | 2103255 | 392 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1176 | 37.3434 | -119.6433 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067444 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840321 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | OCB | 1111/2 | 20230502 | 2329 | 20230503 | 922 | 2103254 | 561 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2892 | 375960 | 36.9832 | -120.0334 | No | Partly Cloudy;32-90 F | Service conductor | Burned/flashed | 23-0067432 | OH | Sus | 45746803 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840315 | 0 | Non-EPSS | N | 2023 | FORCE OUT
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | S1625 | 20230503 | 220 | 20230503 | 357 | 2103302 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1164 | 37.982 | -120.3828 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0067448 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840325 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | SWITCH | PS0295 | 20230503 | 813 | 20230503 | 1438 | 2103416 | 385 | Distribution Circuit | 3rd Party | Other | 6 | 2310 | 37.1477 | -119.4623 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0067651 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1840512 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 127906 | 20230503 | 813 | 20230504 | 116 | 2103920 | 1023 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 7161 | 37.1556 | -119.4744 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0067748 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840550 | 0 | EPSS Ckt | N | 2023 | FORCE OUT
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320479923370 | 20230503 | 849 | 20230503 | 1115 | 2103371 | 146 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 146 | 37.1416 | -120.3365 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 23-0067550 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840449 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | TRANSFORMER | 415228552495 | 20230503 | 857 | 20230504 | 1017 | 2103491 | 1520 | Transformer only | Animal | Other | 2 | 3040 | 36.764 | -120.63 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0068092 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840821 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | 321037817021 | 20230503 | 928 | 20230503 | 1125 | 2103558 | 117 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 117 | 36.9701 | -120.1448 | No | Clear;32-90 F | Fuse | Broken | 23-0067647 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840510 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 319664726370 | 20230503 | 933 | 20230503 | 1225 | 2103368 | 172 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 172 | 37.2248 | -120.6168 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067583 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840473 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321592822453 | 20230503 | 1325 | 20230503 | 1518 | 2103853 | 113 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 113 | 37.1156 | -119.9569 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0067792 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840564 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 2169 | 20230503 | 1418 | 20230506 | 1357 | 2103928 | 4299 | Distribution Circuit | 3rd Party | Other | 2 | 8598 | 37.0286 | -120.7079 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0068014 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840724 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10575 | 20230503 | 1857 | 20230503 | 2037 | 2104121 | 100 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 50 | 5000 | 37.2592 | -119.7305 | No | Overcast;32-90 F |  |  | 23-0067866 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840597 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | TRANSFORMER | 320737526465 | 20230503 | 2003 | 20230504 | 34 | 2104180 | 271 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2981 | 37.2275 | -120.2467 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 23-0067862 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840594 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | RECLOSER | 3810 | 20230503 | 2127 | 20230506 | 1151 | 2104210 | 3744 | Distribution Circuit | Animal | Other | 2 | 7488 | 36.617 | -120.4245 | No | Overcast;32-90 F | Recloser | Normal | 23-0067884 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840605 | 0 | Non-EPSS | N | 2023 | B PH & GRD
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318529729867 | 20230503 | 2129 | 20230503 | 2257 | 2103952 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 88 | 37.3191 | -121.0064 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0067909 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840625 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | FUSE | 466019 | 20230503 | 2304 | 20230504 | 946 | 2104241 | 642 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 1284 | 36.793 | -120.6748 | No | Overcast;32-90 F |  |  | 23-0068069 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840808 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318529729867 | 20230503 | 2309 | 20230504 | 226 | 2104242 | 197 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 197 | 37.3191 | -121.0064 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0067915 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840628 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1103 | 253671103 | FUSE | 965555 | 20230503 | 2341 | 20230504 | 422 | 2104250 | 281 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1124 | 36.6337 | -120.639 | No | Clear;32-90 F |  |  | 23-0067952 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840659 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 2834 | 20230504 | 131 | 20230504 | 758 | 2104399 | 387 | Distribution Circuit | Animal | Other | 1 | 387 | 36.923 | -119.8441 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067986 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840684 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | FUSE | 2063 | 20230504 | 209 | 20230504 | 905 | 2104281 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 628 | 37.0981 | -120.1312 | No | Overcast;32-90 F | Lightning Arrestor | Broken | 23-0067947 | OH | Sus | 31644103 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840654 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 850821 | 20230504 | 312 | 20230504 | 830 | 2104297 | 318 | Distribution Circuit | Animal | Other | 17 | 5406 | 37.0178 | -120.4373 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0068035 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840752 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230504 | 341 | 20230504 | 456 | 2104304 | 75 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 260 | 19500 | 37.0552 | -120.0295 | No | Overcast-Drizzle;32-90 F |  |  | 23-0067956 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840663 | 0 | EPSS Ckt | N | 2023 | C & GRD
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 91827 | 20230504 | 434 | 20230516 | 1400 | 2104333 | 17846 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 37852 | 37.1503 | -120.1019 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0068050 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1840779 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | RECLOSER | 3680 | 20230504 | 458 | 20230504 | 542 | 2104341 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 924 | 37.1002 | -120.9978 | No | Overcast-Fog;32-90 F |  |  | 23-0067965 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840673 | 0 | EPSS Ckt | N | 2023 | B & GRD
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 27293 | 20230504 | 459 | 20230504 | 1325 | 2104345 | 506 | Distribution Circuit | Animal | Other | 3 | 1688 | 37.1633 | -120.2288 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0068280 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840874 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRIP-SAVER | 22774 | 20230504 | 650 | 20230504 | 1314 | 2104381 | 384 | Distribution Circuit | Animal | Other | 85 | 32640 | 37.5883 | -120.2764 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0068019 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840740 | 0 | EPSS Ckt | N | 2023 | #2 AND #3
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | TRANSFORMER | 414970756217 | 20230504 | 715 | 20230504 | 1748 | 2104435 | 633 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 633 | 36.8653 | -120.7214 | No | Overcast;32-90 F |  |  | 23-0068067 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1840806 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 321926015434 | 20230504 | 719 | 20230510 | 1349 | 2104786 | 9030 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 18060 | 36.9212 | -119.8422 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0068327 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840884 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 21066 | 20230504 | 915 | 20230504 | 1339 | 2104569 | 264 | Distribution Circuit | Animal | Other | 9 | 1606 | 37.5067 | -120.4212 | No | Overcast-Fog-Rain;32-90 F | Jumper | Burned/flashed | 23-0068099 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840822 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320665512488 | 20230504 | 923 | 20230504 | 1136 | 2104285 | 133 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 133 | 36.8428 | -120.2735 | No | Overcast;32-90 F | Jumper | Broken | 23-0068049 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840777 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320686012026 | 20230504 | 941 | 20230504 | 1350 | 2104286 | 249 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 498 | 36.8293 | -120.2664 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0068068 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840807 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 11599 | 20230504 | 1047 | 20230504 | 1909 | 2104685 | 502 | Distribution Circuit | 3rd Party | Vehicle | 12 | 6024 | 37.2195 | -120.2163 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0068173 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1840842 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321582115718 | 20230504 | 1108 | 20230505 | 1300 | 2104621 | 1552 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1552 | 36.9299 | -119.9601 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Leaking | 23-0068161 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840838 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7734 | 20230504 | 1354 | 20230504 | 1729 | 2105021 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 645 | 37.2639 | -120.7428 | No | Clear;32-90 F |  |  | 23-0068446 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1840925 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320076519686 | 20230504 | 1536 | 20230505 | 1305 | 2104922 | 1289 | Transformer only | Animal | Other | 1 | 1289 | 37.0408 | -120.4741 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0068451 | OH | Sus | 45749729 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840927 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | TRANSFORMER | 320117329776 | 20230504 | 1915 | 20230504 | 2346 | 2105080 | 271 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 271 | 37.3185 | -120.4595 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0068479 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840940 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | FUSE | 188595 | 20230504 | 1917 | 20230505 | 1230 | 2105078 | 1029 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 8232 | 36.8665 | -120.6267 | No | Overcast;32-90 F |  |  | 23-0068784 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1841170 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | L1165 | 20230504 | 1942 | 20230504 | 2049 | 2105089 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1541 | 38.032 | -120.2249 | No | Partly Cloudy;32-90 F |  |  | 23-0068487 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840944 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | JUMPER | OJ 1 E/OF CGC#318845247094 | 20230504 | 1956 | 20230504 | 2051 | 2105090 | 55 | Distribution Circuit | 3rd Party | Vehicle | 1 | 55 | 37.7928 | -120.9001 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0068483 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840941 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 25385 | 20230504 | 2000 | 20230505 | 433 | 2105095 | 513 | Distribution Circuit | Environmental/External | Lightning | 13 | 5459 | 37.9453 | -120.8992 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0068530 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1840986 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317965337036 | 20230504 | 2102 | 20230505 | 246 | 2105127 | 344 | Transformer only | Animal | Other | 1 | 344 | 37.5151 | -121.2026 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0068491 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840952 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318824552728 | 20230504 | 2202 | 20230505 | 151 | 2105143 | 229 | Transformer only | Equipment Failure/Involved | Fire- pole | 1 | 229 | 37.9472 | -120.9084 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 23-0068534 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840991 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 9900 | 20230504 | 2357 | 20230505 | 735 | 2105162 | 458 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 68 | 8176 | 37.5361 | -121.222 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0068528 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1840985 | 0 | EPSS Ckt | N | 2023 | A- B & C
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230505 | 102 | 20230505 | 453 | 2105170 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 60060 | 37.0552 | -120.0295 | No | Overcast-Drizzle;32-90 F | Lightning Arrestor | Broken | 23-0068540 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840997 | 0 | EPSS Ckt | N | 2023 | C & GRD
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | L1209 | 20230505 | 731 | 20230505 | 824 | 2105227 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 76 | 4028 | 37.9631 | -120.2909 | No | Overcast-Fog;32-90 F |  |  | 23-0068595 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1841026 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318471548750 | 20230505 | 913 | 20230505 | 1039 | 2105269 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 86 | 37.8375 | -121.0302 | No | Clear;32-90 F |  |  | 23-0068699 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1841143 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 1594 | 20230505 | 915 | 20230505 | 1004 | 2105372 | 49 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 53 | 2594 | 36.9231 | -119.8624 | No | Partly Cloudy;32-90 F |  |  | 23-0068676 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841132 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320445741446 | 20230505 | 1146 | 20230505 | 1642 | 2105548 | 296 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 296 | 37.6387 | -120.3464 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0068753 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841164 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318501048385 | 20230505 | 1154 | 20230505 | 1337 | 2105558 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 103 | 37.8277 | -121.02 | No | Clear;32-90 F | Fuse | Broken | 23-0068846 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841185 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319441332515 | 20230505 | 1200 | 20230505 | 1234 | 2105567 | 34 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 34 | 37.3928 | -120.6927 | No | Partly Cloudy;32-90 F |  |  | 23-0068762 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841166 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | TRANSFORMER | 415218156197 | 20230505 | 1239 | 20230505 | 1505 | 2105587 | 146 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 292 | 36.8662 | -120.636 | No | Partly Cloudy;32-90 F | Transformer | Malfunctioning | 23-0068921 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841196 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 319831821900 | 20230505 | 1604 | 20230505 | 1822 | 2105732 | 138 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 138 | 37.1022 | -120.5594 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0069002 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841225 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1102 | 252261102 | TRANSFORMER | 319062731650 | 20230505 | 1708 | 20230505 | 1720 | 2105730 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 12 | 37.3674 | -120.8232 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0068987 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841214 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | FUSE | 6274 | 20230505 | 1909 | 20230505 | 2018 | 2105830 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 184 | 36.953 | -120.278 | No | Overcast;32-90 F |  |  | 23-0069061 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841238 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321202518935 | 20230505 | 2111 | 20230506 | 1140 | 2105855 | 869 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 869 | 37.0193 | -120.0895 | No | Overcast;32-90 F | Connector or Splice (OH) | Arcing | 23-0069071 | OH | Sus | 45750928 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1841244 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320354924394 | 20230505 | 2138 | 20230506 | 1018 | 2105858 | 760 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 760 | 37.1709 | -120.3791 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0069070 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841243 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320354824394 | 20230505 | 2152 | 20230506 | 1018 | 2105859 | 746 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 746 | 37.1709 | -120.3791 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069069 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841242 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | OCB | 1102/2 | 20230506 | 33 | 20230506 | 132 | 2105913 | 59 | Distribution Circuit | Animal | Other | 1894 | 43306 | 37.5231 | -120.3304 | No | Overcast;32-90 F | Recloser | Burned/flashed | 23-0069102 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1841282 | 0 | EPSS Ckt | N | 2023 | B & C
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | SWITCH | 6138 | 20230506 | 120 | 20230506 | 157 | 2105926 | 37 | Distribution Circuit | 3rd Party | Vehicle | 457 | 16909 | 36.923 | -119.8983 | No | Overcast;32-90 F | Anchor or Guy | Broken | 23-0069105 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1841285 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321733033150 | 20230506 | 1022 | 20230506 | 1425 | 2106097 | 243 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 243 | 37.4099 | -119.9045 | No | Overcast;32-90 F |  |  | 23-0069172 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1841372 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | SWITCH | 9704 | 20230506 | 1100 | 20230506 | 1224 | 2106140 | 84 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 84 | 36.5631 | -120.4609 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0069149 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1841350 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 8856 | 20230506 | 1637 | 20230506 | 1842 | 2106350 | 125 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 334 | 37.3853 | -120.7815 | No | Clear;32-90 F |  |  | 23-0069219 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841407 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | TRANSFORMER | 319006120646 | 20230506 | 1839 | 20230506 | 1951 | 2106421 | 72 | Transformer only | Unknown Cause | Patrol - not conducted | 11 | 792 | 37.0662 | -120.841 | No | Partly Cloudy;32-90 F |  |  | 23-0069230 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1841419 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | SWITCH | 13483 | 20230507 | 640 | 20230507 | 659 | 2106565 | 19 | Distribution Circuit | 3rd Party | Vehicle | 8 | 152 | 36.9234 | -119.9907 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0069264 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1841456 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 4904 | 20230507 | 1501 | 20230507 | 1922 | 2106841 | 261 | Distribution Circuit | Equipment Failure/Involved | Underground | 359 | 58815 | 37.3269 | -120.4693 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0069301 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841498 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321228918301 | 20230508 | 711 | 20230508 | 940 | 2107101 | 149 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 447 | 37.0023 | -120.0802 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0069463 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841677 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320029821475 | 20230508 | 721 | 20230508 | 855 | 2107103 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 188 | 37.0896 | -120.4924 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0069433 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841639 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | TRANSFORMER | 415251851440 | 20230508 | 827 | 20230508 | 1252 | 2107157 | 265 | Transformer only | Animal | Other | 2 | 530 | 36.7351 | -120.6219 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0069503 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841705 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318992551975 | 20230508 | 923 | 20230508 | 1055 | 2107252 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 92 | 37.9268 | -120.8501 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0069489 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841698 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 319021729535 | 20230508 | 1054 | 20230509 | 154 | 2107349 | 900 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 900 | 37.3093 | -120.8378 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069501 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841704 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | FUSE | 3117 | 20230508 | 1311 | 20230508 | 1701 | 2107597 | 230 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3989 | 36.9533 | -120.5623 | No | Clear;32-90 F |  |  | 23-0069704 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841779 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 3982 | 20230508 | 1432 | 20230508 | 1551 | 2107660 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1580 | 37.0261 | -120.9089 | No | Clear;32-90 F |  |  | 23-0069684 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1841774 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319729234096 | 20230508 | 1459 | 20230508 | 2119 | 2107686 | 380 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 1520 | 37.4367 | -120.5942 | No | Clear;32-90 F |  |  | 23-0069660 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841766 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 25295 | 20230508 | 1943 | 20230508 | 2024 | 2108131 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 41 | 37.7722 | -120.9135 | No | Partly Cloudy;32-90 F |  |  | 23-0069727 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1841796 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 4621 | 20230508 | 1959 | 20230508 | 2130 | 2108133 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 668 | 37.2567 | -121.0971 | No | Clear;32-90 F |  |  | 23-0069738 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1841804 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322005034268 | 20230509 | 818 | 20230509 | 1410 | 2108342 | 352 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 352 | 37.4401 | -119.8124 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070104 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842052 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1101 | 162671101 | TRANSFORMER | 317908839598 | 20230509 | 838 | 20230509 | 1705 | 2108387 | 507 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1014 | 37.5851 | -121.2233 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070006 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842027 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | FUSE | 9679 | 20230509 | 1026 | 20230509 | 1842 | 2108702 | 496 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 992 | 36.8208 | -120.7286 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 23-0070034 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1842039 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | TRANSFORMER | T1589 | 20230509 | 1045 | 20230509 | 1142 | 2108572 | 57 | Transformer only | 3rd Party | Dig in- 3rd party | 4 | 228 | 37.3732 | -120.4554 | No | Overcast;32-90 F | Service conductor | Broken | 23-0069983 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842020 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320501955035 | 20230509 | 1227 | 20230509 | 1301 | 2108643 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 68 | 38.0112 | -120.3267 | No | Overcast;32-90 F | Fuse | Broken | 23-0070036 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842040 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 4621 | 20230509 | 1450 | 20230510 | 214 | 2108948 | 684 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2628 | 37.2567 | -121.0971 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070181 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842076 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320040220580 | 20230509 | 1505 | 20230510 | 1631 | 2108570 | 1526 | Transformer only | Vegetation | Tree - fell into line | 1 | 1526 | 37.0654 | -120.4885 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070126 | OH | Sus | 35442749 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842058 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320326028035 | 20230509 | 1644 | 20230509 | 1720 | 2108857 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 36 | 37.2736 | -120.3882 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0070171 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842068 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2169 | 20230509 | 1823 | 20230509 | 1947 | 2108915 | 84 | Distribution Circuit | Environmental/External | Lightning | 175 | 14700 | 38.0839 | -120.1525 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0070185 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842081 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 20587 | 20230509 | 1827 | 20230509 | 2015 | 2108919 | 108 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 1188 | 38.1016 | -120.1249 | No | Partly Cloudy;32-90 F |  |  | 23-0070187 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842082 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2267 | 20230509 | 1849 | 20230509 | 2107 | 2108942 | 138 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 1104 | 38.0859 | -120.1567 | No | Partly Cloudy;32-90 F |  |  | 23-0070190 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842085 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 321008057717 | 20230509 | 2112 | 20230510 | 205 | 2109009 | 293 | Transformer only | Environmental/External | Lightning | 7 | 2051 | 38.0842 | -120.1516 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070219 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842119 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | RECLOSER | 90500 | 20230509 | 2309 | 20230510 | 904 | 2109055 | 595 | Distribution Circuit | 3rd Party | Vehicle | 255 | 126381 | 37.2955 | -120.5146 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0070228 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842121 | 0 | Non-EPSS | N | 2023 | B & C
YOSEMITE | STANISLAUS | CROWS LANDING-1102 | 163251102 | FUSE | 23584 | 20230510 | 605 | 20230510 | 820 | 2109193 | 135 | Distribution Circuit | 3rd Party | Vehicle | 4 | 540 | 37.3862 | -121.0672 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0070306 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842186 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321251514475 | 20230510 | 719 | 20230510 | 1027 | 2109137 | 188 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 376 | 36.8968 | -120.0742 | No | Clear;32-90 F |  |  | 23-0070390 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842305 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | S1963 | 20230510 | 814 | 20230510 | 943 | 2109379 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 89 | 38.0945 | -120.1634 | No | Clear;32-90 F |  |  | 23-0070357 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842285 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1104 | 253401104 | TRANSFORMER | 415626051614 | 20230510 | 821 | 20230510 | 1142 | 2109204 | 201 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 201 | 36.7415 | -120.4946 | No | Clear;32-90 F | Fuse | Broken | 23-0070431 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842321 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 5531 | 20230510 | 852 | 20230510 | 1018 | 2109265 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 2838 | 37.3826 | -119.7299 | No | Clear;32-90 F |  |  | 23-0070362 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842287 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10793 | 20230510 | 1033 | 20230511 | 1217 | 2109425 | 1544 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3088 | 37.2852 | -119.725 | No | Clear;32-90 F |  |  | 23-0070668 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842377 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 8281 | 20230510 | 1935 | 20230510 | 2009 | 2109783 | 34 | Distribution Circuit | 3rd Party | Vehicle | 7 | 238 | 37.8863 | -120.9907 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0070651 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842368 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | TRANSFORMER | 321008514525 | 20230511 | 923 | 20230511 | 1051 | 2110190 | 88 | Transformer only | Animal | Other | 1 | 88 | 36.8986 | -120.1559 | No | Clear;32-90 F | Jumper | Normal | 23-0070859 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842556 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 321030857875 | 20230511 | 931 | 20230511 | 1335 | 2110212 | 244 | Transformer only | Environmental/External | Lightning | 1 | 244 | 38.0887 | -120.1434 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070847 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842546 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322249527162 | 20230511 | 943 | 20230511 | 1446 | 2110233 | 303 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 303 | 37.2448 | -119.728 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070979 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842605 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319532332049 | 20230511 | 1045 | 20230511 | 1159 | 2110300 | 74 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 74 | 37.38 | -120.6614 | No | Clear;32-90 F |  |  | 23-0070911 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1842579 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321363121538 | 20230511 | 1128 | 20230511 | 1236 | 2110333 | 68 | Transformer only | Animal | Other | 1 | 68 | 37.0901 | -120.0341 | No | Clear;32-90 F | Fuse | Broken | 23-0070940 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842587 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321542113212 | 20230511 | 1221 | 20230512 | 211 | 2110372 | 830 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 830 | 36.8617 | -119.9742 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071040 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842622 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1102 | 254421102 | FUSE | 10453 | 20230511 | 1256 | 20230511 | 1354 | 2110408 | 58 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 55 | 3190 | 37.3282 | -119.6646 | No | Clear;32-90 F |  |  | 23-0070982 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842606 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 7746 | 20230511 | 1447 | 20230511 | 1540 | 2110507 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 283 | 37.1419 | -120.4644 | No | Partly Cloudy;32-90 F |  |  | 23-0071073 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842627 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320190521370 | 20230511 | 1548 | 20230522 | 1544 | 2110544 | 15836 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 31672 | 37.0871 | -120.4357 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0071064 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842625 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 22402 | 20230511 | 1623 | 20230511 | 2320 | 2110577 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 222 | 37.8904 | -120.3063 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071107 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842645 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | S1381 | 20230511 | 1733 | 20230512 | 152 | 2110612 | 499 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 5506 | 37.7878 | -120.8403 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0070966 | UG | Sus | 35443635 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842640 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5200 | 20230511 | 1855 | 20230511 | 1925 | 2110624 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 30 | 37.0658 | -119.9094 | No | Clear;32-90 F | PT/CCVT | Burned/flashed | 23-0071120 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842655 | 0 | EPSS Ckt | N | 2023 | N/A
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 343 | 20230511 | 1935 | 20230511 | 2056 | 2110699 | 81 | Distribution Circuit | 3rd Party | Vehicle | 75 | 6075 | 37.3335 | -121.0041 | No | Clear;32-90 F | Anchor or Guy | Normal | 23-0071145 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842677 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 4193 | 20230511 | 2146 | 20230511 | 2317 | 2110737 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 364 | 37.8311 | -120.8692 | No | Clear;32-90 F |  |  | 23-0071165 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842703 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | INTERRUPTER | 13426 | 20230512 | 714 | 20230512 | 736 | 2110878 | 22 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 149 | 3278 | 36.9799 | -120.0742 | No | Clear;32-90 F |  |  | 23-0061239 | OH | Sus | 35334485 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842736 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | TRANSFORMER | 100000014801 | 20230512 | 730 | 20230512 | 1042 | 2110885 | 192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 192 | 36.8033 | -120.5159 | No | Clear;32-90 F | Fuse | Broken | 23-0071331 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842875 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 23097 | 20230512 | 734 | 20230512 | 1245 | 2110888 | 311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 5750 | 37.0542 | -120.603 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071297 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842846 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | TRANSFORMER | 415655644499 | 20230512 | 749 | 20230512 | 1215 | 2110899 | 266 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 266 | 36.5454 | -120.4797 | No | Clear;32-90 F | Fuse | Burned Open | 23-0071380 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842893 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321709538394 | 20230512 | 920 | 20230512 | 1053 | 2111108 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 186 | 37.5525 | -119.9112 | No | Clear;32-90 F | Other | Broken | 23-0071290 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842841 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | RECLOSER | 11700 | 20230512 | 1350 | 20230512 | 1408 | 2111320 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 318 | 4780 | 36.88 | -120.2185 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0070308 | OH | Sus | 74041044 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842906 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 9972 | 20230512 | 1554 | 20230512 | 1748 | 2111415 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 5931 | 36.8582 | -120.439 | No | Clear;32-90 F |  |  | 23-0071502 | OH | Sus | 45761468 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842938 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | TRANSFORMER | 319176114713 | 20230512 | 1640 | 20230512 | 2048 | 2111426 | 248 | Transformer only | Wildfire Mitigation | CWSP - Vegetation Removal | 1 | 248 | 36.9036 | -120.7824 | No | Clear;32-90 F | Transformer | Normal | 23-0071486 | OH | Sus | 45761415 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842926 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 7712 | 20230513 | 627 | 20230513 | 822 | 2111614 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1380 | 37.2372 | -120.2436 | No | Clear;32-90 F |  |  | 23-0071540 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1842986 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320225522964 | 20230513 | 1838 | 20230513 | 2029 | 2111924 | 111 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 111 | 37.1312 | -120.4234 | No | Clear;32-90 F |  |  | 23-0071602 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1843052 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 9900 | 20230513 | 2130 | 20230514 | 1310 | 2111979 | 940 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 64860 | 37.5361 | -121.222 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0071605 | OH | Sus | 31645380 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843055 | 0 | EPSS Ckt | N | 2023 | A B
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | S1793 | 20230514 | 622 | 20230514 | 833 | 2112048 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 3799 | 37.9721 | -120.2606 | No | Clear;32-90 F |  |  | 23-0071638 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843094 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320180413032 | 20230514 | 1109 | 20230514 | 1307 | 2112137 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 236 | 36.8576 | -120.4397 | No | Clear;32-90 F | Transformer | Annealed | 23-0071669 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843113 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319376047860 | 20230514 | 2014 | 20230514 | 2332 | 2112374 | 198 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 396 | 37.8144 | -120.717 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071697 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843146 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | JUMPER | BURNT OPEN JUMPER | 20230514 | 2049 | 20230515 | 329 | 2112373 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 6800 | 37.0246 | -120.5995 | No | Clear;32-90 F | Jumper | Burned Open | 23-0071725 | OH | Sus | 45761764 | CENTRAL VALLEY | MAY | Open Circuit | 0 | No | No | No | 1843173 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 66723 | 20230514 | 2335 | 20230514 | 2350 | 2112402 | 15 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 15 | 37.2176 | -120.4295 | No | Clear;32-90 F |  |  | 23-0071726 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843175 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | TRANSFORMER | 320198926020 | 20230515 | 357 | 20230515 | 1045 | 2112420 | 408 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1632 | 37.2156 | -120.4329 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071729 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843180 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321326518100 | 20230515 | 1147 | 20230515 | 1248 | 2113102 | 61 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 244 | 36.9963 | -120.0467 | No | Clear;32-90 F |  |  | 23-0071927 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1843336 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321601015861 | 20230515 | 1156 | 20230515 | 1408 | 2113045 | 132 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 132 | 36.9339 | -119.9538 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0071911 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843331 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | JUMPER | OJ 1 N/OF CGC 319991339512 | 20230515 | 1500 | 20230515 | 1541 | 2113317 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 41 | 37.5853 | -120.504 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0072017 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843383 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 2822 | 20230515 | 2255 | 20230516 | 954 | 2113534 | 659 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 659 | 37.4208 | -119.6358 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0072120 | OH | Sus | 31645625 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843442 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 46623 | 20230515 | 2332 | 20230516 | 248 | 2113345 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2548 | 37.5073 | -119.8431 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072115 | OH | Sus | 31645448 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843437 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3518 | 20230516 | 844 | 20230516 | 958 | 2113895 | 74 | Distribution Circuit | Animal | Bird found | 25 | 1850 | 36.96 | -120.6581 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0072241 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843598 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L1227 | 20230516 | 1258 | 20230516 | 1422 | 2114200 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 84 | 37.9327 | -120.2534 | No | Clear;32-90 F |  |  | 23-0072390 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843658 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | S1749 | 20230516 | 1318 | 20230516 | 2055 | 2114188 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 457 | 38.1537 | -120.061 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Broken | 23-0072359 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843644 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319125828970 | 20230516 | 1336 | 20230516 | 1346 | 2114196 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 10 | 37.2948 | -120.802 | No | Clear;32-90 F | Fuse | Broken | 23-0072372 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843649 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320207438630 | 20230516 | 1504 | 20230516 | 1538 | 2114300 | 34 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 68 | 37.5607 | -120.4295 | No | Clear;Above 90 | Secondary | Deteriorated | 23-0072404 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843662 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 2311 | 20230516 | 1951 | 20230517 | 47 | 2114461 | 296 | Distribution Circuit | Equipment Failure/Involved | Underground | 123 | 36408 | 37.3383 | -119.7083 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0072485 | UG | Sus | 31645733 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843705 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 4553 | 20230516 | 2110 | 20230517 | 239 | 2114508 | 329 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 97 | 31913 | 37.4215 | -119.9663 | No | Clear;32-90 F |  |  | 23-0072520 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843746 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | TRANSFORMER | 318511948499 | 20230516 | 2339 | 20230516 | 2359 | 2114517 | 20 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 20 | 37.831 | -121.0161 | No | Clear;32-90 F |  |  | 23-0072515 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1843739 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | JUMPER | OJ 1 SPAN W/OF CGC 319757250472 | 20230517 | 140 | 20230517 | 742 | 2114581 | 362 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 362 | 37.8865 | -120.5855 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0072518 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843744 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | RECLOSER | 89538 | 20230517 | 159 | 20230517 | 436 | 2114585 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 260 | 39637 | 36.7651 | -120.3812 | No | Clear;32-90 F |  |  | 23-0072524 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843750 | 0 | Non-EPSS | N | 2023 | B PHASE & GRD
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | SWITCH | 965007 | 20230517 | 317 | 20230517 | 718 | 2114586 | 241 | Distribution Circuit | 3rd Party | Vehicle | 147 | 35427 | 37.0102 | -119.7369 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072521 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843747 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | INTERRUPTER | 641566 | 20230517 | 515 | 20230517 | 825 | 2114601 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 16150 | 36.7681 | -120.384 | No | Clear;32-90 F |  |  | 23-0072608 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843841 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7698 | 20230517 | 535 | 20230517 | 735 | 2114603 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2561 | 37.3241 | -120.306 | No | Clear;32-90 F |  |  | 23-0072570 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843768 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | S1949 | 20230517 | 616 | 20230517 | 705 | 2114617 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 343 | 37.7326 | -120.8895 | No | Clear;32-90 F |  |  | 23-0072564 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843767 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | TRANSFORMER | 318504724005 | 20230517 | 810 | 20230517 | 1330 | 2115143 | 320 | Transformer only | 3rd Party | Vehicle | 2 | 640 | 37.158 | -121.0141 | No | Clear;32-90 F | Secondary | Broken | 23-0072783 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843981 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | TRANSFORMER | 320061527360 | 20230517 | 820 | 20230517 | 1705 | 2114701 | 525 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 525 | 37.2519 | -120.4788 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0072628 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843899 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | JUMPER | OJS 2 SPANS S/OF CGC# 320712518405 | 20230517 | 821 | 20230517 | 1055 | 2114670 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 154 | 37.0039 | -120.2566 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0072593 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843783 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | TRANSFORMER | 100000070833 | 20230517 | 1103 | 20230525 | 706 | 2114975 | 11283 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 11283 | 36.6249 | -120.4154 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0072691 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843950 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320834056605 | 20230517 | 1128 | 20230517 | 2114 | 2114977 | 586 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 4 | 2344 | 38.0538 | -120.2109 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0072696 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1843954 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 321021313067 | 20230517 | 1350 | 20230517 | 1535 | 2114637 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 105 | 36.8585 | -120.1509 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0072772 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843976 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319980750788 | 20230517 | 1442 | 20230518 | 58 | 2115124 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 616 | 37.8944 | -120.5062 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0072784 | OH | Sus | 45766308 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843982 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319877836794 | 20230517 | 1610 | 20230517 | 1822 | 2115229 | 132 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 132 | 37.5112 | -120.5429 | No | Clear;Above 90 | Fuse | Failed/Faulted | 23-0072875 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844013 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321444536688 | 20230517 | 1620 | 20230517 | 2147 | 2115240 | 327 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 981 | 37.505 | -120.003 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0072891 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844024 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317865637248 | 20230517 | 1746 | 20230518 | 25 | 2115281 | 399 | Transformer only | Animal | Other | 1 | 399 | 37.5211 | -121.2366 | No | Clear;32-90 F | Other | Burned/flashed | 23-0072866 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844011 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 4653 | 20230517 | 1821 | 20230517 | 1952 | 2115299 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 728 | 37.7383 | -120.9586 | No | Clear;32-90 F |  |  | 23-0072886 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844020 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 86825 | 20230517 | 1831 | 20230517 | 1853 | 2115303 | 22 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 88 | 37.4754 | -120.5931 | No | Clear;Above 90 |  |  | 23-0072878 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844015 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320635156948 | 20230517 | 2148 | 20230518 | 212 | 2115467 | 264 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 792 | 38.0638 | -120.2808 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0072899 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844034 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | L2087 | 20230517 | 2335 | 20230518 | 30 | 2115494 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 1760 | 37.9722 | -120.3339 | No | Clear;32-90 F |  |  | 23-0072933 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844061 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | TRANSFORMER | 319061044310 | 20230518 | 248 | 20230518 | 956 | 2115512 | 428 | Transformer only | 3rd Party | Other | 2 | 856 | 37.7168 | -120.8259 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0072940 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844068 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318679250432 | 20230518 | 1249 | 20230518 | 1533 | 2116176 | 164 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 164 | 37.8843 | -120.9587 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073136 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844219 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | RECLOSER | 9300 | 20230518 | 1436 | 20230518 | 1453 | 2116211 | 17 | Distribution Circuit | Vegetation | Tree - fell into line | 467 | 7939 | 37.012 | -120.1106 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0073194 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844244 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 8253 | 20230518 | 1612 | 20230518 | 2100 | 2116329 | 288 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 2432 | 37.7399 | -120.9592 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0073247 | OH | Sus | 31645798 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1844267 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 320024423080 | 20230518 | 2147 | 20230518 | 2245 | 2116399 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 116 | 37.1339 | -120.4922 | No | Clear;32-90 F | Fuse | Broken | 23-0073291 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844299 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | FUSE | 6008 | 20230519 | 155 | 20230519 | 845 | 2116580 | 410 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3280 | 37.0529 | -120.4451 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0073326 | OH | Sus | 45768828 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1844329 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 673480 | 20230519 | 722 | 20230519 | 741 | s1859472 | 15 | Distribution Circuit | Company Initiated | Personnel- company | 252 | 4536 | 37.288 | -119.5203 | No | Clear;32-90 F | Recloser | Normal | 23-0065854 | OH | Sus | 35093593 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1859472 | 0 | EPSS Ckt | N | 2023 | DCD
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 319953838362 | 20230519 | 1058 | 20230519 | 1222 | 2116960 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 84 | 37.5534 | -120.517 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0073581 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844509 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318943052630 | 20230519 | 1218 | 20230519 | 1237 | 2117017 | 19 | Transformer only | Environmental/External | Lightning | 1 | 19 | 37.9448 | -120.8676 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0073574 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844506 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PINECREST-0401 | 163160401 | FUSE | 1861 | 20230519 | 1233 | 20230519 | 1653 | 2117039 | 260 | Distribution Circuit | Vegetation | Tree - grew into line | 30 | 7800 | 38.1867 | -119.9939 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073583 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844510 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 2352 | 20230519 | 1551 | 20230519 | 1824 | 2117215 | 153 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 459 | 37.0182 | -120.1346 | No | Clear;Above 90 | Transformer (UG) | Broken | 23-0073701 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844540 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 82829 | 20230519 | 1552 | 20230519 | 1645 | 2117220 | 53 | Distribution Circuit | 3rd Party | Vehicle | 5 | 265 | 37.0553 | -120.7319 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0073713 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844547 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 23519 | 20230519 | 1854 | 20230519 | 2112 | 2117350 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 184 | 36.8732 | -119.8538 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0073739 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844564 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318878530014 | 20230519 | 1901 | 20230519 | 2015 | 2117316 | 74 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 148 | 37.3214 | -120.8875 | No | Clear;32-90 F |  |  | 23-0073736 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844561 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320618254129 | 20230520 | 401 | 20230520 | 646 | 2117438 | 165 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 495 | 37.9866 | -120.2861 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0073783 | OH | Sus | 45769776 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844602 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | OJ 2 S/E OF 23936 | 20230520 | 1247 | 20230520 | 1534 | 2117640 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 4509 | 37.7214 | -120.1175 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0073820 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844692 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320132837737 | 20230520 | 1305 | 20230520 | 1426 | 2117647 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 81 | 37.536 | -120.4551 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0073846 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844693 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | TRANSFORMER | 320997514396 | 20230520 | 1336 | 20230520 | 1434 | 2117671 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 58 | 36.8948 | -120.1599 | No | Clear;32-90 F | Fuse | Broken | 23-0073858 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844705 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | TRANSFORMER | 321282217328 | 20230520 | 1354 | 20230520 | 1432 | 2117665 | 38 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 532 | 36.9751 | -120.0626 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0073850 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844696 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | TRANSFORMER | 321142816947 | 20230520 | 1505 | 20230520 | 1606 | 2117707 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 61 | 36.9654 | -120.1101 | No | Clear;32-90 F | Fuse | Broken | 23-0073873 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844712 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | RECLOSER | 6318 | 20230520 | 1617 | 20230520 | 1633 | 2117736 | 16 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 414 | 6624 | 37.7777 | -120.8494 | No | Clear;32-90 F |  |  | 23-0073877 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844714 | 0 | Non-EPSS | N | 2023 | A AND B PHASE
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 9010 | 20230521 | 226 | 20230521 | 1213 | 2117867 | 587 | Distribution Circuit | 3rd Party | Vehicle | 243 | 46181 | 37.5385 | -121.2044 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0073939 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844760 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 9270 | 20230521 | 850 | 20230521 | 1402 | 2117948 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 525 | 89534 | 38.026 | -120.2543 | No | Clear;32-90 F | Jumper | Bent or Twisted | 23-0073958 | OH | Sus | 31646241 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844785 | 0 | EPSS Ckt | Y | 2023 | A PHASE & GRD
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 10300 | 20230521 | 1341 | 20230521 | 1721 | 2118020 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 206 | 38924 | 37.1516 | -119.7343 | No | Clear;32-90 F |  |  | 23-0073989 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844804 | 0 | EPSS Ckt | Y | 2023 | A PHASE AND C
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | FUSE | 23456 | 20230522 | 638 | 20230522 | 1748 | 2118279 | 670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1489 | 37.8094 | -121.0525 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0074078 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844885 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320366024397 | 20230522 | 857 | 20230522 | 1050 | 2118489 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 113 | 37.1709 | -120.3753 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0074180 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845048 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | FUSE | 321381615530 | 20230522 | 1155 | 20230522 | 2332 | 2118749 | 697 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 697 | 36.9256 | -120.0289 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0074307 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845092 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 46124 | 20230522 | 1323 | 20230522 | 2001 | 2118831 | 398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 4029 | 37.0248 | -120.0646 | No | Clear;Above 90 | Transformer (OH) | Leaking | 23-0074295 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1845090 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322166621779 | 20230522 | 1727 | 20230522 | 1923 | 2119029 | 116 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 116 | 37.0949 | -119.7564 | No | Clear;Above 90 |  |  | 23-0074409 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1845131 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | TRANSFORMER | 321240816942 | 20230522 | 1930 | 20230523 | 336 | 2119148 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 5832 | 36.9646 | -120.0767 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0074415 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1845139 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20230523 | 546 | 20230523 | 825 | 2119322 | 159 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 145 | 23055 | 37.0679 | -119.9091 | No | Clear;32-90 F |  |  | 23-0074501 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845229 | 0 | EPSS Ckt | N | 2023 | C PHASE
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | TRANSFORMER | 320780921534 | 20230523 | 655 | 20230523 | 926 | 2119352 | 151 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 151 | 37.0912 | -120.2335 | No | Clear;32-90 F | Fuse | Broken | 23-0074558 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845306 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322153225005 | 20230523 | 746 | 20230523 | 1339 | 2119373 | 353 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 353 | 37.1846 | -119.7601 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0074559 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845307 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320373625934 | 20230523 | 820 | 20230523 | 912 | 2119424 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 52 | 37.2131 | -120.3719 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0074550 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845292 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 840701 | 20230523 | 950 | 20230523 | 1116 | 2119608 | 86 | Distribution Circuit | Animal | Other | 13 | 1118 | 37.3623 | -121.1033 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0074647 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1845350 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | INTERRUPTER | 321318116359 | 20230523 | 1003 | 20230523 | 1405 | 2119622 | 242 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 242 | 36.9485 | -120.0493 | No | Clear;32-90 F |  |  | 23-0074587 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845329 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 5673 | 20230523 | 1218 | 20230523 | 1309 | 2119755 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 1428 | 37.2893 | -119.6522 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0074666 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845358 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | JUMPER | BURNT OPEN #3 LOAD SIDE JUMPER @ 1833 | 20230523 | 1446 | 20230524 | 108 | 2119967 | 622 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 4976 | 37.1334 | -121.0333 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0074838 | OH | Sus | 45771848 | CENTRAL VALLEY | MAY | Open Circuit | 0 | No | No | No | 1845413 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 320861518894 | 20230523 | 1811 | 20230523 | 2008 | 2120017 | 117 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 234 | 37.0181 | -120.2058 | No | Clear;32-90 F | Secondary | Normal | 23-0074873 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845433 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | SWITCH | 3043 | 20230523 | 1811 | 20230524 | 9 | 2120015 | 358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 2178 | 37.0971 | -120.9235 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0074626 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845421 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | FUSE | 13185 | 20230523 | 1916 | 20230524 | 238 | 2120057 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 26962 | 36.9455 | -120.0374 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0074876 | OH | Sus | 45771877 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | Yes | 1845436 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | STANISLAUS-1701 | 162821701 | JUMPER | PRIMARY METERING FUSES | 20230523 | 1945 | 20230523 | 2057 | 2120070 | 72 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 72 | 38.1451 | -120.3799 | No | Clear;32-90 F | Other | Malfunctioning | 23-0074872 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845431 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 667248 | 20230523 | 2105 | 20230523 | 2308 | 2120146 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2891 | 264239 | 38.049 | -120.2357 | No | Clear;32-90 F |  |  | 23-0074884 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845444 | 0 | EPSS Ckt | N | 2023 | SGF
YOSEMITE | STANISLAUS | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320347559920 | 20230523 | 2235 | 20230524 | 52 | 2120164 | 137 | Transformer only | 3rd Party | Customer Equipment | 1 | 137 | 38.1451 | -120.38 | No | Clear;32-90 F | Other | Malfunctioning | 23-0074905 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845461 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 21145 | 20230524 | 614 | 20230524 | 930 | 2120327 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 588 | 36.8931 | -119.9388 | No | Clear;32-90 F |  |  | 23-0075024 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1845607 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 318858844840 | 20230524 | 1159 | 20230524 | 1220 | 2120569 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 21 | 37.7306 | -120.8954 | No | Clear;32-90 F | Service conductor | Annealed | 23-0075128 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845650 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318291831588 | 20230524 | 1201 | 20230524 | 1414 | 2120578 | 133 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 133 | 37.3661 | -121.0884 | No | Clear;32-90 F |  |  | 23-0075199 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1845681 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 4893 | 20230524 | 1233 | 20230524 | 1703 | 2120738 | 268 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 9648 | 37.9596 | -120.4296 | No | Clear;32-90 F |  |  | 23-0075067 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845693 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | SWITCH | 3253 | 20230524 | 1234 | 20230524 | 1551 | 2120611 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 8471 | 37.9597 | -120.4291 | No | Clear;32-90 F | Other | Broken | 23-0075067 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1845661 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319529031118 | 20230524 | 1237 | 20230524 | 1330 | 2120614 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 106 | 37.3541 | -120.6594 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0075175 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845676 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318895422168 | 20230524 | 1632 | 20230525 | 208 | 2120754 | 576 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1728 | 37.1078 | -120.8799 | No | Clear;32-90 F | Other | Failed/Faulted | 23-0075305 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845708 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 367021 | 20230524 | 2034 | 20230524 | 2225 | 2120853 | 111 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 2220 | 37.8422 | -120.8708 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0075317 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1845721 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 2353 | 20230525 | 825 | 20230525 | 1044 | 2121046 | 139 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 65 | 9035 | 37.2842 | -120.316 | No | Clear;32-90 F |  |  | 23-0075511 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845900 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PINECREST-0401 | 163160401 | SWITCH | 27102 | 20230525 | 842 | 20230525 | 1029 | 2120987 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1605 | 38.197 | -119.97 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0075386 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845757 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | MERCED FALLS TEMP GEN | 20230525 | 1700 | 20230525 | 1718 | 2121507 | 18 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1395 | 25110 | 37.6202 | -120.3089 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0067219 | OH | Sus | 35154793 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1845961 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321125516238 | 20230526 | 751 | 20230526 | 1039 | 2121872 | 168 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 504 | 36.9455 | -120.1148 | No | Clear;32-90 F | Secondary | Burned/flashed | 23-0075853 | OH | Sus | 45776673 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846072 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | SWITCH | 81529 | 20230526 | 851 | 20230526 | 1207 | 2121893 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 15876 | 37.3019 | -119.5151 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0075840 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846056 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | JUMPER | OPEN JUMPER 1 SOUTH OF CGC 319885517553 | 20230526 | 1250 | 20230526 | 1555 | 2122202 | 185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 185 | 36.9817 | -120.5406 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0076092 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846198 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322205124935 | 20230526 | 1300 | 20230526 | 1400 | 2122212 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 180 | 37.1829 | -119.7425 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0076146 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846214 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319686244698 | 20230526 | 1400 | 20230526 | 1414 | 2122264 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 14 | 37.7273 | -120.6098 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0076158 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846218 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318291831588 | 20230526 | 1806 | 20230527 | 16 | 2122316 | 370 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 370 | 37.3661 | -121.0884 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0076223 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846242 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | OCB | 1104/2 | 20230527 | 406 | 20230528 | 1858 | 2122481 | 1460 | Distribution Circuit | Equipment Failure/Involved | Underground | 629 | 213599 | 37.6655 | -119.8413 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0076259 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1846279 | 0 | EPSS Ckt | Y | 2023 | A- B- C
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 8717 | 20230527 | 508 | 20230527 | 1553 | 2122540 | 645 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 5160 | 37.3121 | -120.4828 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0076270 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1846289 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | RECLOSER | 39546 | 20230527 | 1044 | 20230527 | 1510 | 2122642 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3724 | 37.7858 | -120.7363 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0076290 | OH | Sus | 31649153 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846321 | 0 | EPSS Ckt | N | 2023 | FORCE OUT
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | INTERRUPTER | 269894 | 20230527 | 2345 | 20230528 | 1223 | 2122873 | 758 | Distribution Circuit | 3rd Party | Vehicle | 30 | 6811 | 36.9978 | -120.0744 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0076393 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846389 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 3439 | 20230528 | 15 | 20230528 | 228 | 2122883 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 532 | 37.0833 | -120.6264 | No | Partly Cloudy;32-90 F |  |  | 23-0076396 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846392 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 8908 | 20230528 | 726 | 20230528 | 938 | 2122932 | 132 | Distribution Circuit | Animal | Other | 11 | 1452 | 37.2995 | -120.7241 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0076428 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846415 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1945 | 20230528 | 858 | 20230528 | 1255 | 2122964 | 237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1002 | 34281 | 37.8518 | -120.1648 | No | Partly Cloudy;32-90 F |  |  | 23-0076431 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846418 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | SWITCH | 976816 | 20230528 | 1231 | 20230528 | 1237 | 2123031 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 8 | 48 | 37.0053 | -120.0744 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0076393 | UG | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1846425 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 6573 | 20230528 | 1552 | 20230528 | 1712 | 2123122 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 960 | 36.8684 | -120.083 | No | Clear;32-90 F |  |  | 23-0076468 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846442 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 912185 | 20230528 | 1623 | 20230528 | 1803 | 2123135 | 100 | Distribution Circuit | Animal | Squirrel | 9 | 900 | 36.9739 | -120.0197 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0076478 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846448 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 8717 | 20230529 | 713 | 20230529 | 840 | 2123337 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 696 | 37.3121 | -120.4828 | No | Clear;32-90 F |  |  | 23-0076559 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846521 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 27239 | 20230529 | 817 | 20230529 | 1040 | 2123355 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 143 | 37.777 | -121.0332 | No | Partly Cloudy;32-90 F |  |  | 23-0076555 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846517 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | OCB | 1102/2 | 20230529 | 925 | 20230529 | 1608 | 2123387 | 34 | Distribution Circuit | 3rd Party | Vehicle | 320 | 6944 | 37.1208 | -120.473 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0076545 | OH | Sus | 35449757 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846510 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | RECLOSER | 99922 | 20230529 | 1248 | 20230529 | 1428 | 2123461 | 100 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 697 | 39340 | 36.9693 | -120.0562 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0076576 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846531 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 6844 | 20230529 | 1537 | 20230529 | 2200 | 2123519 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 20299 | 37.0253 | -120.08 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0076598 | OH | Sus | 45803849 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846545 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | RECLOSER | 55936 | 20230530 | 16 | 20230530 | 1114 | 2123630 | 658 | Distribution Circuit | 3rd Party | Vehicle | 15 | 3097 | 37.3383 | -120.8008 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0076626 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1846572 | 0 | Non-EPSS | N | 2023 | B & GRD
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320241755896 | 20230530 | 45 | 20230530 | 522 | 2123635 | 277 | Transformer only | Vegetation | Tree - fell into line | 3 | 831 | 38.0351 | -120.4166 | No | Clear;32-90 F | Secondary | Broken | 23-0076630 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846576 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319257046955 | 20230530 | 156 | 20230530 | 343 | 2123640 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 214 | 37.7894 | -120.7584 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0076632 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846578 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 5859 | 20230530 | 606 | 20230530 | 730 | 2123670 | 84 | Distribution Circuit | Animal | Bird found | 10 | 840 | 36.8535 | -119.9741 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0076650 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846592 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 20553 | 20230530 | 853 | 20230530 | 1023 | 2123815 | 90 | Distribution Circuit | Animal | Other | 4 | 360 | 37.8131 | -120.924 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0076728 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1846725 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | TRANSFORMER | 320003520954 | 20230530 | 1141 | 20230530 | 1604 | 2124021 | 263 | Transformer only | Animal | Other | 1 | 263 | 37.0762 | -120.5014 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0076946 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846805 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | TRANSFORMER | 319014146173 | 20230530 | 1230 | 20230530 | 1249 | 2124041 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 95 | 37.7676 | -120.8421 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0076812 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846755 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 6229 | 20230531 | 641 | 20230531 | 805 | 2124472 | 84 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 35 | 2969 | 37.1245 | -120.2711 | No | Partly Cloudy;32-90 F |  |  | 23-0077129 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1846913 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 3898 | 20230531 | 1129 | 20230531 | 1407 | 2124788 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 948 | 37.1439 | -120.9529 | No | Clear;32-90 F |  |  | 23-0077339 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1847064 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 20381 | 20230531 | 1142 | 20230531 | 2007 | 2124777 | 135 | Transformer only | 3rd Party | Vehicle | 27 | 3645 | 37.7106 | -120.8484 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0077260 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1847040 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | TRANSFORMER | 320730023949 | 20230531 | 1603 | 20230531 | 1701 | 2124965 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 58 | 37.1581 | -120.2502 | No | Clear;32-90 F | Fuse | Broken | 23-0077435 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1847086 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 7608 | 20230531 | 1643 | 20230601 | 131 | 2125004 | 528 | Distribution Circuit | 3rd Party | Vehicle | 62 | 16095 | 37.268 | -120.4345 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0077436 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1847087 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 6165 | 20230531 | 1903 | 20230531 | 2057 | 2125080 | 114 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 207 | 23598 | 37.2004 | -119.7555 | No | Clear;32-90 F |  |  | 23-0077505 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1847108 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 8523 | 20230531 | 1925 | 20230531 | 2107 | 2125087 | 102 | Distribution Circuit | 3rd Party | Other | 184 | 18768 | 37.6478 | -120.3328 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0077500 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1847104 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | T6689 | 20230601 | 723 | 20230601 | 1428 | 2125234 | 425 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 425 | 37.6762 | -120.3663 | No | Clear;32-90 F |  |  | 23-0077887 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1847334 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 493 | 20230601 | 824 | 20230601 | 845 | 2126453 | 21 | Distribution Circuit | Animal | Squirrel | 172 | 3614 | 37.7769 | -120.8072 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0077661 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847204 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 319613326175 | 20230601 | 1009 | 20230601 | 2340 | 2126621 | 811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 7147 | 37.2192 | -120.6343 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0077845 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847324 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 6165 | 20230601 | 1330 | 20230601 | 1609 | 2126762 | 159 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 69 | 10960 | 37.2004 | -119.7555 | No | Clear;32-90 F |  |  | 23-0077884 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847333 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1102 | 253671102 | RECLOSER | 892696 | 20230602 | 339 | 20230602 | 1400 | 2127033 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 6831 | 36.6321 | -120.5142 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0078064 | OH | Sus | 31650847 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1847414 | 0 | Non-EPSS | N | 2023 | FORCE OUT
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 8523 | 20230602 | 840 | 20230602 | 905 | 2127155 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 625 | 37.7615 | -120.9547 | No | Clear;32-90 F | Conductor- Overhead | Annealed | 23-0078135 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1847489 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | TRANSFORMER | 321274917122 | 20230602 | 957 | 20230602 | 1121 | 2127295 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1092 | 36.9695 | -120.0649 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0078194 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1847551 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | SWITCH | 24433 | 20230602 | 1116 | 20230602 | 1203 | 2127366 | 47 | Distribution Circuit | Company Initiated | Return Circuit Normal | 3 | 141 | 37.8577 | -120.8911 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0078262 | UG | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1847568 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 10916 | 20230602 | 2007 | 20230602 | 2154 | 2127639 | 107 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 18 | 1926 | 37.4257 | -119.9049 | No | Clear;32-90 F |  |  | 23-0078486 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847626 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | SWITCH | 4194 | 20230602 | 2212 | 20230602 | 2249 | 2127686 | 37 | Distribution Circuit | 3rd Party | Vehicle | 81 | 2997 | 37.324 | -120.3071 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0078501 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1847636 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | RECLOSER | 90450 | 20230603 | 454 | 20230603 | 1022 | 2127746 | 328 | Distribution Circuit | Equipment Failure/Involved | Overhead | 422 | 41917 | 37.7401 | -120.94 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0078518 | OH | Sus | 45812185 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847652 | 0 | Non-EPSS | N | 2023 | A PHASE & GRD
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | OTHER | WIRE DOWN @ MTR#1005268227 | 20230603 | 731 | 20230603 | 1341 | 2127778 | 370 | Distribution Circuit | Animal | Bird found | 500 | 13310 | 37.058 | -120.8612 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0078540 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | Yes | Yes | 1847680 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 319892622183 | 20230603 | 918 | 20230603 | 934 | 2127783 | 16 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 16 | 37.109 | -120.5376 | No | Clear;32-90 F |  |  | 23-0078557 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1847699 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BIOLA-1102 | 252211102 | FUSE | 5743 | 20230603 | 949 | 20230603 | 1050 | 2127862 | 61 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 448 | 36.8293 | -120.1527 | No | Clear;32-90 F |  |  | 23-0078570 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847707 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 320961520482 | 20230603 | 1412 | 20230603 | 1945 | 2127976 | 333 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 999 | 37.062 | -120.1711 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078608 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847728 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 5781 | 20230603 | 1932 | 20230603 | 2045 | 2128133 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 73 | 37.1532 | -120.2734 | No | Clear;32-90 F |  |  | 23-0078641 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1847753 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 828842 | 20230604 | 650 | 20230604 | 1720 | 2128307 | 630 | Distribution Circuit | Animal | Squirrel | 1591 | 219231 | 37.2287 | -119.7103 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078676 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1847786 | 0 | EPSS Ckt | Y | 2023 | DCD
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 20230604 | 1031 | 20230604 | 1403 | 2128386 | 212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 48548 | 37.7156 | -120.1933 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078696 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1847806 | 0 | EPSS Ckt | Y | 2023 | A&C PH
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320932244803 | 20230604 | 1825 | 20230605 | 1417 | 2128610 | 1192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1192 | 37.7318 | -120.1787 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078775 | OH | Sus | 35452855 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847876 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321716233765 | 20230604 | 1830 | 20230605 | 122 | 2128612 | 412 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 412 | 37.4271 | -119.9096 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078752 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847854 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | S455 | 20230604 | 2236 | 20230605 | 422 | 2128768 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 6574 | 37.774 | -120.841 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0078773 | OH | Sus | 31651202 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847873 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320662256670 | 20230605 | 533 | 20230605 | 720 | 2128848 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 321 | 38.056 | -120.2712 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0078812 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847910 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320756555900 | 20230605 | 640 | 20230605 | 725 | 2128865 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 405 | 38.0353 | -120.2384 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0078806 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847907 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318598547334 | 20230605 | 802 | 20230605 | 925 | 2128909 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 166 | 37.7989 | -120.9862 | No | Partly Cloudy;32-90 F | Jumper | Broken | 23-0078814 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1847914 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | SWITCH | 24433 | 20230605 | 829 | 20230606 | 816 | 2128955 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 816 | 37.8577 | -120.8911 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0078853 | OH | Sus | 45824387 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848004 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321773736750 | 20230605 | 1013 | 20230605 | 1044 | 2129098 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 93 | 37.5065 | -119.8918 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0078875 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848019 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRANSFORMER | 320604221552 | 20230605 | 1115 | 20230605 | 1520 | 2129161 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 735 | 37.0915 | -120.2926 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0078962 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848063 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 281135 | 20230605 | 1200 | 20230605 | 1337 | 2129248 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 194 | 37.0392 | -119.9744 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0078949 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848055 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321537319177 | 20230605 | 1200 | 20230606 | 152 | 2129297 | 832 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 832 | 37.0254 | -119.975 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0078971 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848069 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | TAR FLAT 0402 | 163240402 | RECLOSER | 3144 | 20230605 | 1559 | 20230605 | 1719 | 2129449 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 253 | 20240 | 37.9906 | -120.3839 | No | Partly Cloudy;32-90 F |  |  | 23-0079045 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848091 | 0 | EPSS Ckt | Y | 2023 | C- GRD
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 32894 | 20230605 | 1607 | 20230605 | 1617 | 2129459 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 10 | 37.0541 | -120.0473 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0079051 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1848093 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321324920057 | 20230605 | 1607 | 20230606 | 1440 | 2129461 | 1353 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1353 | 37.0498 | -120.0472 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0079051 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1848094 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | TRANSFORMER | 320791918838 | 20230605 | 1732 | 20230605 | 1935 | 2129521 | 123 | Transformer only | Vegetation | Tree - grew into line | 2 | 246 | 37.0168 | -120.2294 | No | Partly Cloudy;32-90 F | Secondary | Together | 23-0079107 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848119 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | RECLOSER | 3144 | 20230605 | 1822 | 20230606 | 320 | 2129623 | 538 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 253 | 48418 | 37.9906 | -120.3839 | No | Partly Cloudy;32-90 F |  |  | 23-0079098 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848114 | 0 | EPSS Ckt | Y | 2023 | C PHASE & GRD
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 10400 | 20230605 | 1845 | 20230605 | 2208 | 2129630 | 203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1489 | 302267 | 37.2218 | -119.7687 | No | Partly Cloudy;32-90 F |  |  | 23-0079101 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848115 | 0 | EPSS Ckt | Y | 2023 | B&C PHASE
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 44099 | 20230605 | 1933 | 20230605 | 2303 | 2129662 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1680 | 37.3609 | -120.7057 | No | Partly Cloudy;32-90 F |  |  | 23-0079156 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848164 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | FUSE | 9614 | 20230605 | 2131 | 20230605 | 2220 | 2129476 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 49 | 36.8071 | -120.4924 | No | Overcast;32-90 F |  |  | 23-0079136 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848146 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5503 | 20230606 | 506 | 20230606 | 1651 | 2130183 | 705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 26601 | 37.2077 | -119.5419 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079188 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848202 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 751914 | 20230606 | 509 | 20230606 | 806 | 2130137 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 19824 | 37.2927 | -119.5317 | No | Partly Cloudy;32-90 F |  |  | 23-0079186 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848191 | 0 | EPSS Ckt | N | 2023 | A AND C PHASE
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 1103/2 | 20230606 | 510 | 20230606 | 1859 | 2130134 | 829 | Distribution Circuit | Environmental/External | Lightning | 1377 | 340825 | 37.2537 | -119.5192 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079185 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1848190 | 0 | EPSS Ckt | Y | 2023 | ABC PHASE
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322775527315 | 20230606 | 514 | 20230606 | 1531 | 2130478 | 617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 617 | 37.2482 | -119.5476 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0079296 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848352 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | OCB | 1103/2 | 20230606 | 528 | 20230606 | 643 | 2130160 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 817 | 61275 | 37.2036 | -119.4971 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079188 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848193 | 0 | EPSS Ckt | Y | 2023 | FORCE OUT
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 23266 | 20230606 | 549 | 20230606 | 1236 | 2130171 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 7193 | 37.2105 | -119.692 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Broken | 23-0079289 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1848338 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 100000021965 | 20230606 | 654 | 20230606 | 911 | 2130190 | 137 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 137 | 36.8221 | -120.4761 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0079290 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848340 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | TRANSFORMER | 320325154943 | 20230606 | 812 | 20230606 | 929 | 2130266 | 77 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 154 | 38.0089 | -120.3886 | No | Partly Cloudy;32-90 F |  |  | 23-0079293 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848347 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322781127256 | 20230606 | 824 | 20230606 | 1458 | 2130286 | 394 | Transformer only | Environmental/External | Lightning | 1 | 394 | 37.2475 | -119.5457 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079348 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848386 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | TRANSFORMER | 321030724995 | 20230606 | 933 | 20230606 | 1047 | 2130453 | 74 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 74 | 37.1875 | -120.1461 | No | Partly Cloudy;32-90 F |  |  | 23-0079336 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848380 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 10875 | 20230606 | 1124 | 20230606 | 1217 | 2130583 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 188 | 9964 | 37.2929 | -120.3189 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0079349 | OH | Sus | 31651408 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848387 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 2292 | 20230606 | 1256 | 20230606 | 1358 | 2130647 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 1798 | 37.2261 | -119.728 | No | Partly Cloudy;32-90 F | Jumper | Broken | 23-0079390 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1848405 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | TRANSFORMER | 318374247493 | 20230606 | 1314 | 20230606 | 2159 | 2130593 | 525 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 525 | 37.803 | -121.0636 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079397 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848410 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230606 | 1341 | 20230606 | 1658 | 2130715 | 98 | Distribution Circuit | Animal | Other | 451 | 80930 | 38.0052 | -120.4062 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0079424 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848419 | 0 | EPSS Ckt | Y | 2023 | SGF
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 63334 | 20230607 | 109 | 20230607 | 249 | 2131379 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 3100 | 37.3847 | -119.678 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0079614 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848536 | 0 | EPSS Ckt | N | 2023 | FORCE OUT
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322766527320 | 20230607 | 827 | 20230607 | 1314 | 2131658 | 287 | Transformer only | Environmental/External | Lightning | 1 | 287 | 37.2484 | -119.5507 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079804 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848732 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1102 | 252531102 | TRANSFORMER | 322913626905 | 20230607 | 926 | 20230607 | 1412 | 2131765 | 286 | Transformer only | Environmental/External | Lightning | 4 | 1144 | 37.2367 | -119.4993 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079830 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848753 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | JUMPER | 1 POLE W/ OF CGCV# 319075124422 | 20230607 | 929 | 20230607 | 1525 | 2131778 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 356 | 37.1699 | -120.8202 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0079816 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848743 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322889626201 | 20230607 | 1241 | 20230607 | 1931 | 2131971 | 410 | Distribution Circuit | Environmental/External | Lightning | 2 | 820 | 37.2175 | -119.5085 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079977 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848808 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | JUMPER | OJ @ EDDINGS & TRIESTE | 20230607 | 1302 | 20230607 | 1324 | 2132002 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 594 | 36.9194 | -119.8815 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0072447 | OH | Sus | 35333889 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1848789 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321400861369 | 20230607 | 1456 | 20230607 | 2256 | 2132052 | 480 | Transformer only | Environmental/External | Lightning | 5 | 2400 | 38.1845 | -120.0135 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0080046 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848825 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 10606 | 20230608 | 825 | 20230608 | 1006 | 2132430 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 101 | 37.2108 | -119.5031 | No | Partly Cloudy;32-90 F |  |  | 23-0080250 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1849032 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321645613225 | 20230608 | 901 | 20230608 | 1420 | 2132498 | 319 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 319 | 36.8621 | -119.938 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0080224 | OH | Sus | 31651592 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849000 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 2775 | 20230608 | 948 | 20230608 | 1042 | 2132582 | 54 | Distribution Circuit | Vegetation | Other ground vegetation | 6 | 324 | 37.1265 | -120.0927 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0080258 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1849042 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | JUMPER | OJ 5 POLES S/OF MTR#1006947888 | 20230608 | 1343 | 20230608 | 1720 | 2132808 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 217 | 37.0183 | -120.292 | No | Clear;32-90 F | Woodpin | Broken | 23-0080405 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849094 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | FUSE | 6153 | 20230608 | 1637 | 20230609 | 32 | 2132967 | 475 | Distribution Circuit | 3rd Party | Vehicle | 9 | 4275 | 36.9526 | -120.2646 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0080489 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849119 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | TRANSFORMER | T1784 | 20230608 | 2241 | 20230608 | 2252 | 2133032 | 11 | Transformer only | Equipment Failure/Involved | Underground | 12 | 132 | 37.3665 | -120.5965 | No | Clear;32-90 F | Secondary | Broken | 23-0080585 | UG | Sus | 45834458 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849193 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | TRANSFORMER | T1784 | 20230609 | 146 | 20230609 | 155 | s1849211 | 9 | Transformer only | Equipment Failure/Involved | Underground | 12 | 108 | 37.3665 | -120.5965 | No | Clear;32-90 F | Secondary | Broken | 23-0080585 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849211 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 4518 | 20230609 | 754 | 20230609 | 844 | 2133294 | 50 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 74 | 3700 | 37.2999 | -120.5777 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0080690 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1849306 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 10613 | 20230609 | 848 | 20230609 | 1400 | 2133395 | 312 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2496 | 37.333 | -119.6116 | No | Clear;32-90 F |  |  | 23-0080916 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849420 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | JUMPER | T8191 SEC SW | 20230609 | 959 | 20230609 | 1115 | 2133498 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 228 | 37.8596 | -120.8911 | No | Clear;32-90 F | Customer Equipment | Broken | 23-0080738 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849353 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321433013389 | 20230609 | 1120 | 20230609 | 1133 | 2133585 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 78 | 36.8662 | -120.0104 | No | Clear;32-90 F | Secondary | Broken | 23-0080812 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849389 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 27343 | 20230609 | 1219 | 20230609 | 1830 | 2133627 | 371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 742 | 37.824 | -119.9633 | No | Clear;32-90 F | Insulator | Broken | 23-0080844 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849404 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | RECLOSER | 4470 | 20230609 | 1651 | 20230609 | 2349 | 2133842 | 418 | Distribution Circuit | 3rd Party | Vehicle | 100 | 20191 | 37.1862 | -120.6775 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0081031 | OH | Sus | 31651826 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1849452 | 0 | Non-EPSS | N | 2023 | SGF
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 751914 | 20230610 | 412 | 20230610 | 1130 | 2134044 | 438 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 28860 | 37.2927 | -119.5317 | No | Overcast;32-90 F | Other | Broken | 23-0081089 | OH | Sus | 45838539 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1849502 | 0 | EPSS Ckt | N | 2023 | A C TIME
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 10300 | 20230610 | 719 | 20230610 | 803 | 2134069 | 44 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 206 | 8982 | 37.1516 | -119.7343 | No | Overcast;32-90 F |  |  | 23-0081098 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849514 | 0 | EPSS Ckt | Y | 2023 | C- GRD
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 5778 | 20230610 | 949 | 20230610 | 1923 | 2134247 | 574 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 5009 | 37.1418 | -120.2712 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0081129 | OH | Sus | 45842336 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1849590 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 3847 | 20230610 | 1947 | 20230610 | 2114 | 2134448 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1044 | 36.8909 | -120.7096 | No | Partly Cloudy;32-90 F |  |  | 23-0081190 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1849636 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 9577 | 20230610 | 2108 | 20230611 | 309 | 2134481 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2166 | 36.9025 | -120.4455 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0081228 | OH | Sus | 45843380 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1849675 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | 319710313865 | 20230611 | 616 | 20230611 | 838 | 2134536 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 142 | 36.8807 | -120.5999 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0081255 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849698 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320075428987 | 20230611 | 915 | 20230611 | 1010 | 2134568 | 55 | Transformer only | Equipment Failure/Involved | Underground | 2 | 110 | 37.2967 | -120.4734 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0081264 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849709 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321401861635 | 20230611 | 1234 | 20230611 | 2006 | 2134625 | 452 | Distribution Circuit | Environmental/External | Lightning | 10 | 4520 | 38.1923 | -120.0135 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081299 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849726 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321393561758 | 20230611 | 1246 | 20230611 | 2114 | 2134626 | 508 | Transformer only | Environmental/External | Lightning | 3 | 1524 | 38.1957 | -120.016 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081304 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1849728 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1571 | 20230612 | 1137 | 20230612 | 1236 | 2135303 | 59 | Distribution Circuit | Animal | Squirrel | 11 | 669 | 37.7801 | -120.8041 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0081550 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850013 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321662522161 | 20230612 | 1155 | 20230612 | 1415 | 2135327 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 140 | 37.1072 | -119.9307 | No | Partly Cloudy;32-90 F | Other | Arcing | 23-0081541 | OH | Sus | 31652065 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850010 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | TRANSFORMER | 322164243810 | 20230612 | 1322 | 20230612 | 1508 | 2135405 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 742 | 37.6992 | -119.753 | No | Overcast-Rain;32-90 F | Secondary | Broken | 23-0081584 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850030 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 78053 | 20230612 | 1435 | 20230612 | 1542 | 2135476 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 223 | 37.2294 | -120.5696 | No | Clear;32-90 F |  |  | 23-0081654 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850057 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 321543748307 | 20230613 | 1500 | 20230613 | 1541 | 2136257 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 37.825 | -119.966 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0082003 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850354 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | OCB | 1104/2 | 20230613 | 1503 | 20230614 | 32 | 2136261 | 569 | Distribution Circuit | 3rd Party | Vehicle | 1346 | 95536 | 37.3635 | -120.7606 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0082017 | OH | Sus | 31652246 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1850356 | 0 | Non-EPSS | N | 2023 | A & GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320232049930 | 20230613 | 1515 | 20230613 | 1525 | 2136258 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 30 | 37.871 | -120.4204 | No | Clear;32-90 F | Metering Equipment | Broken | 23-0082006 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850355 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320523344541 | 20230613 | 2235 | 20230614 | 249 | 2136486 | 254 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 254 | 37.7255 | -120.3186 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 23-0082097 | OH | Sus | 45846339 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850412 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | 20957 | 20230614 | 51 | 20230614 | 1030 | 2136503 | 579 | Distribution Circuit | 3rd Party | Vehicle | 41 | 23739 | 37.7282 | -120.9268 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0082112 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1850421 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10408 | 20230614 | 56 | 20230614 | 1426 | 2136504 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 15900 | 37.3671 | -119.6088 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0082122 | OH | Sus | 31652264 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850431 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7013 | 20230614 | 743 | 20230614 | 851 | 2136595 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 7888 | 37.3301 | -120.6872 | No | Clear;32-90 F |  |  | 23-0082187 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1850503 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 21145 | 20230614 | 847 | 20230614 | 944 | 2136720 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 171 | 36.8931 | -119.9388 | No | Clear;32-90 F |  |  | 23-0082218 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1850576 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | JUMPER | OJ 2 SPANS N/OF CGC 321283617175 | 20230614 | 1016 | 20230614 | 1358 | 2136814 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 444 | 36.9716 | -120.0596 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0082238 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850588 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | 321033216305 | 20230614 | 1034 | 20230614 | 1339 | 2136846 | 185 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 185 | 36.9493 | -120.1465 | No | Clear;32-90 F | Other | Broken | 23-0082359 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850638 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | RECLOSER | 5450 | 20230614 | 1037 | 20230614 | 1054 | 2136851 | 17 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 172 | 2924 | 37.0401 | -120.2544 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0065201 | OH | Sus | 74053600 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850600 | 0 | Non-EPSS | N | 2023 | C PHASE
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 4498 | 20230614 | 1403 | 20230615 | 119 | 2137068 | 676 | Distribution Circuit | 3rd Party | Vehicle | 1 | 676 | 37.2 | -120.3522 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0082406 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1850648 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320874546135 | 20230614 | 1607 | 20230615 | 1116 | 2137141 | 1149 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4596 | 37.7694 | -120.1978 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0082538 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850739 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319142530186 | 20230614 | 1642 | 20230614 | 2235 | 2137165 | 353 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 706 | 37.3278 | -120.7963 | No | Clear;Above 90 |  |  | 23-0082526 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1850729 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6554 | 20230614 | 1714 | 20230614 | 1822 | 2137199 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 340 | 36.8803 | -120.0197 | No | Overcast;Above 90 |  |  | 23-0082474 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1850687 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318760521146 | 20230614 | 1734 | 20230615 | 201 | 2137222 | 507 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 507 | 37.0805 | -120.9258 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0082485 | OH | Sus | 35457795 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850694 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | S2161 | 20230615 | 605 | 20230615 | 838 | 2137434 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 459 | 37.7504 | -120.9057 | No | Clear;32-90 F |  |  | 23-0082605 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1850779 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | TAR FLAT 0401 | 163240401 | RECLOSER | 922858 | 20230615 | 621 | 20230615 | 1208 | 2137406 | 347 | Distribution Circuit | 3rd Party | Vehicle | 347 | 29514 | 37.9843 | -120.3794 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0082556 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1850745 | 0 | EPSS Ckt | Y | 2023 | A PHASE- GROUND- INST OC-
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320076519686 | 20230615 | 745 | 20230615 | 936 | 2137466 | 111 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 111 | 37.0408 | -120.4741 | No | Partly Cloudy;32-90 F |  |  | 23-0082650 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1850822 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320585524227 | 20230615 | 1153 | 20230615 | 1309 | 2137682 | 76 | Transformer only | Animal | Other | 1 | 76 | 37.1656 | -120.3002 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0082765 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850864 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 6060 | 20230615 | 2053 | 20230616 | 149 | 2138051 | 296 | Distribution Circuit | 3rd Party | Vehicle | 2011 | 429112 | 37.9892 | -120.3332 | No | Clear;32-90 F | Anchor or Guy | Normal | 23-0082936 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1850921 | 0 | EPSS Ckt | Y | 2023 | A&C PH
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | FUSE | 8727 | 20230615 | 2054 | 20230615 | 2220 | 2138039 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 3440 | 37.0663 | -120.8516 | No | Clear;32-90 F |  |  | 23-0082955 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850944 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | FUSE | 6167 | 20230616 | 620 | 20230616 | 928 | 2138175 | 188 | Distribution Circuit | Animal | Bird found | 10 | 1880 | 36.9344 | -120.0513 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0083086 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851095 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230616 | 857 | 20230616 | 1122 | 2138340 | 145 | Distribution Circuit | Animal | Other | 451 | 65169 | 38.0052 | -120.4062 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0083070 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851066 | 0 | EPSS Ckt | Y | 2023 | SGF AND DCD
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | TRANSFORMER | 100000012702 | 20230616 | 1455 | 20230616 | 1631 | 2138720 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 96 | 37.1879 | -121.0683 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0083274 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851189 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | SWITCH | 976223 | 20230616 | 1935 | 20230616 | 2345 | 2138964 | 250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 235 | 58750 | 37.3242 | -120.5262 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0083289 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1851206 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318653319225 | 20230616 | 2054 | 20230616 | 2112 | 2139054 | 18 | Transformer only | Animal | Other | 1 | 18 | 37.0273 | -120.9631 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0083301 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851215 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230616 | 2058 | 20230617 | 122 | 2139060 | 264 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 451 | 109555 | 38.0052 | -120.4062 | No | Clear;32-90 F |  |  | 23-0083300 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851213 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | FUSE | 3812 | 20230617 | 611 | 20230617 | 906 | 2139151 | 175 | Distribution Circuit | Animal | Bird found | 149 | 24821 | 37.0619 | -120.832 | No | Clear;32-90 F | Fuse | Normal | 23-0083332 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851269 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | OCB | 1106/2 | 20230617 | 1015 | 20230617 | 2056 | 2139264 | 641 | Distribution Circuit | 3rd Party | Vehicle | 396 | 28994 | 37.1208 | -120.2505 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0083358 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1851312 | 0 | Non-EPSS | N | 2023 | A C & GRD TIME OC W/ SET A RLY
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 318502731723 | 20230617 | 1247 | 20230617 | 1633 | 2139410 | 226 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 226 | 37.3707 | -121.0157 | No | Clear;32-90 F | Fuse | Broken | 23-0083408 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851353 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 12302 | 20230617 | 1804 | 20230617 | 1930 | 2139513 | 86 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 5449 | 36.9811 | -119.893 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0083426 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851369 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3389 | 20230617 | 2056 | 20230617 | 2225 | 2139600 | 89 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 801 | 36.9822 | -120.5034 | No | Partly Cloudy;32-90 F |  |  | 23-0083463 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1851405 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 237522 | 20230617 | 2238 | 20230618 | 1042 | 2139623 | 724 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 28960 | 37.536 | -121.2758 | No | Clear;32-90 F |  |  | 23-0083464 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1851407 | 0 | EPSS Ckt | Y | 2023 | A&C & INST
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319143046112 | 20230618 | 921 | 20230618 | 1110 | 2139741 | 109 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 218 | 37.7659 | -120.7974 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0083495 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851440 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | JUMPER | WIRE DOWN AT CGC #321838515471 TWD THE EAST | 20230618 | 1311 | 20230618 | 1433 | 2139822 | 82 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 4100 | 36.9226 | -119.872 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083510 | OH | Sus | 31652682 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | Yes | Yes | 1851453 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 21039 | 20230618 | 1313 | 20230618 | 2232 | 2139823 | 559 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 9722 | 36.9228 | -119.8719 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0083514 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851457 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | RECLOSER | 89060 | 20230618 | 1409 | 20230619 | 155 | 2139824 | 706 | Distribution Circuit | 3rd Party | Vehicle | 1281 | 155674 | 36.9559 | -120.6539 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0083511 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1851454 | 0 | Non-EPSS | N | 2023 | A B C PHASE
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | OTHER | WIRE DOWN @ FUCO 24847 | 20230618 | 1943 | 20230619 | 330 | 2140007 | 467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 160 | 5419 | 37.1381 | -120.3921 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083551 | OH | Sus | 45851891 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1851495 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | SWITCH | 589063 | 20230618 | 2343 | 20230619 | 4 | 2140131 | 21 | Distribution Circuit | Company Initiated | Return Circuit Normal | 68 | 1320 | 36.9217 | -119.8763 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083510 | OH | Sus | 31652682 | CENTRAL VALLEY | JUN | None | 0 | No | Yes | No | 1851519 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230619 | 1057 | 20230619 | 1925 | 2140447 | 508 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 451 | 209101 | 38.0052 | -120.4062 | No | Clear;32-90 F |  |  | 23-0083639 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851623 | 0 | EPSS Ckt | Y | 2023 | SGF AND DCD
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | RECLOSER | 6450 | 20230620 | 2 | 20230620 | 1345 | 2140800 | 823 | Distribution Circuit | Equipment Failure/Involved | Overhead | 801 | 86219 | 36.9094 | -120.0785 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0083752 | OH | Sus | 45852716 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1851716 | 0 | Non-EPSS | N | 2023 | A PH & GRD
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | S837 | 20230620 | 614 | 20230620 | 907 | 2140846 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 865 | 37.7975 | -120.8402 | No | Clear;32-90 F |  |  | 23-0083802 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1851821 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 11900 | 20230620 | 753 | 20230620 | 921 | 2140887 | 88 | Distribution Circuit | Animal | Bird found | 221 | 19448 | 37.334 | -119.6447 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0083772 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1851744 | 0 | EPSS Ckt | Y | 2023 | B C INST GRD AND SGF
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 515797 | 20230620 | 825 | 20230620 | 1125 | 2140946 | 180 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 68 | 3195 | 37.288 | -120.3207 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083799 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1851814 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 27323 | 20230620 | 846 | 20230620 | 932 | 2140980 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 665 | 36.9848 | -120.626 | No | Clear;32-90 F |  |  | 23-0083808 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1851838 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321626716618 | 20230620 | 912 | 20230620 | 1013 | 2141030 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 61 | 36.9548 | -119.9441 | No | Clear;32-90 F |  |  | 23-0083836 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1851881 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 5987 | 20230620 | 932 | 20230620 | 1037 | 2141123 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 845 | 37.0544 | -120.2878 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0083861 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1851894 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320520944414 | 20230620 | 1230 | 20230620 | 1245 | 2141379 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 30 | 37.7222 | -120.3194 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0083886 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1851908 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | JUMPER | 22998 | 20230621 | 544 | 20230621 | 905 | 2141931 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 201 | 37.1576 | -120.4921 | No | Clear;32-90 F | Jumper | Burned Open | 23-0084112 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1852030 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318509528245 | 20230621 | 545 | 20230621 | 718 | 2141909 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 93 | 37.2745 | -121.0128 | No | Clear;32-90 F | Fuse | Broken | 23-0084122 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852035 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 10864 | 20230621 | 627 | 20230621 | 910 | 2141914 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 12551 | 37.2807 | -120.4437 | No | Clear;32-90 F |  |  | 23-0084173 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852098 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320356549565 | 20230621 | 830 | 20230621 | 903 | 2142031 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 66 | 37.8616 | -120.3773 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0084168 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852085 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10133 | 20230621 | 1137 | 20230621 | 1259 | 2142270 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 984 | 37.3763 | -119.6686 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0084264 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852178 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 415900153132 | 20230621 | 1222 | 20230621 | 1244 | 2142324 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 22 | 36.7839 | -120.4009 | No | Clear;32-90 F | Fuse | Broken | 23-0084308 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852197 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | TRANSFORMER | 321242616599 | 20230621 | 2022 | 20230621 | 2133 | 2142701 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 710 | 36.9553 | -120.0761 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0084459 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852249 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | FUSE | 22917 | 20230621 | 2258 | 20230622 | 17 | 2142777 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 316 | 37.3054 | -120.4957 | No | Clear;32-90 F |  |  | 23-0084495 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852276 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20230622 | 152 | 20230622 | 942 | 2142809 | 470 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 608 | 285760 | 37.8306 | -120.2367 | No | Clear;32-90 F |  |  | 23-0084507 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852285 | 0 | EPSS Ckt | Y | 2023 | B- GRD
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319640033636 | 20230622 | 1032 | 20230622 | 1106 | 2143098 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 34 | 37.4241 | -120.6245 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0084626 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852430 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 4320 | 20230622 | 1054 | 20230622 | 1634 | 2143141 | 340 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 122 | 4356 | 37.2283 | -120.4881 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0084654 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1852440 | 0 | Non-EPSS | N | 2023 | GRD & SGF
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S1203 | 20230622 | 1143 | 20230622 | 1302 | 2143181 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 4977 | 37.8134 | -121.0341 | No | Clear;32-90 F |  |  | 23-0084703 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852459 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 20435 | 20230622 | 1500 | 20230622 | 1820 | 2143293 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 800 | 37.8588 | -120.3871 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0084767 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852480 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | SWITCH | 10351 | 20230623 | 930 | 20230623 | 1325 | 2143870 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 14335 | 37.6775 | -119.7744 | No | Clear;32-90 F | Insulator | Broken | 23-0084951 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852628 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319611337036 | 20230623 | 1124 | 20230623 | 1847 | 2144117 | 443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 656 | 37.5172 | -120.6349 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0085083 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852721 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | FUSE | 11987 | 20230623 | 1147 | 20230623 | 1235 | 2144145 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 48 | 37.3317 | -120.5052 | No | Clear;32-90 F |  |  | 23-0085099 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852724 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | JUMPER | BURNT OJ 2 POLES N/OF 9830 | 20230623 | 1454 | 20230623 | 1617 | 2144277 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 3693 | 37.0029 | -120.3101 | No | Clear;32-90 F | Jumper | Burned Open | 23-0085190 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1852750 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 5020 | 20230623 | 1612 | 20230624 | 919 | 2144312 | 1027 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1193 | 259734 | 37.2065 | -119.7142 | No | Clear;32-90 F |  |  | 23-0085208 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852754 | 0 | EPSS Ckt | Y | 2023 | DCD & SGF
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 318433830796 | 20230623 | 1649 | 20230623 | 2330 | 2144323 | 401 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 401 | 37.3446 | -121.0396 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085218 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852756 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 23097 | 20230623 | 1922 | 20230623 | 1932 | 2144398 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 490 | 37.0542 | -120.603 | No | Clear;32-90 F | Jumper | Burned Open | 23-0085239 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1852772 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319790528425 | 20230623 | 1954 | 20230624 | 100 | 2144418 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 612 | 37.2805 | -120.5718 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085251 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852778 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 3705 | 20230624 | 405 | 20230624 | 656 | 2144504 | 171 | Distribution Circuit | Animal | Other | 18 | 3080 | 37.0002 | -120.8551 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0085289 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852811 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | RECLOSER | 2850 | 20230624 | 700 | 20230624 | 834 | 2144526 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2350 | 36.6403 | -120.3884 | No | Partly Cloudy;32-90 F |  |  | 23-0085301 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852840 | 0 | Non-EPSS | N | 2023 | B & GRD
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5503 | 20230624 | 717 | 20230624 | 1059 | 2144533 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 870 | 185363 | 37.2077 | -119.5419 | No | Partly Cloudy;32-90 F |  |  | 23-0085290 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852814 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | FUSE | 24312 | 20230624 | 1703 | 20230624 | 1843 | 2145040 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 267 | 36.8797 | -120.6551 | No | Clear;32-90 F |  |  | 23-0085373 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852914 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 89099 | 20230624 | 2153 | 20230624 | 2323 | 2145125 | 90 | Distribution Circuit | 3rd Party | Vehicle | 34 | 3060 | 37.2496 | -119.5654 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0085397 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852941 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320159350675 | 20230625 | 417 | 20230625 | 1215 | 2145163 | 478 | Distribution Circuit | 3rd Party | Vehicle | 195 | 3000 | 37.8916 | -120.4458 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0085400 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1852944 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321510720466 | 20230625 | 849 | 20230625 | 1049 | 2145217 | 120 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 240 | 37.0615 | -119.9837 | No | Clear;32-90 F | Fuse | Broken | 23-0085426 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852978 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRIP-SAVER | 2553 | 20230625 | 1736 | 20230626 | 154 | 2145430 | 498 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 191 | 66698 | 37.9918 | -120.4016 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0085445 | OH | Sus | 31653482 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852996 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 37288 | 20230625 | 1742 | 20230625 | 2030 | 2145433 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 700 | 117600 | 37.421 | -119.8768 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085442 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852991 | 0 | EPSS Ckt | Y | 2023 | B GND
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320585428590 | 20230625 | 1918 | 20230626 | 135 | 2145470 | 377 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 377 | 37.2841 | -120.2986 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085449 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853002 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 320614511470 | 20230625 | 2052 | 20230626 | 404 | 2145532 | 432 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 432 | 36.8144 | -120.2904 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0085468 | OH | Sus | 31653483 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853022 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321977531008 | 20230625 | 2100 | 20230626 | 103 | 2145535 | 243 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 486 | 37.3505 | -119.8271 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085466 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853020 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 20783 | 20230626 | 801 | 20230626 | 948 | 2145634 | 107 | Distribution Circuit | Animal | Other | 18 | 1926 | 37.7991 | -121.0338 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085530 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1853158 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320268551113 | 20230626 | 832 | 20230626 | 1009 | 2145626 | 97 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 97 | 37.9016 | -120.4078 | No | Clear;32-90 F | Secondary | Broken | 23-0085496 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853050 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | RECLOSER | 84280 | 20230626 | 934 | 20230626 | 1224 | 2145815 | 170 | Distribution Circuit | 3rd Party | Customer Equipment | 23 | 3404 | 37.013 | -120.9431 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 23-0085537 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853166 | 0 | EPSS Ckt | N | 2023 | A & GRD INST
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | 319816014288 | 20230626 | 1020 | 20230626 | 1332 | 2145866 | 192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 192 | 36.8924 | -120.5633 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0085708 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853236 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | JUMPER | 7348 | 20230626 | 1046 | 20230626 | 1720 | 2145937 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 6948 | 37.1849 | -120.5462 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0085765 | OH | Sus | 45860724 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1853256 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | RECLOSER | 7200 | 20230626 | 1058 | 20230626 | 1743 | 2145951 | 405 | Distribution Circuit | Animal | Other | 110 | 33530 | 37.0845 | -121.0161 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0085581 | OH | Sus | 45860656 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853191 | 0 | EPSS Ckt | Y | 2023 | B PHASE & GRD
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320148014213 | 20230626 | 1106 | 20230626 | 1221 | 2145963 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 75 | 36.891 | -120.4508 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0085637 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853213 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | TRANSFORMER | 320766122089 | 20230626 | 1109 | 20230626 | 1128 | 2145993 | 19 | Transformer only | Animal | Bird found | 1 | 19 | 37.1063 | -120.239 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Burned/flashed | 23-0085563 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853200 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 9577 | 20230626 | 1149 | 20230626 | 1425 | 2146025 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 936 | 36.9025 | -120.4455 | No | Clear;32-90 F | Jumper | Burned Open | 23-0085611 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853201 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 4320 | 20230626 | 1258 | 20230626 | 1950 | 2146111 | 412 | Distribution Circuit | 3rd Party | Vehicle | 122 | 10512 | 37.2283 | -120.4881 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0085650 | OH | Sus | 31653630 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853220 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | JUMPER | 322844826760 | 20230626 | 1342 | 20230626 | 1711 | 2146182 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 418 | 37.2324 | -119.5242 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0085680 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853230 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | TRANSFORMER | 321324916889 | 20230626 | 1723 | 20230626 | 1730 | 2146312 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 56 | 36.963 | -120.0474 | No | Clear;32-90 F | Secondary | Broken | 23-0085812 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853280 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321982633801 | 20230626 | 1724 | 20230626 | 1930 | 2146366 | 126 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 126 | 37.4257 | -119.8199 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085827 | OH | Sus | 45860757 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853287 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319882530259 | 20230626 | 1752 | 20230626 | 1831 | 2146375 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 156 | 37.3316 | -120.5401 | No | Clear;32-90 F | Fuse | Broken | 23-0085823 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853285 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 827 | 20230627 | 114 | 20230627 | 503 | 2146517 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 18091 | 37.795 | -120.9784 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0085870 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853330 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 9502 | 20230627 | 410 | 20230627 | 535 | 2146578 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1105 | 36.9973 | -120.6177 | No | Partly Cloudy;32-90 F |  |  | 23-0085876 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1853336 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | SWITCH | 38756 | 20230627 | 412 | 20230627 | 418 | 2146577 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2113 | 12678 | 37.794 | -120.9632 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0085871 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853331 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318575247735 | 20230627 | 657 | 20230627 | 1210 | 2146607 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1489 | 37.81 | -120.9943 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085918 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853351 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | TRANSFORMER | 320950825467 | 20230627 | 718 | 20230627 | 917 | 2146614 | 119 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 119 | 37.1995 | -120.1736 | No | Clear;32-90 F | Fuse | Broken | 23-0085982 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853449 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 6060 | 20230627 | 822 | 20230627 | 855 | 2146754 | 33 | Distribution Circuit | Company Initiated | Personnel- company | 1866 | 61578 | 37.9892 | -120.3332 | No | Clear;32-90 F | Fuse | Normal | 23-0085943 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853400 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322122029195 | 20230627 | 949 | 20230627 | 1011 | 2146878 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 44 | 37.2993 | -119.772 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0085998 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853459 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 13032 | 20230627 | 1314 | 20230627 | 1416 | 2147078 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 2976 | 36.9531 | -120.0851 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0086128 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853503 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 318495429817 | 20230627 | 1410 | 20230628 | 30 | 2147125 | 620 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 6820 | 37.3177 | -121.0183 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0086314 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853545 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 5845 | 20230627 | 1414 | 20230627 | 2025 | 2147178 | 371 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 990 | 37.3626 | -121.1038 | No | Partly Cloudy;32-90 F |  |  | 23-0086320 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853555 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | TRANSFORMER | 320131029860 | 20230627 | 1509 | 20230627 | 1526 | 2147144 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 68 | 37.3208 | -120.4547 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 23-0086215 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853518 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | OJ 2 N/OF MTR# 1007092897 | 20230627 | 2013 | 20230627 | 2232 | 2147320 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 834 | 37.7582 | -120.1483 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0086319 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853554 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | TRANSFORMER | 320846721036 | 20230628 | 814 | 20230628 | 940 | 2147518 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 86 | 37.0771 | -120.2106 | No | Clear;32-90 F | Fuse | Broken | 23-0086485 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853763 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320237523340 | 20230628 | 815 | 20230628 | 858 | 2147521 | 43 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 43 | 37.1417 | -120.4193 | No | Clear;32-90 F |  |  | 23-0086449 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853712 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 319939824030 | 20230628 | 1018 | 20230628 | 1252 | 2147858 | 154 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 154 | 37.1605 | -120.5218 | No | Clear;32-90 F |  |  | 23-0086624 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1853817 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 7746 | 20230628 | 1410 | 20230628 | 1818 | 2148192 | 248 | Distribution Circuit | 3rd Party | Vehicle | 8 | 1984 | 37.1419 | -120.4644 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0086699 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853836 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | S2685 | 20230628 | 1715 | 20230628 | 2320 | 2148305 | 365 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 19342 | 37.8188 | -120.8688 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0086856 | UG | Sus | 45864030 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853865 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319606021510 | 20230629 | 456 | 20230629 | 1236 | 2148594 | 460 | Transformer only | Animal | Bird found | 1 | 460 | 37.0904 | -120.6355 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0087045 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854059 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | RECLOSER | 11060 | 20230629 | 1301 | 20230629 | 2255 | 2148991 | 594 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1432 | 312995 | 37.0699 | -120.8656 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0087177 | OH | Sus | 35463682 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1854102 | 0 | Non-EPSS | N | 2023 | SGF
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | RECLOSER | 78274 | 20230629 | 1319 | 20230630 | 147 | 2149008 | 748 | Distribution Circuit | 3rd Party | Vehicle | 416 | 102538 | 37.0596 | -120.847 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 23-0087185 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1854106 | 0 | Non-EPSS | N | 2023 | C & GRD
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | TRANSFORMER | 321260618797 | 20230629 | 1503 | 20230629 | 1550 | 2149085 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 141 | 37.0155 | -120.0695 | No | Clear;Above 90 | Transformer (OH) | Leaking | 23-0087266 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1854121 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | OTHER | WIRE DOWN @ 3341 TWD WEST | 20230629 | 1513 | 20230630 | 348 | 2149106 | 755 | Distribution Circuit | 3rd Party | Vehicle | 646 | 40667 | 37.9447 | -120.8436 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 23-0087305 | OH | Sus | 35463711 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1854133 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320157523090 | 20230629 | 1552 | 20230630 | 313 | 2148960 | 681 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 681 | 37.1346 | -120.4464 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087307 | OH | Sus | 35463478 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854134 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 100000016204 | 20230629 | 1607 | 20230629 | 1656 | 2149144 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 49 | 37.0924 | -120.5374 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0087333 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854147 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 6413 | 20230629 | 1949 | 20230629 | 2305 | 2149315 | 196 | Distribution Circuit | Animal | Bird found | 4 | 784 | 37.7401 | -120.8022 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0087407 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1854211 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319774529829 | 20230629 | 2013 | 20230630 | 108 | 2149341 | 295 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 590 | 37.3192 | -120.5776 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087370 | OH | Sus | 35463743 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854184 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | RECLOSER | 526442 | 20230629 | 2025 | 20230630 | 144 | 2149348 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 785 | 250415 | 37.7727 | -120.8436 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0087363 | OH | Sus | 45864773 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1854171 | 0 | Non-EPSS | N | 2023 | A- GRD
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 9583 | 20230629 | 2312 | 20230630 | 56 | 2149435 | 104 | Distribution Circuit | 3rd Party | Metallic Balloon | 307 | 31928 | 37.1007 | -121.0162 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0087423 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1854225 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 3186 | 20230629 | 2345 | 20230630 | 924 | 2149451 | 579 | Distribution Circuit | 3rd Party | Vehicle | 1262 | 344541 | 37.8624 | -120.2266 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0087414 | OH | Sus | 35463675 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1854215 | 0 | EPSS Ckt | Y | 2023 | A- B
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 4851 | 20230630 | 147 | 20230630 | 457 | 2149473 | 190 | Distribution Circuit | Equipment Failure/Involved | Underground | 41 | 7790 | 37.3162 | -120.4444 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0087425 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854227 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6692 | 20230630 | 401 | 20230630 | 551 | 2149490 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 694 | 36.8277 | -120.0427 | No | Clear;32-90 F |  |  | 23-0087434 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854237 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | 319659214345 | 20230630 | 738 | 20230630 | 1453 | 2149548 | 435 | Transformer only | Animal | Bird found | 1 | 435 | 36.8942 | -120.6184 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0087699 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854413 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | JUMPER | 310011 FUCO | 20230630 | 858 | 20230630 | 1349 | 2149653 | 291 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 11 | 3201 | 36.8063 | -120.3497 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0087632 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1854391 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320419456018 | 20230630 | 1204 | 20230630 | 2022 | 2149925 | 498 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 498 | 38.0381 | -120.3554 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0087643 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854398 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | TRANSFORMER | 320440019305 | 20230630 | 1228 | 20230630 | 1244 | 2149747 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 16 | 37.0284 | -120.3503 | No | Clear;32-90 F | Fuse | Broken | 23-0087640 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854394 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | SWITCH | 40276 | 20230630 | 1325 | 20230701 | 100 | 2149913 | 690 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 7338 | 37.7674 | -120.8474 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0087654 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1854401 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 39256 | 20230630 | 1451 | 20230701 | 134 | 2150015 | 643 | Distribution Circuit | 3rd Party | Vehicle | 523 | 147451 | 37.9571 | -120.3087 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 23-0087698 | OH | Sus | 31653955 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1854412 | 0 | EPSS Ckt | Y | 2023 | C & GRD
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319808529874 | 20230630 | 1651 | 20230701 | 310 | 2150136 | 619 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1857 | 37.3206 | -120.566 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0087765 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854430 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318795045400 | 20230630 | 1801 | 20230701 | 957 | 2150198 | 956 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 956 | 37.746 | -120.9178 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0087772 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854435 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 2297 | 20230630 | 1852 | 20230630 | 1927 | 2150239 | 35 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 233 | 37.7123 | -120.6917 | No | Clear;Above 90 |  |  | 23-0087778 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854442 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | T0185 | 20230630 | 1914 | 20230701 | 44 | 2150204 | 330 | Transformer only | Equipment Failure/Involved | Underground | 31 | 10230 | 37.3811 | -120.7153 | No | Clear;Above 90 | Connector or Splice (UG) | Burned/flashed | 23-0087776 | UG | Sus | 45867220 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854440 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 9270 | 20230630 | 2019 | 20230630 | 2344 | 2150339 | 205 | Distribution Circuit | Equipment Failure/Involved | Underground | 525 | 29890 | 38.026 | -120.2543 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0087788 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854453 | 0 | EPSS Ckt | Y | 2023 | A/GRD
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 2297 | 20230630 | 2107 | 20230630 | 2226 | 2150383 | 79 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 527 | 37.7123 | -120.6917 | No | Clear;32-90 F |  |  | 23-0087826 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854487 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20230630 | 2141 | 20230701 | 428 | 2150399 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 469 | 190883 | 37.3391 | -119.585 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087805 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854467 | 0 | EPSS Ckt | Y | 2023 | A GRD
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | TRANSFORMER | 319709431237 | 20230630 | 2349 | 20230701 | 59 | 2150505 | 70 | Transformer only | Unknown Cause | Patrol - not conducted | 5 | 350 | 37.3578 | -120.6013 | No | Clear;32-90 F |  |  | 23-0087840 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1854518 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 10140 | 20230701 | 434 | 20230701 | 1030 | 2150564 | 356 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 916 | 325204 | 37.3665 | -119.6296 | No | Clear;32-90 F |  |  | 23-0087805 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854525 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 84944 | 20230701 | 700 | 20230701 | 1708 | 2150603 | 608 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3076 | 1559626 | 37.9525 | -120.3686 | No | Clear;32-90 F |  |  | 23-0087852 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854530 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | TRANSFORMER | 319709431237 | 20230701 | 724 | 20230701 | 1424 | 2150614 | 420 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2100 | 37.3578 | -120.6013 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087859 | OH | Sus | 35463938 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854547 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | FUSE | 3752 | 20230701 | 1013 | 20230701 | 1555 | 2150731 | 342 | Distribution Circuit | 3rd Party | Vehicle | 53 | 18126 | 37.0984 | -120.747 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0087912 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1854579 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | JUMPER | #3 LD SIDE JUMPER AT 11687 | 20230701 | 1410 | 20230701 | 1550 | s1854595 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 11700 | 37.3966 | -120.6216 | No | Clear;32-90 F | Jumper | Burned Open | 23-0087944 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1854595 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 23845 | 20230701 | 1441 | 20230701 | 1839 | 2150877 | 238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1841 | 37.5001 | -119.985 | No | Clear;Above 90 |  |  | 23-0087958 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854606 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | T9925 | 20230701 | 1533 | 20230701 | 2249 | 2151008 | 435 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 435 | 37.7344 | -120.7619 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0087981 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1854626 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | TRANSFORMER | 415959452070 | 20230701 | 1551 | 20230701 | 1805 | 2150934 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 3082 | 36.7556 | -120.3798 | No | Clear;Above 90 | Fuse | Broken | 23-0087980 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854625 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322734629976 | 20230701 | 1552 | 20230701 | 1942 | 2150937 | 230 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1610 | 37.3203 | -119.5606 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0087977 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854622 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | TRANSFORMER | 318985820791 | 20230701 | 1705 | 20230701 | 2011 | 2151018 | 186 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1488 | 37.0702 | -120.8482 | No | Clear;Above 90 | Transformer (OH) | Broken | 23-0087998 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854643 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 8130 | 20230701 | 1840 | 20230702 | 1249 | 2151200 | 1089 | Distribution Circuit | Equipment Failure/Involved | Overhead | 437 | 39723 | 38.0278 | -120.2568 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0087989 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1854632 | 0 | EPSS Ckt | Y | 2023 | A- C & 50 INST
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 84944 | 20230701 | 1847 | 20230702 | 1624 | s1854637 | 1297 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 3076 | 3264435 | 37.9525 | -120.3686 | No | Clear;32-90 F | Recloser | Normal | 23-0087852 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1854637 | 0 | EPSS Ckt | Y | 2023 | BC INST
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321253416867 | 20230701 | 1931 | 20230702 | 108 | 2151334 | 337 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 3370 | 36.9625 | -120.0725 | No | Clear;Above 90 | Transformer (OH) | Leaking | 23-0088000 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854645 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319374030561 | 20230701 | 1950 | 20230701 | 2049 | 2151356 | 59 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 354 | 37.3387 | -120.7165 | No | Clear;Above 90 |  |  | 23-0088025 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854667 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | TRANSFORMER | 318972047275 | 20230701 | 1951 | 20230701 | 2344 | 2151358 | 233 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 466 | 37.798 | -120.8568 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0088053 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854695 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | FUSE | 67863 | 20230702 | 735 | 20230702 | 906 | 2151889 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 243 | 37.0401 | -120.2686 | No | Clear;32-90 F |  |  | 23-0088132 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854766 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 100000007611 | 20230702 | 748 | 20230702 | 1639 | 2151895 | 531 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 531 | 37.2232 | -119.7721 | No | Clear;32-90 F |  |  | 23-0088136 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1854768 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 7948 | 20230702 | 1658 | 20230702 | 1804 | 2152278 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 1584 | 37.3457 | -120.6563 | No | Clear-Heat Wave;Above 90 |  |  | 23-0088212 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1854832 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320339028994 | 20230702 | 1805 | 20230702 | 2200 | 2152341 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1410 | 37.296 | -120.383 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 23-0088228 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854849 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | OCB | 1701/2 | 20230702 | 1822 | 20230703 | 45 | 2152351 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1172 | 448876 | 37.9742 | -120.3199 | No | Clear-Heat Wave;Above 90 | Connector or Splice (OH) | Broken- wire on ground | 23-0088217 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1854837 | 0 | EPSS Ckt | Y | 2023 | AC INST
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | RECLOSER | 9230 | 20230702 | 1822 | 20230703 | 133 | 2152489 | 431 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2084 | 859879 | 37.9737 | -120.3716 | No | Clear-Heat Wave;Above 90 |  |  | 23-0088217 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1854847 | 0 | EPSS Ckt | Y | 2023 | BC
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20230702 | 1822 | 20230703 | 1437 | 2152356 | 1215 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1002 | 1217430 | 37.8473 | -120.2023 | No | Clear-Heat Wave;Above 90 | Recloser | Normal | 23-0088219 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1854839 | 0 | EPSS Ckt | Y | 2023 | BC
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20230702 | 1822 | 20230703 | 1442 | s1854846 | 1220 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 162 | 197640 | 37.8183 | -120.0958 | No | Clear-Heat Wave;Above 90 | Recloser | Normal | 23-0088219 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854846 | 0 | EPSS Ckt | Y | 2023 | B PHASE
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 3186 | 20230702 | 1823 | 20230702 | 2050 | 2152369 | 147 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1262 | 175899 | 37.8624 | -120.2266 | No | Clear-Heat Wave;Above 90 | Recloser | Normal | 23-0088222 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1854841 | 0 | EPSS Ckt | Y | 2023 | AC PHASE
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319701431229 | 20230702 | 1930 | 20230702 | 2242 | 2152214 | 192 | Transformer only | Vegetation | Tree - branch fell on line | 18 | 3456 | 37.3579 | -120.6037 | No | Clear-Heat Wave;Above 90 | Secondary | Normal | 23-0088234 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1854862 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 23865 | 20230702 | 1935 | 20230702 | 2127 | 2152636 | 112 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 98 | 10890 | 37.7734 | -120.8396 | No | Clear-Heat Wave;Above 90 |  |  | 23-0088240 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854869 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320916356848 | 20230702 | 2043 | 20230702 | 2142 | 2152737 | 59 | Transformer only | 3rd Party | Fire- house or bldg. | 8 | 472 | 38.0605 | -120.1822 | No | Clear-Heat Wave;32-90 F | Secondary | Burned/flashed | 23-0088246 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854879 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 14200 | 20230702 | 2047 | 20230703 | 100 | 2152690 | 253 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 19734 | 37.3338 | -120.4809 | No | Clear;Above 90 |  |  | 23-0088293 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854934 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 84944 | 20230702 | 2133 | 20230703 | 1440 | 2152725 | 1027 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1911 | 1833177 | 37.9525 | -120.3686 | No | Clear-Heat Wave;32-90 F | Regulator | Burned/flashed | 23-0088247 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1854880 | 0 | EPSS Ckt | Y | 2023 | BC
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | T4559 | 20230702 | 2159 | 20230703 | 621 | 2152775 | 502 | Distribution Circuit | Equipment Failure/Involved | Underground | 96 | 8241 | 37.7734 | -120.8368 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0088273 | UG | Sus | 35464010 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854912 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 21106 | 20230702 | 2249 | 20230703 | 26 | 2152807 | 97 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 116 | 11252 | 36.8957 | -119.7973 | No | Partly Cloudy;Above 90 |  |  | 23-0088288 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854926 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | TRANSFORMER | T1678 | 20230703 | 209 | 20230703 | 1125 | 2152896 | 556 | Distribution Circuit | Equipment Failure/Involved | Underground | 78 | 10265 | 37.3361 | -120.4814 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0088298 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854941 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 10400 | 20230703 | 756 | 20230703 | 1617 | 2153035 | 425 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2628 | 190863 | 37.2218 | -119.7687 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0088350 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | No | No | 1854963 | 0 | EPSS Ckt | Y | 2023 | A- GROUND- INST OC
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319580729946 | 20230703 | 757 | 20230703 | 1355 | 2153034 | 358 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1074 | 37.3224 | -120.6456 | No | Clear;32-90 F | Fuse | Broken | 23-0088564 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855047 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10330 | 20230703 | 757 | 20230703 | 1504 | 2153038 | 427 | Distribution Circuit | Company Initiated | Personnel- company | 1536 | 618744 | 37.2507 | -119.5619 | No | Clear;32-90 F | Recloser | Normal | 23-0088352 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854964 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318463225756 | 20230703 | 800 | 20230703 | 1435 | 2153585 | 395 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 395 | 37.2066 | -121.0288 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0088611 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855059 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | RECLOSER | 9790 | 20230703 | 844 | 20230703 | 1142 | 2153098 | 178 | Distribution Circuit | 3rd Party | Vehicle | 209 | 23058 | 36.8905 | -120.7444 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0088370 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1854983 | 0 | EPSS Ckt | Y | 2023 | B AND C
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | FUSE | 1823 | 20230703 | 929 | 20230703 | 1025 | 2153171 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 56 | 36.9526 | -120.3042 | No | Clear;32-90 F |  |  | 23-0088421 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855005 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 100000028430 | 20230703 | 1043 | 20230703 | 1424 | 2153277 | 221 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 221 | 37.8349 | -120.9339 | No | Clear;32-90 F |  |  | 23-0084518 | OH | Sus | 35392466 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1855017 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 4686 | 20230703 | 1116 | 20230703 | 1227 | 2153305 | 71 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 34 | 2414 | 37.3579 | -120.6079 | No | Clear;Above 90 | Service conductor | Burned/flashed | 23-0088463 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855024 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6379 | 20230703 | 1424 | 20230703 | 1629 | 2153487 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1501 | 36.8404 | -120.0557 | No | Clear;32-90 F | Fuse | Broken | 23-0088626 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855064 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 10382 | 20230703 | 1440 | 20230704 | 1136 | 2153533 | 1256 | Distribution Circuit | 3rd Party | Vehicle | 13 | 301 | 37.1949 | -119.4673 | No | Clear;Above 90 | Pole-Wood | Normal | 23-0088605 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 10877 | No | No | No | 1855055 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRANSFORMER | 320518121400 | 20230703 | 1504 | 20230703 | 1630 | 2153561 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 172 | 37.0875 | -120.322 | No | Clear;Above 90 | Transformer (OH) | Normal | 23-0088629 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855067 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | TRANSFORMER | 319006320363 | 20230703 | 1640 | 20230703 | 1830 | 2153632 | 110 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 110 | 37.0585 | -120.8412 | No | Clear;Above 90 | Service conductor | Broken- wire on ground | 23-0088635 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855068 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20230703 | 1714 | 20230703 | 1908 | 2153554 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1003 | 100032 | 37.8473 | -120.2023 | No | Clear;32-90 F | Regulator | Failed/Faulted | 23-0088649 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855072 | 0 | EPSS Ckt | N | 2023 | N/A
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 321224935348 | 20230704 | 555 | 20230704 | 1430 | 2153932 | 515 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1030 | 37.4684 | -120.0807 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0088733 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855145 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 21039 | 20230704 | 731 | 20230704 | 810 | 2153962 | 39 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 23 | 883 | 36.9228 | -119.8719 | No | Clear;32-90 F |  |  | 23-0088726 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855137 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 9597 | 20230704 | 1450 | 20230704 | 1609 | 2154130 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 474 | 37.0617 | -120.9353 | No | Clear;Above 90 |  |  | 23-0088765 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855170 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 2297 | 20230705 | 544 | 20230705 | 732 | 2154347 | 108 | Distribution Circuit | Animal | Bird found | 7 | 720 | 37.7123 | -120.6917 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088822 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855224 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 5556 | 20230705 | 738 | 20230705 | 744 | 2154354 | 6 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 90 | 36.9239 | -119.8722 | No | Clear;32-90 F |  |  | 23-0088836 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855227 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 10940 | 20230705 | 825 | 20230705 | 924 | 2154434 | 59 | Distribution Circuit | Vegetation | Tree - branch fell on line | 641 | 37819 | 37.9883 | -120.2832 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088862 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855259 | 0 | EPSS Ckt | Y | 2023 | AC
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 5841 | 20230705 | 908 | 20230705 | 1006 | 2154499 | 58 | Distribution Circuit | Animal | Bird found | 10 | 580 | 37.7762 | -120.7898 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088897 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855301 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 19887 | 20230705 | 1009 | 20230705 | 1120 | 2154568 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 426 | 37.5171 | -121.1954 | No | Clear;32-90 F |  |  | 23-0088954 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855324 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | JUMPER | OJS 4 S/OF MTR 1009999588 | 20230705 | 1026 | 20230705 | 1229 | 2154572 | 123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 246 | 37.7185 | -120.693 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088909 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855311 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 100000021682 | 20230705 | 1218 | 20230705 | 1230 | 2154621 | 12 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 12 | 37.5829 | -120.5145 | No | Clear;32-90 F |  |  | 23-0088995 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1855331 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 100000009743 | 20230705 | 1301 | 20230705 | 1700 | 2154690 | 239 | Transformer only | Animal | Other | 1 | 239 | 37.3459 | -120.2789 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0089137 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855362 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | TRANSFORMER | 320552319099 | 20230705 | 1332 | 20230705 | 1434 | 2154721 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 62 | 37.0241 | -120.3102 | No | Clear;32-90 F | Fuse | Burned Open | 23-0089082 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855342 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318683545110 | 20230705 | 1516 | 20230705 | 1722 | 2154793 | 126 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 378 | 37.738 | -120.9562 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0089103 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855345 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | T0945 | 20230705 | 1608 | 20230705 | 2208 | 2154872 | 360 | Transformer only | Equipment Failure/Involved | Underground | 6 | 2160 | 37.3902 | -120.7169 | No | Clear;Above 90 | Secondary | Deteriorated | 23-0089153 | UG | Sus | 45871044 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855372 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318812718177 | 20230705 | 2049 | 20230706 | 130 | 2154812 | 281 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 281 | 36.9987 | -120.9073 | No | Clear;32-90 F | Transformer (OH) |  | 23-0089160 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855379 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 191939 | 20230706 | 128 | 20230706 | 339 | 2155063 | 131 | Distribution Circuit | 3rd Party | Vehicle | 69 | 9039 | 37.351 | -120.9809 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0089203 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1855412 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 4789 | 20230706 | 641 | 20230706 | 903 | 2155102 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3124 | 37.5189 | -120.588 | No | Clear;32-90 F |  |  | 23-0089287 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855469 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | FUSE | 6839 | 20230706 | 647 | 20230706 | 809 | 2155098 | 82 | Distribution Circuit | Animal | Bird found | 1 | 82 | 37.024 | -120.0593 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0089265 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855429 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | RECLOSER | 7200 | 20230706 | 858 | 20230706 | 950 | 2155231 | 52 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 5772 | 37.0845 | -121.0161 | No | Clear;32-90 F | Lightning Arrestor | Broken | 23-0089291 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855475 | 0 | EPSS Ckt | Y | 2023 | B- GRD
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | TRANSFORMER | 318294518971 | 20230706 | 951 | 20230706 | 1139 | 2155306 | 108 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 864 | 37.0191 | -121.0852 | No | Clear;32-90 F |  |  | 23-0089389 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1855527 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 9981 | 20230706 | 1224 | 20230706 | 1325 | 2155464 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 488 | 36.9909 | -120.873 | No | Clear;32-90 F |  |  | 23-0089460 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855547 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320085329332 | 20230706 | 2022 | 20230706 | 2127 | 2155821 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 715 | 37.3063 | -120.4705 | No | Clear;32-90 F | Secondary | Broken | 23-0089602 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855594 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 24332 | 20230706 | 2027 | 20230706 | 2139 | 2155835 | 72 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 288 | 37.0838 | -120.2836 | No | Clear;32-90 F |  |  | 23-0089607 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855599 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 4789 | 20230707 | 605 | 20230707 | 1123 | 2155989 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 6996 | 37.5189 | -120.588 | No | Clear;32-90 F | Crossarm- Steel | Broken | 23-0089701 | OH | Sus | 31654621 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855655 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | RECLOSER | 7200 | 20230707 | 728 | 20230707 | 1118 | 2156015 | 230 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 111 | 25530 | 37.0845 | -121.0161 | No | Partly Cloudy;32-90 F |  |  | 23-0089671 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855631 | 0 | EPSS Ckt | Y | 2023 | B- GRD
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | S2685 | 20230707 | 756 | 20230707 | 1015 | 2156046 | 139 | Distribution Circuit | Animal | Bird found | 62 | 8618 | 37.8188 | -120.8688 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0089746 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855692 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 319939824030 | 20230707 | 850 | 20230707 | 933 | 2156104 | 43 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 43 | 37.1605 | -120.5218 | No | Clear;32-90 F |  |  | 23-0089764 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1855699 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | FUSE | 6444 | 20230707 | 1229 | 20230707 | 1255 | 2156189 | 26 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 78 | 36.9558 | -119.7443 | No | Clear;32-90 F | Customer Equipment | Broken | 23-0089879 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855726 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10890 | 20230707 | 1230 | 20230707 | 1452 | 2156317 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1368 | 86913 | 37.31 | -119.5845 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0089883 | OH | Sus | 31654569 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855730 | 0 | EPSS Ckt | Y | 2023 | A- B
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | SWITCH | 22272 | 20230707 | 1731 | 20230707 | 2014 | 2156505 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1141 | 37.0424 | -120.8367 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0089930 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855757 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321116744048 | 20230707 | 2005 | 20230708 | 300 | 2156582 | 415 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 415 | 37.7113 | -120.1151 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0090028 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855772 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 5607 | 20230708 | 38 | 20230708 | 107 | 2156885 | 29 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 1064 | 37.7889 | -120.7975 | No | Clear;32-90 F |  |  | 23-0090047 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855799 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 7047 | 20230708 | 248 | 20230708 | 622 | 2156892 | 214 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 7954 | 37.3233 | -120.4554 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0090048 | UG | Sus | 45874679 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855802 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319150047177 | 20230708 | 801 | 20230708 | 914 | 2156919 | 73 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 73 | 37.7957 | -120.7947 | No | Clear;32-90 F |  |  | 23-0090078 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1855842 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | FUSE | 6444 | 20230708 | 908 | 20230708 | 927 | 2157006 | 19 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 57 | 36.9558 | -119.7443 | No | Clear;32-90 F | Other | Normal | 23-0090074 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855833 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321256916874 | 20230708 | 1302 | 20230708 | 1401 | 2157173 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 118 | 36.9627 | -120.0713 | No | Clear;32-90 F | Service conductor | Broken | 23-0090113 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855867 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 6844 | 20230708 | 1508 | 20230709 | 505 | 2157251 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 8311 | 37.0253 | -120.08 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0090141 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1855889 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 5841 | 20230708 | 1716 | 20230708 | 2037 | 2157318 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2010 | 37.7762 | -120.7898 | No | Clear;32-90 F |  |  | 23-0090165 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855908 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318801047970 | 20230708 | 1805 | 20230708 | 1944 | 2157335 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 198 | 37.8166 | -120.9159 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0090162 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855905 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | FUSE | 10979 | 20230708 | 1919 | 20230708 | 2016 | 2157353 | 57 | Distribution Circuit | 3rd Party | Other | 46 | 1110 | 37.2913 | -120.4539 | No | Clear;32-90 F | Customer Equipment | Burned/flashed | 23-0090159 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855902 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 493 | 20230708 | 2026 | 20230708 | 2054 | 2157384 | 28 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 173 | 4856 | 37.7769 | -120.8072 | No | Clear;32-90 F |  |  | 23-0090166 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855909 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 22195 | 20230708 | 2107 | 20230709 | 53 | 2157414 | 226 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 20792 | 37.7801 | -120.8029 | No | Clear;32-90 F |  |  | 23-0090169 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855912 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 6109 | 20230709 | 300 | 20230709 | 444 | 2157564 | 104 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 26 | 2704 | 37.0911 | -120.2686 | No | Partly Cloudy;32-90 F |  |  | 23-0090192 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855934 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 21145 | 20230709 | 908 | 20230709 | 1014 | 2157606 | 66 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 198 | 36.8931 | -119.9388 | No | Clear;32-90 F |  |  | 23-0090216 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855953 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | FUSE | 564207 | 20230709 | 1033 | 20230709 | 1232 | 2157652 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 714 | 36.8365 | -120.5432 | No | Partly Cloudy;32-90 F |  |  | 23-0090234 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1855961 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 13039 | 20230709 | 1038 | 20230709 | 1200 | 2157654 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 246 | 37.0839 | -120.4419 | No | Clear;32-90 F |  |  | 23-0090233 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855960 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 851902 | 20230709 | 1742 | 20230710 | 906 | 2157812 | 924 | Distribution Circuit | Animal | Bird found | 2674 | 936774 | 37.4831 | -119.9631 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090255 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | No | No | 1855985 | 0 | EPSS Ckt | Y | 2023 | GRD INST
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 3872 | 20230710 | 915 | 20230710 | 949 | 2158311 | 34 | Distribution Circuit | Equipment Failure/Involved | Overhead | 110 | 3740 | 36.7644 | -120.3818 | No | Clear;32-90 F | Fuse | Broken | 23-0090370 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856135 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 4786 | 20230710 | 945 | 20230710 | 1057 | 2158348 | 72 | Distribution Circuit | Animal | Bird found | 5 | 360 | 37.4631 | -119.884 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090390 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856154 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | TRANSFORMER | 318369047448 | 20230710 | 1030 | 20230710 | 1500 | 2158213 | 270 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 540 | 37.8018 | -121.0653 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0090399 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856158 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | FUSE | 6447 | 20230710 | 1057 | 20230710 | 1557 | 2158462 | 300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3000 | 37.021 | -119.794 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0090467 | OH | Sus | 31655085 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856197 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321498013089 | 20230710 | 1359 | 20230710 | 2138 | 2158726 | 459 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 918 | 36.8581 | -119.9896 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0090534 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856217 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | TRANSFORMER | 415160056725 | 20230710 | 1656 | 20230711 | 231 | 2158878 | 575 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 575 | 36.8791 | -120.6563 | No | Clear;32-90 F |  |  | 23-0090666 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1856297 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 24332 | 20230710 | 2034 | 20230711 | 950 | 2158989 | 796 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 3184 | 37.0838 | -120.2836 | No | Clear;32-90 F |  |  | 23-0090747 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856458 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | SWITCH | 841371 | 20230710 | 2042 | 20230711 | 333 | 2158992 | 108 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 20 | 2160 | 37.0543 | -120.8053 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0090634 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1856259 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 542583 | 20230711 | 942 | 20230711 | 1127 | 2159692 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 105 | 36.8293 | -120.1956 | No | Clear;32-90 F |  |  | 23-0090810 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856517 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S20385 | 20230711 | 1021 | 20230711 | 1115 | 2159774 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 270 | 37.817 | -121.0154 | No | Clear;32-90 F |  |  | 23-0090796 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856504 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319717537632 | 20230711 | 1154 | 20230711 | 1632 | 2159822 | 278 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 278 | 37.5336 | -120.5987 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0090839 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856528 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 318031838870 | 20230711 | 1816 | 20230712 | 454 | 2160191 | 638 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3190 | 37.5654 | -121.1803 | No | Clear;Above 90 | Cutout- fuse holder | Burned/flashed | 23-0091076 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856635 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319070545245 | 20230711 | 1908 | 20230711 | 2132 | 2160212 | 144 | Transformer only | Vegetation | Tree - fell into line | 1 | 144 | 37.7426 | -120.8223 | No | Clear;32-90 F | Service conductor | Normal | 23-0091046 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856613 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 24332 | 20230711 | 2056 | 20230712 | 1735 | 2160696 | 1239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3831 | 37.0838 | -120.2836 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0091250 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856830 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | OTHER | J22555 TWD T7120 | 20230712 | 48 | 20230712 | 131 | 2160262 | 43 | Transformer only | Equipment Failure/Involved | Underground | 31 | 1333 | 37.0691 | -120.8245 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 23-0091047 | UG | Sus | 35466797 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1856614 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10692 | 20230712 | 156 | 20230712 | 443 | 2160299 | 167 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 334 | 37.3554 | -119.6385 | No | Clear;32-90 F |  |  | 23-0091086 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856643 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7678 | 20230712 | 727 | 20230712 | 839 | 2160412 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 336 | 37.3122 | -120.3239 | No | Clear;32-90 F |  |  | 23-0091162 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856726 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | TRANSFORMER | 415163054071 | 20230712 | 910 | 20230712 | 1005 | 2160593 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 55 | 36.8073 | -120.6522 | No | Clear;32-90 F | Fuse | Broken | 23-0091228 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856823 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 54727 | 20230712 | 1053 | 20230712 | 1515 | 2160966 | 262 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 17 | 4369 | 37.7175 | -120.6184 | No | Clear;Above 90 |  |  | 23-0091424 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856900 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 47747 | 20230712 | 1055 | 20230712 | 1335 | 2160727 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 5600 | 37.7133 | -120.6189 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0091365 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856886 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10990 | 20230712 | 1247 | 20230712 | 1608 | 2160868 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 524 | 105324 | 37.4964 | -119.811 | No | Clear;32-90 F |  |  | 23-0091345 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856871 | 0 | EPSS Ckt | Y | 2023 | A PHASE & GRD
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321268316521 | 20230712 | 1259 | 20230712 | 1417 | 2160862 | 78 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 1170 | 36.9532 | -120.0674 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0091340 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1856870 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | 319686715162 | 20230712 | 1357 | 20230712 | 1710 | 2160923 | 193 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 193 | 36.9166 | -120.6087 | No | Clear;32-90 F |  |  | 23-0091489 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1856917 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320003721641 | 20230712 | 1635 | 20230712 | 1949 | 2161066 | 194 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 194 | 37.0947 | -120.5014 | No | Clear;32-90 F |  |  | 23-0091526 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1856929 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319835330921 | 20230712 | 1639 | 20230712 | 2155 | 2161079 | 316 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 632 | 37.3496 | -120.5569 | No | Clear;Above 90 | Anchor or Guy | Broken | 23-0091534 | OH | Sus | 45884840 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1856931 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | SWITCH | 19757 | 20230712 | 1800 | 20230712 | 1922 | 2161121 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 492 | 37.5349 | -120.0294 | No | Clear;Above 90 | Other | Broken | 23-0091497 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1856919 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | TRANSFORMER | 321370616260 | 20230712 | 1934 | 20230712 | 2140 | 2161206 | 126 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 630 | 36.9454 | -120.0317 | No | Clear;32-90 F | Fuse | Burned Open | 23-0091555 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856943 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 3403 | 20230712 | 2049 | 20230713 | 833 | 2161220 | 704 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 5632 | 37.1828 | -120.9308 | No | Clear;32-90 F |  |  | 23-0091576 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1856958 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 320082311721 | 20230713 | 447 | 20230713 | 750 | 2161289 | 183 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 366 | 36.8215 | -120.4716 | No | Clear;32-90 F |  |  | 23-0091635 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1856986 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | S2239 | 20230713 | 746 | 20230713 | 1008 | 2161342 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 852 | 37.8985 | -120.9447 | No | Clear;32-90 F |  |  | 23-0091706 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857128 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 23723 | 20230713 | 916 | 20230713 | 1525 | 2161479 | 369 | Distribution Circuit | 3rd Party | Vehicle | 10 | 3690 | 37.2696 | -121.0491 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0091728 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | Yes | No | 1857142 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320309556680 | 20230713 | 1011 | 20230713 | 1418 | 2161560 | 247 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 247 | 38.0569 | -120.3935 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0091771 | OH | Sus | 31655432 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857161 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 5899 | 20230713 | 1128 | 20230713 | 1225 | 2161636 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 9619 | 37.0401 | -119.9926 | No | Clear;Above 90 |  |  | 23-0091812 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857175 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322484130401 | 20230713 | 1311 | 20230713 | 1414 | 2161723 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 796 | 37.3323 | -119.6461 | No | Clear;32-90 F | Service conductor | Deteriorated | 23-0091862 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857190 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 667248 | 20230713 | 1314 | 20230713 | 1745 | 2161730 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2890 | 761066 | 38.049 | -120.2357 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0091869 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857193 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321472439015 | 20230713 | 1500 | 20230714 | 517 | 2161844 | 857 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 857 | 37.5692 | -119.9938 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092092 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857282 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318693723000 | 20230713 | 1636 | 20230713 | 1846 | 2161899 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 390 | 37.1305 | -120.949 | No | Clear;Above 90 | Fuse | Failed/Faulted | 23-0092054 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857246 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320756555900 | 20230713 | 2010 | 20230714 | 220 | 2162021 | 370 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3330 | 38.0353 | -120.2384 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0092066 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857256 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 320555913571 | 20230714 | 814 | 20230714 | 1503 | 2162329 | 409 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 409 | 36.8728 | -120.3097 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0092234 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857463 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | TRANSFORMER | 321323816652 | 20230714 | 1355 | 20230714 | 1826 | 2162614 | 271 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 4878 | 36.9566 | -120.0478 | No | Clear;Above 90 | Secondary | Burned/flashed | 23-0092392 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857522 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320504353121 | 20230714 | 1524 | 20230714 | 1651 | 2162846 | 87 | Distribution Circuit | 3rd Party | Vehicle | 1 | 87 | 37.9592 | -120.3268 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0092450 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857542 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 26467 | 20230714 | 1744 | 20230714 | 2027 | 2162880 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 326 | 38.0245 | -120.3342 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 23-0092442 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857544 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1102 | 252091102 | OCB | 1102/2 | 20230715 | 109 | 20230715 | 226 | 2163044 | 77 | Distribution Circuit | 3rd Party | Vehicle | 1901 | 111864 | 37.0663 | -120.8359 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0092520 | UG | Sus | 31655680 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857588 | 0 | Non-EPSS | N | 2023 | B & GRD- TIME
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 4972 | 20230715 | 949 | 20230715 | 955 | 2163261 | 6 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 6 | 37.5136 | -120.5393 | No | Clear;32-90 F |  |  | 23-0092569 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857664 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 26747 | 20230715 | 1139 | 20230715 | 1207 | 2163365 | 28 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 392 | 37.8569 | -120.9195 | No | Clear;Above 90 |  |  | 23-0092599 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857675 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | OCB | 1102/2 | 20230715 | 1238 | 20230715 | 1513 | 2163448 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1844 | 75520 | 37.5231 | -120.3304 | No | Clear;Above 90 |  |  | 23-0092617 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857680 | 0 | EPSS Ckt | N | 2023 | C PH & GRD
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318403545830 | 20230715 | 1428 | 20230715 | 1755 | 2163478 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 207 | 37.7574 | -121.0531 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092648 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857698 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | JUMPER | OJS N/OF CGC 320478553690 | 20230715 | 1541 | 20230715 | 1630 | 2163567 | 49 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2 | 98 | 37.9766 | -120.3333 | No | Clear;Above 90 | Transformer (OH) | Normal | 23-0092655 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857700 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | FUSE | 8962 | 20230715 | 2012 | 20230716 | 1153 | 2163842 | 941 | Distribution Circuit | Equipment Failure/Involved | Underground | 171 | 135759 | 37.3267 | -120.4869 | No | Clear;Above 90 | Elbow | Burned/flashed | 23-0092717 | UG | Sus | 45888781 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857740 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | JUMPER | OJ 1 W/OF CGC# 318795045200 | 20230715 | 2221 | 20230716 | 14 | 2163899 | 113 | Distribution Circuit | 3rd Party | Vehicle | 1 | 113 | 37.7407 | -120.9184 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0092728 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857745 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 9578 | 20230716 | 131 | 20230716 | 407 | 2163962 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1248 | 36.8873 | -120.4456 | No | Partly Cloudy;32-90 F |  |  | 23-0092758 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857777 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | 319581018569 | 20230716 | 903 | 20230716 | 1033 | 2164086 | 90 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 90 | 37.0098 | -120.6447 | No | Partly Cloudy-Heat Wave;32-90 F | Fuse | Failed/Faulted | 23-0092810 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857839 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 667248 | 20230716 | 1031 | 20230716 | 1124 | 2164187 | 53 | Distribution Circuit | Company Initiated | Personnel- company | 2891 | 106096 | 38.049 | -120.2357 | No | Partly Cloudy-Heat Wave;Above 90 | Recloser | Normal | 23-0092767 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1857835 | 0 | EPSS Ckt | Y | 2023 | SGF
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | RECLOSER | 9790 | 20230716 | 1211 | 20230716 | 1452 | 2164205 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 209 | 21781 | 36.8905 | -120.7444 | No | Partly Cloudy-Heat Wave;Above 90 |  |  | 23-0092811 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857840 | 0 | EPSS Ckt | Y | 2023 | A & B
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | FUSE | 8962 | 20230716 | 1417 | 20230716 | 1733 | 2164312 | 196 | Distribution Circuit | Equipment Failure/Involved | Underground | 262 | 29894 | 37.3267 | -120.4869 | No | Partly Cloudy-Heat Wave;Above 90 | Connector or Splice (UG) | Broken | 23-0092830 | UG | Sus | 45888889 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857867 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | TRANSFORMER | 320061029197 | 20230716 | 1424 | 20230716 | 1503 | 2164314 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 64 | 2496 | 37.3026 | -120.4783 | No | Partly Cloudy-Heat Wave;Above 90 | Connector or Splice (OH) | Burned Open | 23-0092837 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857871 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 905960 | 20230716 | 1606 | 20230717 | 742 | 2164435 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2628 | 572661 | 37.2274 | -119.7103 | No | Partly Cloudy-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092848 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857881 | 0 | EPSS Ckt | Y | 2023 | B PHASE DCD SGF
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 415726351626 | 20230716 | 1952 | 20230717 | 30 | 2164729 | 278 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 834 | 36.7417 | -120.4597 | No | Partly Cloudy-Heat Wave;Above 90 | Secondary | Normal | 23-0092968 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857982 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319570435665 | 20230716 | 2001 | 20230716 | 2305 | 2164666 | 184 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 920 | 37.4796 | -120.6489 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092914 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857935 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | RECLOSER | 3400 | 20230716 | 2009 | 20230717 | 508 | 2164746 | 539 | Distribution Circuit | 3rd Party | Vehicle | 287 | 51315 | 36.9816 | -120.5941 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0092939 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857955 | 0 | Non-EPSS | N | 2023 | SE TGT
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | TRIP-SAVER | 9628 | 20230716 | 2013 | 20230717 | 950 | 2164751 | 817 | Distribution Circuit | Equipment Failure/Involved | Overhead | 662 | 98866 | 37.1517 | -121.0323 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0092919 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1857939 | 0 | EPSS Ckt | Y | 2023 | NONE
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322368327232 | 20230716 | 2308 | 20230716 | 2356 | 2164900 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 48 | 37.2465 | -119.6882 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0092966 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857980 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | FUSE | 9756 | 20230717 | 638 | 20230717 | 925 | 2165035 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2228 | 37.0551 | -120.7857 | No | Partly Cloudy;32-90 F |  |  | 23-0093069 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858117 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 6413 | 20230717 | 716 | 20230717 | 803 | 2165052 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 188 | 37.7401 | -120.8022 | No | Partly Cloudy;32-90 F |  |  | 23-0093025 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1858036 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 69563 | 20230717 | 718 | 20230717 | 842 | 2165057 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 84 | 37.3015 | -120.3249 | No | Clear;32-90 F |  |  | 23-0093042 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858078 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322368327232 | 20230717 | 851 | 20230717 | 1238 | 2165098 | 227 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 227 | 37.2465 | -119.6882 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 23-0093073 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858123 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318458229454 | 20230717 | 853 | 20230717 | 1300 | 2165271 | 247 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 247 | 37.3076 | -121.0311 | No | Clear;32-90 F | Fuse | Broken | 23-0093242 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858211 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | RECLOSER | 807088 | 20230717 | 954 | 20230717 | 1516 | 2165333 | 322 | Distribution Circuit | 3rd Party | Vehicle | 13 | 3251 | 37.1665 | -120.2383 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Broken- wire on ground | 23-0093087 | OH | Sus | 35469521 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | Yes | No | 1858135 | 0 | EPSS Ckt | N | 2023 | B-C
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10990 | 20230717 | 1146 | 20230717 | 1902 | 2165511 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 524 | 111956 | 37.4964 | -119.811 | No | Clear-Heat Wave;Above 90 | Other | Broken | 23-0093142 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858176 | 0 | EPSS Ckt | Y | 2023 | A- GRD
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320089629421 | 20230717 | 1355 | 20230717 | 1908 | 2165546 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 4538 | 37.3086 | -120.4689 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 23-0093239 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858209 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 10022 | 20230717 | 1428 | 20230717 | 1643 | 2165681 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 10125 | 37.3041 | -119.6009 | No | Partly Cloudy-Heat Wave;Above 90 | Pole-Wood | Broken | 23-0093266 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858219 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 22804 | 20230717 | 1558 | 20230717 | 2357 | 2165807 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 637 | 37.8569 | -120.9376 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 23-0093355 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1858238 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | JUMPER | OJ @ CGC# 320404253792 | 20230717 | 1813 | 20230717 | 2357 | 2165938 | 344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 11696 | 37.9768 | -120.3602 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Broken | 23-0093400 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858264 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | 319702432028 | 20230717 | 2054 | 20230718 | 145 | 2166044 | 291 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1455 | 37.3797 | -120.6036 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093452 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858306 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 22245 | 20230717 | 2140 | 20230718 | 253 | 2166042 | 313 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 313 | 37.2287 | -120.4563 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0093434 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858289 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | FUSE | 6355 | 20230717 | 2241 | 20230718 | 831 | 2166100 | 590 | Distribution Circuit | Equipment Failure/Involved | Underground | 143 | 21342 | 36.9453 | -120.0476 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0093456 | UG | Sus | 35468089 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1858309 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | TRANSFORMER | 319816617760 | 20230718 | 951 | 20230718 | 1057 | 2166494 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 66 | 36.9882 | -120.5639 | No | Clear;32-90 F | Fuse | Broken | 23-0093642 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858493 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | OCB | 1108/2 | 20230718 | 1617 | 20230718 | 1624 | 2166909 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2343 | 16401 | 37.2732 | -120.4872 | No | Partly Cloudy-Lightning;Above 90 | Jumper | Burned Open | 23-0093901 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1858555 | 0 | Non-EPSS | N | 2023 | NA
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | RECLOSER | 149636 | 20230718 | 1630 | 20230718 | 1701 | 2166925 | 31 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 242 | 3902 | 37.2733 | -120.5259 | No | Partly Cloudy-Lightning;Above 90 |  |  | 23-0093901 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858558 | 0 | Non-EPSS | N | 2023 | 51 TIME
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 25153 | 20230718 | 1720 | 20230719 | 35 | 2167001 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2355 | 36.7672 | -120.3798 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0093934 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1858579 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | 319664532502 | 20230718 | 2141 | 20230719 | 329 | 2167319 | 348 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 696 | 37.3927 | -120.6163 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0093949 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858590 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 6110 | 20230719 | 346 | 20230719 | 827 | 2167381 | 281 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 206 | 48251 | 37.128 | -119.7352 | No | Clear;32-90 F |  |  | 23-0093991 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858631 | 0 | EPSS Ckt | Y | 2023 | C & GRD
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | T2362 | 20230719 | 1023 | 20230719 | 1250 | 2167795 | 147 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 147 | 37.3481 | -119.5893 | No | Clear;32-90 F |  |  | 23-0094234 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1858856 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | S1405 | 20230719 | 1301 | 20230719 | 1326 | 2167953 | 25 | Distribution Circuit | 3rd Party | Vehicle | 38 | 950 | 37.7956 | -120.8246 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0094235 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1858857 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320640040437 | 20230719 | 1358 | 20230719 | 2315 | 2168347 | 557 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 557 | 37.6098 | -120.2789 | No | Clear;Above 90 |  |  | 23-0094387 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858921 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | TRANSFORMER | 320153612287 | 20230719 | 1400 | 20230719 | 2242 | 2168107 | 522 | Transformer only | Environmental/External | Lightning | 2 | 1044 | 36.8373 | -120.4488 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0094375 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858915 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | OCB | 1703/2 | 20230719 | 1504 | 20230719 | 2242 | 2168315 | 458 | Distribution Circuit | 3rd Party | Vehicle | 3106 | 327292 | 37.9799 | -120.4136 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0094307 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858892 | 0 | EPSS Ckt | Y | 2023 | A PHASE AND GRD
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | TRANSFORMER | 320181112037 | 20230719 | 1601 | 20230720 | 1 | 2168357 | 480 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 960 | 36.8301 | -120.439 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 23-0094383 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858917 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | TRANSFORMER | 320149812292 | 20230719 | 1752 | 20230719 | 2139 | 2168421 | 227 | Transformer only | Environmental/External | Lightning | 5 | 1135 | 36.8373 | -120.4496 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0094378 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858916 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | RECLOSER | 9370 | 20230719 | 2046 | 20230720 | 324 | 2168494 | 379 | Distribution Circuit | Equipment Failure/Involved | Overhead | 404 | 23842 | 37.4601 | -120.6179 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0094400 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1858929 | 0 | Non-EPSS | N | 2023 | A PH AND GROUND
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320176413031 | 20230719 | 2234 | 20230720 | 1756 | 2168560 | 1156 | Transformer only | Environmental/External | Lightning | 10 | 11560 | 36.8576 | -120.4411 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0094486 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858978 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | SWITCH | 3141 | 20230720 | 153 | 20230720 | 207 | 2168549 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 362 | 3024 | 36.9275 | -120.5415 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0093910 | OH | Sus | 45893920 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1858974 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320180413032 | 20230720 | 337 | 20230720 | 1750 | 2168561 | 853 | Transformer only | Environmental/External | Lightning | 2 | 1706 | 36.8576 | -120.4397 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0094487 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858979 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320155828431 | 20230720 | 815 | 20230720 | 1410 | 2168666 | 355 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2840 | 37.2814 | -120.446 | No | Clear;32-90 F | Fuse | Broken | 23-0094786 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859131 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | TRANSFORMER | 322107515894 | 20230720 | 1000 | 20230720 | 1324 | 2168625 | 204 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 204 | 36.9343 | -119.7803 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0094591 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859075 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | TRANSFORMER | 318925817044 | 20230720 | 1200 | 20230720 | 1406 | 2168897 | 126 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 126 | 36.9676 | -120.8687 | No | Clear;Above 90 | Connector or Splice (OH) | Burned/flashed | 23-0094777 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859128 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 24755 | 20230720 | 1208 | 20230720 | 1359 | 2168903 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 222 | 37.4024 | -121.009 | No | Clear;32-90 F |  |  | 23-0094763 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1859124 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | RECLOSER | 90100 | 20230720 | 1244 | 20230720 | 2101 | 2168934 | 497 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 472 | 67890 | 37.827 | -120.9975 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0094709 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859106 | 0 | Non-EPSS | N | 2023 | A PH & GRD
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 13193 | 20230720 | 1353 | 20230720 | 1447 | 2169037 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 2052 | 36.967 | -120.029 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0094759 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859121 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4707 | 20230720 | 1410 | 20230720 | 1551 | 2168945 | 101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 6161 | 37.5588 | -119.9703 | No | Clear;Above 90 | Insulator | Broken | 23-0094764 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859129 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7327 | 20230720 | 1651 | 20230720 | 1839 | 2169222 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 108 | 37.4725 | -120.6031 | No | Clear;Above 90 |  |  | 23-0094916 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859178 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S20385 | 20230720 | 1803 | 20230720 | 1848 | 2169266 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 225 | 37.817 | -121.0154 | No | Clear;Above 90 |  |  | 23-0094903 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1859167 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318765647478 | 20230720 | 2026 | 20230720 | 2340 | 2169342 | 194 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 776 | 37.803 | -120.9283 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0094947 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859196 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | JUMPER | OJS AT POLE SAP ID# 101031822 | 20230720 | 2046 | 20230720 | 2238 | 2169344 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 224 | 37.968 | -120.3092 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0094931 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859185 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 9655 | 20230720 | 2228 | 20230721 | 22 | 2169446 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 228 | 36.7901 | -120.3625 | No | Clear;32-90 F |  |  | 23-0094986 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1859228 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 2083 | 20230721 | 827 | 20230721 | 1324 | 2169636 | 297 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 297 | 37.1709 | -120.2607 | No | Clear;32-90 F |  |  | 23-0095050 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1859309 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9645 | 20230721 | 920 | 20230721 | 1418 | 2169741 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3278 | 36.7294 | -120.3146 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0095156 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859413 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | SWITCH | 793657 | 20230721 | 1327 | 20230721 | 1428 | 2170007 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 8601 | 37.357 | -120.5981 | No | Clear;Above 90 | Insulator | Broken | 23-0095299 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859452 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320150129530 | 20230721 | 1521 | 20230721 | 1612 | 2170069 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 153 | 37.3116 | -120.448 | No | Clear;Above 90 | Connector or Splice (OH) | Deteriorated | 23-0095391 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859477 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320858544478 | 20230721 | 1945 | 20230721 | 2037 | 2170343 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 52 | 37.7238 | -120.2044 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0095433 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859499 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318765647478 | 20230721 | 2017 | 20230722 | 22 | 2170371 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 980 | 37.803 | -120.9283 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0095453 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859513 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1751 | 20230722 | 607 | 20230722 | 749 | 2170580 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 117 | 11906 | 37.7783 | -120.7799 | No | Clear;32-90 F |  |  | 23-0095511 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859576 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 318764644707 | 20230722 | 1742 | 20230723 | 455 | 2171049 | 673 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 9422 | 37.7272 | -120.9279 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 23-0095602 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859693 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 3623 | 20230722 | 1814 | 20230722 | 1914 | 2171076 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 311 | 18660 | 36.7487 | -120.3869 | No | Partly Cloudy;Above 90 |  |  | 23-0095604 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1859695 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318598147124 | 20230722 | 1819 | 20230722 | 1950 | 2171080 | 91 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 1365 | 37.7932 | -120.9863 | No | Clear;Above 90 | Fuse | Broken | 23-0095611 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859702 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | T910 | 20230722 | 2059 | 20230723 | 742 | 2171262 | 643 | Distribution Circuit | Equipment Failure/Involved | Underground | 69 | 11334 | 37.7591 | -120.8726 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0095617 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859736 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | T5425 | 20230723 | 53 | 20230723 | 1500 | 2171275 | 847 | Distribution Circuit | Equipment Failure/Involved | Underground | 77 | 10413 | 37.7895 | -121.0093 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0095653 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859746 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319587533980 | 20230723 | 623 | 20230723 | 728 | 2171311 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 65 | 37.4334 | -120.6419 | No | Clear;32-90 F | Fuse | Burned Open | 23-0095659 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859753 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | TRANSFORMER | 320870616496 | 20230723 | 1120 | 20230723 | 1249 | 2171450 | 89 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 267 | 36.9527 | -120.2031 | No | Clear;Above 90 |  |  | 23-0095686 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859786 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | TRANSFORMER | 320899216480 | 20230723 | 1123 | 20230723 | 1255 | 2171452 | 92 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 184 | 36.9527 | -120.1932 | No | Clear;Above 90 |  |  | 23-0095690 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1859789 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318816249358 | 20230723 | 1455 | 20230723 | 1717 | 2171624 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 284 | 37.8548 | -120.9112 | No | Clear;Above 90 | Fuse | Broken | 23-0095712 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859812 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320047029407 | 20230723 | 1735 | 20230724 | 212 | 2171822 | 517 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 5170 | 37.3082 | -120.4837 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0095719 | OH | Sus | 45897594 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859820 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 570682 | 20230723 | 1838 | 20230723 | 2055 | 2171843 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1135 | 155165 | 37.2635 | -119.7123 | No | Partly Cloudy;Above 90 |  |  | 23-0095720 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859821 | 0 | EPSS Ckt | Y | 2023 | C PHASE AND GROUND
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | 319650117583 | 20230723 | 2010 | 20230723 | 2111 | 2171535 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 732 | 36.9831 | -120.6212 | No | Partly Cloudy;Above 90 | Secondary | Deteriorated | 23-0095725 | OH | Sus | 31656644 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859827 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 19826 | 20230724 | 805 | 20230724 | 2237 | 2172178 | 872 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1670 | 28125 | 36.8555 | -120.4564 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0095838 | OH | Sus | 31656631 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1859952 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319160044150 | 20230724 | 853 | 20230724 | 1140 | 2172220 | 167 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 668 | 37.7121 | -120.7916 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0095822 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859930 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | RECLOSER | 3330 | 20230724 | 1153 | 20230725 | 220 | 2172549 | 867 | Distribution Circuit | 3rd Party | Vehicle | 1057 | 114431 | 36.7482 | -120.387 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0095953 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | Yes | No | 1860050 | 0 | Non-EPSS | N | 2023 | A- B- C
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | RECLOSER | 9230 | 20230724 | 1238 | 20230724 | 1343 | 2172586 | 65 | Distribution Circuit | Company Initiated | Coordination failure | 2082 | 135330 | 37.9737 | -120.3716 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0096001 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860071 | 0 | EPSS Ckt | Y | 2023 | B & INST
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | 77073 | 20230724 | 1238 | 20230724 | 1656 | 2172592 | 258 | Distribution Circuit | 3rd Party | Vehicle | 10 | 2580 | 37.9736 | -120.359 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0096001 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1860085 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20230724 | 1238 | 20230724 | 1350 | 2172595 | 72 | Distribution Circuit | Company Initiated | Coordination failure | 583 | 41976 | 38.0085 | -120.3034 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0096002 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1860072 | 0 | EPSS Ckt | Y | 2023 | VOLTAGE
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9815 | 20230724 | 1454 | 20230724 | 1835 | 2172708 | 221 | Distribution Circuit | 3rd Party | Vehicle | 12 | 2652 | 36.7564 | -120.3769 | No | Partly Cloudy;Above 90 | Pole-Wood | Broken | 23-0096205 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860124 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 5817 | 20230725 | 437 | 20230725 | 540 | 2173043 | 63 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 210 | 37.0238 | -119.947 | No | Clear;32-90 F |  |  | 23-0096282 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860182 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 7599 | 20230725 | 447 | 20230725 | 1313 | 2173008 | 506 | Distribution Circuit | 3rd Party | Vehicle | 18 | 2624 | 37.1165 | -120.401 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0096316 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860193 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320004329028 | 20230725 | 816 | 20230725 | 906 | 2173250 | 50 | Transformer only | Company Initiated | Construction Activity/equip- company | 23 | 1150 | 37.2975 | -120.4985 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0096377 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860324 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320860356323 | 20230725 | 933 | 20230725 | 1034 | 2173336 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 61 | 38.046 | -120.2018 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0096379 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860328 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1102 | 254421102 | TRANSFORMER | 322481429621 | 20230725 | 956 | 20230725 | 1227 | 2173394 | 151 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 151 | 37.3109 | -119.6478 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0096403 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860354 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321984535131 | 20230725 | 1157 | 20230725 | 1632 | 2173448 | 275 | Transformer only | Vegetation | Tree - fell into line | 1 | 275 | 37.4618 | -119.8201 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0096491 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860387 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320605254060 | 20230725 | 1239 | 20230726 | 6 | 2173538 | 687 | Transformer only | 3rd Party | Vehicle | 3 | 2061 | 37.9849 | -120.2906 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0096553 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860404 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320692253824 | 20230725 | 1348 | 20230725 | 1545 | 2173607 | 117 | Transformer only | 3rd Party | Vehicle | 2 | 234 | 37.9778 | -120.2596 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0096571 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860406 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 248055 | 20230725 | 1348 | 20230725 | 1634 | 2173610 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 443 | 36.9673 | -120.6265 | No | Clear;Above 90 |  |  | 23-0096743 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860435 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 7599 | 20230725 | 1354 | 20230725 | 1521 | s1860426 | 87 | Distribution Circuit | 3rd Party | Vehicle | 18 | 1566 | 37.1165 | -120.401 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0096316 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860426 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 7915 | 20230725 | 1443 | 20230725 | 1809 | 2173654 | 203 | Distribution Circuit | Animal | Bird found | 20 | 4060 | 37.1203 | -120.502 | No | Clear;Above 90 | Transformer (OH) | Normal | 23-0096751 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1860441 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | FUSE | 563217 | 20230725 | 2145 | 20230725 | 2255 | 2173931 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 514 | 37.0255 | -120.2744 | No | Clear;32-90 F |  |  | 23-0096810 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860484 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 24143 | 20230726 | 813 | 20230726 | 1208 | 2174124 | 235 | Distribution Circuit | 3rd Party | Vehicle | 7 | 1645 | 37.1856 | -120.6192 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0096947 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | Yes | No | 1860640 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 318915919728 | 20230726 | 1145 | 20230726 | 1247 | 2174412 | 62 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 124 | 37.0407 | -120.8722 | No | Clear;32-90 F |  |  | 23-0097091 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860712 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 828842 | 20230726 | 1821 | 20230726 | 2038 | 2174780 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1592 | 171818 | 37.2287 | -119.7103 | No | Clear;32-90 F |  |  | 23-0097247 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860748 | 0 | EPSS Ckt | Y | 2023 | C & GRD
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320532853876 | 20230727 | 426 | 20230727 | 1211 | 2174942 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1860 | 37.9795 | -120.3166 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0097359 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860795 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320111529596 | 20230727 | 1015 | 20230727 | 1105 | 2175243 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 500 | 37.3137 | -120.4615 | No | Clear;32-90 F | Secondary | Broken | 23-0097488 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860951 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | JUMPER | FB 12 E/OF 9699 | 20230727 | 1018 | 20230727 | 1318 | 2175334 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 540 | 36.7207 | -120.3148 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0049398 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860965 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20230727 | 1125 | 20230727 | 1319 | 2175415 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 195 | 15301 | 37.8998 | -120.4541 | No | Clear;32-90 F |  |  | 23-0097568 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1860991 | 0 | EPSS Ckt | Y | 2023 | INST (50)
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 24034 | 20230727 | 1318 | 20230727 | 1539 | 2175513 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 705 | 37.5486 | -120.0983 | No | Clear;Above 90 |  |  | 23-0097699 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861023 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | RECLOSER | 9540 | 20230727 | 1612 | 20230728 | 48 | 2175617 | 516 | Distribution Circuit | 3rd Party | Vehicle | 409 | 23128 | 36.9042 | -120.0559 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 23-0097737 | OH | Sus | 31656992 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | Yes | No | 1861028 | 0 | Non-EPSS | N | 2023 | A- B- C
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319603023648 | 20230727 | 1822 | 20230727 | 1830 | 2175606 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 16 | 37.15 | -120.6376 | No | Clear;Above 90 | Transformer (OH) | Normal | 23-0097808 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861046 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 4532 | 20230727 | 2047 | 20230727 | 2223 | 2175825 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 448 | 37.3325 | -120.4147 | No | Clear;32-90 F |  |  | 23-0097864 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861083 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319412830014 | 20230728 | 832 | 20230728 | 1227 | 2176053 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 235 | 37.3241 | -120.7027 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0097946 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861183 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 2117 | 20230728 | 1000 | 20230728 | 1030 | 2176197 | 30 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 100 | 36.8729 | -120.1193 | No | Clear;32-90 F |  |  | 23-0098027 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861260 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | TRANSFORMER | 415671349994 | 20230728 | 1002 | 20230728 | 1325 | 2176198 | 203 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 406 | 36.6972 | -120.4777 | No | Clear;32-90 F |  |  | 23-0098137 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861306 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1102 | 252531102 | FUSE | 6289 | 20230728 | 1027 | 20230728 | 1219 | 2176256 | 112 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 19040 | 37.2556 | -119.5377 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0098057 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861278 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 4749 | 20230728 | 1029 | 20230728 | 1258 | 2176241 | 149 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 745 | 37.3946 | -120.0854 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0098017 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861255 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | JUMPER | OJ 2 SE/OF CGC# 322760329943 | 20230728 | 1121 | 20230728 | 1522 | 2176286 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 7230 | 37.3183 | -119.5519 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0098050 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861272 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 417043554717 | 20230728 | 1311 | 20230728 | 1415 | 2176534 | 64 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 256 | 36.833 | -120.0107 | No | Clear;32-90 F |  |  | 23-0098169 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861317 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | JUMPER | OJ 1 POLE W/OF CGC#320714922154 | 20230728 | 1411 | 20230728 | 1906 | 2176292 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1475 | 37.1083 | -120.2565 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0098052 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861273 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 570682 | 20230728 | 1904 | 20230728 | 2329 | 2176726 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1135 | 300313 | 37.2635 | -119.7123 | No | Clear;32-90 F |  |  | 23-0098220 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861340 | 0 | EPSS Ckt | Y | 2023 | C & GRD
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 4832 | 20230728 | 2033 | 20230728 | 2130 | 2176783 | 57 | Distribution Circuit | Animal | Bird found | 2 | 114 | 37.2806 | -120.4403 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0098229 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861350 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 4887 | 20230729 | 734 | 20230729 | 1250 | 2176908 | 316 | Distribution Circuit | 3rd Party | Vehicle | 14 | 4424 | 37.2146 | -120.4875 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0098277 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861397 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 7239 | 20230729 | 1618 | 20230729 | 1704 | 2177249 | 46 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 126 | 5796 | 37.3535 | -120.5959 | No | Clear;Above 90 |  |  | 23-0098357 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861494 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 26469 | 20230729 | 1641 | 20230729 | 1837 | 2177260 | 116 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 348 | 37.7893 | -120.7555 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0098354 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861490 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | SWITCH | 6058 | 20230729 | 1645 | 20230729 | 2106 | 2177270 | 261 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 20 | 5220 | 37.1514 | -120.0748 | No | Clear;Above 90 | Pole-Wood | Burned/flashed | 23-0098332 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861493 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 20723 | 20230729 | 1859 | 20230730 | 58 | 2177330 | 359 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 1436 | 37.7894 | -120.7576 | No | Clear;Above 90 | Conductor- Overhead | Burned/flashed | 23-0098367 | OH | Sus | 31657399 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861501 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319167730306 | 20230729 | 1859 | 20230729 | 2027 | 2177331 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 88 | 37.3314 | -120.7872 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0098378 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861514 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | SWITCH | 352740 | 20230729 | 2310 | 20230730 | 144 | 2177452 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1564 | 191537 | 37.3384 | -119.6709 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0098407 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861543 | 0 | EPSS Ckt | Y | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | FUSE | 6624 | 20230730 | 332 | 20230730 | 539 | 2177509 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1016 | 37.018 | -120.3616 | No | Partly Cloudy;32-90 F |  |  | 23-0098421 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861558 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 527766 | 20230730 | 653 | 20230730 | 801 | 2177535 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 68 | 37.4633 | -119.9481 | No | Partly Cloudy;32-90 F |  |  | 23-0098426 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1861562 | 0 | EPSS Ckt | Y | 2023 | NONE
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | FUSE | 13172 | 20230730 | 750 | 20230730 | 855 | 2177569 | 65 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 520 | 36.9601 | -120.1158 | No | Clear;32-90 F |  |  | 23-0098438 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861575 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 322309731094 | 20230730 | 1452 | 20230730 | 2129 | 2177778 | 397 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 397 | 37.3499 | -119.706 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0098462 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861607 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | TRANSFORMER | 321289716899 | 20230730 | 1833 | 20230731 | 238 | 2177937 | 485 | Transformer only | 3rd Party | Fire- house or bldg. | 4 | 1940 | 36.9632 | -120.0601 | No | Clear;Above 90 | Secondary | Broken- wire on ground | 23-0098484 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861623 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | TRANSFORMER | 320102029864 | 20230730 | 1949 | 20230730 | 1955 | 2177938 | 6 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 72 | 37.321 | -120.4647 | No | Partly Cloudy;Above 90 | Connector or Splice (OH) | Burned Open | 23-0098490 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1861629 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | TRANSFORMER | 318964220609 | 20230730 | 2003 | 20230730 | 2117 | 2177973 | 74 | Transformer only | Unknown Cause | Patrol - not conducted | 10 | 740 | 37.0652 | -120.8556 | No | Partly Cloudy;32-90 F |  |  | 23-0098493 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1861631 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230730 | 2332 | 20230731 | 816 | 2178046 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 451 | 196951 | 38.0052 | -120.4062 | No | Partly Cloudy;32-90 F | Recloser | Arcing | 23-0098523 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861661 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | OTHER | WIRE DOWN CORNER OF MCHENRY & JONES | 20230731 | 405 | 20230731 | 830 | 2178100 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 589 | 36116 | 37.7731 | -120.9961 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0098535 | OH | Sus | 31657506 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | Yes | 1861673 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 905960 | 20230731 | 1102 | 20230731 | 1122 | 2178443 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 2504 | 50080 | 37.2274 | -119.7103 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0098669 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861831 | 0 | EPSS Ckt | Y | 2023 | SGF + DCD
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | FUSE | 10839 | 20230731 | 1809 | 20230731 | 1959 | 2178882 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1760 | 37.0352 | -120.8494 | No | Partly Cloudy;Above 90 |  |  | 23-0098889 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861914 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320037928671 | 20230731 | 1820 | 20230731 | 2106 | 2178832 | 166 | Transformer only | Equipment Failure/Involved | Underground | 1 | 166 | 37.2883 | -120.4866 | No | Clear;Above 90 | Conductor- Underground | Deteriorated | 23-0098870 | UG | Sus | 31657577 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861899 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 8170 | 20230731 | 1936 | 20230731 | 2028 | 2178975 | 52 | Distribution Circuit | Animal | Bird found | 501 | 26052 | 37.9873 | -120.2605 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0098883 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861911 | 0 | EPSS Ckt | Y | 2023 | B & C
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 4593 | 20230731 | 2045 | 20230731 | 2327 | 2179039 | 162 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 15 | 2430 | 37.2289 | -120.4609 | No | Clear;32-90 F |  |  | 23-0098916 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1861933 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230801 | 712 | 20230801 | 1014 | 2179150 | 182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 451 | 79370 | 38.0052 | -120.4062 | No | Partly Cloudy;32-90 F | Recloser | Arcing | 23-0098950 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1861964 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 20597 | 20230801 | 744 | 20230801 | 1435 | 2179171 | 411 | Distribution Circuit | 3rd Party | Vehicle | 7 | 2877 | 37.776 | -120.8089 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0098960 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1861982 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | FUSE | 758005 | 20230801 | 1332 | 20230801 | 1652 | 2179605 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 200 | 36.8295 | -120.0981 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0099198 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1862179 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322488630461 | 20230801 | 1345 | 20230801 | 1516 | 2179616 | 91 | Transformer only | 3rd Party | Other | 1 | 91 | 37.334 | -119.6445 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0099246 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862192 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | FUSE | 6688 | 20230801 | 2323 | 20230802 | 223 | 2180044 | 180 | Distribution Circuit | Animal | Bird found | 12 | 2160 | 36.8222 | -120.1059 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0099381 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1862257 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | TRANSFORMER | 320693822288 | 20230802 | 211 | 20230802 | 315 | 2180063 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 64 | 37.112 | -120.2634 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0099385 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862261 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | FUSE | 1815 | 20230802 | 821 | 20230802 | 1152 | 2180244 | 211 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 422 | 36.9672 | -120.301 | No | Partly Cloudy;32-90 F |  |  | 23-0099580 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862483 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | T2196 | 20230802 | 1220 | 20230803 | 248 | 2180778 | 868 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 13441 | 36.9559 | -120.0908 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0099691 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862517 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 90090 | 20230802 | 1302 | 20230802 | 2046 | 2180708 | 464 | Distribution Circuit | 3rd Party | Vehicle | 2704 | 382862 | 37.9028 | -120.4538 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0099632 | OH | Sus | 31658031 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1862502 | 0 | EPSS Ckt | Y | 2023 | A & C
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | FUSE | 5591 | 20230802 | 1615 | 20230802 | 1819 | 2180841 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 10540 | 37.0287 | -119.7252 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0099718 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862534 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 3736 | 20230803 | 314 | 20230803 | 933 | 2181096 | 379 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3790 | 36.792 | -120.2592 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0099880 | OH | Sus | 45908437 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1862597 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 319919722988 | 20230803 | 1104 | 20230803 | 2105 | 2181488 | 601 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 601 | 37.1315 | -120.5285 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0100077 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862789 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320311228948 | 20230803 | 1227 | 20230803 | 1325 | 2181613 | 58 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 58 | 37.2951 | -120.3928 | No | Clear;32-90 F |  |  | 23-0100159 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862834 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 3429 | 20230803 | 1240 | 20230803 | 1458 | 2181619 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 690 | 36.7358 | -120.7124 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0100130 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862813 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | S2689 | 20230803 | 1532 | 20230803 | 1629 | 2181758 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 152 | 37.8568 | -120.9852 | No | Clear;32-90 F |  |  | 23-0100245 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862857 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322375026325 | 20230803 | 1806 | 20230803 | 2022 | 2181863 | 136 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 136 | 37.2203 | -119.6851 | No | Clear;32-90 F |  |  | 23-0100288 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1862872 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 12239 | 20230803 | 1846 | 20230803 | 1935 | 2181882 | 49 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 196 | 37.1443 | -120.9583 | No | Clear;32-90 F | Fuse | Broken | 23-0100307 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1862885 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 1835 | 20230803 | 2347 | 20230804 | 135 | 2182016 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1836 | 37.7838 | -121.0525 | No | Clear;32-90 F |  |  | 23-0100365 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1862924 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320691055922 | 20230804 | 1112 | 20230804 | 1415 | 2182373 | 183 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 549 | 38.0357 | -120.2608 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100625 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863116 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 9806 | 20230804 | 1719 | 20230805 | 1603 | 2182678 | 1364 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 14 | 8384 | 36.8558 | -120.4177 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 23-0100782 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | Yes | No | 1863168 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 7319 | 20230805 | 300 | 20230805 | 835 | 2182822 | 335 | Distribution Circuit | 3rd Party | Vehicle | 216 | 21839 | 37.3968 | -120.7055 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0100835 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1863218 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20230805 | 710 | 20230805 | 1031 | 2182853 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1310 | 262358 | 38.0063 | -120.3474 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100845 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863228 | 0 | EPSS Ckt | Y | 2023 | B & C
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L879 | 20230805 | 1044 | 20230805 | 1512 | 2183034 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1836 | 38.0394 | -120.3454 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100889 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863311 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10284 | 20230805 | 1137 | 20230805 | 1242 | 2183052 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 1300 | 37.3877 | -119.6326 | No | Clear;32-90 F | Insulator | Broken | 23-0100880 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1863306 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 90570 | 20230805 | 1248 | 20230805 | 1451 | 2183109 | 123 | Distribution Circuit | Animal | Bird found | 667 | 53241 | 37.9574 | -120.4481 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0100901 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863313 | 0 | EPSS Ckt | N | 2023 | A & C
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | FUSE | 43661 | 20230805 | 1311 | 20230805 | 2006 | 2183161 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1660 | 37.0409 | -120.274 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0100917 | OH | Sus | 45912119 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1863325 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 90570 | 20230805 | 1502 | 20230805 | 1600 | 2183192 | 58 | Distribution Circuit | Animal | Bird found | 668 | 27053 | 37.9574 | -120.4481 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0100901 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863332 | 0 | EPSS Ckt | N | 2023 | A & C
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230806 | 718 | 20230806 | 955 | 2183507 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 451 | 69112 | 38.0052 | -120.4062 | No | Clear;32-90 F | Recloser | Arcing | 23-0100985 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863388 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 318964046299 | 20230806 | 953 | 20230806 | 1026 | 2183568 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 231 | 37.7707 | -120.8595 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0100997 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1863407 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322476628875 | 20230806 | 1559 | 20230806 | 1703 | 2183714 | 64 | Transformer only | Vegetation | Tree - fell into line | 1 | 64 | 37.2903 | -119.6498 | No | Clear;Above 90 | Transformer (OH) | Broken | 23-0101033 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1863433 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | RECLOSER | 9790 | 20230806 | 1846 | 20230807 | 0 | 2183785 | 314 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 209 | 27750 | 36.8905 | -120.7444 | No | Clear;Above 90 |  |  | 23-0101046 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863446 | 0 | EPSS Ckt | Y | 2023 | B & C
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 6887 | 20230807 | 534 | 20230807 | 703 | 2184007 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 3560 | 36.9592 | -119.9121 | No | Clear;32-90 F |  |  | 23-0101106 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863508 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 320194812473 | 20230807 | 646 | 20230807 | 1633 | 2184040 | 587 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 587 | 36.8419 | -120.4343 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0101168 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863610 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 25154 | 20230807 | 908 | 20230807 | 2148 | 2184276 | 760 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1552 | 36.7613 | -120.3837 | No | Clear;32-90 F | Pole-Wood | On Ground | 23-0101191 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863656 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | TRANSFORMER | T2370 | 20230807 | 1737 | 20230808 | 551 | 2185025 | 734 | Distribution Circuit | Equipment Failure/Involved | Underground | 103 | 29744 | 36.9682 | -120.0753 | No | Partly Cloudy;Above 90 | Transformer (UG) | Broken | 23-0101450 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863785 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 320053524157 | 20230807 | 1803 | 20230807 | 2230 | 2185002 | 267 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 267 | 37.164 | -120.4832 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0101448 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863783 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 11565 | 20230807 | 1935 | 20230808 | 409 | 2185077 | 514 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1028 | 37.2511 | -120.3481 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 23-0101460 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1863795 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | TRANSFORMER | 320114929154 | 20230808 | 3 | 20230808 | 59 | 2185147 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 1400 | 37.3012 | -120.4602 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0101495 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1863824 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 2473 | 20230808 | 700 | 20230808 | 828 | 2185347 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 880 | 37.2821 | -121.031 | No | Clear;32-90 F |  |  | 23-0101597 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863932 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320130222564 | 20230808 | 901 | 20230808 | 2350 | 2185418 | 889 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 889 | 37.12 | -120.4554 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0101617 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863988 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | RECLOSER | 90430 | 20230808 | 922 | 20230808 | 1046 | 2185471 | 84 | Distribution Circuit | Animal | Squirrel | 180 | 14046 | 37.3113 | -121.0479 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0101633 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863999 | 0 | EPSS Ckt | Y | 2023 | A & C
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | TRANSFORMER | T6771 | 20230808 | 1320 | 20230808 | 1816 | 2185840 | 296 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 2960 | 37.0645 | -120.8208 | No | Clear;Above 90 | Transformer (UG) | Leaking | 23-0101822 | UG | Sus | 35475927 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864068 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | INTERRUPTER | 558890 | 20230808 | 1433 | 20230808 | 1611 | 2185899 | 98 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 98 | 36.8516 | -119.9512 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0101824 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864073 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | OCB | 1103/2 | 20230808 | 1545 | 20230809 | 14 | 2185944 | 509 | Distribution Circuit | 3rd Party | Vehicle | 411 | 36399 | 37.1208 | -120.473 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0101885 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1864086 | 0 | Non-EPSS | N | 2023 | A B C TIME
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | JUMPER | 9627 | 20230808 | 1643 | 20230809 | 139 | 2186201 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1977 | 37.0708 | -120.9982 | No | Clear;32-90 F | Jumper | Broken | 23-0101962 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1864129 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | JUMPER | 9883 | 20230808 | 1758 | 20230808 | 2137 | 2186075 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 5694 | 36.7649 | -120.3817 | No | Clear;Above 90 | Jumper | Burned Open | 23-0101934 | OH | Sus | 31662466 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1864110 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 53957 | 20230809 | 543 | 20230809 | 658 | 2186236 | 75 | Distribution Circuit | Animal | Bird found | 73 | 5475 | 38.0333 | -120.4031 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0101994 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1864150 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319409031457 | 20230809 | 748 | 20230809 | 1628 | 2186299 | 520 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1560 | 37.3639 | -120.7037 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0102067 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864304 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 667248 | 20230809 | 1305 | 20230809 | 1333 | 2186750 | 28 | Distribution Circuit | Company Initiated | Personnel- company | 2890 | 71108 | 38.049 | -120.2357 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0102219 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1864377 | 0 | EPSS Ckt | N | 2023 | A-B - SGF & DCD
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 8130 | 20230809 | 1355 | 20230809 | 1528 | 2186793 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 437 | 40641 | 38.0278 | -120.2568 | No | Clear;32-90 F | Metering Equipment | Failed/Faulted | 23-0102219 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864387 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | TRANSFORMER | 318973846041 | 20230809 | 1655 | 20230809 | 1753 | 2186847 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 522 | 37.764 | -120.8561 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0102370 | OH | Sus | 45918517 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864407 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | OTHER | WIRE DOWN 1 SPAN E/OF 4948 | 20230810 | 750 | 20230810 | 2127 | 2187377 | 817 | Distribution Circuit | Equipment Failure/Involved | Overhead | 592 | 23716 | 37.355 | -120.6198 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on object | 23-0102610 | OH | Sus | 45923086 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1864638 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 13214 | 20230810 | 1422 | 20230810 | 1658 | 2187917 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 4368 | 36.9725 | -119.8853 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0102798 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1864720 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 905960 | 20230810 | 1458 | 20230810 | 1739 | 2187965 | 161 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2628 | 416493 | 37.2274 | -119.7103 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 23-0102840 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864725 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230810 | 1727 | 20230810 | 1813 | 2188130 | 46 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 261 | 12006 | 37.0552 | -120.0295 | No | Clear;Above 90 |  |  | 23-0102973 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1864755 | 0 | EPSS Ckt | N | 2023 | GRD
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 22919 | 20230810 | 1954 | 20230810 | 2132 | 2188208 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 588 | 37.1378 | -120.2798 | No | Partly Cloudy;32-90 F |  |  | 23-0102999 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1864767 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318810919972 | 20230810 | 2322 | 20230810 | 2329 | 2187500 | 7 | Transformer only | 3rd Party | Customer Equipment | 1 | 7 | 37.048 | -120.9083 | No | Overcast;32-90 F | Customer Equipment | Burned/flashed | 23-0103042 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864807 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320763148631 | 20230811 | 26 | 20230811 | 209 | 2188285 | 103 | Transformer only | Animal | Other | 1 | 103 | 37.8346 | -120.2362 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0103054 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864817 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 3287 | 20230811 | 941 | 20230811 | 1602 | 2188524 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 381 | 36.9842 | -120.6443 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Burned/flashed | 23-0103227 | OH | Sus | 31662955 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864965 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 9590 | 20230811 | 1002 | 20230811 | 1020 | 2188528 | 18 | Distribution Circuit | Company Initiated | Personnel- company | 502 | 9036 | 37.4593 | -119.8997 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0103200 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864951 | 0 | EPSS Ckt | Y | 2023 | C PHASE & GRD
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | TRANSFORMER | 414925055722 | 20230811 | 1228 | 20230811 | 1429 | 2188655 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 121 | 36.8511 | -120.7363 | No | Clear;32-90 F | Fuse | Broken | 23-0103399 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865038 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | TRANSFORMER | 321945621208 | 20230811 | 1255 | 20230811 | 1345 | 2188674 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 50 | 37.0806 | -119.8331 | No | Clear;32-90 F | Fuse | Broken | 23-0103360 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865022 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | 319581519376 | 20230811 | 1826 | 20230811 | 2005 | 2188897 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 99 | 37.0318 | -120.6447 | No | Clear;32-90 F | Fuse | Broken | 23-0103510 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865082 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 7375 | 20230811 | 2204 | 20230811 | 2318 | 2188960 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 274 | 20276 | 37.2894 | -120.5011 | No | Clear;32-90 F |  |  | 23-0103538 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865110 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 4769 | 20230811 | 2343 | 20230812 | 1132 | 2188981 | 709 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 21979 | 37.2912 | -120.504 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0103540 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865113 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | OCB | 1106/2 | 20230812 | 39 | 20230812 | 1805 | 2188986 | 1046 | Distribution Circuit | 3rd Party | Vehicle | 1658 | 191087 | 37.3159 | -121.0144 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0103541 | OH | Sus | 31663105 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1865114 | 0 | Non-EPSS | N | 2023 | A&B PHASE TIME OC
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | S1805 | 20230812 | 1516 | 20230812 | 2212 | 2189270 | 416 | Distribution Circuit | 3rd Party | Vehicle | 138 | 29273 | 37.8384 | -121.005 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 23-0103659 | OH | Sus | 35480422 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1865246 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 3573 | 20230812 | 1549 | 20230812 | 1945 | 2189310 | 234 | Distribution Circuit | Equipment Failure/Involved | Underground | 37 | 8658 | 36.7506 | -120.3784 | No | Clear;Above 90 | Connector or Splice (UG) | Failed/Faulted | 23-0103672 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1865259 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 86825 | 20230812 | 2023 | 20230812 | 2125 | 2189399 | 62 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 103 | 37.4754 | -120.5931 | No | Clear;32-90 F |  |  | 23-0103680 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865270 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319183043890 | 20230812 | 2126 | 20230813 | 1000 | 2189434 | 754 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 754 | 37.7051 | -120.7836 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103697 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865291 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 5499 | 20230812 | 2229 | 20230812 | 2238 | 2189442 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 30 | 270 | 37.8286 | -121.016 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0103659 | OH | Sus | 35480422 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1865284 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 7726 | 20230813 | 819 | 20230813 | 931 | 2189552 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 1969 | 37.3132 | -120.5755 | No | Clear;32-90 F |  |  | 23-0103723 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865324 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320118054188 | 20230813 | 1505 | 20230813 | 2204 | 2189687 | 419 | Transformer only | Vegetation | Tree - fell into line | 1 | 419 | 37.9884 | -120.4609 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0103773 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1865358 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | OCB | 1104/2 | 20230813 | 1525 | 20230814 | 45 | 2189680 | 560 | Distribution Circuit | Environmental/External | Lightning | 630 | 50310 | 37.6655 | -119.8413 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 23-0103765 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1865351 | 0 | EPSS Ckt | Y | 2023 | BC&GRD
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 8921 | 20230813 | 1529 | 20230813 | 1650 | 2189676 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 486 | 37.636 | -120.5564 | No | Partly Cloudy;Above 90 |  |  | 23-0103770 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865355 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | 20331 | 20230813 | 1746 | 20230814 | 452 | 2189718 | 666 | Distribution Circuit | Environmental/External | Lightning | 38 | 13022 | 38.1982 | -120.013 | No | Clear-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103813 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865393 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 10600 | 20230813 | 1749 | 20230814 | 139 | 2189724 | 470 | Distribution Circuit | Environmental/External | Lightning | 846 | 109102 | 38.066 | -120.1888 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103775 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1865360 | 0 | EPSS Ckt | Y | 2023 | ABC- INST
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20230813 | 1802 | 20230814 | 1044 | 2189730 | 1002 | Distribution Circuit | Environmental/External | Lightning | 2013 | 888641 | 38.0063 | -120.3474 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103777 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865363 | 0 | EPSS Ckt | Y | 2023 | B&C PHASE
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230814 | 208 | 20230814 | 350 | 2189941 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 451 | 46002 | 38.0052 | -120.4062 | No | Partly Cloudy;32-90 F | Other | Malfunctioning | 23-0103837 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865413 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230814 | 818 | 20230814 | 1040 | 2189994 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 451 | 64042 | 38.0052 | -120.4062 | No | Partly Cloudy;32-90 F | Other | Malfunctioning | 23-0103881 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865474 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 180951 | 20230814 | 1332 | 20230814 | 1916 | 2190575 | 344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1032 | 37.0218 | -120.8729 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0104102 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1865636 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 10400 | 20230814 | 1508 | 20230814 | 1834 | 2190664 | 206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1489 | 37406 | 37.2218 | -119.7687 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0104193 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865649 | 0 | EPSS Ckt | N | 2023 | B- G- INST
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20230814 | 1519 | 20230814 | 2218 | 2190683 | 419 | Distribution Circuit | Equipment Failure/Involved | Overhead | 146 | 17239 | 37.0679 | -119.9091 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0104230 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865658 | 0 | EPSS Ckt | N | 2023 | B PH & GRD
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | TRANSFORMER | 320157029613 | 20230814 | 1633 | 20230814 | 2326 | 2190623 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2035 | 37.3139 | -120.4458 | No | Clear;Above 90 | Transformer (OH) | Broken | 23-0104234 | OH | Sus | 31663227 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865660 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321408061965 | 20230814 | 1821 | 20230814 | 2118 | 2190735 | 177 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 531 | 38.2013 | -120.0109 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0104269 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865677 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 43841 | 20230814 | 2030 | 20230814 | 2123 | 2190957 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 53 | 37.9936 | -120.2744 | No | Partly Cloudy;32-90 F |  |  | 23-0104289 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1865696 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | FUSE | 7219 | 20230814 | 2138 | 20230814 | 2333 | 2190985 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 6555 | 37.3208 | -120.5297 | No | Clear;32-90 F |  |  | 23-0104305 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865712 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | T0837 | 20230814 | 2351 | 20230815 | 1209 | 2191178 | 738 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 8226 | 37.3211 | -120.5309 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0104314 | UG | Sus | 35480863 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865719 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | JUMPER | WIRE DOWN | 20230815 | 348 | 20230815 | 1424 | 2191570 | 636 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4452 | 37.0847 | -120.4377 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0104512 | OH | Sus | 45928120 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | Yes | No | 1865902 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 94866 | 20230815 | 519 | 20230815 | 735 | 2191227 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 10200 | 37.7156 | -120.457 | No | Clear;32-90 F |  |  | 23-0104357 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865751 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230815 | 733 | 20230815 | 1244 | 2191267 | 311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 451 | 73361 | 38.0052 | -120.4062 | No | Clear;32-90 F | Insulator | Failed/Faulted | 23-0104369 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865757 | 0 | EPSS Ckt | Y | 2023 | DCD
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230815 | 952 | 20230815 | 1026 | 2191503 | 34 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 261 | 8874 | 37.0552 | -120.0295 | No | Clear;32-90 F |  |  | 23-0104457 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865887 | 0 | EPSS Ckt | N | 2023 | B&C
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | 21133 | 20230815 | 1233 | 20230815 | 1258 | 2191695 | 25 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 25 | 37.7359 | -120.8813 | No | Clear;Above 90 |  |  | 23-0104565 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865920 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321406061966 | 20230815 | 1339 | 20230816 | 315 | 2191758 | 816 | Transformer only | Environmental/External | Lightning | 2 | 1632 | 38.2013 | -120.0116 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0104763 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865972 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9645 | 20230815 | 1440 | 20230815 | 1525 | 2191814 | 45 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 495 | 36.7294 | -120.3146 | No | Clear;Above 90 | Fuse | Broken | 23-0104715 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1865962 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1101 | 162671101 | FUSE | 8905 | 20230815 | 1501 | 20230815 | 2255 | 2191836 | 474 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 5214 | 37.5604 | -121.2117 | No | Clear;Above 90 |  |  | 23-0104854 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866040 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 2083 | 20230815 | 1631 | 20230815 | 2143 | 2191931 | 312 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 624 | 37.1709 | -120.2607 | No | Clear;32-90 F |  |  | 23-0104827 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866014 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320516042098 | 20230815 | 1701 | 20230816 | 54 | 2192004 | 473 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 946 | 37.6572 | -120.3214 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0104808 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865999 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 84944 | 20230815 | 1727 | 20230816 | 58 | 2192023 | 451 | Distribution Circuit | Company Initiated | Personnel- company | 3076 | 1342548 | 37.9525 | -120.3686 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0104770 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865975 | 0 | EPSS Ckt | Y | 2023 | SGF AND DCD
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | RECLOSER | 1990 | 20230815 | 2249 | 20230816 | 1217 | 2192292 | 808 | Distribution Circuit | Equipment Failure/Involved | Underground | 636 | 252719 | 36.9601 | -120.0763 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0104857 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866041 | 0 | Non-EPSS | N | 2023 | E CODE 30
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9645 | 20230816 | 441 | 20230816 | 1243 | 2192353 | 482 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 133 | 12012 | 36.7294 | -120.3146 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 23-0104884 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1866061 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | FUSE | 3855 | 20230816 | 840 | 20230816 | 1723 | 2192571 | 523 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2092 | 36.9278 | -120.4804 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0104999 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866219 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | FUSE | 11544 | 20230816 | 855 | 20230816 | 1006 | 2192605 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 142 | 37.3034 | -120.5029 | No | Clear;32-90 F |  |  | 23-0104994 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866214 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 8997 | 20230816 | 947 | 20230816 | 1135 | 2192865 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 108 | 37.3457 | -120.6733 | No | Clear;Above 90 |  |  | 23-0105046 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866251 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 54727 | 20230816 | 1007 | 20230816 | 1110 | 2192730 | 63 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 17 | 1051 | 37.7175 | -120.6184 | No | Clear;Above 90 |  |  | 23-0105022 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866234 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | RECLOSER | 3144 | 20230816 | 1114 | 20230816 | 1138 | 2192833 | 24 | Distribution Circuit | Company Initiated | Personnel- company | 219 | 5256 | 37.9906 | -120.3839 | No | Partly Cloudy;Above 90 | Conductor- Overhead | Normal | 23-0105032 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866242 | 0 | EPSS Ckt | Y | 2023 | A & GRD
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320664253864 | 20230816 | 1135 | 20230816 | 1409 | 2192938 | 154 | Transformer only | 3rd Party | Vehicle | 1 | 154 | 37.9792 | -120.2697 | No | Partly Cloudy;Above 90 | Fuse | Normal | 23-0105151 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866287 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 23129 | 20230816 | 1500 | 20230816 | 1554 | 2193029 | 54 | Distribution Circuit | 3rd Party | Vehicle | 4 | 216 | 36.8951 | -119.8397 | No | Partly Cloudy;Above 90 | Connector or Splice (OH) | Broken | 23-0105248 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866313 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 319096447133 | 20230816 | 1742 | 20230816 | 1840 | 2193056 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 116 | 37.794 | -120.8137 | No | Partly Cloudy;Above 90 | Connector or Splice (OH) | Broken | 23-0105284 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866329 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320516042098 | 20230816 | 1832 | 20230817 | 33 | 2193193 | 361 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 722 | 37.6572 | -120.3214 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 23-0105297 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866339 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318726347701 | 20230816 | 2149 | 20230817 | 147 | 2193331 | 238 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1428 | 37.8093 | -120.942 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0105325 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866362 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322488030534 | 20230816 | 2311 | 20230817 | 32 | 2193377 | 81 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 648 | 37.3357 | -119.645 | No | Partly Cloudy;32-90 F |  |  | 23-0105362 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1866402 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 19085 | 20230816 | 2351 | 20230817 | 921 | 2193387 | 570 | Distribution Circuit | 3rd Party | Vehicle | 16 | 8964 | 37.3295 | -120.8514 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0105350 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866400 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 5488 | 20230817 | 29 | 20230817 | 300 | 2193395 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2416 | 36.9228 | -119.8581 | No | Partly Cloudy;32-90 F |  |  | 23-0105370 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866411 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | TRANSFORMER | 318848048020 | 20230817 | 531 | 20230817 | 752 | 2193467 | 141 | Transformer only | 3rd Party | Vehicle | 1 | 141 | 37.8183 | -120.8998 | No | Clear;32-90 F | Fuse | Normal | 23-0105418 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866430 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 6225 | 20230817 | 631 | 20230817 | 908 | 2193469 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 628 | 36.8947 | -119.8108 | No | Partly Cloudy;32-90 F |  |  | 23-0105456 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866483 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 5841 | 20230817 | 744 | 20230817 | 854 | 2193509 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 700 | 37.7762 | -120.7898 | No | Clear;32-90 F |  |  | 23-0105433 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866448 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319175844037 | 20230817 | 940 | 20230817 | 1524 | 2193628 | 344 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 344 | 37.7091 | -120.7862 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105538 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866527 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320328723740 | 20230817 | 1353 | 20230817 | 1854 | 2193857 | 301 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 301 | 37.1528 | -120.3883 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0105673 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866575 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | OCB | 2102/2 | 20230817 | 1647 | 20230817 | 2011 | 2194001 | 204 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3330 | 567418 | 37.5045 | -120.0076 | No | Clear;Above 90 | Jumper | Burned Open | 23-0105744 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866586 | 0 | EPSS Ckt | Y | 2023 | PH- GRD- INSTANTANEOUS
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 20230817 | 1727 | 20230818 | 114 | 2194055 | 467 | Distribution Circuit | 3rd Party | Vehicle | 1871 | 451625 | 37.8308 | -120.2369 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0105765 | OH | Sus | 35481654 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866593 | 0 | EPSS Ckt | Y | 2023 | B & C
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 7266 | 20230817 | 1817 | 20230818 | 1048 | 2194096 | 991 | Distribution Circuit | Equipment Failure/Involved | Underground | 114 | 56399 | 37.3184 | -121.0102 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0105839 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866654 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 171061 | 20230818 | 105 | 20230818 | 312 | 2194315 | 127 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 1143 | 37.1579 | -120.2651 | No | Partly Cloudy;32-90 F |  |  | 23-0105852 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866663 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2447 | 20230818 | 644 | 20230818 | 1348 | 2194439 | 424 | Distribution Circuit | Animal | Squirrel | 102 | 10947 | 38.0531 | -120.2027 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105921 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866712 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322157625556 | 20230818 | 654 | 20230818 | 1212 | 2194440 | 318 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 954 | 37.1998 | -119.7591 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0106050 | OH | Sus | 45933286 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866834 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 4984 | 20230818 | 659 | 20230818 | 919 | 2194444 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 4060 | 37.3212 | -120.4658 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0105916 | OH | Sus | 31663958 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866699 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 94507 | 20230818 | 829 | 20230818 | 1059 | 2194592 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1050 | 37.4763 | -120.585 | No | Clear;32-90 F |  |  | 23-0106046 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866831 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | JUMPER | OJ 4 POLES W/OF CGC# 320760428829 | 20230818 | 947 | 20230818 | 1020 | 2194733 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 33 | 37.2873 | -120.2469 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0105985 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866812 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | T507634 | 20230818 | 1016 | 20230818 | 1048 | 2194787 | 32 | Transformer only | Equipment Failure/Involved | Underground | 1 | 32 | 36.8516 | -119.9522 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0106023 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866823 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | SWITCH | L717 | 20230818 | 1032 | 20230818 | 1046 | 2194793 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 318 | 4452 | 37.8526 | -120.1903 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0105765 | OH | Sus | 35481654 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1866825 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7734 | 20230818 | 1124 | 20230818 | 1225 | 2194859 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 122 | 37.2639 | -120.7428 | No | Clear;32-90 F |  |  | 23-0106121 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866874 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | RECLOSER | 421930 | 20230818 | 1146 | 20230818 | 1153 | 2194872 | 7 | Distribution Circuit | Animal | Other | 50 | 350 | 37.4937 | -120.5004 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0106095 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866851 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 25864 | 20230818 | 1424 | 20230818 | 1506 | 2194995 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 168 | 37.0144 | -120.1932 | No | Clear;Above 90 | Crossarm- Wood | Deteriorated | 23-0106166 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866891 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9645 | 20230818 | 2024 | 20230818 | 2220 | 2195337 | 116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1276 | 36.7294 | -120.3146 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0106281 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866928 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320318252968 | 20230818 | 2225 | 20230818 | 2349 | 2195358 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 84 | 37.9546 | -120.391 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0106305 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866948 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320551854747 | 20230819 | 1355 | 20230819 | 1526 | 2195692 | 91 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 273 | 38.0034 | -120.3096 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0106384 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867062 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 13165 | 20230819 | 1752 | 20230819 | 1840 | 2195968 | 48 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 176 | 37.0069 | -119.9917 | No | Partly Cloudy;Above 90 |  |  | 23-0106449 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867115 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 2995 | 20230819 | 1818 | 20230820 | 2004 | 2196072 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 35824 | 36.9129 | -119.795 | No | Overcast-Lightning;32-90 F | Pole-Wood | Broken | 23-0106466 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867132 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 6563 | 20230819 | 1835 | 20230819 | 2238 | 2196139 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 20244 | 36.9353 | -119.912 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0106514 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1867183 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1103 | 253671103 | RECLOSER | 90540 | 20230819 | 1843 | 20230820 | 1335 | 2196163 | 1132 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 3396 | 36.6332 | -120.6422 | No | Partly Cloudy;32-90 F |  |  | 23-0106451 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867117 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 10400 | 20230819 | 1846 | 20230820 | 1225 | 2196165 | 1059 | Distribution Circuit | Environmental/External | Lightning | 1489 | 286755 | 37.2218 | -119.7687 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106454 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867119 | 0 | EPSS Ckt | Y | 2023 | C PHASE & GRD & INSTANTANEOUS
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 929360 | 20230819 | 1921 | 20230819 | 2031 | 2196275 | 70 | Distribution Circuit | Vegetation | Tree - fell into line | 2863 | 197604 | 37.4926 | -119.9661 | No | Overcast-Drizzle-Lightning;32-90 F | Pole-Wood | Broken | 23-0106462 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867128 | 0 | EPSS Ckt | Y | 2023 | A B INST
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20230819 | 1936 | 20230820 | 1201 | 2196287 | 985 | Distribution Circuit | Environmental/External | Lightning | 258 | 245256 | 37.5694 | -120.1177 | No | Overcast-Drizzle-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0106467 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867133 | 0 | EPSS Ckt | Y | 2023 | A C INSTANTANEOUS
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322340226532 | 20230819 | 2000 | 20230819 | 2327 | 2196302 | 207 | Transformer only | Animal | Other | 3 | 621 | 37.2266 | -119.6971 | No | Overcast-Lightning;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0106525 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867194 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320139529662 | 20230819 | 2006 | 20230820 | 1038 | 2196307 | 872 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 9680 | 37.3154 | -120.4517 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106589 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867268 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 76694 | 20230819 | 2008 | 20230820 | 1755 | 2196321 | 1307 | Distribution Circuit | Environmental/External | Lightning | 33 | 19419 | 37.7405 | -120.1279 | No | Overcast-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106474 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1867140 | 0 | EPSS Ckt | Y | 2023 | A B C GRD
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320919146526 | 20230819 | 2029 | 20230821 | 7 | 2196326 | 1658 | Transformer only | Environmental/External | Lightning | 3 | 4974 | 37.7796 | -120.1822 | No | Overcast-Drizzle-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106684 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867337 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20230819 | 2037 | 20230820 | 1215 | 2196349 | 938 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 582 | 498916 | 38.0085 | -120.3034 | No | Overcast-Lightning;32-90 F |  |  | 23-0106483 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867150 | 0 | EPSS Ckt | Y | 2023 | GRD TARGET
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20230819 | 2038 | 20230820 | 851 | 2196347 | 733 | Distribution Circuit | Environmental/External | Lightning | 687 | 169317 | 37.9574 | -120.3132 | No | Overcast-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106484 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1867151 | 0 | EPSS Ckt | Y | 2023 | B PH- GROUND- INST OC
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 10940 | 20230819 | 2041 | 20230819 | 2327 | 2196352 | 166 | Distribution Circuit | Environmental/External | Lightning | 635 | 105410 | 37.9883 | -120.2832 | No | Overcast-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0106493 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1867160 | 0 | EPSS Ckt | Y | 2023 | A PH- GRD- INST OC
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 8170 | 20230819 | 2041 | 20230820 | 1249 | 2196361 | 968 | Distribution Circuit | Environmental/External | Lightning | 502 | 128104 | 37.9873 | -120.2605 | No | Overcast-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106497 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1867166 | 0 | EPSS Ckt | Y | 2023 | A C PHASE AND GROUND
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | JUMPER | OJ 1 S/OF MTR# 1006872390 | 20230819 | 2050 | 20230820 | 1143 | 2196328 | 893 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3572 | 37.179 | -119.7659 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0106492 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867159 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20230819 | 2052 | 20230820 | 1611 | 2196331 | 1159 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 476 | 64580 | 37.4305 | -120.0996 | No | Overcast-Drizzle-Lightning;32-90 F | Pole-Wood | Burned/flashed | 23-0106482 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867149 | 0 | EPSS Ckt | Y | 2023 | FORCE OUT
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 84944 | 20230819 | 2053 | 20230820 | 1311 | 2196470 | 978 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3080 | 3010686 | 37.9525 | -120.3686 | No | Overcast-Lightning;32-90 F | Insulator | Broken | 23-0106488 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867155 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD TARGETS
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 20367 | 20230819 | 2056 | 20230820 | 1417 | 2196400 | 1041 | Distribution Circuit | Environmental/External | Lightning | 11 | 5581 | 37.9963 | -120.2921 | No | Overcast-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106569 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867243 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | S2159 | 20230819 | 2103 | 20230819 | 2313 | 2196455 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2775 | 37.7511 | -120.9036 | No | Overcast-Rain;32-90 F |  |  | 23-0106518 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1867187 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10952 | 20230819 | 2110 | 20230820 | 2108 | 2196479 | 1438 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4314 | 37.5622 | -119.9626 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0106716 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867364 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10466 | 20230819 | 2119 | 20230820 | 529 | 2196503 | 490 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2450 | 37.5129 | -119.8294 | No | Clear;32-90 F |  |  | 23-0106574 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867248 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | JUMPER | OJ 1 SPAN N/OF CGC #318968546019 | 20230819 | 2153 | 20230820 | 1209 | 2196530 | 856 | Distribution Circuit | Vegetation | Tree - grew into line | 6 | 5136 | 37.7636 | -120.8579 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0106498 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867167 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | JUMPER | BURNT OJ 1 POLE S/OF 5027 | 20230819 | 2215 | 20230820 | 248 | 2196556 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 6775 | 37.7258 | -120.7977 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0106560 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1867233 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 10870 | 20230819 | 2256 | 20230820 | 1332 | 2196573 | 876 | Distribution Circuit | Equipment Failure/Involved | Underground | 225 | 45676 | 37.9807 | -120.3916 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 23-0106520 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867189 | 0 | EPSS Ckt | Y | 2023 | A PHASE- GRD- INSTANTANEOUS
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 916436 | 20230819 | 2337 | 20230820 | 1600 | 2196539 | 983 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 458 | 73790 | 37.7217 | -120.2738 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 23-0106529 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867199 | 0 | EPSS Ckt | Y | 2023 | FORCE OUT
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322340226532 | 20230820 | 17 | 20230820 | 309 | 2196648 | 172 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 516 | 37.2266 | -119.6971 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0106566 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867239 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 851343 | 20230820 | 618 | 20230820 | 940 | 2196732 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 7272 | 37.2543 | -119.7118 | No | Overcast;32-90 F |  |  | 23-0106594 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867271 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 318982146367 | 20230820 | 642 | 20230820 | 1001 | 2196739 | 199 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1791 | 37.7729 | -120.8532 | No | Clear;32-90 F | Secondary | Together | 23-0106613 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867285 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | OCB | 1101/2 | 20230820 | 717 | 20230820 | 1638 | 2196768 | 561 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2672 | 257734 | 37.1208 | -120.2506 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106582 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1867257 | 0 | Non-EPSS | N | 2023 | C- GRD- TIME
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | TRANSFORMER | 318957846068 | 20230820 | 1011 | 20230820 | 1107 | 2196872 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 728 | 37.7645 | -120.8615 | No | Clear;32-90 F | Fuse | Broken | 23-0106628 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867297 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20230820 | 1011 | 20230820 | 1325 | 2196869 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 6014 | 37.9913 | -120.4133 | No | Overcast;32-90 F |  |  | 23-0106653 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867315 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L885 | 20230820 | 1118 | 20230820 | 1453 | 2196917 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2365 | 38.0459 | -120.3415 | No | Overcast;32-90 F |  |  | 23-0106668 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867327 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S20385 | 20230820 | 1428 | 20230820 | 1603 | 2197036 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 317 | 37.817 | -121.0154 | No | Clear;32-90 F |  |  | 23-0106700 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867350 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320695554631 | 20230820 | 1434 | 20230820 | 2126 | 2197056 | 412 | Transformer only | Environmental/External | Lightning | 3 | 1236 | 38.0003 | -120.2597 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106740 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867388 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 6064 | 20230820 | 1452 | 20230820 | 1756 | 2197064 | 184 | Distribution Circuit | Animal | Bird found | 383 | 70472 | 37.9603 | -120.3771 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0106677 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867333 | 0 | EPSS Ckt | Y | 2023 | B- C- INST
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 851343 | 20230820 | 1634 | 20230821 | 908 | 2197158 | 994 | Distribution Circuit | Environmental/External | Lightning | 36 | 5649 | 37.2543 | -119.7118 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0106724 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867372 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20230820 | 1844 | 20230820 | 2044 | 2197280 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 451 | 53329 | 38.0052 | -120.4062 | No | Overcast;32-90 F | Other | Malfunctioning | 23-0106738 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867386 | 0 | EPSS Ckt | Y | 2023 | DCD & SGF
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 6899 | 20230821 | 31 | 20230821 | 205 | 2197435 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 313 | 36.896 | -119.8577 | No | Overcast-Fog;32-90 F |  |  | 23-0106789 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867439 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321434513314 | 20230821 | 219 | 20230821 | 319 | 2197470 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 480 | 36.8646 | -120.0103 | No | Overcast-Fog;32-90 F | Fuse | Broken | 23-0106795 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867446 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 768534 | 20230821 | 330 | 20230821 | 349 | 2197492 | 19 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 57 | 37.8867 | -120.925 | No | Partly Cloudy;32-90 F |  |  | 23-0106797 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867448 | 0 | EPSS Ckt | N | 2023 | B VOLTAGE
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6597 | 20230821 | 605 | 20230821 | 1102 | 2197533 | 297 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 16 | 1268 | 36.8496 | -120.0101 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0106812 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1867460 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 1655 | 20230821 | 754 | 20230821 | 840 | 2197581 | 46 | Distribution Circuit | Animal | Other | 1 | 46 | 37.5446 | -121.1999 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 23-0106867 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867524 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | RECLOSER | 90590 | 20230821 | 834 | 20230821 | 1937 | 2197707 | 663 | Distribution Circuit | 3rd Party | Vehicle | 179 | 23769 | 37.3624 | -121.0756 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0106872 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1867532 | 0 | EPSS Ckt | N | 2023 | AB
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20230821 | 923 | 20230821 | 1035 | 2197805 | 72 | Distribution Circuit | Animal | Bird found | 687 | 22568 | 37.9574 | -120.3132 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0106918 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867582 | 0 | EPSS Ckt | Y | 2023 | AB
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 2204 | 20230821 | 952 | 20230821 | 1134 | 2197842 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 612 | 37.1171 | -120.5948 | No | Clear;32-90 F |  |  | 23-0107028 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867647 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320674254478 | 20230821 | 1132 | 20230821 | 1536 | 2197938 | 244 | Transformer only | Environmental/External | Lightning | 1 | 244 | 37.9961 | -120.2671 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 23-0107016 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867641 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1103 | 253671103 | FUSE | 965555 | 20230821 | 1241 | 20230821 | 1826 | 2198152 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 597 | 36.6337 | -120.639 | No | Clear-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 23-0107128 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867694 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | OCB | 1102/2 | 20230821 | 1332 | 20230821 | 1842 | 2198252 | 310 | Distribution Circuit | Environmental/External | Lightning | 267 | 26249 | 36.72 | -120.6027 | No | Partly Cloudy-Drizzle-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0107096 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1867680 | 0 | EPSS Ckt | N | 2023 | GRD
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | TRANSFORMER | 318995720142 | 20230821 | 1517 | 20230822 | 43 | 2198401 | 566 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1132 | 37.0525 | -120.8448 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107244 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867749 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | FUSE | 761498 | 20230821 | 1518 | 20230822 | 204 | 2198405 | 646 | Distribution Circuit | Environmental/External | Lightning | 2 | 715 | 36.7716 | -120.6571 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Broken | 23-0107215 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867734 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | TRANSFORMER | 415151552776 | 20230821 | 1553 | 20230822 | 51 | 2198455 | 538 | Transformer only | Environmental/External | Lightning | 1 | 538 | 36.7726 | -120.6571 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107223 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867736 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 8708 | 20230821 | 1559 | 20230821 | 1634 | 2198546 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 35 | 37.191 | -120.5649 | No | Overcast;32-90 F |  |  | 23-0107228 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867740 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20230821 | 1636 | 20230821 | 1741 | 2198542 | 65 | Distribution Circuit | Animal | Bird found | 582 | 19130 | 38.0085 | -120.3034 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0107224 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867737 | 0 | EPSS Ckt | Y | 2023 | A- B-
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | TRANSFORMER | 415151552993 | 20230821 | 1636 | 20230821 | 1847 | 2198541 | 131 | Transformer only | Environmental/External | Lightning | 1 | 131 | 36.7772 | -120.657 | No | Partly Cloudy;32-90 F | Other | Failed/Faulted | 23-0107235 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867743 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 13165 | 20230821 | 1952 | 20230821 | 2050 | 2198683 | 58 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 212 | 37.0069 | -119.9917 | No | Clear;32-90 F |  |  | 23-0107282 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867780 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | T4343 | 20230822 | 117 | 20230822 | 1639 | 2198805 | 922 | Distribution Circuit | Equipment Failure/Involved | Underground | 143 | 68776 | 36.8653 | -120.46 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0107341 | UG | Sus | 35482487 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867828 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 100000007672 | 20230822 | 130 | 20230822 | 920 | 2198828 | 470 | Distribution Circuit | 3rd Party | Vehicle | 2190 | 20171 | 37.794 | -120.9647 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0107336 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867823 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | RECLOSER | 9850 | 20230822 | 158 | 20230822 | 410 | 2198816 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 818 | 99654 | 37.7622 | -120.9775 | No | Clear;32-90 F |  |  | 23-0107333 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867820 | 0 | Non-EPSS | N | 2023 | BC
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 6849 | 20230822 | 654 | 20230822 | 818 | 2198884 | 84 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 195 | 16360 | 37.0111 | -120.1101 | No | Fog;32-90 F |  |  | 23-0107417 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867877 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320238321369 | 20230822 | 746 | 20230822 | 1036 | 2198922 | 170 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 170 | 37.0871 | -120.4192 | No | Fog;32-90 F | Fuse | Failed/Faulted | 23-0107504 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867997 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 13344 | 20230822 | 926 | 20230822 | 1047 | 2199100 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 243 | 37.4424 | -120.6304 | No | Clear;32-90 F |  |  | 23-0107549 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1868020 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321177918401 | 20230822 | 935 | 20230822 | 1138 | 2199115 | 123 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 492 | 37.0049 | -120.0979 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0107497 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867993 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 851902 | 20230822 | 1017 | 20230822 | 1050 | 2199199 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2666 | 84564 | 37.4831 | -119.9631 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107498 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867994 | 0 | EPSS Ckt | Y | 2023 | A- GRD
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321764934702 | 20230822 | 1057 | 20230822 | 1336 | 2199234 | 159 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 159 | 37.4496 | -119.8923 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0107533 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868010 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10170 | 20230822 | 1455 | 20230822 | 1711 | 2199470 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 208 | 28288 | 37.5163 | -119.835 | No | Clear;32-90 F |  |  | 23-0107693 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1868063 | 0 | EPSS Ckt | Y | 2023 | A- B- C- GRD
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 2495 | 20230822 | 1501 | 20230823 | 203 | 2199476 | 662 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 6 | 4188 | 37.4992 | -119.9831 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0107774 | UG | Sus | 31664368 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868085 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 20367 | 20230822 | 1626 | 20230822 | 1832 | 2199544 | 126 | Distribution Circuit | Animal | Bird found | 11 | 1386 | 37.9963 | -120.2921 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0107773 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1868084 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322120225252 | 20230822 | 2145 | 20230822 | 2342 | 2199631 | 117 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 117 | 37.1915 | -119.7716 | No | Clear;32-90 F | Service conductor | Broken | 23-0107789 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868103 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | RECLOSER | 5490 | 20230823 | 742 | 20230823 | 1218 | 2199808 | 276 | Distribution Circuit | Animal | Bird found | 1557 | 144900 | 37.3399 | -119.6754 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107880 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1868173 | 0 | EPSS Ckt | Y | 2023 | A&C PHASE
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | 319659214345 | 20230823 | 1025 | 20230823 | 1344 | 2200065 | 199 | Transformer only | Animal | Other | 1 | 199 | 36.8942 | -120.6184 | No | Clear;32-90 F | Fuse | Burned Open | 23-0108163 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868371 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | FUSE | 13054 | 20230823 | 1408 | 20230823 | 1731 | 2200274 | 203 | Distribution Circuit | 3rd Party | Vandalism | 305 | 37333 | 36.9746 | -120.0543 | No | Clear;32-90 F | Insulator | Broken | 23-0108090 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1868373 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | RECLOSER | 54694 | 20230823 | 1459 | 20230824 | 16 | 2200334 | 557 | Distribution Circuit | 3rd Party | Vehicle | 121 | 20223 | 37.0179 | -120.428 | No | Clear;Above 90 | Footings- Tower or Pole | Broken- wire on ground | 23-0108237 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1868382 | 0 | Non-EPSS | N | 2023 | ABC PHASE
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | RECLOSER | 9300 | 20230823 | 1735 | 20230823 | 1950 | 2200504 | 135 | Distribution Circuit | 3rd Party | Vehicle | 469 | 56315 | 37.012 | -120.1106 | No | Partly Cloudy;Above 90 | Pole-Wood | Broken | 23-0108230 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1868405 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | FUSE | 7617 | 20230823 | 2117 | 20230824 | 239 | 2200710 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 7084 | 37.3622 | -120.5857 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0108381 | OH | Sus | 31664376 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1868469 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11589 | 20230824 | 7 | 20230824 | 638 | 2200772 | 391 | Distribution Circuit | Vegetation | Tree - bark fell into line | 9 | 3519 | 37.236 | -120.2623 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0108395 | OH | Sus | 45938171 | CENTRAL VALLEY | AUG | Force Out | 0 | No | Yes | No | 1868482 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9542 | 20230824 | 55 | 20230824 | 400 | 2200782 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 189 | 35044 | 36.7548 | -120.3807 | No | Clear;32-90 F |  |  | 23-0108404 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868492 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | TRANSFORMER | 320264916456 | 20230824 | 838 | 20230824 | 1250 | 2201243 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 252 | 36.9524 | -120.4106 | No | Clear;32-90 F | Fuse | Broken | 23-0108649 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868702 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321460513071 | 20230824 | 924 | 20230824 | 1132 | 2201084 | 128 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 128 | 36.8577 | -120.001 | No | Clear;32-90 F |  |  | 23-0108598 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868684 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10506 | 20230824 | 1102 | 20230824 | 1726 | 2201242 | 384 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 21 | 8064 | 37.5019 | -119.9772 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0108615 | UG | Sus | 45940200 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868691 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320865756210 | 20230824 | 1148 | 20230824 | 1427 | 2201281 | 159 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 477 | 38.0429 | -120.2001 | No | Clear;32-90 F |  |  | 23-0108715 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868735 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 26748 | 20230824 | 1707 | 20230824 | 2112 | 2201698 | 245 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 245 | 37.8569 | -120.914 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108818 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1868789 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 9618 | 20230825 | 806 | 20230825 | 1140 | 2201871 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 714 | 36.7488 | -120.6484 | No | Partly Cloudy;32-90 F |  |  | 23-0109135 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869034 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | SWITCH | 929360 | 20230825 | 854 | 20230825 | 1041 | 2201948 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2876 | 112968 | 37.4926 | -119.9661 | No | Clear;32-90 F |  |  | 23-0108983 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1868960 | 0 | EPSS Ckt | Y | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 7204 | 20230825 | 859 | 20230825 | 1616 | 2201997 | 437 | Distribution Circuit | Equipment Failure/Involved | Underground | 227 | 10383 | 37.4953 | -119.9805 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0109106 | UG | Sus | 45941259 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869022 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 3712 | 20230825 | 1221 | 20230825 | 1710 | 2202212 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 5364 | 37.1479 | -120.8228 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0109153 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1869047 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 21116 | 20230825 | 2025 | 20230825 | 2225 | 2202542 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 6720 | 37.3856 | -120.7607 | No | Clear;32-90 F |  |  | 23-0109318 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1869120 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | SWITCH | 2067 | 20230826 | 833 | 20230826 | 1041 | 2202653 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 512 | 36.7358 | -120.72 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0109356 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1869158 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 6107 | 20230826 | 922 | 20230826 | 1908 | 2202771 | 586 | Distribution Circuit | 3rd Party | Vehicle | 57 | 10824 | 37.1041 | -120.2768 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0109392 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1869220 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | FUSE | 20491 | 20230826 | 1136 | 20230826 | 1238 | 2202842 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1117 | 37.1877 | -121.0117 | No | Clear;32-90 F |  |  | 23-0109407 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869227 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | TRANSFORMER | T0358 | 20230826 | 1816 | 20230827 | 144 | 2202975 | 448 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 4660 | 37.3246 | -120.461 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0109450 | UG | Sus | 35484176 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869257 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 562119 | 20230827 | 906 | 20230827 | 1056 | 2203261 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 330 | 37.1752 | -120.5078 | No | Clear;32-90 F |  |  | 23-0109506 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1869327 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | TRANSFORMER | 322153043779 | 20230827 | 1107 | 20230828 | 1101 | 2203300 | 1434 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 10038 | 37.6984 | -119.757 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109554 | OH | Sus | 35484262 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869346 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 8040 | 20230827 | 1539 | 20230827 | 1916 | 2203386 | 217 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 131 | 21061 | 37.8999 | -120.5045 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0109541 | OH | Sus | 31665563 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1869342 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE INST
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | OCB | 1116/2 | 20230827 | 1851 | 20230828 | 318 | 2203447 | 507 | Distribution Circuit | 3rd Party | Other | 2052 | 383954 | 37.2732 | -120.4872 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0109559 | OH | Sus | 35484364 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869351 | 0 | Non-EPSS | N | 2023 | B PH & GRD TIME OC
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 3927 | 20230827 | 2020 | 20230827 | 2236 | 2203464 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3400 | 37.1587 | -121.0096 | No | Clear;32-90 F |  |  | 23-0109582 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869373 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3504 | 20230828 | 758 | 20230828 | 1008 | 2203692 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 867 | 36.9822 | -120.5271 | No | Clear;32-90 F |  |  | 23-0109722 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869553 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318949122397 | 20230828 | 848 | 20230828 | 1230 | 2203790 | 222 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 222 | 37.1141 | -120.8614 | No | Clear;32-90 F | Fuse | Broken | 23-0109805 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869614 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 150668 | 20230828 | 957 | 20230828 | 1053 | 2203930 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 3080 | 37.4807 | -119.6367 | No | Clear;32-90 F |  |  | 23-0109713 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1869550 | 0 | EPSS Ckt | N | 2023 | BC
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 384305 | 20230828 | 1116 | 20230828 | 1338 | 2204030 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 142 | 36.8295 | -120.0496 | No | Clear;32-90 F | Fuse | Broken | 23-0109832 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869626 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 53038 | 20230828 | 1250 | 20230828 | 1332 | 2204163 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 360 | 15120 | 38.0869 | -120.1537 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0109790 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1869617 | 0 | EPSS Ckt | Y | 2023 | N/A
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318634046981 | 20230828 | 1508 | 20230828 | 1820 | 2204279 | 192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 192 | 37.7893 | -120.9741 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0109896 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1869639 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | FUSE | 3132 | 20230828 | 2218 | 20230829 | 121 | 2204501 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 3294 | 37.099 | -120.7776 | No | Clear;32-90 F |  |  | 23-0109989 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1869687 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 13446 | 20230829 | 1016 | 20230829 | 1037 | 2204943 | 14 | Distribution Circuit | Company Initiated | Operating error | 114 | 1596 | 37.5353 | -119.9833 | No | Clear;32-90 F | Fuse | Normal | 23-0110182 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1869902 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S20385 | 20230829 | 1102 | 20230829 | 1150 | 2204964 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 240 | 37.817 | -121.0154 | No | Clear;32-90 F |  |  | 23-0110231 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1869916 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | TRANSFORMER | 318629649317 | 20230829 | 1354 | 20230829 | 1456 | 2205126 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 62 | 37.8534 | -120.9759 | No | Clear;32-90 F | Fuse | Broken | 23-0110398 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869977 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 11742 | 20230829 | 2211 | 20230829 | 2356 | 2205471 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 420 | 37.3167 | -120.7603 | No | Clear;32-90 F |  |  | 23-0110509 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870017 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | OCB | 1110/2 | 20230830 | 630 | 20230830 | 1041 | 2205581 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 236 | 29102 | 37.0551 | -120.3171 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0110563 | OH | Sus | 31665893 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870066 | 0 | Non-EPSS | N | 2023 | B PHASE- GRD & TIME
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 1694 | 20230830 | 910 | 20230830 | 1033 | 2205765 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 166 | 36.9055 | -120.7458 | No | Clear;32-90 F |  |  | 23-0110692 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870202 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 69153 | 20230830 | 921 | 20230830 | 1025 | 2205782 | 64 | Distribution Circuit | 3rd Party | Other | 1 | 85 | 37.3603 | -120.6728 | No | Clear;32-90 F | Fuse | Burned Open | 23-0110690 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870200 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | S2239 | 20230830 | 1932 | 20230830 | 2102 | 2206415 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 540 | 37.8985 | -120.9447 | No | Clear;32-90 F |  |  | 23-0111015 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1870313 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318617027320 | 20230831 | 723 | 20230831 | 1155 | 2206593 | 272 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 272 | 37.2493 | -120.9762 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0111075 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1870355 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | RECLOSER | 9790 | 20230831 | 1319 | 20230831 | 1358 | 2207139 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 209 | 8151 | 36.8905 | -120.7444 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0111335 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1870588 | 0 | EPSS Ckt | Y | 2023 | A&B PHASE
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | RECLOSER | 867748 | 20230831 | 1407 | 20230831 | 2215 | 2207181 | 488 | Distribution Circuit | Equipment Failure/Involved | Overhead | 296 | 14500 | 37.1054 | -120.2114 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 23-0111380 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | Yes | No | 1870597 | 0 | Non-EPSS | N | 2023 | ABC PHASE
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | JUMPER | 2 S/OF CGC 321719634181 | 20230831 | 1939 | 20230831 | 2210 | 2207384 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 906 | 37.4372 | -119.9087 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0111529 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1870628 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | S2003 | 20230901 | 338 | 20230901 | 443 | 2207504 | 65 | Distribution Circuit | Animal | Other | 44 | 2860 | 37.7281 | -120.9444 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 23-0111581 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870681 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | JUMPER | OJ 1 POLE N/E OF CGC 318755445772 | 20230901 | 819 | 20230901 | 1130 | 2207719 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 382 | 37.7567 | -120.931 | No | Partly Cloudy;32-90 F | Service conductor | Deteriorated | 23-0111687 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1870761 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | OTHER | 2040 | 20230901 | 1113 | 20230901 | 1550 | 2207808 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 8441 | 36.8802 | -120.1092 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0111817 | OH | Sus | 45949337 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | Yes | 1870808 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 21201 | 20230901 | 1318 | 20230901 | 1407 | 2207946 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 98 | 37.7445 | -120.9488 | No | Partly Cloudy;32-90 F |  |  | 23-0111886 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1870826 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 20589 | 20230901 | 1631 | 20230901 | 1727 | 2208045 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 280 | 37.7747 | -120.8248 | No | Partly Cloudy;32-90 F |  |  | 23-0111974 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1870843 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 11634 | 20230901 | 1702 | 20230901 | 1810 | 2208060 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 272 | 37.1854 | -120.3379 | No | Partly Cloudy;32-90 F |  |  | 23-0111992 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870849 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 278740 | 20230901 | 1910 | 20230901 | 2019 | 2208177 | 69 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1887 | 127267 | 37.9881 | -120.2845 | No | Overcast;32-90 F |  |  | 23-0112004 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870854 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320251553970 | 20230901 | 2132 | 20230902 | 144 | 2208258 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 252 | 37.9824 | -120.4135 | No | Overcast-Lightning;32-90 F | Transformer (OH) | Broken | 23-0112029 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1870882 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | S2685 | 20230901 | 2156 | 20230902 | 1223 | 2208244 | 867 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 46533 | 37.8188 | -120.8688 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0112031 | UG | Sus | 45949488 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870885 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | FUSE | 6129 | 20230902 | 539 | 20230902 | 825 | 2208311 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2214 | 37.0327 | -120.3076 | No | Partly Cloudy;32-90 F |  |  | 23-0112075 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870934 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 2373 | 20230902 | 617 | 20230902 | 721 | 2208318 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 1408 | 37.7097 | -120.894 | No | Overcast;32-90 F |  |  | 23-0112053 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1870908 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | S407 | 20230902 | 622 | 20230902 | 1250 | 2208320 | 388 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 11300 | 37.2311 | -121.0142 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0112066 | OH | Sus | 45949395 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1870920 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | RECLOSER | 4600 | 20230902 | 902 | 20230902 | 2016 | 2208528 | 674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 387 | 41001 | 37.2009 | -120.2438 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112084 | OH | Sus | 31666998 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1870939 | 0 | EPSS Ckt | N | 2023 | SGF
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | FUSE | 1566 | 20230902 | 2008 | 20230902 | 2108 | 2208922 | 60 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 420 | 36.9229 | -120.065 | No | Partly Cloudy;32-90 F |  |  | 23-0112177 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870987 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321275015400 | 20230902 | 2144 | 20230903 | 1500 | 2208931 | 1036 | Transformer only | Animal | Bird found | 3 | 3108 | 36.9222 | -120.0647 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0112180 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870990 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 59596 | 20230902 | 2151 | 20230903 | 1015 | 2208933 | 744 | Distribution Circuit | 3rd Party | Metallic Balloon | 787 | 576400 | 37.9009 | -120.5804 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0112179 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1870989 | 0 | EPSS Ckt | Y | 2023 | A- B
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | S2677 | 20230902 | 2346 | 20230903 | 250 | 2208946 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 920 | 37.3237 | -120.9803 | No | Clear;32-90 F |  |  | 23-0112199 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871010 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 827 | 20230903 | 7 | 20230903 | 141 | 2208947 | 94 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 79 | 7426 | 37.795 | -120.9784 | No | Partly Cloudy;32-90 F |  |  | 23-0112197 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871007 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319237545055 | 20230903 | 914 | 20230903 | 948 | 2209046 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 102 | 37.737 | -120.7647 | No | Clear;32-90 F | Fuse | Broken | 23-0112232 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871045 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 2076 | 20230903 | 941 | 20230903 | 1405 | 2209121 | 264 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 704 | 37.1784 | -120.2741 | No | Clear;32-90 F |  |  | 23-0112247 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871053 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | RECLOSER | 421930 | 20230903 | 953 | 20230903 | 2126 | 2209058 | 693 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 17164 | 37.4937 | -120.5004 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0112229 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1871040 | 0 | Non-EPSS | N | 2023 | ABC
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 11585 | 20230903 | 1003 | 20230903 | 1450 | 2209064 | 287 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 574 | 37.2051 | -120.2708 | No | Clear;32-90 F |  |  | 23-0112252 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871056 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 388701 | 20230903 | 1147 | 20230903 | 1258 | 2209091 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 142 | 37.8865 | -120.9363 | No | Overcast;32-90 F |  |  | 23-0112242 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871051 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318759620877 | 20230903 | 1431 | 20230903 | 1623 | 2209122 | 112 | Transformer only | 3rd Party | Fire- house or bldg. | 2 | 224 | 37.0721 | -120.926 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0112256 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871059 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 11634 | 20230903 | 1526 | 20230903 | 1601 | 2209141 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 140 | 37.1854 | -120.3379 | No | Partly Cloudy;32-90 F |  |  | 23-0112258 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871061 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318759620850 | 20230903 | 1550 | 20230903 | 1627 | 2209147 | 37 | Transformer only | 3rd Party | Fire- house or bldg. | 3 | 111 | 37.0714 | -120.9257 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0112257 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871060 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 886007 | 20230904 | 534 | 20230904 | 636 | 2209256 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 207 | 37.2953 | -120.3897 | No | Clear;32-90 F |  |  | 23-0112287 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871092 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 7362 | 20230904 | 616 | 20230904 | 1443 | 2209278 | 349 | Distribution Circuit | Equipment Failure/Involved | Underground | 254 | 76168 | 37.3323 | -120.4805 | No | Fog;32-90 F | Conductor- Underground | Deteriorated | 23-0112289 | UG | Sus | 45953212 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871094 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 9606 | 20230904 | 754 | 20230904 | 1042 | 2209288 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2016 | 37.1159 | -120.8979 | No | Clear;32-90 F |  |  | 23-0112319 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871113 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 6225 | 20230904 | 807 | 20230904 | 1153 | 2209298 | 226 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 904 | 36.8947 | -119.8108 | No | Clear;32-90 F |  |  | 23-0112333 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871120 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 21997 | 20230904 | 912 | 20230904 | 1510 | 2209320 | 358 | Distribution Circuit | 3rd Party | Vehicle | 13 | 4654 | 37.0179 | -120.411 | No | Clear;32-90 F | Woodpin | Normal | 23-0112320 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871114 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 409 | 20230904 | 1042 | 20230904 | 1627 | 2209366 | 345 | Distribution Circuit | 3rd Party | Vehicle | 28 | 9660 | 37.2288 | -120.9805 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112342 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1871125 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | JUMPER | FB @ DDE 2 SPANS SS OF MTR# 1009964175 | 20230904 | 1357 | 20230904 | 2146 | 2209451 | 469 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1407 | 37.0473 | -120.2815 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0112348 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871130 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | FUSE | 5797 | 20230904 | 1509 | 20230904 | 1517 | 2209481 | 8 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 96 | 37.0551 | -120.3831 | No | Clear;32-90 F |  |  | 23-0112359 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871137 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | OCB | 1704/2 | 20230904 | 1715 | 20230904 | 1832 | 2209536 | 77 | Distribution Circuit | Animal | Bird found | 462 | 25608 | 37.8561 | -120.9446 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0112372 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871144 | 0 | Non-EPSS | N | 2023 | A- C- TIME OC
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | FUSE | 22419 | 20230904 | 1829 | 20230905 | 410 | 2209546 | 581 | Distribution Circuit | Equipment Failure/Involved | Underground | 87 | 26747 | 37.0696 | -120.8196 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0112397 | UG | Sus | 45952197 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871156 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | FUSE | 1566 | 20230905 | 622 | 20230905 | 720 | 2209662 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 271 | 36.9229 | -120.065 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0112449 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871195 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 24953 | 20230905 | 745 | 20230905 | 1000 | 2209691 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 135 | 37.2283 | -120.2141 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0112456 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871200 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320335154124 | 20230905 | 907 | 20230905 | 1515 | 2209848 | 368 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2208 | 37.9861 | -120.3845 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0112534 | OH | Sus | 31667627 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871322 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | FUSE | 19278 | 20230905 | 1302 | 20230905 | 1352 | 2210143 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 233 | 36.8217 | -120.6551 | No | Clear;32-90 F |  |  | 23-0112685 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871367 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20259 | 20230905 | 1848 | 20230906 | 150 | 2210398 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 689 | 37.7037 | -120.6939 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0112828 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871401 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320226021734 | 20230905 | 1855 | 20230905 | 1905 | 2210342 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 10 | 37.097 | -120.4237 | No | Clear;32-90 F | Fuse | Burned Open | 23-0112815 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871397 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 22919 | 20230905 | 1945 | 20230905 | 2226 | 2210427 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 966 | 37.1378 | -120.2798 | No | Clear;32-90 F |  |  | 23-0112849 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871416 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20230905 | 2105 | 20230906 | 839 | 2210444 | 694 | Distribution Circuit | Company Initiated | Personnel- company | 582 | 259148 | 38.0085 | -120.3034 | No | Clear;32-90 F | Recloser | Normal | 23-0112842 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871411 | 0 | EPSS Ckt | Y | 2023 | GRD- INST
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | T9135 | 20230905 | 2111 | 20230906 | 1510 | 2210448 | 1079 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 15994 | 37.9785 | -120.3808 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0112884 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871431 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 10864 | 20230906 | 800 | 20230906 | 852 | 2210607 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 4004 | 37.2807 | -120.4437 | No | Clear;32-90 F |  |  | 23-0112981 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871525 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 1101/2 | 20230906 | 800 | 20230906 | 820 | 2210618 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 552 | 10794 | 37.2537 | -119.5191 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0112958 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1871472 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | FUSE | 578497 | 20230906 | 957 | 20230906 | 1049 | 2210812 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 52 | 36.9963 | -120.1699 | No | Clear;32-90 F |  |  | 23-0113067 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871600 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 100000009124 | 20230906 | 1208 | 20230906 | 1407 | 2210869 | 119 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 238 | 37.7846 | -120.9103 | No | Clear;32-90 F |  |  | 23-0113159 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871631 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | TRANSFORMER | 321829614439 | 20230906 | 1330 | 20230906 | 1600 | 2211015 | 150 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 150 | 36.8944 | -119.8756 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0113234 | OH | Sus | 31667695 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871651 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318708044964 | 20230906 | 1422 | 20230906 | 1630 | 2210759 | 128 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 640 | 37.7341 | -120.9476 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0113029 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871582 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | TRIP-SAVER | 3983 | 20230906 | 1459 | 20230906 | 1833 | 2211085 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2568 | 36.8512 | -120.5993 | No | Clear;32-90 F |  |  | 23-0113369 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871689 | 0 | Non-EPSS | N | 2023 | B & C
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | SWITCH | 19919BP | 20230906 | 1610 | 20230906 | 1647 | 2211127 | 37 | Distribution Circuit | Equipment Failure/Involved | Underground | 106 | 3922 | 37.0438 | -120.8265 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0113000 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871673 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 5742 | 20230906 | 1652 | 20230907 | 27 | 2211174 | 455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6370 | 36.8147 | -120.2053 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0113375 | OH | Sus | 31667778 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871696 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | TRANSFORMER | 321224716713 | 20230906 | 1725 | 20230906 | 2102 | 2211208 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1736 | 36.9588 | -120.0824 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0113372 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871693 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321087017907 | 20230906 | 2243 | 20230907 | 220 | 2211312 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 217 | 36.9916 | -120.1286 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0113411 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871713 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | RECLOSER | 90360 | 20230906 | 2249 | 20230907 | 129 | 2211313 | 160 | Distribution Circuit | Equipment Failure/Involved | Underground | 425 | 52382 | 37.7635 | -120.8414 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0113412 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871715 | 0 | Non-EPSS | N | 2023 | C- GRD
YOSEMITE | YOSEMITE | EL CAPITAN-1102 | 253881102 | FUSE | 660775 | 20230906 | 2333 | 20230907 | 1047 | 2211335 | 674 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 13090 | 37.3394 | -120.4381 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0113418 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871720 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 8523 | 20230907 | 132 | 20230907 | 303 | 2211346 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2275 | 37.7615 | -120.9547 | No | Clear;32-90 F |  |  | 23-0113423 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871724 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11626 | 20230907 | 505 | 20230907 | 612 | 2211356 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 223 | 37.1908 | -120.307 | No | Clear;32-90 F |  |  | 23-0113429 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871727 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321793317348 | 20230907 | 722 | 20230907 | 1255 | 2211410 | 333 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 666 | 36.9748 | -119.8868 | No | Clear;32-90 F | Fuse | Broken | 23-0113548 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871864 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | S2677 | 20230907 | 755 | 20230907 | 855 | 2211431 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 300 | 37.3237 | -120.9803 | No | Clear;32-90 F |  |  | 23-0113520 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871822 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | JUMPER | OJ @ HARDTAP SOURCE SIDE MTR 1011054998 | 20230907 | 1105 | 20230907 | 1225 | 2211743 | 80 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 80 | 37.9973 | -120.4501 | No | Clear;32-90 F | Bushing | Broken | 23-0113607 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871898 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20230907 | 1617 | 20230907 | 1918 | 2212031 | 181 | Distribution Circuit | Animal | Bird found | 259 | 36000 | 37.5694 | -120.1177 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0113823 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1871957 | 0 | EPSS Ckt | Y | 2023 | B-C-INST
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 416095653203 | 20230907 | 1715 | 20230907 | 1756 | 2212063 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 36.7872 | -120.3346 | No | Clear;Above 90 | Fuse | Burned Open | 23-0113854 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871964 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | TRANSFORMER | 321289323200 | 20230907 | 1805 | 20230908 | 150 | 2212082 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1395 | 37.1363 | -120.0593 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0113860 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1871966 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 23334 | 20230908 | 630 | 20230908 | 747 | 2212379 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 315 | 24255 | 37.9893 | -120.3329 | No | Clear;32-90 F |  |  | 23-0113961 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872017 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 27416 | 20230908 | 722 | 20230908 | 914 | 2212401 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 112 | 37.3583 | -119.6434 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0113962 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872018 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 25162 | 20230908 | 955 | 20230908 | 1156 | 2212640 | 121 | Distribution Circuit | 3rd Party | Vehicle | 2 | 209 | 36.7345 | -120.4412 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0114081 | OH | Sus | 31668173 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872147 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | JUMPER | OJ'S 1 SE/OF CGC# 320286256219 | 20230908 | 1204 | 20230908 | 1322 | 2212761 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 156 | 38.0436 | -120.4007 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0114161 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872176 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318918829717 | 20230908 | 1223 | 20230908 | 1600 | 2212645 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 651 | 37.3134 | -120.8731 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0114184 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872184 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 821491 | 20230908 | 1356 | 20230908 | 1535 | 2212917 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 384 | 37.231 | -120.9773 | No | Clear;Above 90 |  |  | 23-0114283 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872215 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 1694 | 20230908 | 1757 | 20230908 | 1951 | 2213190 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 228 | 36.9055 | -120.7458 | No | Clear;32-90 F |  |  | 23-0114338 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872243 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | OCB | 1116/2 | 20230909 | 500 | 20230909 | 1349 | 2213336 | 529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 39295 | 36.8859 | -120.6559 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114372 | OH | Sus | 31668306 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | Yes | No | 1872273 | 0 | Non-EPSS | N | 2023 | A-B & GRD TIME OC
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320128821496 | 20230909 | 535 | 20230909 | 1930 | 2213464 | 835 | Transformer only | Environmental/External | Lightning | 2 | 1670 | 37.0906 | -120.4555 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114386 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872322 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 100000004842 | 20230909 | 535 | 20230909 | 2030 | 2213467 | 895 | Transformer only | Environmental/External | Lightning | 1 | 895 | 37.0946 | -120.457 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114386 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872324 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 6003 | 20230909 | 540 | 20230909 | 738 | 2213350 | 118 | Distribution Circuit | Environmental/External | Lightning | 18 | 2124 | 37.0981 | -120.4554 | Yes | Clear;32-90 F | Transformer (OH) | Broken | 23-0114386 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872294 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320139721799 | 20230909 | 540 | 20230909 | 2035 | 2213349 | 895 | Transformer only | Environmental/External | Lightning | 1 | 895 | 37.0989 | -120.4524 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114402 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872337 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | OCB | 1112/2 | 20230909 | 551 | 20230909 | 722 | 2213352 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 495 | 36243 | 37.1847 | -120.2736 | Yes | Clear;32-90 F |  |  | 23-0114379 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872281 | 0 | Non-EPSS | N | 2023 | B INSTANT OC
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3518 | 20230909 | 638 | 20230909 | 954 | 2213366 | 196 | Distribution Circuit | Environmental/External | Lightning | 25 | 4900 | 36.96 | -120.6581 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0114425 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1872375 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL SUB | 25209 | JUMPER | CANAL BK 1 SOURCE | 20230909 | 702 | 20230909 | 1243 | 2213401 | 341 | Distribution Circuit | Environmental/External | Lightning | 6083 | 1924204 | 8e-05 | -127.4887 | Yes | Clear;32-90 F | Transformer Power | Failed/Faulted | 23-0114385 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872293 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1102 | 252531102 | RECLOSER | 1102/2 | 20230909 | 731 | 20230909 | 1500 | 2213406 | 449 | Distribution Circuit | Environmental/External | Lightning | 262 | 39018 | 37.2537 | -119.5192 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114389 | OH | Sus | 35487620 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872297 | 0 | EPSS Ckt | Y | 2023 | AB INST OC
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5503 | 20230909 | 737 | 20230909 | 1615 | 2213410 | 518 | Distribution Circuit | Environmental/External | Lightning | 53 | 17262 | 37.2077 | -119.5419 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114426 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872376 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322895725058 | 20230909 | 808 | 20230909 | 2013 | 2213581 | 725 | Transformer only | Environmental/External | Lightning | 2 | 1450 | 37.1854 | -119.5071 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114442 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872394 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | TRANSFORMER | 320565325497 | 20230909 | 810 | 20230909 | 1242 | 2213462 | 272 | Transformer only | Environmental/External | Lightning | 1 | 272 | 37.2 | -120.3069 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114398 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872326 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 65873 | 20230909 | 810 | 20230909 | 1946 | 2213459 | 696 | Distribution Circuit | Environmental/External | Lightning | 4 | 1248 | 37.1858 | -119.5065 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114438 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872389 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 320211511422 | 20230909 | 840 | 20230909 | 1705 | 2213728 | 505 | Transformer only | Environmental/External | Lightning | 1 | 505 | 36.833 | -120.4285 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114462 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872405 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6636 | 20230909 | 902 | 20230911 | 1552 | 2213710 | 3290 | Distribution Circuit | Environmental/External | Lightning | 6 | 9353 | 37.0399 | -120.0293 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114487 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1872425 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6852 | 20230909 | 903 | 20230909 | 1027 | 2213510 | 84 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 728 | 37.04 | -120.0747 | Yes | Clear;32-90 F |  |  | 23-0114428 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872377 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230909 | 905 | 20230909 | 1120 | 2213513 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 261 | 35235 | 37.0552 | -120.0295 | Yes | Clear;32-90 F |  |  | 23-0114440 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872391 | 0 | EPSS Ckt | N | 2023 | GRD
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 43537 | 20230909 | 925 | 20230909 | 1056 | 2213606 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 91 | 37.0541 | -120.0383 | Yes | Clear;32-90 F |  |  | 23-0114429 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872378 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 402242 | 20230909 | 942 | 20230909 | 1019 | 2213559 | 37 | Distribution Circuit | Environmental/External | Lightning | 165 | 6105 | 37.0542 | -120.031 | Yes | Partly Cloudy;32-90 F | Capacitor | Failed/Faulted | 23-0114417 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872366 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 27293 | 20230909 | 1005 | 20230910 | 1023 | 2213594 | 1458 | Distribution Circuit | Environmental/External | Lightning | 5 | 2098 | 37.1633 | -120.2288 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0114456 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872401 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | RECLOSER | 618380 | 20230909 | 1036 | 20230909 | 1428 | 2213614 | 232 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 262 | 60784 | 37.4029 | -119.7327 | Yes | Clear;32-90 F |  |  | 23-0114432 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872381 | 0 | EPSS Ckt | Y | 2023 | A&B
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 320208212119 | 20230909 | 1044 | 20230909 | 1739 | 2213618 | 415 | Transformer only | Environmental/External | Lightning | 1 | 415 | 36.8327 | -120.4288 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114453 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872399 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | RECLOSER | 352740 | 20230909 | 1055 | 20230909 | 1142 | 2213630 | 47 | Distribution Circuit | Company Initiated | Coordination failure | 1302 | 61194 | 37.3384 | -119.6709 | Yes | Clear;32-90 F | Other | Normal | 23-0114433 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872385 | 0 | EPSS Ckt | Y | 2023 | DCD- SGF
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 6923 | 20230909 | 1103 | 20230909 | 1328 | 2213639 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 870 | 37.1129 | -120.3099 | Yes | Clear;32-90 F |  |  | 23-0114470 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872412 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 9655 | 20230909 | 1201 | 20230909 | 1236 | 2213773 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 93 | 36.7901 | -120.3625 | Yes | Clear;32-90 F |  |  | 23-0114476 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872414 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320453743821 | 20230909 | 1254 | 20230910 | 1534 | 2213732 | 1600 | Distribution Circuit | Environmental/External | Lightning | 3 | 4800 | 37.7055 | -120.3429 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114526 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872455 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 916436 | 20230909 | 1258 | 20230909 | 1624 | 2213736 | 206 | Distribution Circuit | Environmental/External | Lightning | 458 | 68973 | 37.7217 | -120.2738 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114464 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1872408 | 0 | EPSS Ckt | Y | 2023 | A- C & SGF
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 20230909 | 1310 | 20230910 | 100 | 2213752 | 710 | Distribution Circuit | Environmental/External | Lightning | 229 | 43188 | 37.7156 | -120.1933 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114468 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872410 | 0 | EPSS Ckt | Y | 2023 | A & C
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 13430 | 20230909 | 1314 | 20230909 | 1605 | 2213753 | 171 | Distribution Circuit | Environmental/External | Lightning | 129 | 22059 | 37.7499 | -120.1362 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114469 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1872411 | 0 | EPSS Ckt | Y | 2023 | B- C GRD
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | RECLOSER | 999258 | 20230909 | 1328 | 20230909 | 1826 | 2213775 | 298 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 7450 | 37.1542 | -121.0608 | Yes | Partly Cloudy;32-90 F |  |  | 23-0114528 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872457 | 0 | EPSS Ckt | Y | 2023 | A & B
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 5893 | 20230909 | 1336 | 20230909 | 1425 | 2213761 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 980 | 37.0474 | -120.1114 | Yes | Partly Cloudy;Above 90 |  |  | 23-0114478 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872416 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 21237 | 20230909 | 1413 | 20230909 | 1500 | 2213790 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 235 | 37.7186 | -120.8667 | Yes | Partly Cloudy-Lightning;32-90 F |  |  | 23-0114484 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872423 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321224620300 | 20230909 | 1415 | 20230909 | 2050 | 2213791 | 395 | Transformer only | Environmental/External | Lightning | 1 | 395 | 37.0565 | -120.0818 | Yes | Partly Cloudy;Above 90 | Fuse | Failed/Faulted | 23-0114578 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872512 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319279046780 | 20230909 | 1422 | 20230909 | 2254 | 2213793 | 512 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1536 | 37.7847 | -120.7501 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114500 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872438 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319282046788 | 20230909 | 1431 | 20230909 | 2251 | 2213801 | 500 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2000 | 37.7851 | -120.7491 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114530 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872460 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 59596 | 20230909 | 1435 | 20230910 | 526 | 2213804 | 891 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 657 | 585387 | 37.9009 | -120.5804 | Yes | Partly Cloudy-Lightning;32-90 F |  |  | 23-0114479 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872417 | 0 | EPSS Ckt | Y | 2023 | A & C
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 10940 | 20230909 | 1505 | 20230910 | 1950 | 2214722 | 1725 | Distribution Circuit | Environmental/External | Lightning | 635 | 866229 | 37.9883 | -120.2832 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114494 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872614 | 0 | EPSS Ckt | N | 2023 | GRD INST
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20230909 | 1506 | 20230910 | 1745 | 2213827 | 1599 | Distribution Circuit | Environmental/External | Lightning | 582 | 930618 | 38.0085 | -120.3034 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114493 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872431 | 0 | EPSS Ckt | Y | 2023 | GRD INST
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 84944 | 20230909 | 1508 | 20230910 | 1520 | 2213846 | 1452 | Distribution Circuit | Environmental/External | Lightning | 3080 | 4389658 | 37.9525 | -120.3686 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114482 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872420 | 0 | EPSS Ckt | Y | 2023 | DCD & SGF
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23252 | 20230909 | 1511 | 20230911 | 2107 | 2214637 | 3236 | Distribution Circuit | Environmental/External | Lightning | 19 | 35436 | 38.0012 | -120.2967 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114551 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872593 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 47488 | 20230909 | 1512 | 20230910 | 1848 | 2214662 | 1656 | Distribution Circuit | Environmental/External | Lightning | 590 | 848049 | 37.9655 | -120.2508 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114483 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872600 | 0 | EPSS Ckt | Y | 2023 | C GRD
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 39256 | 20230909 | 1513 | 20230912 | 834 | 2213859 | 3921 | Distribution Circuit | Environmental/External | Lightning | 523 | 562821 | 37.9571 | -120.3087 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114489 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872427 | 0 | EPSS Ckt | Y | 2023 | C GRD INST
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | SWITCH | 21168 | 20230909 | 1515 | 20230909 | 1529 | 2213854 | 14 | Distribution Circuit | Company Initiated | Other Circuits | 391 | 5474 | 37.0594 | -120.8354 | Yes | Clear;Above 90 | Conductor- Overhead | Normal | 23-0114385 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872421 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9280 | 20230909 | 1516 | 20230909 | 1555 | 2213886 | 39 | Distribution Circuit | Company Initiated | Coordination failure | 847 | 33033 | 38.1994 | -120.0195 | Yes | Partly Cloudy;32-90 F | Recloser | Normal | 23-0114492 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872430 | 0 | EPSS Ckt | Y | 2023 | B & GRD
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20230909 | 1516 | 20230909 | 1737 | 2213892 | 141 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 578 | 81498 | 38.1888 | -120.0082 | Yes | Partly Cloudy-Lightning;32-90 F |  |  | 23-0114492 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872433 | 0 | EPSS Ckt | Y | 2023 | C & GRD
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321279660420 | 20230909 | 1516 | 20230910 | 1738 | 2213995 | 1582 | Distribution Circuit | Environmental/External | Lightning | 582 | 501096 | 38.1579 | -120.0557 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114492 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1872463 | 0 | EPSS Ckt | Y | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | 26323 | 20230909 | 1516 | 20230910 | 1635 | 2214289 | 1519 | Distribution Circuit | Environmental/External | Lightning | 107 | 162533 | 38.1574 | -120.0552 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114571 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1872507 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | SWITCH | 3101 | 20230909 | 1612 | 20230909 | 1623 | 2213906 | 11 | Distribution Circuit | Company Initiated | Other Circuits | 207 | 2277 | 37.0555 | -120.7517 | Yes | Clear;Above 90 |  |  | 23-0114385 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872439 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 65678 | 20230909 | 1618 | 20230909 | 1938 | 2213912 | 200 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 2200 | 37.8095 | -120.8685 | Yes | Partly Cloudy;32-90 F |  |  | 23-0114534 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872468 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | OCB | 1703/2 | 20230909 | 1625 | 20230912 | 855 | 2213913 | 3870 | Distribution Circuit | Environmental/External | Lightning | 3108 | 1476332 | 37.9799 | -120.4136 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0114513 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872445 | 0 | EPSS Ckt | Y | 2023 | C INSTANT & GRD TARGETS
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 20413 | 20230909 | 1627 | 20230911 | 1650 | 2213914 | 2903 | Distribution Circuit | Environmental/External | Lightning | 20 | 23005 | 37.8626 | -120.776 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0114579 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872513 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L2633 | 20230909 | 1628 | 20230910 | 1943 | 2213955 | 1635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 692 | 635279 | 37.9736 | -120.4349 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114518 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872448 | 0 | EPSS Ckt | Y | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 10268 | 20230909 | 1637 | 20230910 | 230 | 2213921 | 593 | Distribution Circuit | Environmental/External | Lightning | 7 | 1109 | 37.7952 | -120.1793 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114529 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872459 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1102 | 252531102 | TRANSFORMER | 322801127245 | 20230909 | 1639 | 20230910 | 1033 | 2213922 | 1074 | Transformer only | Environmental/External | Lightning | 3 | 3222 | 37.2465 | -119.5391 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114583 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872519 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1112 | 252761112 | OCB | 1112/2 | 20230909 | 1642 | 20230909 | 1920 | 2213924 | 158 | Distribution Circuit | 3rd Party | Vehicle | 626 | 86528 | 36.9234 | -120.0551 | Yes | Clear;Above 90 | Pole-Wood | Broken | 23-0114498 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872444 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320874446004 | 20230909 | 1643 | 20230910 | 415 | 2213925 | 692 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1384 | 37.7661 | -120.1982 | Yes | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0114535 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872469 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318558047211 | 20230909 | 1652 | 20230911 | 2330 | 2213929 | 3278 | Transformer only | Environmental/External | Lightning | 10 | 32780 | 37.7956 | -121.0002 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114599 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872536 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | RECLOSER | 3144 | 20230909 | 1707 | 20230910 | 1027 | 2213967 | 1040 | Distribution Circuit | Environmental/External | Lightning | 255 | 265200 | 37.9906 | -120.3839 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0114520 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872450 | 0 | EPSS Ckt | Y | 2023 | B & GRD
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20230909 | 1708 | 20230910 | 2205 | 2213971 | 1737 | Distribution Circuit | Environmental/External | Lightning | 1298 | 1100374 | 38.0063 | -120.3474 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114521 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872451 | 0 | EPSS Ckt | Y | 2023 | BC
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L1411 | 20230909 | 1708 | 20230910 | 2208 | 2214521 | 1740 | Distribution Circuit | Environmental/External | Lightning | 13 | 16249 | 38.0384 | -120.3554 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114521 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872561 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 6060 | 20230909 | 1712 | 20230910 | 37 | 2213975 | 445 | Distribution Circuit | Environmental/External | Lightning | 705 | 313725 | 37.9892 | -120.3332 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114523 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1872452 | 0 | EPSS Ckt | Y | 2023 | A&B - SGF/DCD
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 667248 | 20230909 | 1716 | 20230910 | 2154 | 2213980 | 1658 | Distribution Circuit | Environmental/External | Lightning | 2889 | 4771377 | 38.049 | -120.2357 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114524 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872453 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320658456831 | 20230909 | 1716 | 20230912 | 1047 | 2215600 | 3931 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3931 | 38.0605 | -120.2725 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1873002 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9280 | 20230909 | 1749 | 20230909 | 1824 | 2213994 | 35 | Distribution Circuit | Company Initiated | Coordination failure | 847 | 29645 | 38.1994 | -120.0195 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114492 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1872458 | 0 | EPSS Ckt | Y | 2023 | A & B
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 4155 | 20230909 | 1806 | 20230910 | 1405 | 2214003 | 1199 | Distribution Circuit | Environmental/External | Lightning | 8 | 6302 | 37.7913 | -120.7821 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114604 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872541 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319128746499 | 20230909 | 1837 | 20230911 | 1404 | 2214315 | 2607 | Transformer only | Environmental/External | Lightning | 1 | 2607 | 37.7765 | -120.8028 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114708 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872665 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | S713 | 20230909 | 1837 | 20230910 | 1403 | 2214464 | 1166 | Distribution Circuit | Environmental/External | Lightning | 8 | 8404 | 37.7628 | -120.8094 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114611 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872548 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | OCB | 1705/2 | 20230909 | 1859 | 20230910 | 158 | 2214044 | 419 | Distribution Circuit | Environmental/External | Lightning | 2219 | 929761 | 37.9035 | -120.4971 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114543 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1872477 | 0 | EPSS Ckt | Y | 2023 | A B C GRD INST
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 10580 | 20230909 | 1859 | 20230910 | 1749 | 2214747 | 1370 | Distribution Circuit | Environmental/External | Lightning | 351 | 480870 | 37.9489 | -120.4255 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114543 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872624 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 20599 | 20230909 | 1901 | 20230911 | 900 | 2214030 | 2279 | Distribution Circuit | Environmental/External | Lightning | 4 | 9056 | 37.7766 | -120.8007 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114709 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872666 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 6064 | 20230909 | 1906 | 20230911 | 1500 | 2214097 | 2634 | Distribution Circuit | Environmental/External | Lightning | 383 | 486057 | 37.9603 | -120.3771 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114547 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872481 | 0 | EPSS Ckt | Y | 2023 | B INST
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 26483 | 20230909 | 1908 | 20230910 | 1151 | 2214392 | 1003 | Distribution Circuit | Environmental/External | Lightning | 2 | 2006 | 37.8211 | -120.7037 | Yes | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0114600 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872537 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | RECLOSER | 9230 | 20230909 | 1908 | 20230910 | 905 | 2214099 | 837 | Distribution Circuit | Environmental/External | Lightning | 1829 | 1381526 | 37.9737 | -120.3716 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114548 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872482 | 0 | EPSS Ckt | Y | 2023 | B- INSTA
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | RECLOSER | 78452 | 20230909 | 1909 | 20230911 | 2122 | 2214024 | 3013 | Distribution Circuit | Environmental/External | Lightning | 345 | 96610 | 37.82 | -120.7083 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114546 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1872480 | 0 | EPSS Ckt | N | 2023 | GRD & SGF
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 318087838520 | 20230909 | 1914 | 20230909 | 2254 | 2214103 | 220 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 220 | 37.556 | -121.1598 | Yes | Partly Cloudy-Lightning;32-90 F | Fuse | Broken | 23-0114592 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872530 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 8040 | 20230909 | 1921 | 20230910 | 246 | 2214107 | 445 | Distribution Circuit | Environmental/External | Lightning | 131 | 58295 | 37.8999 | -120.5045 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114550 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1872484 | 0 | EPSS Ckt | Y | 2023 | ABC TIME/INS
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 8000 | 20230909 | 1924 | 20230910 | 1916 | 2214153 | 1432 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 604 | 864928 | 38.0083 | -120.301 | Yes | Partly Cloudy-Lightning;32-90 F |  |  | 23-0114553 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872487 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 295684 | 20230909 | 1924 | 20230910 | 1507 | 2214213 | 1183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 175 | 207025 | 37.9792 | -120.2764 | Yes | Partly Cloudy-Lightning;32-90 F |  |  | 23-0114555 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872489 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 34426 | 20230909 | 1924 | 20230910 | 1610 | 2214783 | 1246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 563 | 701498 | 37.9661 | -120.2384 | Yes | Partly Cloudy-Lightning;32-90 F |  |  | 23-0114555 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872645 | 0 | EPSS Ckt | Y | 2023 | NONE
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 68380 | 20230909 | 1924 | 20230910 | 2116 | 2214934 | 1552 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 551 | 855152 | 38.0151 | -120.2744 | Yes | Partly Cloudy-Lightning;32-90 F |  |  | 23-0114553 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872691 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 767890 | 20230909 | 1924 | 20230910 | 940 | 2214270 | 856 | Distribution Circuit | Environmental/External | Lightning | 1237 | 1058872 | 38.0568 | -120.203 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114562 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872498 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 953336 | 20230909 | 1925 | 20230910 | 949 | 2214240 | 864 | Distribution Circuit | Environmental/External | Lightning | 922 | 796608 | 38.0678 | -120.1869 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114559 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872494 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | OCB | 1701/2 | 20230909 | 1926 | 20230910 | 106 | 2214281 | 340 | Distribution Circuit | Environmental/External | Lightning | 1572 | 534480 | 38.0529 | -120.2172 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114556 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872503 | 0 | EPSS Ckt | Y | 2023 | N/A
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | OCB | 1702/2 | 20230909 | 1927 | 20230910 | 122 | 2214284 | 355 | Distribution Circuit | Environmental/External | Lightning | 943 | 334765 | 38.0529 | -120.2172 | Yes | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0114556 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872505 | 0 | EPSS Ckt | Y | 2023 | N/A
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 26493 | 20230909 | 2018 | 20230911 | 1945 | 2214287 | 2847 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5694 | 37.7502 | -120.8171 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114723 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872688 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 98991 | 20230909 | 2021 | 20230911 | 1051 | 2214304 | 2310 | Distribution Circuit | Environmental/External | Lightning | 11 | 19185 | 37.7839 | -120.7527 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114670 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872630 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20645 | 20230909 | 2026 | 20230911 | 1550 | 2214937 | 2604 | Distribution Circuit | Environmental/External | Lightning | 6 | 9389 | 37.7433 | -120.8307 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114726 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872693 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319149845960 | 20230909 | 2028 | 20230910 | 1905 | 2214292 | 1357 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1357 | 37.7619 | -120.7952 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114614 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872552 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319160945981 | 20230909 | 2032 | 20230910 | 1803 | 2214294 | 1291 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1291 | 37.7622 | -120.7915 | Yes | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114612 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872550 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 628595 | 20230909 | 2333 | 20230911 | 1143 | 2214389 | 2170 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 2583 | 37.8282 | -120.7364 | Yes | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0114619 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872556 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318545046915 | 20230909 | 2335 | 20230910 | 1012 | 2214382 | 637 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1274 | 37.7875 | -121.0045 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114598 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872535 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318547346916 | 20230909 | 2343 | 20230910 | 1012 | 2213947 | 629 | Transformer only | Environmental/External | Lightning | 1 | 629 | 37.7875 | -121.0038 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114594 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872533 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | 180505 | 20230910 | 26 | 20230910 | 1846 | 2214404 | 1100 | Distribution Circuit | Environmental/External | Lightning | 70 | 77000 | 37.9749 | -120.3625 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114719 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872678 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | L1719 | 20230910 | 32 | 20230911 | 1319 | 2214393 | 2207 | Distribution Circuit | Environmental/External | Lightning | 95 | 110456 | 37.9765 | -120.3659 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114732 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872699 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 70198 | 20230910 | 334 | 20230910 | 1739 | 2214462 | 845 | Distribution Circuit | Environmental/External | Lightning | 1110 | 937950 | 37.9574 | -120.4389 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114610 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1872547 | 0 | EPSS Ckt | Y | 2023 | AC GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320232952560 | 20230910 | 334 | 20230911 | 1208 | 2214809 | 1954 | Transformer only | Environmental/External | Lightning | 1 | 1954 | 37.9437 | -120.4201 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114610 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872656 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320249551535 | 20230910 | 334 | 20230911 | 1400 | 2214811 | 2066 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 6198 | 37.9162 | -120.4144 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0114610 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872658 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320224052354 | 20230910 | 334 | 20230911 | 1246 | 2214812 | 1992 | Distribution Circuit | Environmental/External | Lightning | 2 | 3984 | 37.9371 | -120.4234 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114610 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872659 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 26453 | 20230910 | 409 | 20230910 | 753 | 2214474 | 224 | Distribution Circuit | 3rd Party | Metallic Balloon | 5 | 1195 | 37.1586 | -120.995 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114629 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872574 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 20230910 | 444 | 20230911 | 1617 | 2214448 | 2133 | Distribution Circuit | Environmental/External | Lightning | 139 | 131160 | 38.0064 | -120.3467 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114613 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872551 | 0 | EPSS Ckt | Y | 2023 | B GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 52495 | 20230910 | 457 | 20230912 | 1056 | 2214494 | 3239 | Distribution Circuit | Environmental/External | Lightning | 41 | 64880 | 37.9657 | -120.4034 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114884 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872927 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | TRANSFORMER | 318903047450 | 20230910 | 553 | 20230911 | 1922 | 2214504 | 2249 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2249 | 37.8026 | -120.8806 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114737 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872704 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1779 | 20230910 | 608 | 20230910 | 1130 | 2214508 | 322 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1718 | 37.8216 | -120.6787 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0114651 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872604 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 318086038520 | 20230910 | 741 | 20230910 | 925 | 2214537 | 104 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 208 | 37.556 | -121.1605 | No | Clear;32-90 F |  |  | 23-0114637 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872585 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320196853128 | 20230910 | 742 | 20230912 | 1007 | 2214538 | 3025 | Transformer only | Environmental/External | Lightning | 2 | 6050 | 37.9593 | -120.4327 | No | Clear;32-90 F | Stepdown | Failed/Faulted | 23-0115039 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873007 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 100000056020 | 20230910 | 753 | 20230911 | 1821 | 2214546 | 2068 | Transformer only | Environmental/External | Lightning | 1 | 2068 | 38.0355 | -120.3504 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114943 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872963 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319276046765 | 20230910 | 759 | 20230911 | 1231 | 2214550 | 1712 | Transformer only | Environmental/External | Lightning | 1 | 1712 | 37.7845 | -120.7512 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114683 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872643 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320426855933 | 20230910 | 808 | 20230911 | 1715 | 2214596 | 1987 | Transformer only | Environmental/External | Lightning | 1 | 1987 | 38.0358 | -120.3528 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114913 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872943 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319994950672 | 20230910 | 823 | 20230911 | 1930 | 2214573 | 2107 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2107 | 37.8923 | -120.5017 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115004 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872990 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L443 | 20230910 | 830 | 20230910 | 1456 | 2214581 | 386 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 41688 | 37.9891 | -120.4626 | No | Clear;32-90 F |  |  | 23-0114682 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872642 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320146054210 | 20230910 | 830 | 20230911 | 1337 | 2214786 | 1747 | Transformer only | Environmental/External | Lightning | 1 | 1747 | 37.9886 | -120.4509 | No | Clear;32-90 F | Transformer | Broken | 23-0114682 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872646 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320123254232 | 20230910 | 830 | 20230911 | 1040 | 2214787 | 1570 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 6280 | 37.9892 | -120.4593 | No | Clear;32-90 F | Transformer | Broken | 23-0114682 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872647 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320113454238 | 20230910 | 830 | 20230911 | 913 | 2214788 | 1483 | Transformer only | Environmental/External | Lightning | 2 | 2966 | 37.9898 | -120.4621 | No | Clear;32-90 F | Transformer | Broken | 23-0114682 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872648 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 787277 | 20230910 | 830 | 20230910 | 2028 | 2214587 | 718 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 84724 | 37.9599 | -120.4517 | No | Clear;32-90 F |  |  | 23-0114734 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872702 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L2619 | 20230910 | 830 | 20230911 | 1244 | 2214577 | 1694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 13552 | 37.9611 | -120.4494 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115005 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1872991 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320167553190 | 20230910 | 830 | 20230911 | 1812 | 2215582 | 2022 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 4044 | 37.9607 | -120.4434 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115005 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1872993 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319408048080 | 20230910 | 847 | 20230910 | 1736 | 2214589 | 529 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 529 | 37.8204 | -120.7055 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114659 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872619 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320420056136 | 20230910 | 854 | 20230912 | 1037 | 2215430 | 2983 | Transformer only | Environmental/External | Lightning | 1 | 2983 | 38.0414 | -120.3552 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114886 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872930 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 11708 | 20230910 | 858 | 20230910 | 1408 | 2214601 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 4030 | 36.8905 | -120.7369 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0114649 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1872602 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320147553226 | 20230910 | 900 | 20230911 | 1832 | 2215807 | 2012 | Transformer only | Environmental/External | Lightning | 3 | 6036 | 37.9621 | -120.4499 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115179 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873075 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | TRANSFORMER | 320339554144 | 20230910 | 928 | 20230911 | 128 | 2214615 | 960 | Transformer only | Environmental/External | Lightning | 8 | 7680 | 37.9871 | -120.3832 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114700 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872660 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319413548103 | 20230910 | 938 | 20230910 | 1310 | 2214618 | 212 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 212 | 37.8209 | -120.7041 | No | Clear;32-90 F |  |  | 23-0114660 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872620 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321458761475 | 20230910 | 948 | 20230911 | 1438 | 2214622 | 1730 | Transformer only | Environmental/External | Lightning | 7 | 12110 | 38.1868 | -119.9932 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114695 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872655 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320420556107 | 20230910 | 951 | 20230911 | 1928 | 2215406 | 2017 | Transformer only | Environmental/External | Lightning | 3 | 6051 | 38.0405 | -120.3549 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114876 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872919 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 24323 | 20230910 | 953 | 20230910 | 1740 | 2214625 | 467 | Distribution Circuit | Environmental/External | Lightning | 2 | 934 | 37.7476 | -120.8308 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0114712 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1872669 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 6865 | 20230910 | 1014 | 20230911 | 1312 | 2214634 | 1618 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 4854 | 37.9682 | -120.2637 | No | Clear;32-90 F |  |  | 23-0115024 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873000 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | S717 | 20230910 | 1016 | 20230910 | 2016 | 2214636 | 600 | Distribution Circuit | Environmental/External | Lightning | 8 | 4800 | 37.7617 | -120.791 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114727 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872694 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320338153427 | 20230910 | 1016 | 20230911 | 1113 | 2215381 | 1497 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2994 | 37.9673 | -120.384 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114863 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872904 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321292460311 | 20230910 | 1117 | 20230911 | 919 | 2214664 | 1322 | Transformer only | Environmental/External | Lightning | 6 | 7932 | 38.1553 | -120.0513 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114689 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872651 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321275660555 | 20230910 | 1229 | 20230911 | 1007 | 2214714 | 1298 | Transformer only | Environmental/External | Lightning | 2 | 2596 | 38.1621 | -120.0571 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0114677 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872639 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320247054400 | 20230910 | 1252 | 20230911 | 1626 | 2214727 | 1654 | Transformer only | Environmental/External | Lightning | 2 | 3308 | 37.9942 | -120.4167 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114938 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872962 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | S1791 | 20230910 | 1302 | 20230912 | 1112 | 2214781 | 2770 | Distribution Circuit | Environmental/External | Lightning | 15 | 24182 | 37.904 | -120.4541 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114724 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872689 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | TAR FLAT-0401 | 163240401 | TRANSFORMER | 320347954135 | 20230910 | 1306 | 20230911 | 946 | 2214733 | 1240 | Transformer only | Environmental/External | Lightning | 13 | 16120 | 37.9868 | -120.3804 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114706 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872663 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320340753395 | 20230910 | 1321 | 20230911 | 1029 | 2215380 | 1268 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2536 | 37.9667 | -120.3831 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114902 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872939 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | FUSE | 13278 | 20230910 | 1326 | 20230910 | 1420 | 2214695 | 54 | Distribution Circuit | 3rd Party | Vehicle | 42 | 2268 | 36.9425 | -120.0285 | No | Clear;32-90 F | Anchor or Guy | Deteriorated | 23-0114663 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872623 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319160545970 | 20230910 | 1348 | 20230910 | 1427 | 2214751 | 39 | Transformer only | Environmental/External | Lightning | 1 | 39 | 37.7619 | -120.7917 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0114667 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872627 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | L1179 | 20230910 | 1400 | 20230911 | 1646 | 2214754 | 1606 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1606 | 38.0684 | -120.186 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0114716 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872675 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321277160380 | 20230910 | 1430 | 20230911 | 951 | 2214782 | 1161 | Transformer only | Environmental/External | Lightning | 5 | 5805 | 38.1568 | -120.0566 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0114684 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872644 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321389261842 | 20230910 | 1532 | 20230911 | 1245 | 2214797 | 1273 | Distribution Circuit | Environmental/External | Lightning | 2 | 2546 | 38.1972 | -120.0173 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 23-0114703 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872661 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | TRANSFORMER | 319978631047 | 20230910 | 1558 | 20230910 | 1645 | 2214804 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 94 | 37.3537 | -120.5074 | No | Clear;Above 90 | Transformer (OH) | Normal | 23-0114707 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872664 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320275653939 | 20230910 | 1708 | 20230912 | 936 | 2214829 | 2428 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 7284 | 37.9802 | -120.403 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114979 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872981 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 851902 | 20230910 | 1719 | 20230910 | 2018 | 2214865 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2673 | 251677 | 37.4831 | -119.9631 | No | Clear;32-90 F |  |  | 23-0114711 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872668 | 0 | EPSS Ckt | Y | 2023 | B GRD
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 322287632128 | 20230910 | 1847 | 20230911 | 938 | 2215018 | 891 | Transformer only | Environmental/External | Lightning | 2 | 1782 | 37.3796 | -119.7138 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114725 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872723 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | SWITCH | 352740 | 20230910 | 1849 | 20230910 | 2254 | 2214923 | 245 | Distribution Circuit | Environmental/External | Lightning | 1562 | 225712 | 37.3384 | -119.6709 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114725 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872690 | 0 | EPSS Ckt | Y | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320198153100 | 20230910 | 1853 | 20230912 | 1244 | 2214928 | 2511 | Distribution Circuit | Environmental/External | Lightning | 3 | 7533 | 37.9585 | -120.4319 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115089 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873023 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320565056420 | 20230910 | 1905 | 20230911 | 1945 | 2215458 | 1480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1480 | 38.0504 | -120.3071 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114903 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872940 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 278740 | 20230910 | 1936 | 20230911 | 1945 | 2214946 | 1449 | Distribution Circuit | Environmental/External | Lightning | 1333 | 601854 | 37.9881 | -120.2845 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114730 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872697 | 0 | EPSS Ckt | N | 2023 | SGF/DCD
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320499155246 | 20230910 | 1942 | 20230911 | 1633 | 2214960 | 1251 | Transformer only | Environmental/External | Lightning | 1 | 1251 | 38.0171 | -120.3275 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114921 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872952 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320213252319 | 20230910 | 1945 | 20230912 | 1032 | 2214952 | 2327 | Transformer only | Environmental/External | Lightning | 2 | 4654 | 37.9368 | -120.4271 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115041 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873008 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320424354131 | 20230910 | 2013 | 20230911 | 1537 | 2215146 | 1164 | Transformer only | Environmental/External | Lightning | 3 | 3492 | 37.9866 | -120.3534 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114807 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872791 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319461348430 | 20230910 | 2015 | 20230911 | 1540 | 2214966 | 1165 | Transformer only | Environmental/External | Lightning | 1 | 1165 | 37.8298 | -120.6884 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114744 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872711 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320604854675 | 20230910 | 2040 | 20230912 | 1317 | 2214981 | 2437 | Transformer only | Environmental/External | Lightning | 2 | 4874 | 38.0011 | -120.2915 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115135 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873043 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320260152761 | 20230910 | 2042 | 20230911 | 2006 | 2214982 | 1404 | Transformer only | Environmental/External | Lightning | 2 | 2808 | 37.949 | -120.4109 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114960 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872971 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320449954113 | 20230910 | 2045 | 20230911 | 1247 | 2215145 | 962 | Transformer only | Environmental/External | Lightning | 4 | 3848 | 37.9859 | -120.3447 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114813 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872808 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | L1169 | 20230910 | 2048 | 20230910 | 2349 | 2214989 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 12670 | 38.0252 | -120.2416 | No | Clear;32-90 F |  |  | 23-0114757 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872727 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320711355426 | 20230910 | 2058 | 20230912 | 1537 | 2215767 | 2559 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 7677 | 38.0221 | -120.2537 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1873066 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320651056790 | 20230910 | 2117 | 20230912 | 1057 | 2215053 | 2260 | Transformer only | Environmental/External | Lightning | 2 | 4520 | 38.0595 | -120.2748 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114759 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872731 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320629656822 | 20230910 | 2117 | 20230912 | 1249 | 2215054 | 2372 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 4744 | 38.0604 | -120.2824 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114760 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872732 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320653256752 | 20230910 | 2127 | 20230912 | 1419 | 2215647 | 2452 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 4904 | 38.0583 | -120.2741 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1873015 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320693856851 | 20230910 | 2343 | 20230912 | 934 | 2215679 | 2031 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2031 | 38.061 | -120.2601 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1873029 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 667248 | 20230911 | 115 | 20230911 | 1224 | 2215001 | 669 | Distribution Circuit | Environmental/External | Lightning | 812 | 543228 | 38.049 | -120.2357 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872730 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 8130 | 20230911 | 115 | 20230911 | 1225 | 2215245 | 670 | Distribution Circuit | Environmental/External | Lightning | 437 | 292790 | 38.0278 | -120.2568 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872837 | 0 | EPSS Ckt | Y | 2023 | NONE
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 47143 | 20230911 | 115 | 20230911 | 1721 | 2215270 | 966 | Distribution Circuit | Environmental/External | Lightning | 340 | 328440 | 38.0046 | -120.2629 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872858 | 0 | EPSS Ckt | Y | 2023 | NONE
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 9270 | 20230911 | 115 | 20230911 | 1605 | 2215304 | 890 | Distribution Circuit | Environmental/External | Lightning | 181 | 161090 | 38.026 | -120.2543 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872871 | 0 | EPSS Ckt | Y | 2023 | NONE
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 36888 | 20230911 | 115 | 20230911 | 1640 | 2215344 | 925 | Distribution Circuit | Environmental/External | Lightning | 276 | 255300 | 38.0285 | -120.2514 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872887 | 0 | EPSS Ckt | Y | 2023 | NONE
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 823548 | 20230911 | 115 | 20230911 | 1536 | 2215415 | 861 | Distribution Circuit | Environmental/External | Lightning | 833 | 717213 | 38.0441 | -120.248 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872922 | 0 | EPSS Ckt | Y | 2023 | NONE
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | TRANSFORMER | 320339554144 | 20230911 | 635 | 20230911 | 1122 | 2215084 | 287 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2296 | 37.9871 | -120.3832 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114874 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872918 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320220452379 | 20230911 | 711 | 20230912 | 1138 | 2215105 | 1707 | Transformer only | Environmental/External | Lightning | 2 | 3414 | 37.9384 | -120.4248 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115087 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873022 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319931851820 | 20230911 | 827 | 20230911 | 1048 | 2215206 | 141 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 141 | 37.9241 | -120.525 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114816 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1872814 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 206989 | 20230911 | 832 | 20230911 | 913 | 2215222 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 123 | 37.231 | -120.9875 | No | Clear;32-90 F |  |  | 23-0114846 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872866 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | TRANSFORMER | 318921047136 | 20230911 | 856 | 20230911 | 1845 | 2215269 | 589 | Transformer only | Environmental/External | Lightning | 1 | 589 | 37.7947 | -120.8746 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114897 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872937 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321287021163 | 20230911 | 936 | 20230911 | 952 | 2215126 | 16 | Transformer only | Environmental/External | Lightning | 1 | 16 | 37.0802 | -120.0602 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0114871 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872914 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320407056135 | 20230911 | 946 | 20230911 | 1240 | 2215431 | 174 | Transformer only | Environmental/External | Lightning | 2 | 348 | 38.0415 | -120.3596 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115078 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873017 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 4916 | 20230911 | 1023 | 20230911 | 1136 | 2215438 | 73 | Distribution Circuit | 3rd Party | Vehicle | 11 | 828 | 37.2407 | -120.4166 | No | Clear;32-90 F | Secondary | Broken | 23-0114932 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872959 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320194654003 | 20230911 | 1029 | 20230912 | 1332 | 2215563 | 1623 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1623 | 37.9831 | -120.4334 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115144 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873051 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | 20323 | 20230911 | 1032 | 20230912 | 1229 | 2215630 | 1555 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 59090 | 38.144 | -120.0646 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114916 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1873011 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321285360345 | 20230911 | 1032 | 20230912 | 1036 | 2215733 | 1444 | Transformer only | Environmental/External | Lightning | 4 | 5776 | 38.1563 | -120.0538 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115141 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873049 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320174851927 | 20230911 | 1033 | 20230915 | 1355 | 2215094 | 5962 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 5962 | 37.9272 | -120.4403 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115012 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872994 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20230911 | 1033 | 20230911 | 1401 | 2215465 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 647 | 134576 | 38.1888 | -120.0082 | No | Clear;32-90 F |  |  | 23-0114916 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872944 | 0 | EPSS Ckt | Y | 2023 | C & GRD
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | TRANSFORMER | 318905047302 | 20230911 | 1054 | 20230911 | 1951 | 2215487 | 537 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 537 | 37.7986 | -120.8799 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114931 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872957 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320560455122 | 20230911 | 1238 | 20230911 | 1546 | 2215576 | 188 | Transformer only | Environmental/External | Lightning | 1 | 188 | 38.0134 | -120.3064 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115131 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1873040 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320284553976 | 20230911 | 1242 | 20230912 | 850 | 2215578 | 1208 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2416 | 37.9825 | -120.4016 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115021 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872998 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322200535289 | 20230911 | 1310 | 20230911 | 1331 | 2215606 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 21 | 37.4656 | -119.7434 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0115026 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873004 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 362721 | 20230911 | 1321 | 20230911 | 1452 | 2215612 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1456 | 36.8803 | -119.9382 | No | Clear;32-90 F |  |  | 23-0115107 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1873027 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1102 | 252531102 | TRANSFORMER | 322823527705 | 20230911 | 1349 | 20230911 | 1654 | 2215637 | 185 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 185 | 37.2592 | -119.5304 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115122 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873032 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318581826732 | 20230911 | 1350 | 20230911 | 1700 | 2215542 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 190 | 37.2338 | -120.9877 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 23-0115145 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873053 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320424354059 | 20230911 | 1417 | 20230911 | 1845 | 2215659 | 268 | Transformer only | Environmental/External | Lightning | 1 | 268 | 37.9844 | -120.3537 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115106 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873026 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320624356144 | 20230911 | 1459 | 20230912 | 1557 | 2215589 | 1498 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1498 | 38.042 | -120.2838 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115123 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873033 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320275252912 | 20230911 | 1506 | 20230912 | 1704 | 2215707 | 1558 | Transformer only | Environmental/External | Lightning | 1 | 1558 | 37.9529 | -120.4058 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115162 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873070 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320639556265 | 20230911 | 1550 | 20230912 | 1026 | 2215976 | 1116 | Transformer only | Environmental/External | Lightning | 3 | 3348 | 38.0459 | -120.2793 | No | Clear;32-90 F | Transformer | Broken | 23-0115234 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873096 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320631356781 | 20230911 | 1551 | 20230912 | 1323 | 2215764 | 1292 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1292 | 38.0592 | -120.2818 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115211 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873087 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320651056597 | 20230911 | 1557 | 20230912 | 1132 | 2215978 | 1175 | Transformer only | Environmental/External | Lightning | 2 | 2350 | 38.054 | -120.2752 | No | Clear;32-90 F | Transformer | Broken | 23-0115231 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873093 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320642556335 | 20230911 | 1558 | 20230912 | 904 | 2215977 | 1026 | Transformer only | Environmental/External | Lightning | 1 | 1026 | 38.0476 | -120.2776 | No | Clear;32-90 F | Transformer | Broken | 23-0115233 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873095 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320199326845 | 20230911 | 1602 | 20230911 | 1938 | 2215769 | 216 | Transformer only | Environmental/External | Lightning | 2 | 432 | 37.2381 | -120.4329 | No | Clear;Above 90 | Transformer | Deteriorated | 23-0115158 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873068 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320701355315 | 20230911 | 1616 | 20230912 | 1117 | 2215779 | 1141 | Transformer only | Environmental/External | Lightning | 4 | 4564 | 38.0191 | -120.2574 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115184 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873077 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320701055306 | 20230911 | 1621 | 20230912 | 953 | 2215784 | 1052 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2104 | 38.0187 | -120.2575 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115188 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873080 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320700155420 | 20230911 | 1651 | 20230912 | 1342 | 2215811 | 1251 | Transformer only | Environmental/External | Lightning | 5 | 6255 | 38.0218 | -120.2575 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115183 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873076 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | RECLOSER | 10690 | 20230911 | 1734 | 20230912 | 337 | 2215833 | 603 | Distribution Circuit | 3rd Party | Vehicle | 363 | 160895 | 37.2878 | -120.3249 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0115208 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1873085 | 0 | EPSS Ckt | N | 2023 | ABC
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320427853955 | 20230911 | 1741 | 20230911 | 1848 | 2215840 | 67 | Transformer only | Environmental/External | Lightning | 1 | 67 | 37.9819 | -120.3512 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115203 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873084 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320546556360 | 20230911 | 1748 | 20230912 | 1044 | 2215844 | 1016 | Transformer only | Environmental/External | Lightning | 1 | 1016 | 38.0477 | -120.3095 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115235 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873098 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321387161557 | 20230911 | 1800 | 20230912 | 1040 | 2215795 | 1000 | Transformer only | Environmental/External | Lightning | 1 | 1000 | 38.1902 | -120.0179 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115229 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873092 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320397713061 | 20230911 | 2018 | 20230912 | 125 | 2215180 | 307 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 307 | 36.8584 | -120.3641 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115256 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873110 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | OCB | 1701/2 | 20230912 | 547 | 20230912 | 1000 | 2216091 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2333 | 530707 | 37.7729 | -120.8261 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0115294 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1873138 | 0 | EPSS Ckt | N | 2023 | SET A RLY
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 4913 | 20230912 | 1034 | 20230912 | 1212 | 2216582 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 686 | 37.3866 | -120.7597 | No | Clear;32-90 F |  |  | 23-0115458 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1873345 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320134352913 | 20230912 | 1050 | 20230912 | 1640 | 2216581 | 350 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 350 | 37.9531 | -120.4555 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115497 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873368 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320507254094 | 20230912 | 1209 | 20230912 | 1557 | 2216635 | 228 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 228 | 37.9855 | -120.3251 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115495 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873367 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320135352919 | 20230912 | 1214 | 20230912 | 1642 | 2216666 | 268 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 268 | 37.9534 | -120.4545 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115500 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873370 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | FUSE | 23417 | 20230912 | 1246 | 20230912 | 1356 | 2216702 | 70 | Distribution Circuit | 3rd Party | Other | 135 | 9450 | 37.0571 | -120.8225 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0115576 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1873395 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319583435437 | 20230912 | 1249 | 20230912 | 1541 | 2216727 | 172 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 172 | 37.4732 | -120.6442 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0115543 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873387 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320688655707 | 20230912 | 1413 | 20230912 | 1435 | 2216777 | 22 | Transformer only | Environmental/External | Lightning | 1 | 22 | 38.0296 | -120.2616 | No | Clear;32-90 F | Lightning Arrestor | Broken | 23-0115593 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873397 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320639556380 | 20230912 | 1514 | 20230912 | 1650 | 2216715 | 96 | Transformer only | Environmental/External | Lightning | 1 | 96 | 38.0488 | -120.2789 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115640 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873406 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320311254695 | 20230912 | 1600 | 20230912 | 1919 | 2216861 | 199 | Transformer only | Environmental/External | Lightning | 2 | 398 | 38.0022 | -120.3935 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115694 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873417 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 351809 | 20230912 | 1703 | 20230912 | 2008 | 2216915 | 185 | Distribution Circuit | 3rd Party | Vehicle | 408 | 5648 | 36.8512 | -120.044 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0115695 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873418 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 278740 | 20230912 | 1801 | 20230912 | 2050 | 2216973 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1887 | 280565 | 37.9881 | -120.2845 | No | Clear;32-90 F |  |  | 23-0115712 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873424 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | FUSE | 26869 | 20230912 | 1842 | 20230912 | 2013 | 2217016 | 91 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 182 | 37.2879 | -120.4312 | No | Clear;32-90 F |  |  | 23-0115729 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1873434 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 20230912 | 2006 | 20230913 | 34 | 2217075 | 268 | Distribution Circuit | Vegetation | Tree - fell into line | 904 | 242272 | 37.6313 | -120.1536 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0115714 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873433 | 0 | EPSS Ckt | Y | 2023 | N/A
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 6064 | 20230913 | 333 | 20230913 | 1547 | 2217247 | 734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 383 | 106846 | 37.9603 | -120.3771 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115839 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873509 | 0 | EPSS Ckt | Y | 2023 | GRD INST
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20230913 | 722 | 20230913 | 1041 | 2217356 | 199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 6169 | 37.9913 | -120.4128 | No | Clear;32-90 F |  |  | 23-0115921 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1873631 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 319813522946 | 20230913 | 748 | 20230913 | 830 | 2217372 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 42 | 37.1303 | -120.5652 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0115889 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873540 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 318050338317 | 20230913 | 855 | 20230913 | 1036 | 2217505 | 101 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 101 | 37.5505 | -121.1739 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115994 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873704 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 9615 | 20230913 | 1112 | 20230913 | 1319 | 2217732 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 3175 | 36.7853 | -120.6557 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0116019 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873715 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20230913 | 1307 | 20230913 | 1416 | 2217844 | 69 | Distribution Circuit | Company Initiated | Coordination failure | 582 | 40158 | 38.0085 | -120.3034 | No | Clear;32-90 F | Recloser | Normal | 23-0116129 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873748 | 0 | EPSS Ckt | Y | 2023 | GRD INST
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | OCB | 1703/2 | 20230913 | 1307 | 20230913 | 1548 | 2217955 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3879 | 622884 | 37.9742 | -120.3198 | No | Clear;32-90 F |  |  | 23-0116127 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873746 | 0 | EPSS Ckt | Y | 2023 | A PH & GRD
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320363213061 | 20230913 | 1320 | 20230913 | 2324 | 2217895 | 604 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 604 | 36.8584 | -120.3757 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0116304 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873789 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | FUSE | 27329 | 20230913 | 1459 | 20230913 | 1631 | 2218055 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 92 | 37.3361 | -120.9034 | No | Clear;Above 90 |  |  | 23-0116274 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873774 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 2076 | 20230914 | 546 | 20230914 | 703 | 2218431 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 205 | 37.1784 | -120.2741 | No | Clear;32-90 F |  |  | 23-0116414 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873866 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318790545485 | 20230914 | 729 | 20230914 | 2330 | 2218464 | 961 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 961 | 37.7484 | -120.9195 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0116502 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873996 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | FUSE | 3747 | 20230914 | 902 | 20230914 | 1146 | 2218622 | 164 | Distribution Circuit | Animal | Bird found | 1 | 164 | 37.0337 | -121.0667 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0116473 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873945 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5503 | 20230914 | 940 | 20230914 | 2356 | 2218758 | 856 | Distribution Circuit | Equipment Failure/Involved | Overhead | 871 | 83334 | 37.2077 | -119.5419 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0116544 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874021 | 1 | EPSS Ckt | Y | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 27099 | 20230914 | 1101 | 20230914 | 1134 | 2218796 | 33 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 66 | 37.7837 | -120.1714 | No | Clear;32-90 F | Secondary | Bent or Twisted | 23-0116589 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874040 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319184546290 | 20230914 | 1129 | 20230916 | 38 | 2218824 | 2229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 4458 | 37.7708 | -120.7833 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0116686 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874068 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 321429448365 | 20230914 | 1135 | 20230914 | 2140 | 2218826 | 605 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1210 | 37.826 | -120.0089 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0116733 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874075 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4572 | 20230914 | 1553 | 20230914 | 1719 | 2219043 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 4214 | 37.5217 | -119.9394 | No | Clear;32-90 F | Other | Broken | 23-0116804 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874090 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322790525832 | 20230914 | 1704 | 20230915 | 125 | 2219066 | 501 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 501 | 37.2068 | -119.5427 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0116850 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874100 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5503 | 20230914 | 1708 | 20230914 | 1803 | 2219113 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 1871 | 37.2077 | -119.5419 | No | Clear;32-90 F |  |  | 23-0116863 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874104 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | T0386 | 20230914 | 1737 | 20230915 | 444 | 2219117 | 667 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 8095 | 37.3792 | -120.617 | No | Clear;Above 90 | Secondary | Broken | 23-0116887 | UG | Sus | 45979819 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874117 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 318054038195 | 20230914 | 1836 | 20230915 | 444 | 2219015 | 608 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 608 | 37.5472 | -121.1726 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0116873 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874110 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 318041238265 | 20230914 | 1858 | 20230915 | 444 | 2219152 | 586 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 586 | 37.5491 | -121.176 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0116880 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874114 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | TRANSFORMER | 321307115937 | 20230914 | 1928 | 20230915 | 132 | 2219139 | 364 | Transformer only | Vegetation | Tree - branch fell on line | 12 | 4368 | 36.937 | -120.0537 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0116892 | OH | Sus | 31669156 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874119 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 11270 | 20230914 | 1930 | 20230915 | 148 | 2219167 | 378 | Distribution Circuit | Vegetation | Tree - branch fell on line | 338 | 41064 | 38.022 | -120.4319 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0116885 | OH | Sus | 31669157 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1874116 | 0 | EPSS Ckt | Y | 2023 | AB INST
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 5679 | 20230914 | 2346 | 20230915 | 931 | 2219240 | 585 | Distribution Circuit | 3rd Party | Vehicle | 125 | 37635 | 37.2396 | -119.7772 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0116930 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1874154 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | T7289 | 20230915 | 100 | 20230915 | 439 | 2219259 | 219 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 1752 | 37.2599 | -121.0177 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0116932 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874156 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | S1299 | 20230915 | 323 | 20230915 | 437 | 2219268 | 74 | Distribution Circuit | Animal | Bird found | 55 | 4070 | 37.9777 | -120.3168 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0116945 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874162 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320185715113 | 20230915 | 711 | 20230915 | 1011 | 2219363 | 180 | Transformer only | Animal | Other | 1 | 180 | 36.9151 | -120.4374 | No | Partly Cloudy;32-90 F | Transformer (OH) |  | 23-0117105 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874336 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321458114408 | 20230915 | 809 | 20230916 | 1206 | 2219421 | 1677 | Transformer only | 3rd Party | Customer Equipment | 1 | 1677 | 36.8942 | -120.0016 | No | Clear;32-90 F | Customer Equipment | Broken | 23-0111796 | OH | Sus | 35377756 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1874204 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 100000119848 | 20230915 | 905 | 20230915 | 1446 | 2219549 | 341 | Transformer only | Environmental/External | Lightning | 1 | 341 | 37.9253 | -120.4452 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0117086 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874322 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322130825147 | 20230915 | 917 | 20230915 | 1400 | 2219654 | 283 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 283 | 37.1886 | -119.768 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117071 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874312 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318954845256 | 20230915 | 945 | 20230915 | 1500 | 2219430 | 315 | Transformer only | Environmental/External | Lightning | 1 | 315 | 37.7423 | -120.8628 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117106 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874337 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321253659739 | 20230915 | 1045 | 20230915 | 1551 | 2219914 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 918 | 38.1395 | -120.0649 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0117229 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874380 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322793325545 | 20230915 | 1203 | 20230915 | 1635 | 2219847 | 272 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 272 | 37.1986 | -119.542 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117264 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874395 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321454861521 | 20230915 | 1556 | 20230916 | 1237 | 2220032 | 1241 | Transformer only | Environmental/External | Lightning | 1 | 1241 | 38.1879 | -119.9946 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117352 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874416 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1102 | 163251102 | FUSE | 23584 | 20230916 | 722 | 20230916 | 922 | 2220460 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 476 | 37.3862 | -121.0672 | No | Clear;32-90 F |  |  | 23-0117406 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1874504 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20230916 | 732 | 20230916 | 1115 | 2220369 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 6913 | 37.9913 | -120.4128 | No | Clear;32-90 F |  |  | 23-0117403 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874489 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9280 | 20230916 | 757 | 20230916 | 1626 | 2220378 | 509 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1535 | 188185 | 38.1994 | -120.0195 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117397 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874471 | 0 | EPSS Ckt | Y | 2023 | A PHASE & GRD TARGETS
YOSEMITE | YOSEMITE | PANOCHE-1103 | 253671103 | TRANSFORMER | 415361046655 | 20230916 | 1207 | 20230916 | 1252 | 2220617 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 45 | 36.6046 | -120.5819 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0117449 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874537 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321286560359 | 20230916 | 1343 | 20230916 | 1558 | 2220638 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 270 | 38.1566 | -120.0534 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0117475 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874554 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | TRANSFORMER | 318959320626 | 20230916 | 2034 | 20230917 | 414 | 2220795 | 460 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 6900 | 37.0657 | -120.8573 | No | Clear;32-90 F | Secondary | Arcing | 23-0117509 | OH | Sus | 31669300 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874587 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | OCB | 1101/2 | 20230916 | 2115 | 20230917 | 205 | 2220804 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2573 | 28861 | 36.9751 | -120.6348 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0117495 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874576 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 6676 | 20230916 | 2153 | 20230917 | 18 | 2220829 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1160 | 36.9091 | -119.8209 | No | Clear;32-90 F |  |  | 23-0117510 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874590 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | FUSE | 21046 | 20230917 | 429 | 20230917 | 1230 | 2220866 | 481 | Distribution Circuit | 3rd Party | Vehicle | 42 | 3462 | 37.4038 | -120.6148 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0117515 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874595 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | 319665932911 | 20230917 | 549 | 20230917 | 1348 | 2220870 | 479 | Transformer only | 3rd Party | Vehicle | 1 | 479 | 37.4038 | -120.6194 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117519 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874600 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | TRANSFORMER | 320550919674 | 20230917 | 703 | 20230917 | 822 | 2220921 | 79 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 237 | 37.0399 | -120.3108 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0117530 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874616 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20230917 | 855 | 20230917 | 1930 | 2220965 | 635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3108 | 131641 | 37.9913 | -120.4128 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117529 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874614 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1102 | 252531102 | TRANSFORMER | 322824227653 | 20230917 | 1200 | 20230918 | 35 | 2221015 | 755 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 755 | 37.2579 | -119.5307 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117549 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874630 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319886551808 | 20230917 | 1310 | 20230917 | 1745 | 2221047 | 275 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 550 | 37.9216 | -120.5401 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117557 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874637 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318734345049 | 20230917 | 1711 | 20230917 | 1810 | 2221082 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 590 | 37.7365 | -120.9385 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0117566 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874647 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230917 | 2158 | 20230917 | 2323 | 2221137 | 85 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 261 | 22185 | 37.0552 | -120.0295 | No | Clear;32-90 F |  |  | 23-0117592 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874673 | 0 | EPSS Ckt | N | 2023 | BC
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 3525 | 20230918 | 344 | 20230918 | 527 | 2221166 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 515 | 37.0399 | -120.6329 | No | Clear;32-90 F |  |  | 23-0117603 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874683 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 2051 | 20230918 | 726 | 20230918 | 1023 | 2221230 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 177 | 36.86 | -120.3684 | No | Clear;32-90 F |  |  | 23-0117726 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1874861 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 20477 | 20230918 | 900 | 20230918 | 1030 | 2221374 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 120 | 37.786 | -121.0338 | No | Clear;32-90 F |  |  | 23-0117738 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874869 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | TRANSFORMER | 415079853577 | 20230918 | 920 | 20230918 | 1421 | 2221431 | 301 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 301 | 36.793 | -120.6813 | No | Clear;32-90 F |  |  | 23-0117891 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1874932 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | T0241 | 20230918 | 1030 | 20230918 | 1155 | 2221521 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 85 | 37.634 | -120.3572 | No | Clear;32-90 F |  |  | 23-0117788 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874891 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321622235091 | 20230918 | 1236 | 20230918 | 1423 | 2221650 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 107 | 37.4614 | -119.9412 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0117805 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874902 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 415952553321 | 20230918 | 1409 | 20230918 | 2051 | 2221754 | 402 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 402 | 36.789 | -120.3832 | No | Clear;32-90 F | Fuse | Broken | 23-0118003 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874978 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 485817 | 20230918 | 1426 | 20230919 | 129 | 2221771 | 663 | Distribution Circuit | 3rd Party | Vehicle | 1 | 663 | 36.8513 | -120.0143 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0117916 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | Yes | 1874939 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319838830458 | 20230918 | 1755 | 20230919 | 45 | 2221922 | 410 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 820 | 37.337 | -120.5555 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117988 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874965 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 851902 | 20230918 | 1805 | 20230918 | 2024 | 2221944 | 139 | Distribution Circuit | Animal | Bird found | 2673 | 218506 | 37.4831 | -119.9631 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0117987 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874964 | 0 | EPSS Ckt | Y | 2023 | A GRD
YOSEMITE | YOSEMITE | BIOLA-1102 | 252211102 | FUSE | 5744 | 20230919 | 600 | 20230919 | 818 | 2222077 | 138 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 920 | 36.8221 | -120.1522 | No | Clear;32-90 F |  |  | 23-0118074 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875059 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322491535098 | 20230919 | 826 | 20230919 | 1310 | 2222201 | 284 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 284 | 37.4603 | -119.6433 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118149 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875198 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | 319633014272 | 20230919 | 832 | 20230919 | 2314 | 2222209 | 882 | Transformer only | Animal | Other | 1 | 882 | 36.909 | -120.6264 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0118470 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875317 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIGARDEN-2107 | 254552107 | TRANSFORMER | 417436455525 | 20230919 | 903 | 20230919 | 1832 | 2222773 | 569 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1138 | 36.8548 | -119.8759 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118435 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875293 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321567437873 | 20230919 | 915 | 20230919 | 1006 | 2222256 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 51 | 37.5381 | -119.9608 | No | Clear;32-90 F | Secondary | Broken | 23-0118093 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875106 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230919 | 1243 | 20230919 | 1340 | 2222540 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 261 | 14877 | 37.0552 | -120.0295 | No | Clear;32-90 F |  |  | 23-0118271 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1875248 | 0 | EPSS Ckt | N | 2023 | B & C
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | TRANSFORMER | 318633521953 | 20230919 | 1400 | 20230919 | 1931 | 2222754 | 331 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 331 | 37.1018 | -120.9699 | No | Clear;32-90 F |  |  | 23-0118438 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1875297 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | TRANSFORMER | 320725124157 | 20230919 | 1401 | 20230920 | 44 | 2222591 | 643 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 643 | 37.1637 | -120.252 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118413 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875282 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 319038051565 | 20230919 | 1415 | 20230920 | 325 | 2222602 | 790 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 790 | 37.9157 | -120.8346 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118436 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875294 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | TRANSFORMER | 415959852008 | 20230919 | 1427 | 20230919 | 1541 | 2222599 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1036 | 36.7539 | -120.3798 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0118291 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875256 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | RECLOSER | 9910 | 20230919 | 1613 | 20230920 | 818 | 2222678 | 965 | Distribution Circuit | 3rd Party | Vehicle | 553 | 133445 | 36.9918 | -120.6355 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0118388 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1875272 | 0 | Non-EPSS | N | 2023 | A & GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 59596 | 20230919 | 1759 | 20230920 | 144 | 2222759 | 465 | Distribution Circuit | Animal | Bird found | 786 | 189498 | 37.9009 | -120.5804 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118426 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1875288 | 0 | EPSS Ckt | Y | 2023 | AB
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321770934816 | 20230919 | 2207 | 20230919 | 2339 | 2222816 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 92 | 37.4522 | -119.8896 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0118477 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875319 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 7875 | 20230920 | 223 | 20230920 | 358 | 2222841 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 5415 | 37.3529 | -120.6583 | No | Clear;32-90 F |  |  | 23-0118502 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1875325 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | JUMPER | FBS 1 POLE N/OF CGC 321310117432 | 20230920 | 543 | 20230920 | 1244 | 2222821 | 421 | Distribution Circuit | 3rd Party | Vehicle | 158 | 66518 | 36.978 | -120.052 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0118503 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875326 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | TRANSFORMER | 318549548655 | 20230920 | 649 | 20230920 | 1445 | 2223520 | 476 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 476 | 37.8353 | -121.0036 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118871 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875621 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 19083 | 20230920 | 735 | 20230921 | 1515 | 2222942 | 1900 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 6100 | 36.814 | -120.3067 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118701 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875557 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10257 | 20230920 | 1858 | 20230921 | 150 | 2223697 | 412 | Distribution Circuit | Environmental/External | Lightning | 1 | 412 | 37.4591 | -119.6405 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118976 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875658 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 258550 | 20230921 | 821 | 20230921 | 1147 | 2223839 | 206 | Distribution Circuit | Animal | Squirrel | 2562 | 284650 | 37.8844 | -120.3058 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 23-0119095 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875720 | 0 | EPSS Ckt | Y | 2023 | C PHASE & GRD
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20643 | 20230921 | 1913 | 20230921 | 2055 | 2224290 | 102 | Distribution Circuit | Animal | Bird found | 1 | 102 | 37.7426 | -120.824 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0119471 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1875831 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | RECLOSER | 815510 | 20230921 | 2337 | 20230922 | 1320 | 2224364 | 704 | Distribution Circuit | Animal | Bird found | 2574 | 352191 | 37.3958 | -120.7178 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0119512 | OH | Sus | 45986978 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1875861 | 0 | Non-EPSS | N | 2023 | B
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 7313 | 20230922 | 919 | 20230922 | 1014 | 2224620 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 3080 | 37.2948 | -120.491 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0119629 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875993 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1105 | 254101105 | FUSE | 6973 | 20230922 | 1014 | 20230922 | 1058 | 2224727 | 44 | Distribution Circuit | Animal | Bird found | 41 | 1804 | 37.1193 | -120.2618 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0119706 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876052 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 5480 | 20230922 | 1027 | 20230922 | 1712 | 2224752 | 405 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1150 | 182289 | 37.3755 | -119.6292 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0119701 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876049 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | FUSE | 9677 | 20230922 | 1049 | 20230922 | 1218 | 2224795 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 801 | 36.8223 | -120.7282 | No | Partly Cloudy;32-90 F |  |  | 23-0119903 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876110 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | FUSE | 4171 | 20230922 | 1204 | 20230922 | 1250 | 2224872 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 2254 | 37.2887 | -120.4335 | No | Clear;32-90 F |  |  | 23-0119796 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876076 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 22227 | 20230922 | 1302 | 20230922 | 1420 | 2224907 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1561 | 37.7741 | -120.8278 | No | Clear;32-90 F |  |  | 23-0119863 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876098 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | SWITCH | S1537 | 20230922 | 1432 | 20230922 | 2032 | 2224955 | 360 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 720 | 37.8651 | -120.1692 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0119886 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1876105 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 12302 | 20230923 | 23 | 20230923 | 240 | 2225157 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 8681 | 36.9811 | -119.893 | No | Partly Cloudy;32-90 F |  |  | 23-0119985 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876143 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 21637 | 20230923 | 428 | 20230923 | 1205 | 2225175 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3670 | 37.3108 | -121.0194 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0119992 | OH | Sus | 45988076 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876152 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | OCB | 1704/2 | 20230923 | 838 | 20230923 | 1109 | 2225273 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3216 | 485616 | 37.9035 | -120.4971 | No | Clear;32-90 F | Regulator | Burned/flashed | 23-0120012 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1876192 | 0 | EPSS Ckt | Y | 2023 | A- B & GRD
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319609034623 | 20230923 | 1530 | 20230923 | 1749 | 2225519 | 139 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 417 | 37.4506 | -120.635 | No | Clear;32-90 F | Fuse | Broken | 23-0120083 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876239 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | SWITCH | 9516 | 20230923 | 1629 | 20230923 | 1818 | 2225533 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 281 | 7813 | 36.7512 | -120.3856 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0120046 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1876237 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20230923 | 1659 | 20230923 | 1909 | 2225550 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 261 | 33930 | 37.0552 | -120.0295 | No | Clear;32-90 F |  |  | 23-0120092 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876245 | 0 | EPSS Ckt | N | 2023 | A PHASE
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 10864 | 20230923 | 1822 | 20230923 | 2048 | 2225585 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 11242 | 37.2807 | -120.4437 | No | Clear;32-90 F |  |  | 23-0120096 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876249 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | OCB | 1103/2 | 20230923 | 1916 | 20230923 | 2116 | 2225601 | 120 | Distribution Circuit | 3rd Party | Vehicle | 2278 | 273360 | 36.7203 | -120.4588 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0120093 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1876246 | 0 | Non-EPSS | N | 2023 | ABC TIME
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20230923 | 1944 | 20230924 | 942 | 2225607 | 838 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 583 | 221497 | 38.0085 | -120.3034 | No | Clear;32-90 F |  |  | 23-0120095 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876248 | 0 | EPSS Ckt | Y | 2023 | DCD & SGF
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 3715 | 20230924 | 1212 | 20230924 | 1812 | 2225888 | 360 | Distribution Circuit | 3rd Party | Vehicle | 26 | 5175 | 37.0545 | -120.5724 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0120148 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876316 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 3955 | 20230924 | 1401 | 20230924 | 1523 | 2225912 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 5084 | 36.7661 | -120.3798 | No | Clear;32-90 F | Fuse | Broken | 23-0120151 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1876319 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 7207 | 20230924 | 2244 | 20230925 | 1406 | 2226010 | 922 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 18440 | 37.3176 | -120.4444 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0120190 | UG | Sus | 45988230 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876354 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L2183 | 20230925 | 934 | 20230925 | 956 | 2226415 | 22 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 22 | 37.9908 | -120.4797 | No | Partly Cloudy;32-90 F |  |  | 23-0120302 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876553 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 6903 | 20230925 | 1206 | 20230925 | 1417 | 2226623 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 774 | 36.9091 | -119.9652 | No | Clear-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0120498 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876646 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 13022 | 20230925 | 1300 | 20230925 | 1353 | 2226664 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 212 | 37.0689 | -120.1269 | No | Partly Cloudy;32-90 F |  |  | 23-0120481 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876637 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | JUMPER | OJ 2 POLES N/O CGC 319553719368 | 20230925 | 1310 | 20230925 | 1600 | 2226682 | 170 | Distribution Circuit | 3rd Party | Vehicle | 2 | 340 | 37.0326 | -120.6538 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on object | 23-0120461 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | Yes | Yes | 1876626 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320935156827 | 20230925 | 1335 | 20230925 | 1427 | 2226709 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 156 | 38.0602 | -120.1758 | No | Partly Cloudy;32-90 F | Secondary |  | 23-0120471 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1876628 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20230925 | 1523 | 20230925 | 1640 | 2226813 | 77 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 583 | 44891 | 38.0085 | -120.3034 | No | Partly Cloudy;32-90 F |  |  | 23-0120555 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876666 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | JUMPER | 321264116442 | 20230925 | 2100 | 20230926 | 208 | 2227010 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 616 | 36.9511 | -120.0688 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0120629 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1876689 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | SWITCH | 10358 | 20230925 | 2151 | 20230926 | 234 | 2227024 | 283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3679 | 37.3335 | -119.6453 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0120624 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1876695 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319670031131 | 20230925 | 2323 | 20230926 | 46 | 2227051 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 913 | 37.355 | -120.6144 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0120686 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876728 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 22142 | 20230926 | 405 | 20230926 | 501 | 2227155 | 56 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 411 | 37.7849 | -120.8494 | No | Clear;32-90 F |  |  | 23-0120693 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876735 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 53957 | 20230926 | 630 | 20230926 | 740 | 2227190 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 5110 | 38.0333 | -120.4031 | No | Clear;32-90 F | Lightning Arrestor | Broken | 23-0120725 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876748 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | RECLOSER | 3290 | 20230926 | 705 | 20230926 | 1425 | 2227210 | 440 | Distribution Circuit | 3rd Party | Vehicle | 348 | 47102 | 37.7466 | -120.8398 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0120734 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1876750 | 0 | Non-EPSS | N | 2023 | A B C 51 TIME
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 9744 | 20230926 | 848 | 20230926 | 1000 | 2227368 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 72 | 37.1294 | -120.9482 | No | Clear;32-90 F |  |  | 23-0120845 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876924 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 9460 | 20230926 | 910 | 20230926 | 1114 | 2227433 | 124 | Distribution Circuit | Animal | Bird found | 1307 | 121575 | 37.591 | -120.3071 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0120796 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876885 | 0 | EPSS Ckt | Y | 2023 | A B 50 INST
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 153021 | 20230926 | 921 | 20230926 | 1052 | 2227451 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 91 | 37.8276 | -121.006 | No | Clear;32-90 F |  |  | 23-0120886 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876947 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 7886 | 20230926 | 923 | 20230926 | 1555 | 2227456 | 392 | Distribution Circuit | 3rd Party | Vehicle | 18 | 1956 | 37.2653 | -120.469 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0120876 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1876943 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | TRANSFORMER | 415728250800 | 20230926 | 1005 | 20230926 | 1100 | 2227507 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 55 | 36.7198 | -120.4586 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0120850 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | Yes | No | 1876926 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320743352555 | 20230926 | 1144 | 20230926 | 1345 | 2227614 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 121 | 37.9433 | -120.2437 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0121035 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1876998 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 3959 | 20230926 | 1246 | 20230926 | 1306 | 2227626 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 2600 | 36.7631 | -120.3766 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0120957 | OH | Sus | 45991322 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1876977 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320148350161 | 20230926 | 1537 | 20230926 | 1807 | 2227816 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 178 | 10593 | 37.8779 | -120.4497 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0121107 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1877008 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 3652 | 20230926 | 1935 | 20230926 | 1944 | 2227988 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 130 | 1170 | 36.7599 | -120.3791 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0120957 | OH | Sus | 45991322 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1877046 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 3645 | 20230926 | 2133 | 20230926 | 2254 | 2228074 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 486 | 37.3038 | -120.5235 | No | Clear;32-90 F |  |  | 23-0121213 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877074 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | RECLOSER | 5570 | 20230926 | 2234 | 20230927 | 1010 | 2228087 | 696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 437 | 55605 | 37.0543 | -120.3521 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0121215 | OH | Sus | 45991558 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1877079 | 0 | Non-EPSS | N | 2023 | GRD FAULT
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 3439 | 20230927 | 220 | 20230927 | 540 | 2228143 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 800 | 37.0833 | -120.6264 | No | Clear;32-90 F |  |  | 23-0121260 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877104 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 24349 | 20230927 | 1120 | 20230927 | 2153 | 2228566 | 633 | Distribution Circuit | 3rd Party | Vehicle | 19 | 12027 | 37.2312 | -121.0308 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0121519 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1877319 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | OTHER | WIRE DOWN @ 247767 | 20230927 | 1325 | 20230927 | 1618 | 2228669 | 173 | Distribution Circuit | 3rd Party | Vehicle | 208 | 26400 | 37.0849 | -120.6355 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0121583 | OH | Sus | 45992606 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | Yes | Yes | 1877340 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 9927 | 20230927 | 1433 | 20230927 | 2120 | 2228714 | 407 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 3529 | 37.0719 | -120.9614 | No | Clear;32-90 F |  |  | 23-0121783 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877390 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | FUSE | 19095 | 20230927 | 1456 | 20230927 | 1606 | 2228734 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 280 | 37.3281 | -120.9149 | No | Clear;32-90 F |  |  | 23-0121712 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877359 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320394513062 | 20230927 | 1501 | 20230927 | 1945 | 2228737 | 284 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 284 | 36.8584 | -120.3649 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0121696 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877354 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | RECLOSER | 11490 | 20230927 | 1558 | 20230927 | 2152 | 2228786 | 354 | Distribution Circuit | 3rd Party | Vehicle | 63 | 14856 | 37.14 | -120.2742 | No | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0121719 | OH | Sus | 45992531 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1877361 | 0 | Non-EPSS | N | 2023 | C- GRD
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23225 | 20230927 | 1849 | 20230927 | 1950 | 2228939 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 2135 | 37.9777 | -120.3149 | No | Clear;32-90 F |  |  | 23-0121771 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877379 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE SUB | 16371 | OCB | 1700/2 | 20230928 | 314 | 20230928 | 325 | 2229051 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5350 | 58850 | 37.7729 | -120.8261 | No | Clear;32-90 F |  |  | 23-0121811 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1877408 | 0 | Non-EPSS | N | 2023 | A & B- TIME OC
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 5845 | 20230928 | 433 | 20230928 | 623 | 2229073 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 293 | 37.3626 | -121.1038 | No | Clear;32-90 F |  |  | 23-0121828 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877418 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 20230928 | 925 | 20230928 | 1055 | 2229334 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 903 | 81270 | 37.6313 | -120.1536 | No | Clear;32-90 F |  |  | 23-0121950 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877562 | 0 | EPSS Ckt | Y | 2023 | BC
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320927056818 | 20230928 | 1400 | 20230928 | 1722 | 2229625 | 202 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 202 | 38.0595 | -120.1787 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0122222 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877672 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | S1949 | 20230928 | 1435 | 20230928 | 1622 | 2229652 | 107 | Distribution Circuit | 3rd Party | Vehicle | 7 | 749 | 37.7326 | -120.8895 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0122264 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877694 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7323 | 20230928 | 1546 | 20230928 | 1821 | 2229727 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1240 | 37.4792 | -120.5767 | No | Clear;32-90 F |  |  | 23-0122291 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877707 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | TRANSFORMER | 320899216480 | 20230928 | 1639 | 20230928 | 2117 | 2229706 | 278 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 556 | 36.9527 | -120.1932 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0122278 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877696 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1116 | 252761116 | FUSE | 6555 | 20230928 | 1654 | 20230928 | 1736 | 2229781 | 42 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 588 | 36.8794 | -120.0196 | No | Clear;32-90 F |  |  | 23-0122284 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877701 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 7608 | 20230928 | 2215 | 20230929 | 728 | 2229922 | 553 | Distribution Circuit | 3rd Party | Vehicle | 63 | 16349 | 37.268 | -120.4345 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0122323 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1877738 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | FUSE | 6599 | 20230929 | 633 | 20230929 | 822 | 2230032 | 109 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 218 | 36.8948 | -120.1689 | No | Clear;32-90 F |  |  | 23-0122414 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1877825 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319518836063 | 20230929 | 1309 | 20230929 | 1353 | 2230500 | 44 | Transformer only | 3rd Party | Other | 2 | 88 | 37.4901 | -120.6669 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0122635 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1877956 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | TRANSFORMER | 321406215997 | 20230929 | 1428 | 20230929 | 1550 | 2230563 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 164 | 36.9382 | -120.0196 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0122681 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1877971 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 9559 | 20230930 | 551 | 20230930 | 1220 | 2231305 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2854 | 37.1894 | -120.7084 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 23-0122870 | OH | Sus | 31670896 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1878119 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 5025 | 20230930 | 637 | 20230930 | 757 | 2231327 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1281 | 37.7727 | -121.0678 | No | Overcast;32-90 F |  |  | 23-0122849 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1878091 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | FUSE | 6225 | 20230930 | 733 | 20230930 | 845 | 2231358 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 288 | 37.2408 | -120.9399 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0122874 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1878131 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 7035 | 20230930 | 846 | 20230930 | 956 | 2231421 | 70 | Distribution Circuit | Animal | Bird found | 6 | 420 | 37.2728 | -120.5784 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0122913 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1878172 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 9893 | 20230930 | 1031 | 20231001 | 1611 | 2231521 | 1780 | Distribution Circuit | Equipment Failure/Involved | Underground | 1079 | 351607 | 37.9707 | -120.4299 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0122918 | UG | Sus | 45995380 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1878174 | 0 | EPSS Ckt | Y | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | 5983 | 20230930 | 1110 | 20231002 | 934 | 2231594 | 2784 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 2784 | 37.9741 | -120.3774 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 23-0122944 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | No | No | 1878194 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7977 | 20230930 | 1307 | 20230930 | 1748 | 2231627 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 843 | 37.4917 | -120.652 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0122958 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1878205 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 21145 | 20230930 | 1320 | 20230930 | 2125 | 2231648 | 485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1455 | 36.8931 | -119.9388 | No | Partly Cloudy;32-90 F | Insulator | Failed/Faulted | 23-0122984 | OH | Sus | 31670981 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1878221 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 6563 | 20230930 | 1510 | 20231001 | 45 | 2231738 | 575 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 8448 | 36.9353 | -119.912 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0122995 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1878228 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318766344976 | 20230930 | 2024 | 20230930 | 2356 | 2231940 | 212 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1696 | 37.7345 | -120.9274 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0123042 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1878270 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | RECLOSER | 979850 | 20231001 | 326 | 20231002 | 1550 | 2232006 | 2051 | Distribution Circuit | Animal | Other | 136 | 29184 | 37.0097 | -119.7952 | No | Partly Cloudy-Fog;32-90 F | Customer Equipment | Burned/flashed | 23-0123067 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878295 | 0 | EPSS Ckt | N | 2023 | A AND B
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 5607 | 20231001 | 1234 | 20231001 | 1620 | 2232179 | 226 | Distribution Circuit | Animal | Bird found | 372 | 36961 | 37.7889 | -120.7975 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0123103 | OH | Sus | 31671040 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | Yes | 1878343 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BONITA-1103 | 255391103 | FUSE | 6585 | 20231001 | 2206 | 20231002 | 42 | 2232305 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2964 | 36.9692 | -120.2203 | No | Partly Cloudy;32-90 F |  |  | 23-0123165 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878394 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | T0645 | 20231001 | 2244 | 20231002 | 1444 | 2232317 | 960 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 17643 | 37.3758 | -120.7153 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0123170 | UG | Sus | 35493001 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1878400 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320385012478 | 20231002 | 1045 | 20231002 | 1103 | 2232730 | 18 | Transformer only | Equipment Failure/Involved | Fire- pole | 2 | 36 | 36.8424 | -120.368 | No | Clear;32-90 F | Fuse | Broken | 23-0123323 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1878570 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | FUSE | 23408 | 20231002 | 1056 | 20231002 | 1205 | 2232802 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 2622 | 36.9926 | -120.0562 | No | Clear;32-90 F |  |  | 23-0123353 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878589 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318540846840 | 20231002 | 1342 | 20231002 | 1839 | 2232971 | 297 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 594 | 37.7853 | -121.0059 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0123493 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1878639 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320321654569 | 20231002 | 1434 | 20231002 | 1609 | 2233085 | 95 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 95 | 37.9987 | -120.3895 | No | Clear;32-90 F | Fuse | Broken | 23-0123518 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1878649 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | OTHER | J26186 TWD T24707 | 20231002 | 1536 | 20231002 | 1707 | 2233084 | 91 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 3458 | 36.9508 | -120.0418 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0123457 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1878643 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 7034 | 20231002 | 2243 | 20231003 | 151 | 2233297 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1880 | 37.2673 | -120.5973 | No | Clear;32-90 F |  |  | 23-0123602 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878729 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | RECLOSER | 361564 | 20231003 | 1002 | 20231003 | 1021 | 2233644 | 19 | Distribution Circuit | Company Initiated | Personnel- company | 69 | 1311 | 37.24 | -119.552 | No | Clear;32-90 F | Fuse | Normal | 23-0123722 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878923 | 0 | EPSS Ckt | N | 2023 | A-C
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 6757 | 20231003 | 1126 | 20231003 | 1352 | 2233703 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1022 | 37.808 | -120.7218 | No | Clear;32-90 F |  |  | 23-0123818 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878944 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | JUMPER | OJ S/SIDE OF CGC 320206036720 | 20231003 | 1159 | 20231003 | 1505 | 2233746 | 186 | Distribution Circuit | Animal | Other | 9 | 554 | 37.5073 | -120.4302 | No | Clear;32-90 F | Jumper | Burned Open | 23-0123817 | OH | Sus | 45998163 | CENTRAL VALLEY | OCT | Open Circuit | 0 | No | No | No | 1878942 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 891371 | 20231003 | 1247 | 20231003 | 1515 | 2233777 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 296 | 36.8851 | -120.1103 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0123839 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1878954 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 786213 | 20231003 | 1333 | 20231003 | 1500 | 2233819 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1218 | 37.0907 | -120.2971 | No | Clear;32-90 F |  |  | 23-0123952 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1878984 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320902349385 | 20231003 | 1526 | 20231003 | 1617 | 2233923 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 306 | 37.8558 | -120.1884 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0123973 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1878989 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10890 | 20231003 | 1716 | 20231004 | 225 | 2234009 | 549 | Distribution Circuit | 3rd Party | Vehicle | 1366 | 191915 | 37.31 | -119.5845 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0124040 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1879005 | 0 | EPSS Ckt | Y | 2023 | A-C
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | JUMPER | OJ 1 E/OF MTR# 1010092435 | 20231004 | 746 | 20231004 | 939 | 2234213 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 339 | 37.2119 | -120.2165 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0124182 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1879094 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318660127541 | 20231004 | 1020 | 20231004 | 1128 | 2234527 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 68 | 37.2557 | -120.9614 | No | Clear;32-90 F | Fuse | Broken | 23-0124350 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879307 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322513035823 | 20231004 | 1020 | 20231004 | 1041 | 2234524 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 189 | 37.4797 | -119.6356 | No | Clear;32-90 F | Bushing | Bent or Twisted | 23-0124300 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879277 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 320530114896 | 20231004 | 1144 | 20231004 | 1438 | 2234623 | 174 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 174 | 36.9095 | -120.3183 | No | Clear;32-90 F |  |  | 23-0124497 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1879355 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | JUMPER | OJ 2 SW/OF MTR# 1006942508 | 20231004 | 1230 | 20231004 | 1430 | 2234680 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 240 | 37.3594 | -119.6036 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0124387 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879325 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 8522 | 20231004 | 1238 | 20231004 | 1328 | 2234688 | 50 | Distribution Circuit | Animal | Other | 51 | 2550 | 37.6559 | -120.349 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0124390 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879329 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | FUSE | 1575 | 20231004 | 1244 | 20231004 | 1313 | 2234694 | 29 | Distribution Circuit | 3rd Party | Metallic Balloon | 65 | 1885 | 36.936 | -120.0557 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0124395 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879331 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321533818132 | 20231004 | 1349 | 20231004 | 1611 | 2234774 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 426 | 36.9966 | -119.9758 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0124531 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879358 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318691846655 | 20231004 | 1512 | 20231004 | 1649 | 2234833 | 97 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 97 | 37.7803 | -120.9534 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0124553 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879366 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 21856 | 20231004 | 1550 | 20231004 | 1607 | 2234855 | 17 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 1837 | 36.995 | -119.9916 | No | Clear;32-90 F |  |  | 23-0124574 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879373 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321933636008 | 20231004 | 1558 | 20231004 | 1613 | 2234860 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 15 | 37.487 | -119.8346 | No | Clear;32-90 F | Bushing | Broken | 23-0124568 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879370 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 7746 | 20231004 | 1559 | 20231004 | 1909 | 2234865 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1014 | 37.1419 | -120.4644 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0124632 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879387 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | 318763726584 | 20231004 | 1932 | 20231005 | 354 | 2235046 | 502 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 8534 | 37.2295 | -120.9254 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0124689 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879423 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321485418063 | 20231004 | 2043 | 20231004 | 2135 | 2235067 | 52 | Transformer only | Animal | Bird found | 3 | 156 | 36.9947 | -119.9926 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0124670 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879402 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | FUSE | 7399 | 20231005 | 830 | 20231005 | 915 | 2235387 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 45 | 37.3049 | -120.4846 | No | Clear;32-90 F |  |  | 23-0124778 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879560 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320297527152 | 20231005 | 832 | 20231005 | 1215 | 2235391 | 223 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 446 | 37.2464 | -120.3976 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0124756 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879493 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320547513859 | 20231005 | 1013 | 20231005 | 1151 | 2235571 | 98 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 98 | 36.8804 | -120.3138 | No | Clear;32-90 F |  |  | 23-0124882 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1879638 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | OCB | 1101/2 | 20231005 | 1100 | 20231005 | 1800 | 2235636 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 8724 | 36.6512 | -120.5803 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0124855 | OH | Sus | 46001145 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1879623 | 0 | Non-EPSS | N | 2023 | B- C
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | S407 | 20231005 | 1612 | 20231005 | 1748 | 2235926 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 7008 | 37.2311 | -121.0142 | No | Clear;Above 90 |  |  | 23-0125089 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1879712 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | JUMPER | OJ 1 S/OF C1470 | 20231006 | 1004 | 20231006 | 1133 | 2236523 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 663 | 55911 | 37.2435 | -121.0128 | No | Clear;32-90 F | Jumper | Broken | 23-0125315 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879953 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | TRANSFORMER | 318549048860 | 20231006 | 1021 | 20231006 | 1226 | 2236578 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 125 | 37.8406 | -121.0038 | No | Clear;32-90 F | Fuse | Broken | 23-0125465 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1879988 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | FUSE | 3539 | 20231006 | 1028 | 20231006 | 1610 | 2236937 | 342 | Distribution Circuit | Animal | Other | 1 | 342 | 36.5647 | -120.4611 | No | Clear;32-90 F | Fuse | Normal | 23-0125595 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880057 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 13335 | 20231006 | 1528 | 20231007 | 8 | 2236952 | 520 | Distribution Circuit | 3rd Party | Vehicle | 1 | 520 | 37.4537 | -120.622 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0125606 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Multi-Fault | 0 | No | No | No | 1880063 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 20871 | 20231006 | 1638 | 20231006 | 1753 | 2236942 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 450 | 37.7436 | -120.9403 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0125598 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880059 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 25106 | 20231006 | 1651 | 20231006 | 2153 | 2236950 | 302 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 5436 | 37.6992 | -120.3346 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0125604 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880062 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319243630600 | 20231007 | 909 | 20231007 | 922 | 2237373 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 13 | 37.3397 | -120.7614 | No | Fog;32-90 F | Fuse | Broken | 23-0125700 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880182 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L2183 | 20231007 | 1104 | 20231007 | 1230 | 2237667 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 86 | 37.9908 | -120.4797 | No | Clear;32-90 F |  |  | 23-0125731 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1880215 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | OTHER | WIRE DOWN 2 E/OF 10853 | 20231007 | 1255 | 20231007 | 1958 | s1880229 | 423 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1692 | 0 | 0 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 23-0125758 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | Yes | 1880229 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 25095 | 20231007 | 1342 | 20231007 | 1946 | 2237708 | 364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 13104 | 37.7276 | -120.3475 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0125743 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880222 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 11633 | 20231007 | 1703 | 20231007 | 2224 | 2237847 | 321 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 642 | 37.1854 | -120.3474 | No | Clear;Above 90 | Customer Equipment | Malfunctioning | 23-0125799 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880266 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320447543967 | 20231007 | 1749 | 20231007 | 2045 | 2237873 | 176 | Transformer only | Animal | Other | 1 | 176 | 37.7096 | -120.345 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0125780 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880247 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 7160 | 20231007 | 1750 | 20231009 | 1057 | 2237874 | 2467 | Distribution Circuit | Animal | Bird found | 91 | 11827 | 37.3012 | -120.6331 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0125786 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880254 | 0 | Non-EPSS | N | 2023 | A & GRD
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | T9390 | 20231007 | 1751 | 20231008 | 1637 | 2237879 | 1366 | Distribution Circuit | Equipment Failure/Involved | Underground | 165 | 33602 | 37.7267 | -120.9452 | No | Clear;Above 90 | Conductor- Underground | Burned/flashed | 23-0125785 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880253 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | FUSE | 24789 | 20231007 | 2309 | 20231009 | 30 | 2238289 | 1521 | Distribution Circuit | 3rd Party | Vehicle | 6 | 9075 | 36.96 | -120.1004 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0125825 | UG | Sus | 35494840 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880340 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | SWITCH | 38524 | 20231008 | 11 | 20231008 | 1614 | 2238020 | 963 | Distribution Circuit | 3rd Party | Vehicle | 448 | 293097 | 36.96 | -120.1025 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0125825 | OH | Sus | 35494840 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880285 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | OTHER | J26155 TWD T14364 | 20231008 | 18 | 20231008 | 111 | 2238029 | 53 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 795 | 36.8419 | -120.4419 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0125797 | UG | Sus | 35494686 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880286 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | OCB | 2103/2 | 20231008 | 130 | 20231008 | 1502 | 2238036 | 812 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1192 | 62744 | 37.4285 | -120.6386 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0125828 | OH | Sus | 31671940 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1880288 | 0 | Non-EPSS | N | 2023 | A- B- TIME OC
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 5033 | 20231008 | 1907 | 20231008 | 2040 | 2238386 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 682 | 37.3746 | -121.056 | No | Clear;32-90 F |  |  | 23-0125883 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880362 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | SWITCH | 65648 | 20231009 | 356 | 20231009 | 1438 | 2238510 | 642 | Distribution Circuit | 3rd Party | Vehicle | 735 | 6514 | 36.9599 | -120.0508 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0125906 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880394 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20231009 | 822 | 20231009 | 1104 | 2238648 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 451 | 72384 | 38.0052 | -120.4062 | No | Partly Cloudy;32-90 F |  |  | 23-0125951 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1880473 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 322266733030 | 20231009 | 1248 | 20231009 | 1422 | 2239050 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 752 | 37.4045 | -119.7208 | No | Overcast;32-90 F | Secondary | Broken | 23-0126108 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1880645 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | JUMPER | OJ 2SP W/OF 25107 | 20231009 | 1536 | 20231009 | 1950 | 2239185 | 254 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 762 | 37.6944 | -120.3358 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0126183 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1880676 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 8536 | 20231009 | 1720 | 20231009 | 1750 | 2239267 | 30 | Distribution Circuit | Animal | Bird found | 26 | 780 | 37.3007 | -120.4796 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0126243 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1880698 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | RECLOSER | 37478 | 20231011 | 415 | 20231011 | 646 | 2240357 | 151 | Distribution Circuit | Vegetation | Tree - branch fell on line | 945 | 142695 | 36.9892 | -120.6347 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 23-0126810 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881076 | 0 | Non-EPSS | N | 2023 | B & GRD
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 1101/2 | 20231011 | 905 | 20231011 | 1015 | 2240591 | 70 | Distribution Circuit | Company Initiated | Personnel- company | 702 | 48771 | 37.2537 | -119.5191 | No | Clear;32-90 F | Elbow | Normal | 23-0126905 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881212 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | CHOWCHILLA-1102 | 254101102 | FUSE | 23586 | 20231011 | 923 | 20231011 | 1448 | 2240629 | 325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 3925 | 37.1222 | -120.251 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0126970 | OH | Sus | 46009788 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1881305 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | TRANSFORMER | 321324115846 | 20231011 | 938 | 20231011 | 1518 | 2240766 | 340 | Transformer only | Vegetation | Tree - grew into line | 1 | 340 | 36.9344 | -120.0479 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0127019 | OH | Sus | 46009714 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881324 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | OCB | 1716/2 | 20231011 | 1302 | 20231011 | 1623 | 2240945 | 201 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3385 | 329319 | 37.7688 | -120.9077 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0127056 | OH | Sus | 46009905 | CENTRAL VALLEY | OCT | Multi-Fault | 0 | No | Yes | No | 1881343 | 0 | Non-EPSS | N | 2023 | ABC
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | RECLOSER | 421930 | 20231011 | 1309 | 20231011 | 1359 | 2241019 | 50 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 2500 | 37.4937 | -120.5004 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0127063 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1881345 | 0 | Non-EPSS | N | 2023 | B- C
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | 5983 | 20231011 | 1348 | 20231011 | 1401 | 2241035 | 13 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 13 | 37.9741 | -120.3774 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0127075 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881352 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | RECLOSER | 90340 | 20231011 | 1446 | 20231011 | 1826 | 2241118 | 220 | Distribution Circuit | 3rd Party | Vehicle | 306 | 67320 | 37.281 | -120.4874 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0127148 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1881374 | 0 | Non-EPSS | N | 2023 | B AND C
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 59596 | 20231011 | 1946 | 20231011 | 2334 | 2241307 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 657 | 149796 | 37.9009 | -120.5804 | No | Clear;32-90 F |  |  | 23-0127256 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1881403 | 0 | EPSS Ckt | Y | 2023 | B & C
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | TRANSFORMER | 319762819413 | 20231011 | 2016 | 20231012 | 36 | 2241314 | 260 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 520 | 37.0333 | -120.5814 | No | Clear;32-90 F | Other | Failed/Faulted | 23-0127270 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881413 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | JUMPER | OJ'S 2 N/OF CGC# 318532048840 | 20231011 | 2148 | 20231012 | 245 | 2241321 | 297 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4 | 1188 | 37.8406 | -121.0094 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0127265 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881408 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 10967 | 20231011 | 2333 | 20231011 | 2350 | 2241366 | 17 | Distribution Circuit | 3rd Party | Metallic Balloon | 49 | 833 | 37.2952 | -120.3792 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0127289 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881427 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1102 | 252091102 | JUMPER | OPEN JUPMERS 1 POLE E/OF CGC#318859520473 | 20231012 | 1133 | 20231012 | 1715 | 2241800 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1710 | 37.0615 | -120.8904 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0127490 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881636 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 8519 | 20231012 | 1157 | 20231012 | 1457 | 2241821 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 2520 | 37.6889 | -120.3272 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0127513 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881646 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 319773124958 | 20231012 | 1207 | 20231012 | 2110 | 2241838 | 543 | Transformer only | 3rd Party | Vehicle | 1 | 543 | 37.1859 | -120.5789 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0127585 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1881674 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320214020715 | 20231012 | 1410 | 20231012 | 1826 | 2241949 | 256 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 256 | 37.0688 | -120.4276 | No | Clear;32-90 F | Fuse | Broken | 23-0127745 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881711 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 196877 | 20231012 | 1427 | 20231012 | 1723 | 2241960 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 352 | 36.8498 | -120.0007 | No | Clear;32-90 F |  |  | 23-0127731 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881703 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 100000011676 | 20231012 | 1445 | 20231012 | 1509 | 2241980 | 24 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 24 | 36.9988 | -120.8551 | No | Clear;32-90 F |  |  | 23-0127648 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1881691 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 11547 | 20231012 | 1619 | 20231012 | 1818 | 2242060 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2380 | 37.171 | -120.3832 | No | Clear;32-90 F |  |  | 23-0127741 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1881710 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 8763 | 20231012 | 1728 | 20231012 | 1900 | 2242111 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 920 | 37.1786 | -120.5736 | No | Clear;32-90 F |  |  | 23-0127747 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1881713 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 320905819660 | 20231012 | 1902 | 20231012 | 2050 | 2242168 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 324 | 37.0394 | -120.1905 | No | Clear;32-90 F | Fuse | Broken | 23-0127769 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881730 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318747630670 | 20231012 | 1940 | 20231012 | 2047 | 2242177 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 67 | 37.3392 | -120.9329 | No | Clear;32-90 F | Fuse | Broken | 23-0127768 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881729 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIGARDEN-2113 | 254552113 | FUSE | 6559 | 20231013 | 744 | 20231013 | 918 | 2242335 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1128 | 36.8588 | -119.9283 | No | Clear;32-90 F |  |  | 23-0127903 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1881895 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320465515569 | 20231013 | 821 | 20231013 | 1115 | 2242402 | 174 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 174 | 36.9289 | -120.3414 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0128001 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881945 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | FUSE | 21588 | 20231013 | 835 | 20231013 | 1215 | 2242423 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2420 | 37.3254 | -121.0322 | No | Clear;32-90 F |  |  | 23-0127944 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1881917 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | FUSE | 6815 | 20231013 | 933 | 20231013 | 1022 | 2242539 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 131 | 36.9382 | -120.2301 | No | Partly Cloudy;32-90 F |  |  | 23-0127975 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1881938 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 322055816749 | 20231013 | 1458 | 20231013 | 1557 | 2242820 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 177 | 36.9577 | -119.7984 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0128122 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881992 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | FUSE | 6815 | 20231013 | 1502 | 20231013 | 1609 | 2242832 | 67 | Distribution Circuit | Animal | Bird found | 4 | 268 | 36.9382 | -120.2301 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0128155 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882001 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | JUMPER | .5 SPAN S/OF CGC# 320495443184 | 20231013 | 1527 | 20231013 | 2117 | 2242831 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 5250 | 37.6881 | -120.3274 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0128129 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881995 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 24108 | 20231013 | 1532 | 20231013 | 1711 | 2242837 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 297 | 37.3407 | -120.4323 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0128138 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881996 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | JUMPER | OJ'S 2 POLES S/OF CGC# 318772730325 | 20231013 | 2247 | 20231014 | 540 | 2243049 | 413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1239 | 37.3284 | -120.924 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0128196 | OH | Sus | 35498126 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882049 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 667248 | 20231014 | 120 | 20231014 | 1235 | 2243075 | 675 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2845 | 1734317 | 38.049 | -120.2357 | No | Partly Cloudy;32-90 F |  |  | 23-0128243 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882054 | 0 | EPSS Ckt | Y | 2023 | SGF
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20231014 | 720 | 20231014 | 844 | 2243163 | 84 | Distribution Circuit | Animal | Bird found | 687 | 57708 | 37.9574 | -120.3132 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0128252 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882069 | 0 | EPSS Ckt | Y | 2023 | B PH
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 10940 | 20231014 | 745 | 20231014 | 1019 | 2243172 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 635 | 72248 | 37.9883 | -120.2832 | No | Partly Cloudy;32-90 F |  |  | 23-0128255 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882076 | 0 | EPSS Ckt | Y | 2023 | AB
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRANSFORMER | 320586022569 | 20231014 | 826 | 20231014 | 1010 | 2243213 | 104 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 208 | 37.12 | -120.2998 | No | Partly Cloudy;32-90 F |  |  | 23-0128270 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882158 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | TRANSFORMER | 319051045966 | 20231014 | 1622 | 20231014 | 1721 | 2243485 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 354 | 37.762 | -120.8297 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0128340 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882198 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | SWITCH | 4344 | 20231014 | 1631 | 20231014 | 2121 | 2243492 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1416 | 410640 | 37.5242 | -120.3119 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0128338 | OH | Sus | 35498133 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882197 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | TRANSFORMER | 100000083973 | 20231014 | 1820 | 20231014 | 2015 | 2243529 | 115 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 345 | 37.0766 | -120.9805 | No | Clear;32-90 F |  |  | 23-0128362 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882213 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | FUSE | 23156 | 20231014 | 1838 | 20231014 | 2040 | 2243530 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 366 | 36.8217 | -120.5036 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0128348 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882202 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 7707 | 20231014 | 1908 | 20231014 | 2026 | 2243538 | 78 | Distribution Circuit | Animal | Bird found | 5 | 416 | 37.2731 | -120.2873 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128358 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882210 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 2076 | 20231015 | 656 | 20231015 | 830 | 2243638 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 251 | 37.1784 | -120.2741 | No | Clear;32-90 F |  |  | 23-0128402 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882251 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | RECLOSER | 3830 | 20231015 | 722 | 20231015 | 1923 | 2243644 | 721 | Distribution Circuit | 3rd Party | Vehicle | 389 | 71943 | 36.8655 | -120.4719 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0128403 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1882252 | 0 | Non-EPSS | N | 2023 | A-B-C
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRANSFORMER | 320638421971 | 20231015 | 730 | 20231015 | 1515 | s1882279 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1395 | 37.1037 | -120.2816 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0128407 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882279 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | S1949 | 20231015 | 743 | 20231015 | 1016 | 2243670 | 153 | Distribution Circuit | Animal | Bird found | 7 | 1071 | 37.7326 | -120.8895 | No | Partly Cloudy-Fog;32-90 F | Jumper | Burned Open | 23-0128404 | OH | Sus | 46015781 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882253 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | JUMPER | BURNT OJ SS MTR #1010780318 | 20231015 | 858 | 20231015 | 950 | 2243703 | 52 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 1272 | 37.1055 | -120.293 | No | Clear;32-90 F | Jumper | Burned Open | 23-0128407 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Open Circuit | 0 | No | No | No | 1882260 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 5845 | 20231015 | 1116 | 20231015 | 1632 | 2243726 | 316 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1264 | 37.3626 | -121.1038 | No | Clear;32-90 F |  |  | 23-0128437 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882283 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 6868 | 20231015 | 1806 | 20231015 | 1916 | 2243897 | 70 | Distribution Circuit | Animal | Bird found | 18 | 1261 | 36.9614 | -120.0591 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128459 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882296 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | SWITCH | 445811 | 20231015 | 1937 | 20231015 | 1944 | 2243959 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 133 | 931 | 36.8722 | -120.4636 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128403 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1882300 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | JUMPER | BROKEN JUMPER @ 7682 | 20231015 | 2002 | 20231016 | 55 | 2243966 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1465 | 37.3898 | -120.5158 | No | Clear;32-90 F | Jumper | Broken | 23-0128471 | OH | Sus | 46015811 | CENTRAL VALLEY | OCT | Open Circuit | 0 | No | No | No | 1882307 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 76694 | 20231015 | 2141 | 20231016 | 258 | 2243987 | 317 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 10461 | 37.7405 | -120.1279 | No | Clear;32-90 F |  |  | 23-0128472 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882308 | 0 | EPSS Ckt | Y | 2023 | C & GRD
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20231015 | 2222 | 20231015 | 2327 | 2243992 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 261 | 16965 | 37.0552 | -120.0295 | No | Clear;32-90 F |  |  | 23-0128491 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882323 | 0 | EPSS Ckt | N | 2023 | B & C
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320602254702 | 20231016 | 648 | 20231016 | 1017 | 2244061 | 209 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 418 | 38.0019 | -120.2923 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0128518 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882346 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | FUSE | 2898 | 20231016 | 704 | 20231016 | 925 | 2244090 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 97 | 13731 | 36.9435 | -120.0558 | No | Clear;32-90 F |  |  | 23-0128543 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882376 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | TRANSFORMER | 322687029300 | 20231016 | 1110 | 20231016 | 1652 | 2244471 | 342 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 342 | 37.3013 | -119.5776 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0128813 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882567 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320038228954 | 20231016 | 1450 | 20231016 | 1637 | 2244657 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 642 | 37.296 | -120.4863 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0128792 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882561 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4669 | 20231016 | 1545 | 20231016 | 1656 | 2244788 | 71 | Distribution Circuit | Animal | Bird found | 7 | 497 | 37.1857 | -120.6006 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128875 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882577 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | OJ 2 E/O CGC 320484944112 | 20231016 | 1757 | 20231016 | 2210 | 2244823 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 759 | 37.7143 | -120.3299 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 23-0128881 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882579 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320447455975 | 20231016 | 1949 | 20231017 | 251 | 2244861 | 422 | Transformer only | Environmental/External | Lightning | 1 | 422 | 38.0369 | -120.3456 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0128906 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882596 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | FUSE | 24908 | 20231017 | 646 | 20231017 | 942 | 2244944 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 247 | 43472 | 36.9818 | -120.0527 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0129036 | OH | Sus | 46018196 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882768 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S731 | 20231017 | 747 | 20231017 | 1812 | 2244974 | 624 | Distribution Circuit | Animal | Bird found | 29 | 5514 | 37.8351 | -120.8428 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0129046 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882797 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | FUSE | 793511 | 20231017 | 839 | 20231017 | 1213 | 2245317 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 214 | 37.3315 | -120.5048 | No | Clear;32-90 F |  |  | 23-0129172 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882871 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321322018020 | 20231017 | 1016 | 20231017 | 1059 | 2245264 | 43 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 86 | 36.994 | -120.0482 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0129121 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882849 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 787277 | 20231017 | 1122 | 20231017 | 1159 | 2245330 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 4292 | 37.9599 | -120.4517 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0129127 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882854 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 25892 | 20231017 | 1325 | 20231017 | 1333 | 2245413 | 8 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 8 | 37.1198 | -120.1788 | No | Clear;32-90 F |  |  | 23-0129223 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882904 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 320025423520 | 20231017 | 1401 | 20231017 | 1635 | 2245517 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 462 | 37.1459 | -120.492 | No | Clear;32-90 F | Secondary | Normal | 23-0129250 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882915 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 870965 | 20231017 | 1552 | 20231017 | 2101 | 2245593 | 309 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 309 | 37.4283 | -120.5759 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0129322 | OH | Sus | 46022499 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1882929 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | JUMPER | WIRE DOWN | 20231017 | 2005 | 20231017 | 2305 | 2245698 | 180 | Distribution Circuit | 3rd Party | Vehicle | 558 | 5750 | 37.0602 | -120.7076 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0129350 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Open Circuit | 0 | No | Yes | Yes | 1882938 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | JUMPER | OJ'S 1 W/ OF MTR# 1003778151 | 20231017 | 2016 | 20231017 | 2155 | 2245702 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 198 | 37.7955 | -120.9599 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0129344 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1882935 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | OCB | 1704/2 | 20231018 | 824 | 20231018 | 1613 | 2245908 | 469 | Distribution Circuit | 3rd Party | Vehicle | 463 | 56428 | 37.8561 | -120.9446 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0129458 | OH | Sus | 35503504 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | No | No | 1883020 | 0 | Non-EPSS | N | 2023 | A-B-C
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320547513859 | 20231018 | 825 | 20231018 | 1420 | 2245893 | 355 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 355 | 36.8804 | -120.3138 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0129591 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883165 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 14523 | 20231018 | 1117 | 20231018 | 1155 | 2246148 | 38 | Distribution Circuit | 3rd Party | Vehicle | 94 | 3572 | 36.8545 | -120.4527 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0129664 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1883183 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7549 | 20231018 | 1128 | 20231018 | 1527 | 2246067 | 239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1195 | 37.3003 | -120.8525 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0129599 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1883170 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 416250153175 | 20231018 | 1520 | 20231018 | 1702 | 2246319 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 102 | 36.7863 | -120.2822 | No | Clear;32-90 F | Fuse | Broken | 23-0129832 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883226 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320113422309 | 20231018 | 1627 | 20231018 | 1655 | 2246369 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 37.1129 | -120.4612 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0129812 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1883223 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319408048080 | 20231018 | 1805 | 20231018 | 1909 | 2246444 | 64 | Transformer only | Vegetation | Tree - grew into line | 1 | 64 | 37.8204 | -120.7055 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0129860 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1883233 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 20465 | 20231019 | 645 | 20231019 | 850 | 2246611 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 375 | 37.711 | -120.8534 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0129978 | OH | Sus | 46025765 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | Yes | 1883293 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320449854217 | 20231019 | 811 | 20231019 | 909 | 2246712 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 58 | 37.9888 | -120.3447 | No | Clear;32-90 F | Fuse | Broken | 23-0130043 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883336 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 9900 | 20231019 | 1009 | 20231019 | 1420 | 2246818 | 251 | Distribution Circuit | 3rd Party | Vehicle | 69 | 4195 | 37.5361 | -121.222 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0130099 | OH | Sus | 31673467 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1883353 | 0 | EPSS Ckt | N | 2023 | A-B-C
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | FUSE | 9673 | 20231019 | 1300 | 20231019 | 1420 | 2246954 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1120 | 36.8821 | -120.7217 | No | Clear;32-90 F |  |  | 23-0130270 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1883405 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321461512825 | 20231019 | 1344 | 20231019 | 1901 | 2247116 | 317 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 317 | 36.8509 | -120.0011 | No | Clear;32-90 F | Fuse | Broken | 23-0130372 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883437 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 321023549315 | 20231019 | 1608 | 20231019 | 1910 | 2246957 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 182 | 37.8535 | -120.1454 | No | Clear;32-90 F |  |  | 23-0130352 | OH | Sus | 31673472 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883428 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRANSFORMER | 320558622664 | 20231019 | 1628 | 20231019 | 1814 | 2247102 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 106 | 37.1219 | -120.3093 | No | Clear;32-90 F | Fuse | Broken | 23-0130362 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883432 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 20007 | 20231019 | 1751 | 20231019 | 1922 | 2247133 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1092 | 37.7623 | -120.9502 | No | Clear;32-90 F |  |  | 23-0130365 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1883434 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | TRANSFORMER | T653183 | 20231019 | 1931 | 20231020 | 339 | 2247183 | 488 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 8423 | 36.9217 | -119.8091 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0130383 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883446 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 20007 | 20231020 | 151 | 20231020 | 328 | 2247267 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1164 | 37.7623 | -120.9502 | No | Clear;32-90 F |  |  | 23-0130427 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1883477 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 10864 | 20231020 | 758 | 20231020 | 1140 | 2247317 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 17094 | 37.2807 | -120.4437 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0130496 | OH | Sus | 46026950 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1883529 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | S2093 | 20231020 | 1832 | 20231021 | 18 | 2247872 | 346 | Distribution Circuit | 3rd Party | Vehicle | 27 | 3414 | 37.7839 | -120.936 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0130806 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1883722 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | TRANSFORMER | 318912723475 | 20231020 | 2007 | 20231020 | 2345 | 2247910 | 218 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 436 | 37.1438 | -120.8735 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0130814 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883724 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 24335 | 20231020 | 2117 | 20231020 | 2228 | 2247921 | 71 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 663 | 37.091 | -120.2745 | No | Clear;32-90 F |  |  | 23-0130835 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883744 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 8000 | 20231021 | 748 | 20231021 | 1115 | 2248029 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1152 | 234852 | 38.0083 | -120.301 | No | Partly Cloudy;32-90 F |  |  | 23-0130856 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883772 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | FUSE | 863883 | 20231021 | 1412 | 20231021 | 1519 | 2248343 | 67 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 89 | 36.9653 | -120.1085 | No | Clear;32-90 F |  |  | 23-0130933 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883897 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 2101 | 20231021 | 1458 | 20231021 | 1615 | 2248367 | 77 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 154 | 37.1641 | -120.1385 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0130926 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1883894 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | FUSE | 9803 | 20231021 | 1844 | 20231021 | 2056 | 2248458 | 132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 660 | 36.8217 | -120.4103 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0130948 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1883911 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319166445965 | 20231022 | 648 | 20231022 | 1122 | 2248746 | 274 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 274 | 37.7619 | -120.7893 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0131005 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1883974 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319675930905 | 20231022 | 704 | 20231022 | 836 | 2248744 | 92 | Transformer only | 3rd Party | Vehicle | 1 | 92 | 37.349 | -120.6124 | No | Fog;32-90 F | Anchor or Guy | Broken | 23-0130998 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1883967 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319708729139 | 20231022 | 1534 | 20231022 | 1947 | 2249138 | 253 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 506 | 37.2998 | -120.6012 | No | Clear;32-90 F | Fuse | Broken | 23-0131088 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884051 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319351048070 | 20231022 | 1534 | 20231022 | 1629 | 2249020 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 110 | 37.8201 | -120.7258 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0131052 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1884020 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319401520640 | 20231022 | 1555 | 20231022 | 1955 | 2249057 | 240 | Transformer only | Environmental/External | Fire- Forest/Grass | 1 | 240 | 37.0654 | -120.7067 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0131062 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884029 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | TRANSFORMER | 321266519027 | 20231022 | 1821 | 20231022 | 1945 | 2249121 | 84 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 168 | 37.0219 | -120.0674 | No | Overcast-Drizzle;32-90 F |  |  | 23-0131087 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884050 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | OCB | 1704/2 | 20231022 | 2055 | 20231022 | 2249 | 2249276 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3217 | 345246 | 37.9035 | -120.4971 | No | Overcast;32-90 F |  |  | 23-0131096 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Multi-Fault | 0 | No | No | No | 1884056 | 0 | EPSS Ckt | Y | 2023 | B C GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 67898 | 20231022 | 2056 | 20231022 | 2118 | 2249285 | 22 | Distribution Circuit | Company Initiated | Coordination failure | 1079 | 23738 | 37.9584 | -120.4387 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0131098 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884058 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 67898 | 20231022 | 2128 | 20231023 | 417 | 2249332 | 409 | Distribution Circuit | Company Initiated | Coordination failure | 1079 | 376295 | 37.9584 | -120.4387 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0131101 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884062 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 13377 | 20231022 | 2316 | 20231023 | 21 | 2249369 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 130 | 37.4272 | -120.6487 | No | Overcast-Fog;32-90 F |  |  | 23-0131127 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884086 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 768534 | 20231023 | 648 | 20231023 | 743 | 2249474 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 165 | 37.8867 | -120.925 | No | Overcast-Fog;32-90 F |  |  | 23-0131157 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884116 | 0 | EPSS Ckt | N | 2023 | B- VOLTAGE
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | OTHER | WIRE DOWN 1SP W/O CGC# 319684430742 | 20231023 | 802 | 20231023 | 1436 | 2249537 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 1258 | 37.3437 | -120.6098 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0131199 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Open Circuit | 0 | No | Yes | Yes | 1884177 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | TRANSFORMER | 320447924840 | 20231023 | 1417 | 20231024 | 849 | 2250046 | 1112 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1112 | 37.1828 | -120.3473 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0131446 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884357 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320482854573 | 20231023 | 1437 | 20231023 | 1541 | 2250058 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 384 | 37.9987 | -120.3327 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0131445 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1884356 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320440744543 | 20231023 | 1736 | 20231023 | 2358 | 2250152 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 382 | 37.7254 | -120.347 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0131560 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1884382 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 4669 | 20231023 | 1745 | 20231023 | 1952 | 2250165 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 593 | 37.1857 | -120.6006 | No | Clear;32-90 F |  |  | 23-0131572 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884387 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | TRANSFORMER | 319686219646 | 20231023 | 1928 | 20231024 | 55 | 2250206 | 327 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 654 | 37.0396 | -120.608 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0131616 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884421 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 4914 | 20231023 | 1947 | 20231023 | 2109 | 2250210 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 3198 | 37.3749 | -120.7606 | No | Clear;32-90 F |  |  | 23-0131582 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1884393 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319240631888 | 20231023 | 1947 | 20231024 | 305 | 2250229 | 438 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1314 | 37.3749 | -120.7623 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0131583 | OH | Sus | 31673904 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1884394 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1102 | 252091102 | OCB | 1102/2 | 20231024 | 729 | 20231024 | 1700 | 2250368 | 571 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 1901 | 70301 | 37.0663 | -120.8359 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0131648 | OH | Sus | 31673961 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1884446 | 0 | Non-EPSS | N | 2023 | B- GRD
YOSEMITE | STANISLAUS | STANISLAUS-1701 | 162821701 | SWITCH | L6223 | 20231024 | 835 | 20231024 | 1640 | 2250408 | 485 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 485 | 38.1453 | -120.3796 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0131666 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1884470 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1104 | 253401104 | TRANSFORMER | 415585151914 | 20231024 | 935 | 20231024 | 1200 | 2250617 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 145 | 36.7498 | -120.5074 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0131839 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884648 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 23522 | 20231024 | 1117 | 20231024 | 1242 | 2250789 | 85 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 170 | 36.8613 | -119.8475 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0131867 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884658 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | TRANSFORMER | 415640651613 | 20231024 | 1828 | 20231025 | 200 | 2250937 | 452 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 452 | 36.7415 | -120.4891 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0132054 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884700 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | JUMPER | OJ 1 POLE S/OF CGC 318492929065 | 20231024 | 1954 | 20231024 | 2051 | 2251019 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 171 | 37.2966 | -121.0189 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0132066 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1884706 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 21139 | 20231025 | 314 | 20231025 | 1058 | 2251107 | 464 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1856 | 37.7546 | -120.8401 | No | Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0132117 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1884740 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 3927 | 20231025 | 502 | 20231025 | 835 | 2251116 | 213 | Distribution Circuit | 3rd Party | Vehicle | 25 | 5325 | 37.1587 | -121.0096 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0132126 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1884746 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 25024 | 20231025 | 758 | 20231025 | 1224 | 2251186 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 532 | 37.3386 | -120.7926 | No | Clear;32-90 F | Jumper | Broken | 23-0132219 | OH | Sus | 46031031 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1884846 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 67898 | 20231025 | 921 | 20231025 | 934 | 2251379 | 13 | Distribution Circuit | Company Initiated | Personnel- company | 901 | 11713 | 37.9584 | -120.4387 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0132243 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1884892 | 0 | EPSS Ckt | N | 2023 | SGF & DCD
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 57760 | 20231025 | 1222 | 20231025 | 1315 | 2251620 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 53 | 37.318 | -120.3971 | No | Clear;32-90 F |  |  | 23-0132407 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1884986 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 12315 | 20231025 | 1249 | 20231025 | 1500 | 2251627 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 262 | 36.8798 | -120.2303 | No | Clear;32-90 F |  |  | 23-0132512 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885018 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 9648 | 20231025 | 1925 | 20231025 | 2250 | 2251882 | 205 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1435 | 36.7753 | -120.2882 | No | Partly Cloudy;32-90 F |  |  | 23-0132657 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885080 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1102 | 252091102 | TRANSFORMER | T1993 | 20231026 | 414 | 20231026 | 505 | 2251891 | 51 | Transformer only | Equipment Failure/Involved | Underground | 11 | 561 | 37.0762 | -120.8408 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0132668 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885081 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 169700 | 20231026 | 659 | 20231026 | 1117 | 2252111 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1506 | 388548 | 37.8364 | -120.2605 | No | Clear-Drizzle;32-90 F |  |  | 23-0132696 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885102 | 0 | EPSS Ckt | Y | 2023 | A- C- INST
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 319810522946 | 20231026 | 846 | 20231026 | 940 | 2252247 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 54 | 37.1303 | -120.5662 | No | Clear;32-90 F | Fuse | Broken | 23-0132779 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885275 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 9470 | 20231026 | 923 | 20231026 | 1309 | 2252342 | 226 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 665 | 98958 | 37.6459 | -120.3113 | No | Partly Cloudy;32-90 F |  |  | 23-0132772 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885261 | 0 | EPSS Ckt | Y | 2023 | A&B
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 763481 | 20231026 | 943 | 20231026 | 1041 | 2252379 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 58 | 37.2443 | -120.7789 | No | Clear;32-90 F |  |  | 23-0132814 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885305 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7952 | 20231026 | 1231 | 20231026 | 1354 | 2252530 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1577 | 37.2665 | -120.6704 | No | Clear;32-90 F |  |  | 23-0132935 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885366 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321284060352 | 20231026 | 1322 | 20231026 | 1718 | 2252580 | 236 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 708 | 38.1564 | -120.0542 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0132932 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885364 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | RECLOSER | 11680 | 20231027 | 304 | 20231027 | 838 | 2252932 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 556 | 105204 | 37.0982 | -120.2011 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0133060 | OH | Sus | 31674252 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1885441 | 0 | Non-EPSS | N | 2023 | C & GRD
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | FUSE | 37440 | 20231027 | 1028 | 20231027 | 1523 | 2253267 | 295 | Distribution Circuit | 3rd Party | Vehicle | 7 | 2065 | 36.9933 | -120.3555 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0133260 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885656 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | S1333 | 20231027 | 1456 | 20231028 | 1351 | 2253515 | 1375 | Distribution Circuit | Equipment Failure/Involved | Underground | 112 | 67219 | 37.3059 | -121.0311 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0133420 | UG | Sus | 35508101 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885705 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | 319679132551 | 20231027 | 1508 | 20231027 | 1935 | 2253524 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3500 | 37.3941 | -120.6111 | No | Clear;32-90 F | Secondary | Broken | 23-0133387 | OH | Sus | 31674360 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1885694 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321838118060 | 20231028 | 720 | 20231028 | 1353 | 2253908 | 393 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 786 | 36.9946 | -119.8719 | No | Clear;32-90 F | Secondary | Broken | 23-0133477 | OH | Sus | 31674363 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1885758 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | TRANSFORMER | 321341717344 | 20231028 | 949 | 20231028 | 1210 | 2254151 | 141 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 282 | 36.9751 | -120.0417 | No | Clear;32-90 F |  |  | 23-0133526 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1885846 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6648 | 20231028 | 958 | 20231028 | 1118 | 2254157 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 80 | 37.0326 | -120.0292 | No | Clear;32-90 F |  |  | 23-0133531 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885849 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | S1333 | 20231028 | 1424 | 20231029 | 416 | 2254343 | 832 | Distribution Circuit | Equipment Failure/Involved | Underground | 112 | 31636 | 37.3059 | -121.0311 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0133574 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885878 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 6623 | 20231028 | 1850 | 20231028 | 2047 | 2254460 | 117 | Distribution Circuit | Animal | Other | 21 | 2457 | 37.0311 | -120.3648 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0133611 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885899 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 180075 | 20231028 | 1943 | 20231028 | 2357 | 2254469 | 251 | Distribution Circuit | 3rd Party | Vehicle | 6 | 1496 | 36.8515 | -120.0282 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0133608 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1885896 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 950599 | 20231028 | 2054 | 20231028 | 2244 | 2254501 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 880 | 37.3137 | -120.3514 | No | Clear;32-90 F |  |  | 23-0133616 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885901 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 3844 | 20231029 | 1002 | 20231029 | 1300 | 2254777 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1187 | 36.8916 | -120.6724 | No | Clear;32-90 F |  |  | 23-0133706 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885993 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | OCB | 1701/2 | 20231029 | 1841 | 20231029 | 2317 | 2255109 | 276 | Distribution Circuit | Animal | Bird found | 2488 | 662833 | 37.7729 | -120.8261 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0133736 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1886030 | 0 | EPSS Ckt | N | 2023 | A- B- TIME OC
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 2844 | 20231029 | 1902 | 20231029 | 1948 | 2255113 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 138 | 37.3041 | -120.4984 | No | Clear;32-90 F | Jumper | Burned Open | 23-0133743 | OH | Sus | 46033698 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886035 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | TRANSFORMER | 321249012680 | 20231030 | 753 | 20231030 | 1029 | 2255270 | 156 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 156 | 36.8483 | -120.0742 | No | Clear;32-90 F | Fuse | Broken | 23-0133909 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886227 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 953336 | 20231030 | 830 | 20231030 | 1159 | 2255304 | 209 | Distribution Circuit | Company Initiated | Personnel- company | 887 | 185383 | 38.0678 | -120.1869 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0133821 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886104 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 953336 | 20231030 | 1305 | 20231030 | 1405 | 2255810 | 60 | Distribution Circuit | Company Initiated | Personnel- company | 887 | 53220 | 38.0678 | -120.1869 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0134043 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886281 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | TRANSFORMER | 319175614095 | 20231030 | 1416 | 20231101 | 853 | 2255932 | 2557 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 5114 | 36.8869 | -120.7839 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0134091 | OH | Sus | 46037543 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886309 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | JUMPER | OPEN JUMPERS @ CGC 319953936149 | 20231030 | 1610 | 20231030 | 1926 | 2255970 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2156 | 37.4932 | -120.517 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0134087 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1886305 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 493157 | 20231030 | 2127 | 20231030 | 2350 | 2256153 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 572 | 37.4975 | -120.491 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0134159 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1886344 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | TRANSFORMER | 415295955671 | 20231031 | 429 | 20231031 | 1000 | 2256265 | 331 | Transformer only | 3rd Party | Vehicle | 1 | 331 | 36.8506 | -120.6091 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0134198 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886371 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 3816 | 20231031 | 544 | 20231031 | 1349 | 2256301 | 485 | Distribution Circuit | 3rd Party | Vehicle | 11 | 5335 | 37.0543 | -120.7261 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0134217 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | No | No | 1886378 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318897029730 | 20231031 | 742 | 20231031 | 853 | 2256318 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 213 | 37.3137 | -120.8806 | No | Clear;32-90 F | Fuse | Broken | 23-0134245 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1886464 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 8817 | 20231031 | 903 | 20231031 | 1652 | 2256459 | 469 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 2345 | 37.1859 | -120.548 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0134250 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1886495 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 6413 | 20231031 | 1031 | 20231031 | 1105 | 2256579 | 34 | Distribution Circuit | Animal | Bird found | 4 | 136 | 37.7401 | -120.8022 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0134287 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1886567 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 19108 | 20231101 | 44 | 20231101 | 618 | 2257006 | 334 | Distribution Circuit | 3rd Party | Vehicle | 35 | 11678 | 37.3352 | -120.5772 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0134486 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | Yes | 1886686 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320283419923 | 20231101 | 318 | 20231101 | 1032 | 2257473 | 434 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 868 | 37.0471 | -120.4039 | No | Clear;32-90 F | Secondary | Broken | 23-0134633 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1886899 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 23875 | 20231101 | 558 | 20231101 | 1644 | 2257028 | 646 | Distribution Circuit | Equipment Failure/Involved | Underground | 155 | 33601 | 37.7744 | -120.8459 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0134506 | UG | Sus | 46043888 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1886698 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | TRANSFORMER | 414835254094 | 20231101 | 1139 | 20231101 | 1154 | 2257499 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 15 | 36.8047 | -120.7655 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0134723 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1886936 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 20231101 | 1141 | 20231101 | 1650 | s1887175 | 309 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 722 | 220183 | 38.0064 | -120.3467 | No | Clear;32-90 F |  |  | 23-0126234 | OH | Sus | 31662048 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | Yes | No | No | 1887175 | 0 | EPSS Ckt | Y | 2023 | A/B/C
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 434305 | 20231101 | 1441 | 20231102 | 542 | 2257700 | 901 | Distribution Circuit | 3rd Party | Vehicle | 1032 | 119047 | 37.5603 | -121.1785 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0134803 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1886953 | 0 | EPSS Ckt | N | 2023 | ABC
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320342424435 | 20231101 | 1523 | 20231101 | 1603 | 2257716 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 40 | 37.1719 | -120.3833 | No | Clear;32-90 F | Fuse | Broken | 23-0134864 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1886959 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | RECLOSER | 3290 | 20231101 | 1724 | 20231102 | 12 | 2257821 | 408 | Distribution Circuit | Animal | Other | 348 | 18974 | 37.7466 | -120.8398 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0134918 | OH | Sus | 31675044 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1886970 | 0 | Non-EPSS | N | 2023 | GRD
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319247731723 | 20231102 | 248 | 20231102 | 349 | 2257939 | 61 | Transformer only | Unknown Cause | Patrol - not conducted | 6 | 366 | 37.3703 | -120.7598 | No | Clear;32-90 F |  |  | 23-0134966 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887011 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | TRANSFORMER | 322006521475 | 20231102 | 559 | 20231102 | 1048 | 2257957 | 289 | Transformer only | Animal | Other | 1 | 289 | 37.0874 | -119.8123 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0135005 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887037 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 4593 | 20231102 | 710 | 20231102 | 841 | 2257986 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1365 | 37.2289 | -120.4609 | No | Clear;32-90 F |  |  | 23-0135047 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1887101 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 27265 | 20231102 | 757 | 20231102 | 1350 | 2258011 | 353 | Distribution Circuit | 3rd Party | Other | 1 | 353 | 37.7668 | -121.0696 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0135037 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1887074 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322121935418 | 20231102 | 854 | 20231102 | 1130 | 2258112 | 156 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 312 | 37.4694 | -119.77 | No | Partly Cloudy;32-90 F | Service conductor | Normal | 23-0135051 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887108 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | JUMPER | OJ @ AVE 23 1/2 & RD 23 1/2 TWD EAST | 20231102 | 1225 | 20231102 | 1441 | 2258407 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 136 | 37.134 | -120.1198 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0135232 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1887247 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318766344976 | 20231102 | 1326 | 20231102 | 1457 | 2258464 | 91 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 728 | 37.7345 | -120.9274 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0135263 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1887258 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319721030725 | 20231102 | 1845 | 20231102 | 2323 | 2258682 | 278 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1946 | 37.3441 | -120.5968 | No | Partly Cloudy;32-90 F | Transformer (OH) | Arcing | 23-0135392 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1887301 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | FUSE | 1995 | 20231103 | 311 | 20231103 | 434 | 2258734 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 388 | 37.0034 | -120.3101 | No | Partly Cloudy;32-90 F |  |  | 23-0135429 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887338 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 7839 | 20231103 | 708 | 20231103 | 820 | 2258783 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 360 | 37.3097 | -120.4547 | No | Clear;32-90 F |  |  | 23-0135456 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1887353 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 9649 | 20231103 | 916 | 20231103 | 1206 | 2259169 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 227 | 36.7752 | -120.2833 | No | Clear;32-90 F |  |  | 23-0135625 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887563 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | TRIP-SAVER | 66907 | 20231103 | 1117 | 20231103 | 1500 | 2259112 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 3568 | 37.0977 | -120.0656 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0135597 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1887544 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321820936833 | 20231103 | 1134 | 20231103 | 1432 | 2259153 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 178 | 37.5095 | -119.8728 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0135623 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1887559 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | TRANSFORMER | 319022520734 | 20231103 | 1140 | 20231103 | 1907 | 2259168 | 447 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4470 | 37.0688 | -120.8357 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0135629 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887567 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318368047245 | 20231103 | 1303 | 20231103 | 1625 | 2259231 | 202 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 202 | 37.7962 | -121.0657 | No | Clear;32-90 F | Fuse | Broken | 23-0135764 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887622 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | TRANSFORMER | 318945746118 | 20231103 | 1501 | 20231103 | 2212 | 2259360 | 431 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 431 | 37.7659 | -120.8658 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0135773 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887629 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | FUSE | 21074 | 20231103 | 1702 | 20231103 | 1823 | 2259452 | 81 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 2997 | 37.297 | -120.4578 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0135767 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1887623 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | RECLOSER | 90340 | 20231103 | 1920 | 20231104 | 133 | 2259536 | 373 | Distribution Circuit | 3rd Party | Vehicle | 306 | 114138 | 37.281 | -120.4874 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0135796 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1887639 | 0 | Non-EPSS | N | 2023 | B PH & GRD
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1723 | 20231103 | 1944 | 20231103 | 2315 | 2259506 | 211 | Distribution Circuit | Company Initiated | Personnel- company | 3084 | 171204 | 37.9316 | -120.3365 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0135801 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1887641 | 0 | EPSS Ckt | Y | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 1960 | 20231104 | 336 | 20231104 | 537 | 2259661 | 121 | Distribution Circuit | Animal | Other | 959 | 100240 | 37.4587 | -119.9001 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0135837 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887672 | 0 | EPSS Ckt | Y | 2023 | B PH & GRD
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 922075 | 20231104 | 711 | 20231104 | 853 | 2259702 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 204 | 36.7946 | -120.3261 | No | Partly Cloudy;32-90 F |  |  | 23-0135866 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1887734 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321889631296 | 20231104 | 857 | 20231104 | 1314 | 2259834 | 257 | Transformer only | Animal | Other | 2 | 514 | 37.3595 | -119.8512 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0135886 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887770 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319803529413 | 20231104 | 944 | 20231104 | 1020 | 2259877 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 108 | 37.3081 | -120.5676 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0135879 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887764 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 10880 | 20231104 | 2317 | 20231105 | 132 | 2260276 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 483 | 65205 | 37.4619 | -119.9501 | No | Partly Cloudy;32-90 F |  |  | 23-0135967 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1887843 | 0 | EPSS Ckt | Y | 2023 | AB PH INST
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320342424435 | 20231105 | 922 | 20231105 | 1003 | 2260422 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 37.1719 | -120.3833 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0135995 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887893 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320640655726 | 20231105 | 1253 | 20231105 | 2235 | 2260678 | 582 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1746 | 38.0302 | -120.2783 | No | Overcast;32-90 F | Secondary | Deteriorated | 23-0136037 | UG | Sus | 46048003 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887934 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 22804 | 20231105 | 1729 | 20231105 | 1845 | 2260671 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 76 | 37.8569 | -120.9376 | No | Clear;32-90 F |  |  | 23-0136035 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1887931 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321171543701 | 20231105 | 2029 | 20231106 | 415 | 2260698 | 466 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 932 | 37.7014 | -120.096 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136076 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887959 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | OCB | 1106/2 | 20231106 | 354 | 20231106 | 535 | 2260985 | 101 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 372 | 35995 | 36.8862 | -120.6558 | No | Overcast;32-90 F |  |  | 23-0136100 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887979 | 0 | EPSS Ckt | N | 2023 | A- GRD- OC TIME
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 2076 | 20231106 | 412 | 20231106 | 600 | 2260987 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 288 | 37.1784 | -120.2741 | No | Clear;32-90 F |  |  | 23-0136108 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887987 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 5987 | 20231106 | 427 | 20231106 | 636 | 2260990 | 129 | Distribution Circuit | 3rd Party | Metallic Balloon | 13 | 1677 | 37.0544 | -120.2878 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0136115 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1887998 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 182315 | 20231106 | 450 | 20231106 | 810 | 2260996 | 200 | Distribution Circuit | Animal | Other | 8 | 1601 | 37.3307 | -120.2882 | No | Overcast;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0136109 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887988 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 628263 | 20231106 | 646 | 20231106 | 858 | 2261054 | 132 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 13 | 1716 | 37.1858 | -120.4877 | No | Overcast;32-90 F | Pole-Wood | Normal | 23-0136114 | OH | Sus | 46048009 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1887995 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | MTR#1004519497 | 20231106 | 718 | 20231106 | 1158 | 2261076 | 280 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 280 | 37.2992 | -120.5178 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136140 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888036 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319512822526 | 20231106 | 819 | 20231106 | 833 | 2261096 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 14 | 37.1187 | -120.6679 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0136152 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888049 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | RECLOSER | 11730 | 20231106 | 946 | 20231106 | 1313 | 2261299 | 207 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 280 | 14868 | 36.9382 | -120.0546 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0136192 | OH | Sus | 31675386 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1888150 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10170 | 20231106 | 951 | 20231106 | 1022 | 2261397 | 31 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 181 | 5611 | 37.5163 | -119.835 | No | Partly Cloudy;32-90 F |  |  | 23-0136198 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1888153 | 0 | EPSS Ckt | Y | 2023 | A&C
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 75413 | 20231106 | 951 | 20231106 | 1147 | 2261480 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 3132 | 37.5797 | -119.8523 | No | Partly Cloudy;32-90 F |  |  | 23-0136239 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1888176 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320505242360 | 20231106 | 1030 | 20231106 | 1050 | 2261458 | 20 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 60 | 37.6646 | -120.3254 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0136227 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1888171 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320191820186 | 20231106 | 1213 | 20231106 | 1321 | 2261674 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 68 | 37.0544 | -120.4351 | No | Overcast;32-90 F | Fuse | Broken | 23-0136330 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888227 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | RECLOSER | 3144 | 20231106 | 1231 | 20231106 | 1247 | 2261693 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 139 | 2224 | 37.9906 | -120.3839 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0136291 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888208 | 0 | EPSS Ckt | N | 2023 | A & GRD
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318863048140 | 20231106 | 1312 | 20231106 | 1342 | 2261734 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 60 | 37.8213 | -120.8946 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0136321 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1888222 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | FUSE | 10988 | 20231106 | 1410 | 20231106 | 1616 | 2261780 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 7304 | 37.2978 | -120.4672 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0136352 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1888235 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | OCB | 1106/2 | 20231106 | 1726 | 20231106 | 1824 | 2261974 | 58 | Distribution Circuit | Animal | Other | 372 | 21576 | 36.8862 | -120.6558 | No | Partly Cloudy;32-90 F | Regulator | Failed/Faulted | 23-0136453 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | No | No | 1888266 | 0 | EPSS Ckt | N | 2023 | A&B GRD TIME OC
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321282260592 | 20231106 | 1954 | 20231107 | 1025 | 2262108 | 871 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 871 | 38.1626 | -120.0547 | No | Overcast-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 23-0136467 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1888301 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20231106 | 1955 | 20231107 | 848 | 2262069 | 773 | Distribution Circuit | Equipment Failure/Involved | Overhead | 688 | 531824 | 38.1888 | -120.0082 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136467 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1888277 | 0 | EPSS Ckt | Y | 2023 | A- C
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 21073 | 20231107 | 336 | 20231107 | 515 | 2262227 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 4653 | 37.1056 | -120.4734 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0136521 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1888336 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 2076 | 20231107 | 704 | 20231107 | 935 | 2262280 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 403 | 37.1784 | -120.2741 | No | Clear;32-90 F | Jumper | Burned/flashed | 23-0136564 | OH | Sus | 46049471 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888354 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 3892 | 20231107 | 1614 | 20231107 | 2055 | 2263070 | 281 | Distribution Circuit | 3rd Party | Vehicle | 8 | 1168 | 36.9834 | -120.8471 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0136872 | OH | Sus | 31675672 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1888643 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 1960 | 20231107 | 1622 | 20231107 | 2353 | 2263101 | 451 | Distribution Circuit | Company Initiated | Personnel- company | 959 | 20310 | 37.4587 | -119.9001 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136854 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888634 | 0 | EPSS Ckt | N | 2023 | C & GRD
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | RECLOSER | 5040 | 20231107 | 1625 | 20231108 | 107 | 2263091 | 522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 535 | 101819 | 36.9264 | -120.1105 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0136856 | OH | Sus | 46049817 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | Yes | No | 1888635 | 0 | Non-EPSS | N | 2023 | B&C & GRD
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 5837 | 20231107 | 1709 | 20231108 | 158 | 2263135 | 529 | Distribution Circuit | 3rd Party | Vehicle | 16 | 8464 | 37.7578 | -121.0649 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0136863 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1888639 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | TRANSFORMER | 415302049478 | 20231108 | 647 | 20231108 | 1738 | 2263324 | 651 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 651 | 36.6817 | -120.6037 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0137082 | OH | Sus | 46050794 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888918 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320863148835 | 20231108 | 1003 | 20231108 | 1602 | 2264376 | 359 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3231 | 37.841 | -120.2024 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0137197 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1888977 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320117022449 | 20231108 | 1013 | 20231108 | 1053 | 2263792 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 40 | 37.117 | -120.4597 | No | Clear;32-90 F | Fuse | Broken | 23-0137066 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888905 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320161829526 | 20231108 | 1140 | 20231108 | 1215 | 2264147 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 35 | 37.3114 | -120.444 | No | Clear;32-90 F | Secondary | Broken | 23-0137096 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1888928 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | JUMPER | COIS @ T14367 TWD T14368 | 20231108 | 1456 | 20231108 | 1555 | 2264405 | 59 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 885 | 36.8408 | -120.4418 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0137000 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1888984 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 8110 | 20231108 | 1543 | 20231108 | 1557 | 2264471 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 400 | 5600 | 37.9862 | -120.2607 | No | Clear;32-90 F | Fuse | Normal | 23-0137236 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888997 | 0 | EPSS Ckt | Y | 2023 | DCD & SGF
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | TRANSFORMER | 415936351986 | 20231109 | 457 | 20231109 | 840 | 2264732 | 223 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 4014 | 36.7544 | -120.3877 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0137396 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889132 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3518 | 20231109 | 535 | 20231109 | 739 | 2264785 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2728 | 36.96 | -120.6581 | No | Clear;32-90 F |  |  | 23-0137361 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1889084 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | TRANSFORMER | 321235012000 | 20231109 | 721 | 20231109 | 1828 | 2264768 | 667 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 667 | 36.8296 | -120.0787 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0137501 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889272 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319312729815 | 20231109 | 928 | 20231109 | 1025 | 2264969 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 114 | 37.318 | -120.7376 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0137416 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1889200 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | JUMPER | 2 SPANS S/O CGC 319042619320 | 20231109 | 1837 | 20231110 | 22 | 2265492 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1725 | 37.0277 | -120.8286 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0137650 | OH | Sus | 31675882 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1889343 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320121328783 | 20231110 | 5 | 20231110 | 144 | 2265683 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 297 | 37.2948 | -120.458 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0137689 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1889388 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321707915742 | 20231110 | 352 | 20231110 | 502 | 2265805 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 140 | 36.9312 | -119.9165 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0137709 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889408 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319712734424 | 20231110 | 1016 | 20231110 | 1320 | 2266150 | 184 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 368 | 37.445 | -120.6 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0137852 | OH | Sus | 31676060 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889578 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | TRANSFORMER | 320097729209 | 20231110 | 1342 | 20231110 | 1722 | 2266303 | 220 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1760 | 37.3027 | -120.4662 | No | Clear;32-90 F | Secondary | Broken | 23-0137929 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1889611 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | MTR#1004902681 | 20231111 | 712 | 20231111 | 900 | 2266575 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 108 | 37.965 | -120.3802 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0138067 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889735 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 3799 | 20231111 | 1507 | 20231111 | 1715 | 2266826 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1281 | 36.7699 | -120.3146 | No | Clear;32-90 F |  |  | 23-0138128 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889779 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7877 | 20231111 | 1515 | 20231111 | 1637 | 2266832 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1367 | 37.3308 | -120.6507 | No | Clear;32-90 F |  |  | 23-0138124 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889777 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 6669 | 20231111 | 2122 | 20231112 | 515 | 2266947 | 473 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1419 | 36.8625 | -119.9108 | No | Clear;32-90 F |  |  | 23-0138167 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889828 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 28537 | 20231112 | 649 | 20231112 | 802 | 2267030 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 292 | 37.1146 | -120.8939 | No | Partly Cloudy;32-90 F |  |  | 23-0138178 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1889841 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 6669 | 20231112 | 1027 | 20231112 | 1616 | 2267115 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 698 | 36.8625 | -119.9108 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0138203 | OH | Sus | 31676074 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889877 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 20821 | 20231112 | 1144 | 20231112 | 2340 | 2267177 | 716 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2572 | 37.8109 | -120.9603 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0138199 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1889873 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 2471 | 20231112 | 1159 | 20231112 | 1330 | 2267181 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2821 | 37.8286 | -120.9124 | No | Clear;32-90 F |  |  | 23-0138204 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1889878 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 6864 | 20231112 | 1741 | 20231112 | 1900 | 2267321 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 790 | 36.8784 | -119.9249 | No | Partly Cloudy;32-90 F |  |  | 23-0138240 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1889911 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | OCB | 1102/2 | 20231112 | 2247 | 20231113 | 736 | 2267383 | 529 | Distribution Circuit | 3rd Party | Vehicle | 1339 | 162262 | 36.7204 | -120.4588 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0138270 | OH | Sus | 35511357 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1889942 | 0 | Non-EPSS | N | 2023 | A- B- C TIME OC
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | FUSE | 1927 | 20231113 | 443 | 20231113 | 617 | 2267406 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 564 | 37.7973 | -121.0703 | No | Clear;32-90 F |  |  | 23-0138279 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1889953 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321409412600 | 20231113 | 811 | 20231113 | 1016 | 2267522 | 125 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 500 | 36.845 | -120.0192 | No | Clear;32-90 F |  |  | 23-0138384 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890141 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | TRANSFORMER | 318369047561 | 20231113 | 1049 | 20231113 | 1540 | 2267807 | 291 | Transformer only | 3rd Party | Vehicle | 1 | 291 | 37.8048 | -121.0654 | No | Clear;32-90 F | Service conductor | Broken | 23-0138431 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890167 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321143614989 | 20231113 | 1433 | 20231113 | 1600 | 2267991 | 87 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 174 | 36.9112 | -120.1102 | No | Clear;32-90 F | Fuse | Burned Open | 23-0138552 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890221 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 25739 | 20231113 | 1517 | 20231113 | 1650 | 2268041 | 93 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 8 | 744 | 37.8167 | -120.8415 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0138551 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890220 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 55798 | 20231113 | 1601 | 20231113 | 1707 | 2268083 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 368 | 19530 | 37.9754 | -120.4464 | No | Partly Cloudy;32-90 F |  |  | 23-0138546 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890217 | 0 | EPSS Ckt | Y | 2023 | B & C INST
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320340022714 | 20231113 | 1626 | 20231113 | 1716 | 2268102 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 50 | 37.1235 | -120.3841 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0138566 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890229 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318428546415 | 20231113 | 1810 | 20231113 | 2212 | 2268351 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 242 | 37.7738 | -121.0446 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0138590 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890247 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | JUMPER | BURNT OJ ON HIGH SIDE OF 1597 C PH | 20231114 | 51 | 20231114 | 1409 | 2268711 | 798 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1288 | 36.9316 | -120.0652 | No | Clear;32-90 F | Jumper | Burned Open | 23-0138759 | OH | Sus | 46058043 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1890432 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 2924 | 20231114 | 726 | 20231114 | 937 | 2268596 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1572 | 37.346 | -120.9329 | No | Clear;32-90 F |  |  | 23-0138778 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890454 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 87551 | 20231114 | 834 | 20231114 | 945 | 2268715 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 142 | 37.0179 | -120.175 | No | Clear;32-90 F |  |  | 23-0138773 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1890448 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 1738 | 20231114 | 2337 | 20231115 | 235 | 2269357 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 594 | 36.9156 | -120.7825 | No | Partly Cloudy;32-90 F |  |  | 23-0139092 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890576 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 9559 | 20231115 | 53 | 20231115 | 424 | 2269397 | 211 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 1548 | 37.1894 | -120.7084 | No | Partly Cloudy;32-90 F |  |  | 23-0139093 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890578 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | OCB | 1102/2 | 20231115 | 503 | 20231115 | 1450 | 2269410 | 587 | Distribution Circuit | 3rd Party | Vehicle | 1339 | 122841 | 36.7204 | -120.4588 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0139094 | OH | Sus | 31676276 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | Yes | No | 1890579 | 0 | Non-EPSS | N | 2023 | A- C- GRD- TIME OC
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320126928917 | 20231115 | 949 | 20231115 | 1016 | 2269587 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 81 | 37.2948 | -120.4561 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 23-0139235 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890754 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320425041862 | 20231115 | 1100 | 20231115 | 1110 | 2269758 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 10 | 37.6501 | -120.3535 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0139245 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890763 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320484041776 | 20231115 | 1304 | 20231115 | 1334 | 2269927 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 30 | 37.6478 | -120.3332 | No | Overcast-Drizzle;32-90 F | Cutout- fuse holder | Broken | 23-0139352 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890811 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319340147705 | 20231115 | 1656 | 20231115 | 1830 | 2270126 | 94 | Transformer only | 3rd Party | Dig in- 3rd party | 1 | 94 | 37.81 | -120.7289 | No | Overcast-Drizzle;32-90 F | Secondary | Broken | 23-0139607 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890890 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 3695 | 20231115 | 1738 | 20231115 | 1850 | 2270352 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 96 | 36.7054 | -120.3868 | No | Overcast-Drizzle;32-90 F | Lightning Arrestor | Broken | 23-0139638 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890911 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 73700 | 20231115 | 1917 | 20231116 | 24 | 2270437 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 921 | 37.3241 | -120.8511 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Arcing | 23-0139644 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1890914 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | RECLOSER | 11370 | 20231115 | 2158 | 20231116 | 218 | 2270483 | 260 | Distribution Circuit | 3rd Party | Other | 1 | 260 | 37.1125 | -120.9433 | No | Partly Cloudy-Drizzle;32-90 F | Bushing | Normal | 23-0139737 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1890963 | 0 | EPSS Ckt | N | 2023 | A GRD
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320406542113 | 20231116 | 855 | 20231116 | 912 | 2270702 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 17 | 37.6572 | -120.3599 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0139800 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891009 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | JUMPER | BURNED OJ 2 S/OF CGC# 320728315693 | 20231116 | 901 | 20231116 | 1305 | 2270626 | 244 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 732 | 36.9302 | -120.2511 | No | Partly Cloudy-Drizzle;32-90 F | Connector or Splice (OH) | Broken | 23-0139810 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1891019 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 28537 | 20231116 | 1002 | 20231116 | 1140 | 2270828 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 392 | 37.1146 | -120.8939 | No | Overcast-Drizzle;32-90 F |  |  | 23-0139916 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891058 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320509541765 | 20231116 | 1046 | 20231116 | 1110 | 2270796 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 24 | 37.6468 | -120.3242 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0139886 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891051 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | TRANSFORMER | 320786324946 | 20231116 | 1114 | 20231116 | 1124 | 2270823 | 10 | Transformer only | Animal | Other | 1 | 10 | 37.1853 | -120.231 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0139910 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891057 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320461544056 | 20231116 | 1242 | 20231116 | 1256 | 2270884 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 14 | 37.7122 | -120.3399 | No | Overcast;32-90 F | Fuse | Broken | 23-0139971 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891075 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319165045322 | 20231116 | 1332 | 20231116 | 1425 | 2270929 | 53 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 53 | 37.7447 | -120.7893 | No | Clear;32-90 F |  |  | 23-0140087 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1891096 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | OCB | 2103/2 | 20231116 | 2221 | 20231117 | 26 | 2271157 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2061 | 181329 | 37.2274 | -119.6906 | No | Partly Cloudy;32-90 F |  |  | 23-0140230 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891147 | 0 | EPSS Ckt | Y | 2023 | GRD/INST
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 10720 | 20231117 | 916 | 20231117 | 1134 | 2271437 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 155 | 21390 | 38.1995 | -120.0203 | No | Overcast;32-90 F |  |  | 23-0140334 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891302 | 0 | EPSS Ckt | Y | 2023 | C- GRD
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320437444262 | 20231117 | 918 | 20231117 | 937 | 2271429 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 76 | 37.7178 | -120.3482 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0140330 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891296 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320475641917 | 20231117 | 1133 | 20231117 | 1143 | 2271508 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 20 | 37.6516 | -120.3357 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0140386 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891326 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 4387 | 20231117 | 2210 | 20231118 | 505 | 2271957 | 415 | Distribution Circuit | 3rd Party | Vehicle | 35 | 14525 | 37.7103 | -120.8666 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 23-0140731 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1891447 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 22772 | 20231118 | 148 | 20231118 | 308 | 2271998 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 3200 | 37.6291 | -120.3084 | No | Clear;32-90 F |  |  | 23-0140744 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891460 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 37282 | 20231118 | 314 | 20231118 | 616 | 2272009 | 182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2127 | 387114 | 37.462 | -119.9483 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140743 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891459 | 0 | EPSS Ckt | Y | 2023 | B GRD
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321512729699 | 20231118 | 314 | 20231118 | 1400 | 2272230 | 646 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 646 | 37.3146 | -119.9801 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140834 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891544 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 11585 | 20231118 | 607 | 20231118 | 811 | 2272052 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 248 | 37.2051 | -120.2708 | No | Clear;32-90 F |  |  | 23-0140826 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891537 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318460029653 | 20231118 | 659 | 20231118 | 819 | 2272073 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 240 | 37.3131 | -121.0305 | No | Overcast-Rain;32-90 F | Fuse | Burned Open | 23-0140801 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891515 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7619 | 20231118 | 802 | 20231118 | 909 | 2272253 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 513 | 37.5364 | -120.6272 | No | Overcast-Drizzle;32-90 F |  |  | 23-0140806 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891522 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | FUSE | 698201 | 20231118 | 827 | 20231118 | 1148 | 2272290 | 201 | Distribution Circuit | Animal | Other | 2 | 402 | 37.387 | -120.4682 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Normal | 23-0140828 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891539 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1102 | 253881102 | FUSE | 24157 | 20231118 | 858 | 20231118 | 1332 | 2272372 | 274 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 274 | 37.3323 | -120.4779 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 23-0140827 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891538 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 2042 | 20231118 | 930 | 20231118 | 1342 | 2272338 | 252 | Distribution Circuit | Animal | Other | 4 | 702 | 36.9164 | -120.3367 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Broken | 23-0140871 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891571 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 2379 | 20231118 | 1010 | 20231118 | 1105 | 2272374 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 293 | 37.8278 | -121.0396 | No | Overcast-Fog;32-90 F | Fuse | Broken | 23-0140845 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891551 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 3948 | 20231118 | 1101 | 20231118 | 1655 | 2272457 | 354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3186 | 37.0709 | -120.9596 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0140872 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891572 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 25738 | 20231118 | 1848 | 20231118 | 2207 | 2273107 | 199 | Distribution Circuit | Environmental/External | Lightning | 9 | 1042 | 37.7005 | -120.6963 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0140984 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891656 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321632935188 | 20231118 | 1949 | 20231119 | 1127 | 2273585 | 938 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 938 | 37.4626 | -119.9375 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0141103 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891773 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | SWITCH | 299321 | 20231118 | 2000 | 20231118 | 2152 | 2273160 | 112 | Distribution Circuit | 3rd Party | Vehicle | 55 | 6160 | 37.9908 | -120.4618 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 23-0140977 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891648 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320840950312 | 20231118 | 2130 | 20231119 | 40 | 2273325 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 380 | 37.8816 | -120.2092 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0141036 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891707 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 171061 | 20231119 | 1018 | 20231119 | 1611 | 2273530 | 353 | Distribution Circuit | 3rd Party | Vehicle | 9 | 3177 | 37.1579 | -120.2651 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0141096 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891766 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | RECLOSER | 4760 | 20231119 | 1613 | 20231120 | 131 | 2273636 | 558 | Distribution Circuit | 3rd Party | Gun Shot | 58 | 15159 | 37.0986 | -120.4938 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0141124 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1891790 | 0 | Non-EPSS | N | 2023 | C & GRD
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | FUSE | 21109 | 20231119 | 1647 | 20231120 | 246 | 2273650 | 599 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 599 | 37.1004 | -120.9698 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0141129 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1891793 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | TRANSFORMER | 321321315874 | 20231119 | 1649 | 20231119 | 2236 | 2273652 | 347 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 5205 | 36.9352 | -120.0489 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0141131 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891795 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 2092 | 20231119 | 1724 | 20231119 | 1829 | 2273664 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 347 | 37.1447 | -120.1629 | No | Partly Cloudy;32-90 F |  |  | 23-0141138 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1891798 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 99295 | 20231119 | 1926 | 20231119 | 2113 | 2273711 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2782 | 37.5445 | -120.4624 | No | Clear;32-90 F |  |  | 23-0141161 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891821 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | S991 | 20231120 | 923 | 20231120 | 1301 | 2274105 | 218 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 218 | 37.7362 | -120.9316 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 23-0141247 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891918 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 10841 | 20231120 | 1421 | 20231120 | 1509 | 2274441 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 384 | 37.0276 | -120.8545 | No | Clear;32-90 F |  |  | 23-0141499 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1891999 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319358232036 | 20231120 | 1529 | 20231120 | 1922 | 2274469 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 3871 | 37.3792 | -120.7217 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0141495 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891996 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | OTHER | WIRE DOWN RIVER RD. & HAROLD RD. | 20231120 | 1740 | 20231120 | 2235 | 2274598 | 295 | Distribution Circuit | 3rd Party | Vehicle | 2234 | 34910 | 37.7623 | -120.9684 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0141568 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1892021 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | TRANSFORMER | 318924517078 | 20231121 | 920 | 20231122 | 140 | 2275268 | 980 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1960 | 36.9686 | -120.8693 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142032 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892231 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 7745 | 20231121 | 1041 | 20231121 | 1445 | 2274986 | 244 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1464 | 37.1418 | -120.4464 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0141787 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892173 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 9657 | 20231121 | 1947 | 20231121 | 2250 | 2275388 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1098 | 36.7991 | -120.3335 | No | Overcast;32-90 F |  |  | 23-0142117 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892281 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | TRANSFORMER | T8410 | 20231121 | 2108 | 20231122 | 1222 | 2275408 | 914 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 12416 | 37.0623 | -120.8096 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0142130 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892290 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | TRANSFORMER | 319632119842 | 20231121 | 2343 | 20231122 | 402 | 2275395 | 259 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1554 | 37.045 | -120.6265 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142128 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892287 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | FUSE | 6042 | 20231122 | 543 | 20231122 | 1210 | 2275490 | 387 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1548 | 37.0468 | -120.3124 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0142156 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892301 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 20231122 | 625 | 20231122 | 953 | 2275493 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 139 | 28912 | 38.0064 | -120.3467 | No | Partly Cloudy;32-90 F |  |  | 23-0142140 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892297 | 0 | EPSS Ckt | Y | 2023 | AC
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20231122 | 643 | 20231122 | 916 | 2275497 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1313 | 200889 | 38.0063 | -120.3474 | No | Partly Cloudy;32-90 F |  |  | 23-0142144 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892300 | 0 | EPSS Ckt | Y | 2023 | AB
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L2075 | 20231122 | 1048 | 20231122 | 1221 | 2275685 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 837 | 38.0207 | -120.3837 | No | Partly Cloudy;32-90 F |  |  | 23-0142345 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892364 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320400249270 | 20231122 | 1139 | 20231122 | 1147 | 2275716 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 8 | 37.8536 | -120.3624 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0142336 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892362 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | RECLOSER | 11060 | 20231122 | 1154 | 20231122 | 2217 | 2275732 | 623 | Distribution Circuit | 3rd Party | Vehicle | 267 | 128166 | 37.0699 | -120.8656 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0142352 | OH | Sus | 35513563 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1892368 | 0 | Non-EPSS | N | 2023 | A/B
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | JUMPER | BLOWN JMPR AT CGC #319198321824 | 20231122 | 1717 | 20231123 | 206 | 2275922 | 529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 14171 | 37.0989 | -120.7756 | No | Overcast;32-90 F | Jumper | Broken | 23-0142462 | OH | Sus | 31677106 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892405 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 8289 | 20231122 | 1851 | 20231124 | 1101 | 2275966 | 886 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 8026 | 37.7293 | -120.9405 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0142458 | UG | Sus | 46064880 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892403 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | TRANSFORMER | 319007022285 | 20231123 | 600 | 20231123 | 1229 | 2276032 | 389 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1167 | 37.111 | -120.8415 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0142525 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892461 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319312729815 | 20231123 | 721 | 20231123 | 819 | 2276045 | 58 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 116 | 37.318 | -120.7376 | No | Clear;32-90 F |  |  | 23-0142496 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1892434 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | RECLOSER | 29612 | 20231123 | 2048 | 20231124 | 214 | 2276262 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 567 | 59893 | 37.3585 | -120.8503 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0142561 | OH | Sus | 46064439 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1892493 | 0 | Non-EPSS | N | 2023 | A-B-C INSTANT
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | RECLOSER | 4000 | 20231123 | 2320 | 20231124 | 1204 | 2276274 | 620 | Distribution Circuit | 3rd Party | Vehicle | 462 | 157164 | 37.5266 | -120.442 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0142579 | OH | Sus | 35513586 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | Yes | No | 1892511 | 0 | Non-EPSS | N | 2023 | A-C & GRD
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20231124 | 2 | 20231124 | 1040 | 2276288 | 638 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 583 | 185438 | 38.0085 | -120.3034 | No | Clear;32-90 F |  |  | 23-0142580 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892512 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | FUSE | 6816 | 20231124 | 37 | 20231124 | 847 | 2276301 | 490 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1470 | 36.9382 | -120.2097 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0142582 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892516 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 8513 | 20231124 | 37 | 20231124 | 312 | 2276302 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 620 | 37.5362 | -120.4873 | No | Clear;32-90 F |  |  | 23-0142583 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892517 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 6060 | 20231124 | 559 | 20231124 | 1455 | 2276378 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2019 | 708635 | 37.9892 | -120.3332 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142590 | OH | Sus | 35513642 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892524 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3757 | 20231124 | 637 | 20231124 | 840 | 2276393 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 410 | 36.9241 | -120.6889 | No | Clear;32-90 F |  |  | 23-0142613 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892544 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7312 | 20231124 | 958 | 20231124 | 1345 | 2276484 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 907 | 37.4911 | -120.6306 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0142663 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892576 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | RECLOSER | 551990 | 20231124 | 1248 | 20231124 | 1324 | 2276552 | 36 | Distribution Circuit | Company Initiated | Return Circuit Normal | 67 | 2409 | 37.5222 | -120.5783 | No | Clear;32-90 F | Regulator | Normal | 23-0142579 | OH | Sus | 35513586 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1892568 | 0 | Non-EPSS | N | 2023 | A PH
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 659827 | 20231124 | 1329 | 20231124 | 1503 | 2276629 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 376 | 37.154 | -120.2744 | No | Clear;32-90 F |  |  | 23-0142672 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892583 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319676337124 | 20231124 | 1336 | 20231124 | 2130 | 2276738 | 474 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1422 | 37.519 | -120.6121 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142696 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892603 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319716037040 | 20231124 | 1343 | 20231125 | 1020 | 2276638 | 1237 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1237 | 37.5168 | -120.5991 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142691 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892598 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | OCB | 1103/2 | 20231124 | 1422 | 20231124 | 1645 | 2276640 | 143 | Distribution Circuit | 3rd Party | Vehicle | 4 | 572 | 37.3359 | -120.5053 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0142667 | OH | Sus | 31677122 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892579 | 0 | Non-EPSS | N | 2023 | NA
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320769055984 | 20231124 | 1735 | 20231124 | 2028 | 2276719 | 173 | Transformer only | Equipment Failure/Involved | Electrical Overload | 16 | 2768 | 38.0376 | -120.2341 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142697 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892604 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | OCB | 1103/2 | 20231124 | 2126 | 20231125 | 1047 | 2276747 | 801 | Distribution Circuit | 3rd Party | Vehicle | 871 | 208611 | 37.2036 | -119.4971 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0142725 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1892632 | 0 | EPSS Ckt | Y | 2023 | A&C INSTANT
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321378820352 | 20231125 | 752 | 20231125 | 940 | 2276890 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 324 | 37.0587 | -120.0296 | No | Clear;32-90 F | Fuse | Burned Open | 23-0142755 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892659 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | S715 | 20231125 | 1017 | 20231125 | 1100 | 2276963 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 301 | 37.7618 | -120.8136 | No | Clear;32-90 F |  |  | 23-0142770 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892667 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 4320 | 20231125 | 1510 | 20231125 | 2028 | 2277070 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 13741 | 37.2283 | -120.4881 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0142808 | OH | Sus | 46065471 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1892679 | 0 | Non-EPSS | N | 2023 | A AND GROUND
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | T4313 | 20231126 | 559 | 20231126 | 1028 | 2277282 | 269 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 1076 | 36.9779 | -120.8722 | No | Partly Cloudy;32-90 F |  |  | 23-0142904 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1892747 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 350427 | 20231126 | 740 | 20231126 | 946 | 2277304 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1890 | 38.0008 | -120.3126 | No | Clear;32-90 F |  |  | 23-0142899 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892743 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | RECLOSER | 9410 | 20231126 | 813 | 20231126 | 912 | 2277313 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 9314 | 37.5204 | -120.6262 | No | Partly Cloudy;32-90 F | Regulator | Burned/flashed | 23-0142890 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892732 | 0 | Non-EPSS | N | 2023 | AB
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 828842 | 20231126 | 901 | 20231126 | 1107 | 2277350 | 126 | Distribution Circuit | Animal | Squirrel | 1596 | 104027 | 37.2287 | -119.7103 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0142894 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | No | No | 1892739 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 26747 | 20231126 | 1258 | 20231126 | 1425 | 2277437 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1218 | 37.8569 | -120.9195 | No | Clear;32-90 F |  |  | 23-0142933 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892764 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | RECLOSER | 11870 | 20231126 | 1516 | 20231126 | 1541 | 2277474 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 2650 | 36.9658 | -120.1284 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0142934 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892767 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322500528885 | 20231126 | 1527 | 20231126 | 1755 | 2277481 | 148 | Transformer only | Animal | Squirrel | 1 | 148 | 37.2907 | -119.6418 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0142945 | OH | Sus | 31677162 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892777 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 3966 | 20231126 | 1541 | 20231126 | 2237 | 2277488 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 555 | 37.1833 | -120.9488 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0142956 | OH | Sus | 31677245 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892786 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | RECLOSER | 9740 | 20231126 | 1559 | 20231127 | 222 | 2277479 | 623 | Distribution Circuit | 3rd Party | Vehicle | 3426 | 345986 | 37.282 | -120.4877 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0142942 | OH | Sus | 35513683 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892774 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 68931 | 20231127 | 131 | 20231127 | 424 | 2277593 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2941 | 37.0395 | -120.0017 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0142974 | OH | Sus | 46068406 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1892804 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | FUSE | 2695 | 20231127 | 716 | 20231127 | 816 | 2277661 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 420 | 36.9592 | -120.0646 | No | Clear;32-90 F |  |  | 23-0143018 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892861 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | 21119 | 20231127 | 741 | 20231127 | 840 | 2277681 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 531 | 37.7669 | -120.8817 | No | Clear;32-90 F |  |  | 23-0143003 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892839 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 506555 | 20231127 | 1014 | 20231127 | 1127 | 2277997 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 73 | 37.322 | -120.7786 | No | Clear;32-90 F |  |  | 23-0143126 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1893023 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | FUSE | 24262 | 20231127 | 1104 | 20231127 | 1234 | 2278072 | 90 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 8820 | 37.3334 | -120.5501 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0143121 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1893020 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318689223485 | 20231127 | 1212 | 20231127 | 1300 | 2278024 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 96 | 37.144 | -120.9511 | No | Clear;32-90 F | Customer Equipment | Broken | 23-0143144 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893036 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 13274 | 20231127 | 1503 | 20231128 | 342 | 2278299 | 759 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 145 | 101499 | 36.9657 | -120.0608 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0143239 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893069 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 26503 | 20231127 | 1610 | 20231127 | 1649 | 2278339 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 78 | 37.7257 | -120.803 | No | Clear;32-90 F |  |  | 23-0143268 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893084 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320906949564 | 20231127 | 1956 | 20231127 | 2210 | 2278453 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 134 | 37.8606 | -120.1869 | No | Clear;32-90 F | Insulator | Broken | 23-0143278 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893093 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 7042 | 20231128 | 356 | 20231128 | 610 | 2278532 | 134 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 4824 | 37.3141 | -120.4515 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0143320 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893135 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 9203 | 20231128 | 524 | 20231128 | 656 | 2278548 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 3007 | 37.2302 | -120.9942 | No | Partly Cloudy;32-90 F |  |  | 23-0143327 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893142 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BONITA-1103 | 255391103 | SWITCH | 5068 | 20231128 | 810 | 20231128 | 1225 | 2278511 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 14560 | 37.0099 | -120.2385 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0143346 | OH | Sus | 46070710 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893167 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | JUMPER | FB 1 S & 1 E/OF CGC# 320546054944 | 20231128 | 1027 | 20231128 | 1612 | 2278680 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 690 | 38.0076 | -120.3124 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0143365 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893207 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319667728333 | 20231128 | 1121 | 20231128 | 1212 | 2278948 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 51 | 37.2784 | -120.6156 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0143465 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893355 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | JUMPER | OJ 1 SPAN NE OF CGC#319633034917 | 20231128 | 1645 | 20231128 | 1852 | 2279183 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 127 | 37.4585 | -120.6252 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0143604 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893395 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 371015 | 20231128 | 2356 | 20231129 | 53 | 2279309 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 456 | 37.7715 | -120.7752 | No | Clear;32-90 F |  |  | 23-0143666 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1893456 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | OCB | 1104/2 | 20231129 | 523 | 20231129 | 533 | 2279367 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 169 | 1688 | 37.1847 | -120.2736 | No | Clear;32-90 F | Regulator | Malfunctioning | 23-0136700 | OH | Sus | 74044788 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893470 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 25437 | 20231129 | 951 | 20231129 | 1134 | 2279798 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 275 | 37.3385 | -120.6238 | No | Partly Cloudy;32-90 F |  |  | 23-0143807 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893693 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 5854 | 20231129 | 951 | 20231129 | 1119 | 2279889 | 88 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 21 | 1820 | 36.8803 | -119.9102 | No | Clear;32-90 F |  |  | 23-0143795 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893688 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318737530663 | 20231129 | 1036 | 20231129 | 1045 | 2279747 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 9 | 37.3407 | -120.9362 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0143788 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893680 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1102 | 254101102 | OTHER | T7924 TWD J24048 | 20231129 | 1247 | 20231129 | 1350 | 2279993 | 63 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 756 | 37.1139 | -120.2289 | No | Partly Cloudy;32-90 F | Secondary | Burned Open | 23-0143846 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893714 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321718015995 | 20231129 | 1307 | 20231129 | 1358 | 2280049 | 51 | Transformer only | Equipment Failure/Involved | Underground | 2 | 102 | 36.9376 | -119.9128 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 23-0143892 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893731 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | RECLOSER | 5450 | 20231129 | 1500 | 20231129 | 1518 | s1893745 | 18 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 173 | 3114 | 37.0401 | -120.2544 | No | Clear;32-90 F |  |  | 23-0058482 |  | Sus | 45591160 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1893745 | 0 | Non-EPSS | N | 2023 | AC
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | RECLOSER | 78274 | 20231130 | 729 | 20231130 | 753 | 2280368 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 416 | 9984 | 37.0596 | -120.847 | No | Partly Cloudy-Fog;32-90 F | Service conductor | Broken- wire on object | 23-0144109 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893822 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | JUMPER | HIGH SIDE JUMPERS @ 25044 | 20231130 | 821 | 20231130 | 951 | 2280420 | 90 | Distribution Circuit | 3rd Party | Vehicle | 35 | 3150 | 37.7943 | -120.9962 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0144124 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1893832 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1111 | 252421111 | FUSE | 465575 | 20231130 | 857 | 20231130 | 950 | 2280564 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 53 | 37.0881 | -120.3289 | No | Partly Cloudy;32-90 F |  |  | 23-0144187 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1893996 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321782713877 | 20231130 | 906 | 20231130 | 1707 | 2280593 | 481 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 481 | 36.8799 | -119.8915 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0144183 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893989 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321782713878 | 20231130 | 906 | 20231130 | 1702 | 2280597 | 476 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 952 | 36.8802 | -119.8915 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0144193 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1893997 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1112 | 252761112 | OCB | 1112/2 | 20231130 | 1129 | 20231130 | 1220 | 2280782 | 51 | Distribution Circuit | 3rd Party | Vehicle | 627 | 31977 | 36.9234 | -120.0551 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0144259 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1894032 | 0 | Non-EPSS | N | 2023 | SET A
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318949122397 | 20231130 | 1523 | 20231130 | 1728 | 2280959 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 125 | 37.1141 | -120.8614 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0144432 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1894088 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20231130 | 1605 | 20231201 | 946 | 2280990 | 1061 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 583 | 211148 | 38.0085 | -120.3034 | No | Partly Cloudy;32-90 F |  |  | 23-0144397 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1894078 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
YOSEMITE | YOSEMITE | FIGARDEN-2107 | 254552107 | TRANSFORMER | 321448215702 | 20231130 | 2124 | 20231201 | 420 | 2280422 | 416 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 416 | 36.8596 | -119.874 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0144313 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1894059 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | PANOCHE-1103 | 253671103 | JUMPER | OJ 1 SPAN SS/OF CGC# 415189447687 | 20231201 | 230 | 20231201 | 1252 | 2281129 | 622 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2 | 1244 | 36.6332 | -120.6407 | No | Clear;32-90 F | Jumper | Normal | 23-0144498 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1894142 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 99563 | 20231201 | 559 | 20231201 | 722 | 2281158 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 747 | 36.8805 | -119.8976 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0144532 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1894163 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 10880 | 20231202 | 8 | 20231202 | 143 | 2281942 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 483 | 45885 | 37.4619 | -119.9501 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0144873 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1894457 | 0 | EPSS Ckt | Y | 2023 | B & GRD INST OC
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 10880 | 20231202 | 213 | 20231202 | 905 | 2281953 | 412 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 482 | 4680 | 37.4619 | -119.9501 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0144876 | OH | Sus | 35514477 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1894461 | 0 | EPSS Ckt | Y | 2023 | B & GRD INST OC
YOSEMITE | YOSEMITE | BONITA-1103 | 255391103 | RECLOSER | 6020 | 20231202 | 500 | 20231202 | 1527 | 2281963 | 627 | Distribution Circuit | Vegetation | Tree - bark fell into line | 217 | 42382 | 36.9675 | -120.2232 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0144880 | OH | Sus | 31677836 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1894465 | 0 | Non-EPSS | N | 2023 | ABC
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | OCB | 1101/2 | 20231202 | 819 | 20231202 | 1811 | 2282032 | 592 | Distribution Circuit | 3rd Party | Vehicle | 232 | 9916 | 37.0856 | -121.0131 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0144891 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1894500 | 0 | EPSS Ckt | N | 2023 | NONE
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | SWITCH | 929360 | 20231202 | 1835 | 20231203 | 936 | 2282438 | 901 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2876 | 196819 | 37.4926 | -119.9661 | No | Partly Cloudy;32-90 F |  |  | 23-0144970 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1894599 | 0 | EPSS Ckt | Y | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | RECLOSER | 7190 | 20231203 | 5 | 20231203 | 805 | 2282568 | 480 | Distribution Circuit | 3rd Party | Vehicle | 1183 | 280040 | 37.3624 | -120.6412 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 23-0144994 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1894626 | 0 | Non-EPSS | N | 2023 | A & C
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320439022640 | 20231203 | 1430 | 20231203 | 1528 | 2282766 | 58 | Transformer only | Equipment Failure/Involved | Underground | 3 | 174 | 37.1217 | -120.3494 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0145037 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1894686 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | FUSE | 24262 | 20231203 | 1441 | 20231203 | 1534 | 2282772 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 5194 | 37.3334 | -120.5501 | No | Partly Cloudy;32-90 F |  |  | 23-0145045 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1894690 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319835430476 | 20231203 | 1655 | 20231203 | 1733 | 2282811 | 38 | Transformer only | Animal | Other | 2 | 76 | 37.3375 | -120.5567 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0145051 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1894696 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 3736 | 20231204 | 808 | 20231204 | 1027 | 2283175 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1390 | 36.792 | -120.2592 | No | Overcast-Fog;32-90 F |  |  | 23-0145165 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1894920 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | OJ'S @ CGC# 320502144160 | 20231204 | 910 | 20231204 | 922 | 2283294 | 12 | Distribution Circuit | 3rd Party | Gun Shot | 1 | 12 | 37.715 | -120.3258 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0145149 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1894870 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319117346116 | 20231204 | 954 | 20231204 | 1114 | 2283384 | 80 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 80 | 37.7659 | -120.8063 | No | Clear;32-90 F |  |  | 23-0145210 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1894971 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | JUMPER | OPEN HS JUMPER OF S20385 | 20221204 | 1319 | 20231204 | 1427 | 2283604 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 340 | 37.817 | -121.0155 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0145295 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1895021 | 1 | Non-EPSS | N | 2022
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | JUMPER | OPEN HS JUMPER OF S20385 | 20231204 | 1319 | 20231204 | 1427 | 2283604 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 340 | 37.817 | -121.0155 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0145295 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1895021 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319609034623 | 20231204 | 1327 | 20231204 | 1400 | 2283605 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 99 | 37.4506 | -120.635 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0145261 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1895007 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | FUSE | 3836 | 20231204 | 1714 | 20231204 | 1820 | 2283782 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 264 | 36.8954 | -120.5854 | No | Clear;32-90 F |  |  | 23-0145388 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895056 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | TRANSFORMER | 320116129064 | 20231204 | 1724 | 20231204 | 2334 | 2283789 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3700 | 37.2988 | -120.4599 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0145387 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895055 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318351646967 | 20231205 | 517 | 20231205 | 700 | 2283957 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 206 | 37.789 | -121.0716 | No | Clear;32-90 F | Fuse | Broken | 23-0145427 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895100 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319185022176 | 20231205 | 520 | 20231205 | 650 | 2283958 | 90 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 180 | 37.1087 | -120.7801 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0145424 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1895097 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 41506 | 20231205 | 709 | 20231205 | 810 | 2283985 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 549 | 37.8495 | -120.8806 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0145439 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1895108 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | RECLOSER | 11490 | 20231205 | 746 | 20231205 | 1415 | 2283998 | 389 | Distribution Circuit | 3rd Party | Vehicle | 1089 | 101946 | 37.14 | -120.2742 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0145441 | OH | Sus | 31678380 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1895110 | 0 | Non-EPSS | N | 2023 | A- B & C
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | FUSE | 9633 | 20231205 | 751 | 20231205 | 920 | 2284001 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1069 | 37.1805 | -121.0309 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0145474 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895235 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | TRANSFORMER | 320707021395 | 20231205 | 813 | 20231205 | 909 | 2284066 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 56 | 37.0872 | -120.2582 | No | Partly Cloudy-Fog;32-90 F | Fuse | Failed/Faulted | 23-0145471 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895228 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 320677111470 | 20231205 | 925 | 20231205 | 1008 | 2284192 | 43 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 43 | 36.8143 | -120.2683 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0145505 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895294 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320076519686 | 20231205 | 1330 | 20231205 | 1450 | 2284460 | 80 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 80 | 37.0408 | -120.4741 | No | Clear;32-90 F |  |  | 23-0145617 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1895367 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 21102 | 20231205 | 1503 | 20231205 | 1652 | 2284578 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 218 | 37.3043 | -120.7735 | No | Clear;32-90 F |  |  | 23-0145668 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1895380 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318302231643 | 20231205 | 1522 | 20231205 | 2015 | 2284553 | 293 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 586 | 37.3676 | -121.0853 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0145666 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895378 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 24824 | 20231206 | 302 | 20231206 | 440 | 2284754 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 392 | 37.1035 | -120.4371 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0145740 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1895440 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | TRANSFORMER | 320291822084 | 20231206 | 907 | 20231206 | 959 | 2284971 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 52 | 37.1066 | -120.4008 | No | Clear;32-90 F | Fuse | Broken | 23-0145829 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895580 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321434033592 | 20231206 | 937 | 20231206 | 1646 | 2285038 | 429 | Transformer only | Company Initiated | Personnel- company | 1 | 429 | 37.4202 | -120.0073 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0145850 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895608 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20639 | 20231206 | 1046 | 20231206 | 1450 | 2284911 | 244 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1220 | 37.7281 | -120.8122 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0145847 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1895603 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321764934702 | 20231206 | 1212 | 20231206 | 2225 | 2285341 | 613 | Transformer only | Vegetation | Tree - fell into line | 1 | 613 | 37.4496 | -119.8923 | No | Partly Cloudy;32-90 F | Service conductor | Broken- wire on ground | 23-0146032 | OH | Sus | 46080161 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895701 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320759453760 | 20231206 | 1247 | 20231206 | 1424 | 2285219 | 97 | Transformer only | 3rd Party | Vehicle | 1 | 97 | 37.976 | -120.2375 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0145948 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895661 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7258 | 20231206 | 1438 | 20231206 | 1650 | 2285328 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2640 | 37.303 | -120.7908 | No | Partly Cloudy;32-90 F |  |  | 23-0146004 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1895684 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1779 | 20231207 | 1610 | 20231207 | 1710 | 2286405 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 320 | 37.8216 | -120.6787 | No | Partly Cloudy;32-90 F |  |  | 23-0146309 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896010 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 4141 | 20231207 | 1715 | 20231207 | 2107 | 2286540 | 232 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 696 | 37.3626 | -120.5956 | No | Fog;32-90 F |  |  | 23-0146333 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896028 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | RECLOSER | 11942 | 20231207 | 1912 | 20231208 | 300 | 2286509 | 468 | Distribution Circuit | 3rd Party | Vehicle | 208 | 27036 | 37.1 | -120.9306 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0146328 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | Yes | No | 1896022 | 0 | EPSS Ckt | N | 2023 | GROUND- SGF
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 7348 | 20231208 | 706 | 20231208 | 826 | 2286652 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1227 | 37.1849 | -120.5462 | No | Overcast-Fog;32-90 F |  |  | 23-0146419 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896146 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10070 | 20231208 | 1059 | 20231208 | 1322 | 2287014 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 297 | 42471 | 37.5079 | -119.9962 | No | Clear;32-90 F |  |  | 23-0146492 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896251 | 0 | EPSS Ckt | Y | 2023 | B PH
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 11634 | 20231208 | 1126 | 20231208 | 1214 | 2287044 | 48 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 4 | 192 | 37.1854 | -120.3379 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0146509 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896264 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L459 | 20231208 | 1200 | 20231208 | 1311 | 2287091 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 2485 | 37.9828 | -120.444 | No | Clear;32-90 F |  |  | 23-0146536 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896280 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319914636257 | 20231208 | 1326 | 20231208 | 1415 | 2287166 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 343 | 37.4954 | -120.5302 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0146543 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1896284 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | TRANSFORMER | 320127328948 | 20231208 | 1328 | 20231208 | 1427 | 2287170 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 472 | 37.2955 | -120.456 | No | Clear;32-90 F | Secondary | Broken | 23-0146548 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1896287 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320090549416 | 20231208 | 1625 | 20231208 | 1835 | 2287313 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 260 | 37.8565 | -120.1875 | No | Clear;32-90 F | Fuse | Normal | 23-0146599 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896323 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | FUSE | 8962 | 20231208 | 1653 | 20231208 | 1933 | 2287343 | 160 | Distribution Circuit | Equipment Failure/Involved | Underground | 171 | 27360 | 37.3267 | -120.4869 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0146569 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1896314 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321384814462 | 20231209 | 639 | 20231209 | 1003 | 2287809 | 204 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 204 | 36.8963 | -120.027 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0146646 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896463 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7548 | 20231210 | 657 | 20231210 | 851 | 2288238 | 114 | Distribution Circuit | Animal | Bird found | 33 | 3802 | 37.3058 | -120.8469 | No | Clear;Below 32 F | Conductor- Overhead | Normal | 23-0146734 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896578 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 4996 | 20231210 | 1708 | 20231210 | 1843 | 2288474 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2945 | 37.2874 | -120.3927 | No | Partly Cloudy;32-90 F |  |  | 23-0146766 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896624 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 602735 | 20231210 | 1753 | 20231210 | 1854 | 2288483 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 2013 | 37.2547 | -121.0013 | No | Partly Cloudy;32-90 F |  |  | 23-0146767 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896625 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 7055 | 20231210 | 1801 | 20231211 | 238 | 2288484 | 517 | Distribution Circuit | 3rd Party | Vehicle | 20 | 10340 | 37.3605 | -120.7083 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0146771 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896630 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | TRANSFORMER | T34156 | 20231211 | 936 | 20231211 | 1553 | 2289093 | 377 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 2103 | 37.3409 | -120.4956 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0146859 | UG | Sus | 35516616 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896853 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 23519 | 20231211 | 1053 | 20231211 | 1353 | 2289366 | 180 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 180 | 36.8732 | -119.8538 | No | Partly Cloudy;32-90 F |  |  | 23-0146899 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896908 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 6082 | 20231211 | 1107 | 20231212 | 957 | 2289213 | 1370 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1370 | 37.0081 | -120.1107 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0146875 | UG | Sus | 46087645 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896876 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | S2613 | 20231211 | 2338 | 20231212 | 200 | 2289643 | 142 | Distribution Circuit | 3rd Party | Metallic Balloon | 16 | 2272 | 37.7036 | -120.818 | No | Fog;32-90 F | Conductor- Overhead | Normal | 23-0146964 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1896973 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | TRANSFORMER | 320556616227 | 20231212 | 757 | 20231212 | 1121 | 2289718 | 204 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 408 | 36.9458 | -120.3095 | No | Fog;32-90 F | Secondary | Broken | 23-0147015 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897109 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 21157 | 20231212 | 811 | 20231212 | 840 | 2289742 | 29 | Distribution Circuit | 3rd Party | Vehicle | 86 | 2494 | 37.7701 | -120.8458 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 23-0147005 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897032 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | FUSE | 7393 | 20231212 | 1015 | 20231212 | 1416 | 2290021 | 241 | Distribution Circuit | Equipment Failure/Involved | Underground | 91 | 19930 | 37.326 | -120.4869 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0147058 | UG | Sus | 31678988 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897185 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRANSFORMER | T3028 | 20231212 | 1051 | 20231212 | 1122 | 2289994 | 31 | Transformer only | 3rd Party | Vandalism | 9 | 279 | 37.1118 | -120.2751 | No | Clear;32-90 F | Secondary | Broken | 23-0147049 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1897170 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | 77073 | 20231212 | 1704 | 20231212 | 1812 | 2290253 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 680 | 37.9736 | -120.359 | No | Clear;32-90 F |  |  | 23-0147124 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1897236 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 6819 | 20231213 | 734 | 20231213 | 1217 | 2290513 | 283 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1415 | 36.971 | -120.184 | No | Fog;32-90 F |  |  | 23-0147259 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1897534 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | OCB | 1117/2 | 20231213 | 754 | 20231213 | 906 | 2290539 | 72 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 204 | 14688 | 36.8859 | -120.6559 | No | Fog;32-90 F |  |  | 23-0147175 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1897309 | 0 | EPSS Ckt | N | 2023 | A- B- C
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | OTHER | WIRE DOWN ON MAINLINE JUST S/OF 23135 | 20231213 | 846 | 20231213 | 1220 | 2290648 | 214 | Distribution Circuit | Animal | Bird found | 556 | 103544 | 36.9747 | -120.0597 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0147193 | OH | Sus | 46089645 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | Yes | 1897418 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319516032745 | 20231213 | 911 | 20231213 | 929 | 2290603 | 18 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 18 | 37.3991 | -120.6667 | No | Clear;32-90 F |  |  | 23-0147203 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1897446 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 7454 | 20231213 | 1314 | 20231213 | 1421 | 2291126 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1139 | 37.2196 | -120.2151 | No | Clear;32-90 F |  |  | 23-0147282 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1897565 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320076519686 | 20231213 | 1346 | 20231213 | 1743 | 2291149 | 237 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 237 | 37.0408 | -120.4741 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147293 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897571 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 57215 | 20231213 | 1423 | 20231213 | 1538 | 2291212 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 150 | 36.733 | -120.3391 | No | Clear;32-90 F |  |  | 23-0147296 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897577 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | TRANSFORMER | T4045 | 20231214 | 852 | 20231214 | 910 | 2291511 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 36 | 36.8613 | -120.7826 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0147406 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897771 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | RECLOSER | 3214 | 20231214 | 856 | 20231214 | 1551 | 2291647 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 220 | 24564 | 37.7904 | -120.8634 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0147369 | OH | Sus | 35517349 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1897729 | 0 | Non-EPSS | N | 2023 | NONE
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7975 | 20231214 | 903 | 20231214 | 1010 | 2291656 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 67 | 37.4851 | -120.6485 | No | Partly Cloudy;32-90 F |  |  | 23-0147421 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897826 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320564455140 | 20231214 | 1103 | 20231214 | 1357 | 2291853 | 174 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 174 | 38.0139 | -120.305 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0144001 | OH | Sus | 31673067 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1897846 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320355827187 | 20231214 | 2013 | 20231214 | 2240 | 2292093 | 147 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 441 | 37.2478 | -120.3781 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147494 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1897920 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321756215995 | 20231214 | 2058 | 20231214 | 2221 | 2292151 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 166 | 36.9376 | -119.8998 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0147512 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1897946 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 20381 | 20231214 | 2118 | 20231215 | 510 | 2292155 | 472 | Distribution Circuit | 3rd Party | Vehicle | 27 | 12744 | 37.7106 | -120.8484 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0147509 | OH | Sus | 35517606 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | Yes | 1897940 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 3618 | 20231215 | 749 | 20231215 | 920 | 2292238 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 546 | 37.1622 | -121.0139 | No | Partly Cloudy;32-90 F |  |  | 23-0147541 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898041 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 11708 | 20231215 | 803 | 20231215 | 1235 | 2292260 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3536 | 36.8905 | -120.7369 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0147558 | OH | Sus | 46092847 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1898144 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | OCB | 1103/2 | 20231215 | 820 | 20231215 | 1256 | 2292291 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 850 | 52005 | 37.1208 | -120.473 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147532 | OH | Sus | 46092846 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | Yes | No | 1898010 | 0 | Non-EPSS | N | 2023 | BC & GRD
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7554 | 20231215 | 918 | 20231215 | 1036 | 2292409 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 234 | 37.3025 | -120.7879 | No | Partly Cloudy;32-90 F |  |  | 23-0147561 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898156 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | RECLOSER | 130318 | 20231215 | 1236 | 20231215 | 2009 | 2292603 | 453 | Distribution Circuit | 3rd Party | Vehicle | 817 | 58849 | 37.8276 | -120.9591 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0147580 | OH | Sus | 35517693 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1898179 | 0 | Non-EPSS | N | 2023 | ABC
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 4190 | 20231215 | 1254 | 20231215 | 2000 | 2292622 | 426 | Distribution Circuit | 3rd Party | Vehicle | 2832 | 347077 | 37.5051 | -120.038 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0147584 | OH | Sus | 35517751 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1898182 | 0 | EPSS Ckt | Y | 2023 | SGF
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | SWITCH | 4893 | 20231215 | 1312 | 20231215 | 1323 | 2292654 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 17 | 187 | 37.1267 | -120.5378 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0147532 | OH | Sus | 46092846 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1898196 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 320025423253 | 20231215 | 1430 | 20231215 | 1514 | 2292706 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 44 | 37.1388 | -120.4921 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0147601 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898212 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 13156 | 20231215 | 1814 | 20231215 | 2013 | 2292842 | 119 | Distribution Circuit | Animal | Bird found | 3 | 357 | 37.0159 | -120.0012 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0147619 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898236 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | OCB | 1110/2 | 20231216 | 724 | 20231216 | 1912 | 2292986 | 708 | Distribution Circuit | 3rd Party | Vehicle | 251 | 37742 | 37.0551 | -120.3171 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0147634 | OH | Sus | 31679756 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 1898269 | 0 | Non-EPSS | N | 2023 | AC&GRD
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 3568 | 20231216 | 810 | 20231216 | 1003 | 2293022 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 339 | 36.7708 | -120.7115 | No | Clear;32-90 F |  |  | 23-0147642 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898350 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | RECLOSER | 78842 | 20231216 | 1358 | 20231216 | 1657 | 2293260 | 179 | Distribution Circuit | Company Initiated | Contact with High Voltage- company | 759 | 18431 | 37.7908 | -120.867 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147663 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | Yes | No | 1898383 | 0 | Non-EPSS | N | 2023 | A-B-C & GRD
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 11713 | 20231216 | 1550 | 20231216 | 1645 | 2293302 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 165 | 37.3023 | -120.6511 | No | Clear;32-90 F |  |  | 23-0147669 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898389 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | JUMPER | OJ AT CGC #322585529760 | 20231216 | 1724 | 20231216 | 1838 | 2293343 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 148 | 37.3141 | -119.6122 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0147679 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898401 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | JUMPER | OJ 1P S/OF CGC #320005738320 | 20231216 | 1732 | 20231216 | 2218 | 2293338 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 286 | 37.5512 | -120.4994 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0147677 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898399 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9645 | 20231217 | 714 | 20231217 | 1000 | 2293470 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1826 | 36.7294 | -120.3146 | No | Overcast;32-90 F |  |  | 23-0147741 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898487 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 23718 | 20231217 | 1421 | 20231217 | 1850 | 2293736 | 269 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 8339 | 37.2602 | -121.048 | No | Clear-Lightning;32-90 F | Fuse | Failed/Faulted | 23-0147792 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898549 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | RECLOSER | 9140 | 20231217 | 1428 | 20231217 | 1600 | 2293739 | 92 | Distribution Circuit | Environmental/External | Lightning | 3 | 276 | 37.3244 | -121.0007 | No | Clear-Lightning;32-90 F | Fuse | Failed/Faulted | 23-0147754 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898503 | 0 | Non-EPSS | N | 2023 | B&C
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 602122 | 20231217 | 1428 | 20231218 | 1017 | 2293830 | 1189 | Distribution Circuit | Environmental/External | Lightning | 2 | 1881 | 37.3357 | -120.9887 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0147754 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1898522 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | JUMPER | OJ AT CGC #318539330356 | 20231217 | 1429 | 20231217 | 2154 | 2293763 | 445 | Distribution Circuit | Environmental/External | Lightning | 1 | 445 | 37.3327 | -121.0036 | No | Clear-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147758 | OH | Sus | 31679706 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | Yes | Yes | 1898518 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | OCB | 1101/2 | 20231217 | 1434 | 20231217 | 1843 | 2293755 | 249 | Distribution Circuit | Environmental/External | Lightning | 233 | 48518 | 37.0856 | -121.0131 | No | Partly Cloudy-Lightning;32-90 F | Regulator | Failed/Faulted | 23-0147761 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1898510 | 0 | EPSS Ckt | N | 2023 | A-B-C TIME OC
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 8901 | 20231217 | 1437 | 20231217 | 1750 | 2293758 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 257 | 37.361 | -120.9866 | No | Clear-Lightning;32-90 F |  |  | 23-0147787 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898538 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWMAN-1106 | 162741106 | FUSE | 9839 | 20231217 | 1510 | 20231217 | 1752 | 2293775 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1621 | 37.3352 | -120.9063 | No | Clear-Lightning;32-90 F |  |  | 23-0147786 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898537 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318765530530 | 20231217 | 1521 | 20231218 | 143 | 2293821 | 622 | Transformer only | Environmental/External | Lightning | 1 | 622 | 37.3353 | -120.9265 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147782 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898533 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWMAN-1106 | 162741106 | TRANSFORMER | 318772930068 | 20231217 | 1523 | 20231217 | 2230 | 2293781 | 427 | Transformer only | Environmental/External | Lightning | 1 | 427 | 37.3219 | -120.9239 | No | Clear-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147779 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898530 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWMAN-1106 | 162741106 | TRANSFORMER | 318772130092 | 20231217 | 1647 | 20231218 | 25 | 2293866 | 458 | Transformer only | Environmental/External | Lightning | 1 | 458 | 37.3227 | -120.924 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147780 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898531 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 23719 | 20231217 | 1807 | 20231217 | 1915 | 2293897 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 204 | 37.2602 | -121.0433 | No | Partly Cloudy;32-90 F |  |  | 23-0147794 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898551 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWMAN-1106 | 162741106 | TRANSFORMER | 318795630535 | 20231217 | 1830 | 20231218 | 255 | 2293912 | 505 | Transformer only | Environmental/External | Lightning | 4 | 2020 | 37.3353 | -120.9165 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147798 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898555 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318404127289 | 20231217 | 1917 | 20231218 | 333 | 2293918 | 496 | Transformer only | Environmental/External | Lightning | 2 | 992 | 37.2482 | -121.0491 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147797 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898554 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | OCB | 1101/2 | 20231217 | 2157 | 20231217 | 2309 | 2293948 | 72 | Distribution Circuit | Environmental/External | Lightning | 233 | 16776 | 37.0856 | -121.0131 | No | Overcast;32-90 F | Regulator | Burned/flashed | 23-0147811 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898569 | 0 | EPSS Ckt | N | 2023 | A & B / TIME
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 1895 | 20231217 | 2222 | 20231218 | 538 | 2293951 | 436 | Distribution Circuit | 3rd Party | Vehicle | 86 | 37496 | 37.9124 | -120.4147 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0147812 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898571 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | RECLOSER | 41394 | 20231217 | 2328 | 20231218 | 1140 | 2293964 | 732 | Distribution Circuit | Equipment Failure/Involved | Overhead | 193 | 29722 | 37.1859 | -120.575 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0147818 | OH | Sus | 31679763 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1898577 | 0 | Non-EPSS | N | 2023 | SGF
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321316512994 | 20231218 | 338 | 20231218 | 1449 | 2294040 | 671 | Distribution Circuit | Animal | Other | 2 | 1003 | 36.8563 | -120.0515 | No | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 23-0147868 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898652 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 5905 | 20231218 | 542 | 20231218 | 744 | 2294072 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 732 | 36.9524 | -120.3522 | No | Overcast-Drizzle;32-90 F |  |  | 23-0147848 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898615 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 19093 | 20231218 | 647 | 20231218 | 1505 | 2294139 | 498 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 1239 | 37.328 | -120.892 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147894 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898688 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 4669 | 20231218 | 709 | 20231218 | 840 | 2294158 | 91 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 637 | 37.1857 | -120.6006 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0147854 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898634 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20231218 | 906 | 20231218 | 1040 | 2294314 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 259 | 24346 | 37.5694 | -120.1177 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0147867 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898651 | 0 | EPSS Ckt | Y | 2023 | A & C & 50 (INST)
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRANSFORMER | MTR#1006635457 | 20231218 | 928 | 20231218 | 959 | 2294333 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 124 | 37.3159 | -119.6024 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Leaking | 23-0147873 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898660 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 5611 | 20231218 | 951 | 20231219 | 156 | 2294383 | 965 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1991 | 37.2026 | -121.0683 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0147901 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1898710 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20231218 | 1051 | 20231218 | 1329 | 2294452 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 259 | 13166 | 37.5694 | -120.1177 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0147896 | OH | Sus | 46094668 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898690 | 0 | EPSS Ckt | Y | 2023 | A & C & 50 (INST)
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318566430280 | 20231218 | 1254 | 20231218 | 1932 | 2294557 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 398 | 37.3304 | -120.9942 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147917 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898726 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320405622892 | 20231218 | 1707 | 20231218 | 2144 | 2294956 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 351 | 37.129 | -120.3616 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147959 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898768 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 25247 | 20231218 | 2047 | 20231218 | 2325 | 2295147 | 158 | Distribution Circuit | 3rd Party | Vehicle | 2 | 316 | 37.332 | -120.3921 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0147988 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898800 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 2775 | 20231219 | 510 | 20231219 | 1810 | 2295639 | 780 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 6 | 4680 | 37.1265 | -120.0927 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0148091 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1898954 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | FUSE | 9719 | 20231219 | 716 | 20231219 | 824 | 2295330 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 1768 | 37.0129 | -120.818 | No | Overcast-Fog;32-90 F |  |  | 23-0148063 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898883 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 1027 | 20231219 | 738 | 20231219 | 855 | 2295396 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 616 | 37.3473 | -121.015 | No | Clear;32-90 F |  |  | 23-0148070 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898896 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320279022570 | 20231219 | 826 | 20231219 | 853 | 2295450 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 27 | 37.1201 | -120.4052 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Broken | 23-0148068 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898894 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 11708 | 20231219 | 919 | 20231219 | 1011 | 2295505 | 52 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 13 | 676 | 36.8905 | -120.7369 | No | Overcast;32-90 F | Crossarm- Wood | Burned/flashed | 23-0148074 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898911 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | SWITCH | 286703 | 20231219 | 1003 | 20231219 | 1506 | 2295559 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2121 | 37.1563 | -120.3488 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 23-0148064 | OH | Sus | 35518526 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898934 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRIP-SAVER | 10342 | 20231219 | 1039 | 20231219 | 1343 | 2295596 | 184 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 5554 | 37.2706 | -119.5342 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148088 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898951 | 1 | EPSS Ckt | N | 2023 | A
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | FUSE | 6747 | 20231219 | 1158 | 20231219 | 1257 | 2295691 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 118 | 36.9239 | -120.1554 | No | Clear;32-90 F |  |  | 23-0148107 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1898967 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 5905 | 20231219 | 1445 | 20231219 | 1722 | 2295832 | 157 | Distribution Circuit | Animal | Other | 9 | 733 | 36.9524 | -120.3522 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148135 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1898998 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | TRANSFORMER | 318958043460 | 20231219 | 1509 | 20231219 | 2013 | 2295862 | 304 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 304 | 37.6929 | -120.8609 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Broken | 23-0148141 | OH | Sus | 46096920 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899003 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23225 | 20231219 | 1516 | 20231219 | 1533 | 2295874 | 17 | Distribution Circuit | Animal | Squirrel | 35 | 595 | 37.9777 | -120.3149 | No | Overcast-Fog-Drizzle-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0148129 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1898992 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | JUMPER | VERT JUMPERS 1 SP W/OF CGC #322631530005 | 20231219 | 1537 | 20231219 | 1835 | 2295884 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1068 | 37.3203 | -119.5964 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Deteriorated | 23-0148125 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1898987 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 25386 | 20231219 | 1659 | 20231219 | 1832 | 2295956 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 465 | 37.9448 | -120.8971 | No | Clear;32-90 F |  |  | 23-0148149 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899011 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRIP-SAVER | 7056 | 20231219 | 1930 | 20231220 | 230 | 2296080 | 420 | Distribution Circuit | 3rd Party | Vehicle | 70 | 29400 | 37.3599 | -120.6868 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 23-0148159 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899024 | 0 | Non-EPSS | N | 2023 | NOENE
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 19703 | 20231219 | 2121 | 20231219 | 2345 | 2296122 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2736 | 37.2588 | -120.4407 | No | Overcast;32-90 F |  |  | 23-0148193 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899062 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320166527582 | 20231220 | 7 | 20231220 | 510 | 2296151 | 303 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 303 | 37.258 | -120.4436 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148196 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899065 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 23519 | 20231220 | 612 | 20231220 | 1030 | 2296468 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 258 | 36.8732 | -119.8538 | No | Overcast;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0148241 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899169 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | JUMPER | BLOWN OPEN JUMPER 1 POLE S/OF 9777 | 20231220 | 658 | 20231220 | 915 | 2296223 | 137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 685 | 37.1231 | -120.9846 | No | Overcast-Fog-Drizzle;32-90 F | Jumper | Burned Open | 23-0148221 | OH | Sus | 46096938 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899120 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | 319683432248 | 20231220 | 845 | 20231220 | 1034 | 2296338 | 109 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 654 | 37.3858 | -120.6098 | No | Partly Cloudy-Drizzle;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0148243 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899172 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | FUSE | 9719 | 20231220 | 854 | 20231220 | 919 | 2296350 | 25 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 434 | 37.0129 | -120.818 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0148227 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899144 | 1 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | JUMPER | OPEN JUMPER 2 POLES N/OF CGC# 318721445836 | 20231220 | 949 | 20231220 | 1220 | 2296330 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 151 | 37.7584 | -120.9435 | No | Overcast;32-90 F | Insulator | Failed/Faulted | 23-0148231 | OH | Sus | 46097114 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899153 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | TRANSFORMER | 318533548730 | 20231220 | 1119 | 20231220 | 1250 | 2296497 | 91 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 91 | 37.8371 | -121.0089 | No | Clear;32-90 F | Fuse | Broken | 23-0148262 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899192 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321871318190 | 20231220 | 1137 | 20231220 | 1818 | 2296492 | 401 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 1203 | 36.9981 | -119.8607 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148252 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899184 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 57215 | 20231220 | 1314 | 20231220 | 1520 | 2296589 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 252 | 36.733 | -120.3391 | No | Overcast-Drizzle;32-90 F |  |  | 23-0148288 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899223 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | OCB | 1101/2 | 20231220 | 1431 | 20231221 | 229 | 2296672 | 718 | Distribution Circuit | 3rd Party | Vehicle | 2677 | 391477 | 37.1208 | -120.2506 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0148283 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899218 | 0 | Non-EPSS | N | 2023 | B GRD
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | FUSE | 6954 | 20231220 | 1438 | 20231220 | 1454 | 2296655 | 16 | Distribution Circuit | 3rd Party | Vehicle | 2 | 32 | 36.844 | -120.1114 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0148281 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899216 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 25738 | 20231220 | 1548 | 20231221 | 213 | 2296806 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1345 | 37.7005 | -120.6963 | No | Overcast-Fog;32-90 F | Transformer (OH) | Burned/flashed | 23-0148303 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899240 | 1 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 25386 | 20231220 | 1615 | 20231220 | 1935 | 2296831 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 667 | 37.9448 | -120.8971 | No | Clear;32-90 F |  |  | 23-0148337 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899278 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1111 | 252421111 | RECLOSER | 279006 | 20231220 | 1930 | 20231221 | 339 | 2297053 | 489 | Distribution Circuit | 3rd Party | Vehicle | 94 | 2195 | 37.0982 | -120.3313 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 23-0148329 | OH | Sus | 35519128 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899280 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 5742 | 20231220 | 2124 | 20231221 | 1334 | 2297126 | 970 | Distribution Circuit | Animal | Other | 14 | 10720 | 36.8147 | -120.2053 | No | Overcast-Fog-Drizzle;32-90 F | Lightning Arrestor | Burned/flashed | 23-0148457 | OH | Sus | 46098553 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899440 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321620534025 | 20231220 | 2229 | 20231221 | 115 | 2297214 | 166 | Transformer only | Animal | Other | 1 | 166 | 37.4325 | -119.943 | No | Overcast-Fog;32-90 F | Fuse | Failed/Faulted | 23-0148408 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899364 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 321039520605 | 20231220 | 2231 | 20231220 | 2353 | 2297195 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 82 | 37.0653 | -120.1449 | No | Overcast-Fog;32-90 F | Fuse | Broken | 23-0148402 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899356 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 6452 | 20231220 | 2334 | 20231221 | 446 | 2297232 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 5367 | 37.0394 | -120.2566 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0148403 | OH | Sus | 31679959 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899359 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 25158 | 20231221 | 7 | 20231221 | 159 | 2297223 | 112 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4 | 444 | 36.7511 | -120.3872 | No | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 23-0148395 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899348 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6855 | 20231221 | 24 | 20231221 | 1129 | 2297265 | 665 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 12635 | 36.9894 | -120.0128 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0148413 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1899370 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 54727 | 20231221 | 427 | 20231221 | 632 | 2297330 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3125 | 37.7175 | -120.6184 | No | Clear;32-90 F |  |  | 23-0148432 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899392 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 6452 | 20231221 | 507 | 20231221 | 910 | 2297333 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 5346 | 37.0394 | -120.2566 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Broken | 23-0148450 | OH | Sus | 31680080 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899425 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 24387 | 20231221 | 1125 | 20231221 | 1212 | 2297698 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 47 | 37.2531 | -120.9652 | No | Partly Cloudy;32-90 F |  |  | 23-0148475 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899467 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 6165 | 20231221 | 1127 | 20231221 | 1545 | 2297641 | 258 | Distribution Circuit | 3rd Party | Vehicle | 207 | 53406 | 37.2004 | -119.7555 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0148472 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899460 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 1027 | 20231221 | 1329 | 20231221 | 1644 | 2297755 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1560 | 37.3473 | -121.015 | No | Clear;32-90 F |  |  | 23-0148513 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899510 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | SWITCH | 961347 | 20231221 | 1537 | 20231221 | 1705 | 2297763 | 88 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 88 | 37.1005 | -121.0125 | No | Overcast;32-90 F | Interrupter | Failed/Faulted | 23-0148504 | UG | Sus | 46098666 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899500 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 19763 | 20231221 | 1650 | 20231221 | 1756 | 2297939 | 66 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 176 | 37.3318 | -121.096 | No | Clear;32-90 F |  |  | 23-0148516 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899512 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319873029526 | 20231222 | 718 | 20231222 | 824 | 2298139 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 132 | 37.3116 | -120.5436 | No | Overcast-Fog;32-90 F | Fuse | Broken | 23-0148572 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899589 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | SWITCH | 5035 | 20231222 | 924 | 20231222 | 930 | 2298243 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 33 | 198 | 37.0553 | -120.2928 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Normal | 23-0148283 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1899619 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 19763 | 20231222 | 1454 | 20231222 | 1636 | 2298497 | 102 | Distribution Circuit | Animal | Bird found | 3 | 272 | 37.3318 | -121.096 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0148611 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899668 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | TRANSFORMER | 318948720534 | 20231223 | 314 | 20231223 | 758 | 2298663 | 284 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1136 | 37.0632 | -120.8609 | No | Partly Cloudy-Fog;32-90 F | Transformer | Normal | 23-0148645 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899706 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | FUSE | 2928 | 20231223 | 932 | 20231223 | 1046 | 2298716 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 4060 | 36.8519 | -120.451 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0148659 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899725 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | RECLOSER | 4470 | 20231223 | 2307 | 20231224 | 1106 | 2299000 | 719 | Distribution Circuit | 3rd Party | Vehicle | 100 | 29707 | 37.1862 | -120.6775 | No | Fog;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0148723 | OH | Sus | 31680220 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1899791 | 0 | Non-EPSS | N | 2023 | A- B- C
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | SWITCH | 5134 | 20231223 | 2331 | 20231224 | 753 | 2298984 | 502 | Distribution Circuit | 3rd Party | Vehicle | 29 | 14558 | 36.8647 | -120.074 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0148724 | OH | Sus | 35519640 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1899792 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 921 | 20231224 | 659 | 20231224 | 919 | 2299057 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 10500 | 38.0203 | -120.3351 | No | Partly Cloudy;32-90 F |  |  | 23-0148740 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899808 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 7509 | 20231224 | 820 | 20231224 | 1100 | s1899818 | 160 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 1280 | 37.2843 | -120.4741 | No | Clear;32-90 F |  |  | 23-0148738 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899818 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321439417911 | 20231224 | 1040 | 20231224 | 1158 | 2299122 | 78 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 156 | 36.9907 | -120.0081 | No | Clear;32-90 F | Fuse | Broken | 23-0148750 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899820 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7258 | 20231224 | 1535 | 20231224 | 1848 | 2299206 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2575 | 37.303 | -120.7908 | No | Clear;32-90 F |  |  | 23-0148772 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899844 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | T2000 | 20231226 | 923 | 20231226 | 1039 | 2299719 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 228 | 37.0112 | -120.112 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0148873 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1899982 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6852 | 20231226 | 1101 | 20231226 | 1134 | 2299816 | 33 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 286 | 37.04 | -120.0747 | No | Partly Cloudy;32-90 F |  |  | 23-0148876 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899993 | 1 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321988734875 | 20231226 | 1132 | 20231226 | 1626 | 2299847 | 294 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 1470 | 37.455 | -119.8168 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148895 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900012 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | FUSE | 888372 | 20231226 | 1304 | 20231226 | 1619 | 2300004 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1171 | 36.9751 | -120.3103 | No | Partly Cloudy;32-90 F |  |  | 23-0148909 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900028 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | TRANSFORMER | 100000034493 | 20231226 | 1353 | 20231226 | 1450 | 2299965 | 57 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 57 | 37.0793 | -120.1108 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0148902 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900021 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | OCB | 1103/2 | 20231226 | 1549 | 20231226 | 2055 | 2300053 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2636 | 213933 | 37.0663 | -120.836 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0148907 | OH | Sus | 46101247 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1900026 | 0 | Non-EPSS | N | 2023 | C- GRD & TIME OC
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | TRANSFORMER | 321382216644 | 20231226 | 1837 | 20231226 | 1918 | 2300143 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 36.9561 | -120.028 | No | Clear;32-90 F | Fuse | Broken | 23-0148918 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900035 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | NEWMAN-1106 | 162741106 | FUSE | 21781 | 20231226 | 2119 | 20231226 | 2128 | 2300219 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 42 | 378 | 37.1467 | -120.8239 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0148907 | OH | Sus | 46101247 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1900060 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320226021734 | 20231227 | 828 | 20231227 | 1011 | 2300461 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 103 | 37.097 | -120.4237 | No | Overcast;32-90 F | Fuse | Broken | 23-0148985 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900153 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | MTR#1010075472 | 20231227 | 833 | 20231227 | 945 | 2300468 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 72 | 37.0616 | -120.3735 | No | Overcast;32-90 F | Fuse | Broken | 23-0148982 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900148 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRANSFORMER | 322610529195 | 20231227 | 838 | 20231227 | 945 | 2300579 | 67 | Transformer only | 3rd Party | Vehicle | 1 | 67 | 37.2985 | -119.6041 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0148984 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1900152 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | JUMPER | 320068828132 | 20231227 | 958 | 20231227 | 1144 | 2300559 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 2426 | 37.2733 | -120.4753 | No | Clear;32-90 F | Jumper | Broken | 23-0148988 | OH | Sus | 46101849 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1900156 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | TRANSFORMER | 415110055414 | 20231227 | 1327 | 20231227 | 1732 | 2300747 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 245 | 36.8435 | -120.6718 | No | Overcast;32-90 F | Fuse | Broken | 23-0149038 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900211 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 5607 | 20231227 | 1400 | 20231227 | 1509 | 2300758 | 69 | Distribution Circuit | 3rd Party | Vehicle | 56 | 3864 | 37.7889 | -120.7975 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0149024 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900195 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318676744727 | 20231227 | 1927 | 20231227 | 1948 | 2300952 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 42 | 37.7275 | -120.9584 | No | Partly Cloudy-Rain;32-90 F | Secondary | Broken | 23-0149046 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1900220 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 6453 | 20231227 | 1934 | 20231227 | 2150 | 2300964 | 136 | Distribution Circuit | Environmental/External | Lightning | 7 | 952 | 37.04 | -120.2205 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149048 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900226 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 320818319408 | 20231227 | 1934 | 20231228 | 456 | 2300985 | 562 | Transformer only | Environmental/External | Lightning | 1 | 562 | 37.0324 | -120.2205 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149048 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900249 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 320819019576 | 20231227 | 1934 | 20231228 | 258 | 2300986 | 444 | Transformer only | Environmental/External | Lightning | 1 | 444 | 37.0375 | -120.2204 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149048 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900250 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | SECTIONALIZER | 11990 | 20231228 | 614 | 20231228 | 1023 | 2301035 | 249 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 4980 | 36.8809 | -120.6722 | No | Partly Cloudy-Fog;32-90 F | Woodpin | Broken | 23-0149097 | OH | Sus | 31680484 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900335 | 0 | EPSS Ckt | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 318862544275 | 20231228 | 809 | 20231228 | 822 | 2301063 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 13 | 37.7154 | -120.894 | No | Partly Cloudy-Fog;32-90 F | Fuse | Broken | 23-0149090 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900281 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 30131 | 20231228 | 843 | 20231228 | 854 | 2301103 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 132 | 37.0037 | -120.1932 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0149091 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900287 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 7552 | 20231228 | 1052 | 20231228 | 1146 | 2301277 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 270 | 37.1199 | -120.4285 | No | Partly Cloudy;32-90 F |  |  | 23-0149107 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900349 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318554547580 | 20231228 | 1538 | 20231228 | 1545 | 2301462 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 28 | 37.8058 | -121.0014 | No | Partly Cloudy;32-90 F | Insulator | Arcing | 23-0149121 | OH | Sus | 46102803 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900379 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317967638032 | 20231228 | 2310 | 20231229 | 104 | 2301644 | 114 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 114 | 37.5423 | -121.2022 | No | Clear;32-90 F | Connector or Splice (OH) | Contaminated | 23-0149174 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900434 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1102 | 254421102 | TRANSFORMER | 322517030100 | 20231229 | 832 | 20231229 | 1100 | 2301737 | 148 | Transformer only | Animal | Other | 1 | 148 | 37.3234 | -119.6345 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0149191 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900456 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | OAKHURST-1102 | 254421102 | TRANSFORMER | 322521330085 | 20231229 | 839 | 20231229 | 1059 | 2301736 | 140 | Transformer only | Animal | Other | 1 | 140 | 37.3232 | -119.6338 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0149190 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900455 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 4832 | 20231229 | 906 | 20231229 | 938 | 2301773 | 32 | Distribution Circuit | Animal | Bird found | 2 | 64 | 37.2806 | -120.4403 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0149194 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900479 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | OTHER | S1813 | 20231229 | 1315 | 20231229 | 1514 | 2302000 | 119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 7195 | 37.8151 | -120.8949 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149230 | OH | Sus | 46106406 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | Yes | Yes | 1900527 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 11803 | 20231229 | 1336 | 20231229 | 1430 | 2302021 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 108 | 36.928 | -120.4647 | No | Overcast;32-90 F |  |  | 23-0149238 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900536 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | TRANSFORMER | 322895527569 | 20231229 | 1413 | 20231229 | 1514 | 2302045 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 122 | 37.2555 | -119.506 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 23-0149233 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900531 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | TRANSFORMER | 322929527120 | 20231229 | 1547 | 20231229 | 1556 | 2302110 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 9 | 37.2432 | -119.4935 | No | Overcast;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0149248 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900545 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 911059 | 20231230 | 449 | 20231230 | 1655 | 2302418 | 726 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 4258 | 37.1267 | -120.1072 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0149317 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900618 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 4913 | 20231230 | 638 | 20231230 | 748 | 2302443 | 70 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 327 | 37.3866 | -120.7597 | No | Clear;32-90 F |  |  | 23-0149322 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900624 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | TRANSFORMER | 319331614217 | 20231230 | 737 | 20231230 | 1223 | 2302470 | 286 | Transformer only | Vegetation | Tree - palm frond fell into line | 3 | 858 | 36.8901 | -120.7298 | No | Overcast-Fog-Drizzle;32-90 F | Cutout- fuse holder | Arcing | 23-0149342 | OH | Sus | 31680560 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900651 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322312026191 | 20231230 | 904 | 20231230 | 940 | 2302529 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 144 | 37.2168 | -119.7066 | No | Overcast-Fog-Drizzle;32-90 F | Secondary | Deteriorated | 23-0149329 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900637 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322160524725 | 20231230 | 1015 | 20231230 | 1045 | 2302628 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 60 | 37.1769 | -119.7578 | No | Overcast-Fog-Drizzle;32-90 F | Secondary | Deteriorated | 23-0149350 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1900659 | 0 | EPSS Ckt | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 58637 | 20231230 | 1123 | 20231230 | 1220 | 2302708 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 190 | 37.3603 | -120.6822 | No | Partly Cloudy;32-90 F |  |  | 23-0149368 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900677 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 5598 | 20231230 | 1233 | 20231230 | 1627 | 2302772 | 234 | Distribution Circuit | 3rd Party | Vehicle | 12 | 2808 | 37.0908 | -120.291 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 23-0149367 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1900676 | 0 | Non-EPSS | N | 2023
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 26922 | 20231230 | 1246 | 20231230 | 1400 | 2302790 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 1554 | 37.3473 | -121.0359 | No | Clear;32-90 F |  |  | 23-0149378 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1900690 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7258 | 20231230 | 1253 | 20231230 | 1323 | 2302797 | 30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 400 | 37.303 | -120.7908 | No | Partly Cloudy;32-90 F |  |  | 23-0149377 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900689 | 1 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318790630934 | 20231230 | 2220 | 20231231 | 415 | 2303052 | 355 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 355 | 37.3462 | -120.9184 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0149444 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900759 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 57215 | 20231231 | 928 | 20231231 | 1149 | 2303156 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 423 | 36.733 | -120.3391 | No | Overcast-Fog;32-90 F |  |  | 23-0149472 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1900792 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | JUMPER | OJS | 20231231 | 1046 | 20231231 | 1504 | 2303237 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 5016 | 37.3044 | -120.795 | No | Clear;32-90 F | Jumper | Burned Open | 23-0149483 | OH | Sus | 46122463 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1900803 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319568026796 | 20231231 | 1130 | 20231231 | 1457 | 2303207 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 414 | 37.236 | -120.6493 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149474 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1900794 | 0 | Non-EPSS | N | 2023
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | RECLOSER | 73322 | 20231231 | 2216 | 20231231 | 2311 | 2303366 | 55 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 181 | 9955 | 37.2954 | -120.4434 | No | Fog;32-90 F |  |  | 23-0149513 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1900834 | 0 | Non-EPSS | N | 2023 | N/A
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | OTHER | BROKEN WIRE | 20240101 | 507 | 20240101 | 931 | 2304118 | 264 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1423 | 37.3926 | -120.7597 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken | 24-0005753 | OH | Sus | 31680686 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1900865 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 19689 | 20240101 | 654 | 20240101 | 1006 | 2304131 | 192 | Distribution Circuit | Animal | Bird found | 5 | 960 | 37.9372 | -120.3842 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0005772 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1900878 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1945 | 20240101 | 807 | 20240101 | 1226 | 2304147 | 259 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 10101 | 37.8518 | -120.1648 | No | Partly Cloudy;32-90 F |  |  | 24-0005783 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1900888 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 3773 | 20240101 | 1629 | 20240101 | 1755 | 2304368 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 975 | 36.9623 | -120.8898 | No | Clear;32-90 F |  |  | 24-0005815 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1900916 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7547 | 20240101 | 2051 | 20240101 | 2150 | 2304413 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1338 | 37.3347 | -120.8477 | No | Clear;32-90 F |  |  | 24-0005840 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1900941 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318472548355 | 20240102 | 746 | 20240102 | 835 | 2304540 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 196 | 37.8269 | -121.0298 | No | Overcast-Fog;32-90 F | Fuse | Burned Open | 24-0005904 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1900979 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | RECLOSER | 10800 | 20240102 | 756 | 20240102 | 1055 | 2304548 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1826 | 276143 | 37.2974 | -121.0128 | No | Overcast-Fog;32-90 F | Lightning Arrestor | Broken- wire on object | 24-0005886 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1900962 | 0 | Non-EPSS | N | 2024 | C PH & GRD
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | TRANSFORMER | 321274611894 | 20240102 | 935 | 20240102 | 1000 | 2304680 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 100 | 36.8269 | -120.0651 | No | Clear;32-90 F | Fuse | Broken | 24-0005944 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901039 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 41506 | 20240102 | 1252 | 20240102 | 1433 | 2304911 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 909 | 37.8495 | -120.8806 | No | Clear;32-90 F |  |  | 24-0006086 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901085 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | SWITCH | 22684 | 20240102 | 2111 | 20240102 | 2202 | 2305481 | 51 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2636 | 66576 | 37.0999 | -120.8605 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0005911 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1901159 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | RECLOSER | 787210 | 20240102 | 2130 | 20240102 | 2345 | 2305494 | 135 | Distribution Circuit | Animal | Other | 154 | 20790 | 36.8585 | -120.4219 | No | Overcast-Drizzle;32-90 F | Recloser | Burned/flashed | 24-0006267 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | No | No | 1901163 | 0 | Non-EPSS | N | 2024 | A- B- C
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 44555 | 20240102 | 2135 | 20240102 | 2324 | 2305495 | 109 | Distribution Circuit | Animal | Bird found | 5 | 545 | 37.9697 | -120.331 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Normal | 24-0006287 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901184 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10466 | 20240102 | 2210 | 20240102 | 2347 | 2305519 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 485 | 37.5129 | -119.8294 | No | Overcast-Rain;32-90 F |  |  | 24-0006285 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901182 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 5583 | 20240103 | 241 | 20240103 | 507 | 2305680 | 146 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 81 | 11826 | 37.3195 | -119.5001 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0006310 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901210 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | JUMPER | OJ 4 POLES SE/OF MTR#1005007157 | 20240103 | 905 | 20240103 | 1032 | 2306162 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 696 | 37.6644 | -120.3322 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Deteriorated | 24-0006454 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1901343 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 361811 | 20240103 | 1102 | 20240103 | 1145 | 2306311 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 172 | 38.0021 | -120.398 | No | Overcast;32-90 F |  |  | 24-0006474 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901350 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 667249 | 20240103 | 1212 | 20240103 | 1341 | 2306382 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 712 | 36.8508 | -119.9832 | No | Clear;32-90 F | Secondary | Broken | 24-0006532 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901374 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 6026 | 20240103 | 1405 | 20240103 | 1639 | 2306486 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1078 | 37.1301 | -120.3202 | No | Partly Cloudy;32-90 F |  |  | 24-0006617 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901397 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | TRANSFORMER | 322889326620 | 20240103 | 1417 | 20240103 | 1645 | 2306430 | 148 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1924 | 37.2289 | -119.5084 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0006504 | OH | Sus | 31680616 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1901358 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | FUSE | 3285 | 20240103 | 1619 | 20240103 | 2055 | 2306594 | 276 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 3036 | 37.1536 | -121.0791 | No | Partly Cloudy;32-90 F |  |  | 24-0006647 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901412 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 21096 | 20240104 | 802 | 20240104 | 854 | 2306818 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 312 | 37.2742 | -120.5603 | No | Overcast-Fog;32-90 F |  |  | 24-0006743 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901498 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | JUMPER | 7554 | 20240104 | 816 | 20240104 | 1205 | 2306836 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 687 | 37.3025 | -120.7879 | No | Partly Cloudy-Fog;32-90 F | Jumper | Burned Open | 24-0006768 | OH | Sus | 46129299 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1901539 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 19693 | 20240104 | 1022 | 20240104 | 1240 | 2307097 | 138 | Distribution Circuit | Animal | Bird found | 5 | 690 | 37.9371 | -120.3796 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0006865 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901604 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | TRANSFORMER | 318580023056 | 20240104 | 1523 | 20240104 | 2031 | 2307278 | 308 | Transformer only | 3rd Party | Customer Equipment | 1 | 308 | 37.1319 | -120.9874 | No | Fog;32-90 F | Customer Equipment | Burned Open | 24-0007136 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901691 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 21102 | 20240104 | 1546 | 20240104 | 1632 | 2307306 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 92 | 37.3043 | -120.7735 | No | Clear;32-90 F |  |  | 24-0007069 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901646 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 19088 | 20240104 | 1605 | 20240104 | 1720 | 2307329 | 75 | Distribution Circuit | Animal | Other | 2 | 150 | 37.3279 | -120.8666 | No | Clear;32-90 F | Anchor or Guy | Normal | 24-0007081 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901651 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321855518588 | 20240104 | 1742 | 20240104 | 2150 | 2307404 | 248 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 496 | 37.0093 | -119.8654 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0007138 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901692 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | TRANSFORMER | T278 | 20240104 | 2231 | 20240104 | 2320 | 2307495 | 49 | Transformer only | Equipment Failure/Involved | Underground | 10 | 490 | 37.7563 | -120.863 | No | Partly Cloudy-Fog;32-90 F | Secondary | Broken | 24-0007141 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1901694 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 361811 | 20240105 | 1635 | 20240105 | 1745 | 2308130 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 280 | 38.0021 | -120.398 | No | Clear;32-90 F |  |  | 24-0007495 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1901891 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | OCB | 1105/2 | 20240105 | 2102 | 20240106 | 649 | 2308236 | 587 | Distribution Circuit | Equipment Failure/Involved | Overhead | 924 | 337589 | 37.3635 | -120.7606 | No | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0007532 | OH | Sus | 31681090 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1901919 | 0 | Non-EPSS | N | 2024 | B - GRD- TIME OC
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 473349 | 20240106 | 709 | 20240106 | 1230 | 2308400 | 321 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 963 | 37.2584 | -120.402 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0007570 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1901961 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1101 | 162671101 | OCB | 1101/2 | 20240106 | 733 | 20240106 | 852 | 2308408 | 79 | Distribution Circuit | 3rd Party | Vehicle | 639 | 50481 | 37.5792 | -121.2056 | No | Overcast;32-90 F | Anchor or Guy | Broken | 24-0007564 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | No | No | 1901947 | 0 | EPSS Ckt | N | 2024 | A- B- C
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | FUSE | 34368 | 20240106 | 1100 | 20240106 | 1459 | 2308595 | 239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 239 | 36.8364 | -120.1376 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0007600 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1901990 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 76907 | 20240106 | 1609 | 20240106 | 1724 | 2308878 | 75 | Distribution Circuit | Animal | Bird found | 50 | 3750 | 36.9702 | -120.0585 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0007669 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1902040 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320505028973 | 20240107 | 408 | 20240107 | 951 | 2309078 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1029 | 37.295 | -120.3257 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0007727 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902101 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7546 | 20240107 | 715 | 20240107 | 836 | 2309104 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 3321 | 37.3132 | -120.841 | No | Clear;32-90 F |  |  | 24-0007739 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1902113 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | S787 | 20240107 | 1114 | 20240107 | 1209 | 2309192 | 55 | Distribution Circuit | Animal | Bird found | 58 | 3190 | 37.7743 | -120.8544 | No | Clear;32-90 F | Fuse | Normal | 24-0007754 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902123 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320503342852 | 20240107 | 1711 | 20240107 | 1722 | 2309278 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 22 | 37.6788 | -120.3263 | No | Clear;32-90 F | Fuse | Broken | 24-0007777 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902139 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319882530259 | 20240108 | 946 | 20240108 | 1003 | 2309608 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 68 | 37.3316 | -120.5401 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0007914 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902338 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 5675 | 20240108 | 1100 | 20240108 | 1216 | 2309778 | 76 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 37 | 2812 | 37.2321 | -119.7418 | No | Clear;32-90 F |  |  | 24-0008006 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1902377 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320551728730 | 20240108 | 1126 | 20240108 | 1558 | 2309810 | 272 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 544 | 37.288 | -120.3103 | No | Clear;32-90 F | Secondary | Broken | 24-0007978 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902367 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | SWITCH | 890679 | 20240108 | 1217 | 20240108 | 1558 | 2309813 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 221 | 37.288 | -120.319 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0008002 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902376 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | INTERRUPTER | 558890 | 20240108 | 1238 | 20240108 | 1339 | 2309872 | 61 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 61 | 36.8516 | -119.9512 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0007957 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902382 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1116 | 252761116 | FUSE | 6553 | 20240108 | 1500 | 20240108 | 2150 | 2310034 | 410 | Distribution Circuit | 3rd Party | Vehicle | 5 | 710 | 36.8985 | -120.0195 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0008164 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1902414 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | JUMPER | EAST PH BURNT OPEN JMPR | 20240108 | 1536 | 20240108 | 1946 | 2310191 | 250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2500 | 37.0714 | -120.9804 | No | Clear;32-90 F | Jumper | Burned Open | 24-0008215 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1902430 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 5905 | 20240108 | 1632 | 20240108 | 2147 | 2310116 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1579 | 36.9524 | -120.3522 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0008213 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | No | No | 1902428 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319296721800 | 20240109 | 1045 | 20240109 | 1227 | 2310697 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 102 | 37.0983 | -120.7396 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0008465 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902674 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321596334449 | 20240109 | 1055 | 20240109 | 1115 | 2310731 | 20 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 40 | 37.4447 | -119.9506 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0008397 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902658 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319360744102 | 20240109 | 1142 | 20240109 | 1440 | 2310779 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 356 | 37.711 | -120.7218 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0008484 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902685 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 6698 | 20240109 | 1142 | 20240109 | 1635 | 2310783 | 293 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1172 | 36.8583 | -120.2914 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0008429 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1902668 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 13156 | 20240109 | 1222 | 20240109 | 2306 | 2310820 | 644 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1932 | 37.0159 | -120.0012 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 24-0008511 | OH | Sus | 31681187 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1902689 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20240109 | 1625 | 20240110 | 325 | 2311044 | 594 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 11220 | 37.1863 | -120.6348 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0008691 | OH | Sus | 46135580 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1902718 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 319019630736 | 20240109 | 1720 | 20240109 | 1857 | 2311072 | 97 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 291 | 37.342 | -120.838 | No | Clear;32-90 F | Fuse | Broken | 24-0008696 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902721 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | FUSE | 11857 | 20240109 | 2308 | 20240110 | 131 | 2311265 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 2671 | 37.4453 | -120.4306 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0008747 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1902773 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 81675 | 20240110 | 1219 | 20240110 | 1316 | 2311784 | 57 | Distribution Circuit | Animal | Other | 1 | 57 | 36.8526 | -119.8227 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0009062 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903019 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | TRANSFORMER | 319932719667 | 20240110 | 1540 | 20240110 | 1651 | 2311840 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 213 | 37.0403 | -120.5251 | No | Overcast-Drizzle;32-90 F | Secondary | Deteriorated | 24-0009110 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903030 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | L1707 | 20240110 | 2102 | 20240110 | 2210 | 2312391 | 68 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 1904 | 38.1872 | -120.0021 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0009347 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903108 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | RECLOSER | 257152 | 20240111 | 2 | 20240111 | 252 | 2312518 | 170 | Distribution Circuit | Animal | Other | 38 | 6460 | 37.1634 | -120.1016 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0009373 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903128 | 0 | EPSS Ckt | N | 2024 | AB
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | FUSE | 5591 | 20240111 | 34 | 20240111 | 915 | 2312529 | 521 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 85 | 44285 | 37.0287 | -119.7252 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0009406 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903158 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20240111 | 718 | 20240111 | 1237 | 2312657 | 319 | Distribution Circuit | 3rd Party | Vehicle | 196 | 58495 | 37.8998 | -120.4541 | No | Overcast-Fog-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0009431 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903174 | 0 | EPSS Ckt | N | 2024 | B- C- TIME
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | TRANSFORMER | 415330851156 | 20240111 | 1032 | 20240111 | 1152 | 2312960 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 80 | 36.728 | -120.5942 | No | Overcast-Strong Winds;32-90 F | Fuse | Broken | 24-0009642 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903375 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318552946390 | 20240111 | 1045 | 20240111 | 1127 | 2312979 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 42 | 37.7731 | -121.0015 | No | Overcast-Strong Winds;32-90 F | Fuse | Broken | 24-0009643 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903376 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 6529 | 20240111 | 1120 | 20240111 | 1151 | 2313007 | 31 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 31 | 37.0432 | -120.166 | No | Overcast-Strong Winds;32-90 F | Circuit Breaker | Malfunctioning | 24-0009623 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903369 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | 20357 | 20240111 | 1140 | 20240111 | 1606 | 2313026 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 532 | 38.1819 | -120.0094 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0009738 | OH | Sus | 46147224 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903396 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | JUMPER | TSB 1 SPAN LD SIDE OF CGC# 322616331511 | 20240111 | 1201 | 20240111 | 1552 | 2312852 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2541 | 37.3629 | -119.5996 | No | Overcast-Strong Winds;32-90 F | Pole-Wood | Deteriorated | 24-0009525 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903303 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 7623 | 20240111 | 1716 | 20240111 | 2100 | 2313263 | 224 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 818 | 37.3403 | -120.6033 | No | Overcast-Strong Winds;32-90 F | Transformer (UG) | Leaking | 24-0009707 | UG | Sus | 35523075 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903420 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | OTHER | WIRE DOWN S/OF 3485 | 20240111 | 1839 | 20240111 | 2251 | 2313347 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 8064 | 36.6779 | -120.6217 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0009907 | OH | Sus | 46147416 | CENTRAL VALLEY | JAN | Force Out | 0 | No | Yes | No | 1903424 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 714513 | 20240111 | 1913 | 20240111 | 2247 | 2313329 | 214 | Distribution Circuit | Animal | Other | 5 | 1070 | 37.0544 | -120.496 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0009953 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903459 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 343 | 20240111 | 2047 | 20240111 | 2239 | 2313366 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 8176 | 37.3335 | -121.0041 | No | Clear;32-90 F |  |  | 24-0009943 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903452 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | FUSE | 4666 | 20240112 | 50 | 20240112 | 114 | 2313431 | 24 | Distribution Circuit | 3rd Party | Vandalism | 2 | 48 | 37.306 | -120.4928 | No | Overcast-Strong Winds;32-90 F | Secondary | Broken | 24-0009962 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903464 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 4320 | 20240112 | 724 | 20240112 | 1132 | 2313531 | 248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 11218 | 37.2283 | -120.4881 | No | Partly Cloudy;32-90 F | Insulator | Broken- wire on ground | 24-0010001 | OH | Sus | 31681555 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1903481 | 0 | Non-EPSS | N | 2024 | B- GROUND
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319654537635 | 20240112 | 1328 | 20240112 | 1728 | 2313996 | 240 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 240 | 37.5334 | -120.62 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0010284 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903675 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 7919 | 20240112 | 2308 | 20240113 | 26 | 2314391 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 546 | 37.1003 | -120.5583 | No | Partly Cloudy;32-90 F |  |  | 24-0010378 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903720 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10948 | 20240113 | 713 | 20240113 | 827 | 2314458 | 74 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 46 | 3404 | 37.5608 | -119.9664 | No | Overcast-Rain;32-90 F |  |  | 24-0010415 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903746 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 21035 | 20240113 | 917 | 20240113 | 1008 | 2314551 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 374 | 37.3671 | -120.6502 | No | Overcast;32-90 F |  |  | 24-0010437 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903777 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 6715 | 20240113 | 1314 | 20240113 | 1440 | 2314695 | 86 | Distribution Circuit | Animal | Bird found | 5 | 430 | 36.8656 | -120.1665 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0010496 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903808 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 91331 | 20240113 | 1702 | 20240113 | 1828 | 2314928 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 115 | 37.0797 | -120.1658 | No | Partly Cloudy;32-90 F |  |  | 24-0010547 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903838 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7619 | 20240114 | 35 | 20240114 | 134 | 2315151 | 59 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 452 | 37.5364 | -120.6272 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0010637 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903931 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318925530774 | 20240114 | 248 | 20240114 | 355 | 2315188 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 134 | 37.3422 | -120.8722 | No | Clear;32-90 F | Fuse | Burned Open | 24-0010643 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903938 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10338 | 20240114 | 852 | 20240114 | 1402 | 2315249 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 6200 | 37.2814 | -119.6699 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Together | 24-0010669 | OH | Sus | 46153485 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903963 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | T14239 | 20240114 | 1234 | 20240114 | 1419 | 2315387 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1365 | 37.0474 | -120.8759 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0010700 | OH | Sus | 31681821 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903979 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | TRANSFORMER | 320222326101 | 20240115 | 1440 | 20240115 | 1520 | 2315868 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 80 | 37.2178 | -120.425 | No | Overcast;32-90 F | Secondary | Broken | 24-0010811 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904068 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320761156455 | 20240115 | 1703 | 20240115 | 2038 | 2315975 | 215 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 215 | 38.0509 | -120.2366 | No | Partly Cloudy;32-90 F |  |  | 24-0010833 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1904083 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | TRANSFORMER | T0305 | 20240115 | 2035 | 20240116 | 758 | 2316047 | 683 | Distribution Circuit | Equipment Failure/Involved | Underground | 323 | 24234 | 37.3222 | -120.499 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0010852 | UG | Sus | 35523874 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904106 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320218853151 | 20240116 | 632 | 20240116 | 723 | 2316079 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 102 | 37.9598 | -120.4251 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0010878 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904121 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | JUMPER | OJ AT MTR #1004591380 | 20240116 | 925 | 20240116 | 1203 | 2316326 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 592 | 83225 | 37.2602 | -120.9959 | No | Partly Cloudy-Fog;32-90 F | Jumper | Broken | 24-0010949 | OH | Sus | 46155778 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904261 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2481 | 20240116 | 1124 | 20240116 | 1213 | 2316485 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 2695 | 38.0325 | -120.2248 | No | Overcast;32-90 F |  |  | 24-0011059 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1904304 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | T9317 | 20240116 | 1836 | 20240116 | 1851 | 2316853 | 15 | Transformer only | Equipment Failure/Involved | Underground | 15 | 225 | 37.7714 | -120.826 | No | Overcast-Fog;32-90 F | Secondary | Broken | 24-0011303 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1904366 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | OCB | 1705/2 | 20240116 | 2359 | 20240117 | 959 | 2317176 | 600 | Distribution Circuit | Animal | Other | 2222 | 595817 | 37.9035 | -120.4971 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0011395 | OH | Sus | 35524091 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1904432 | 0 | EPSS Ckt | N | 2024 | ABC
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | FUSE | 544633 | 20240117 | 214 | 20240117 | 607 | 2317210 | 233 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 7149 | 37.3184 | -121.0303 | No | Overcast;32-90 F | Elbow | Normal | 24-0011416 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904439 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | TRANSFORMER | T4890 | 20240117 | 305 | 20240117 | 1040 | 2317239 | 455 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 521 | 37.1569 | -120.2671 | No | Overcast-Fog;32-90 F | Fuse | Normal | 24-0011543 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904606 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | FUSE | 544633 | 20240117 | 814 | 20240117 | 955 | 2317301 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 3099 | 37.3184 | -121.0303 | No | Clear;32-90 F |  |  | 24-0011536 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904601 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | S1319 | 20240117 | 1138 | 20240117 | 1242 | 2317623 | 64 | Distribution Circuit | 3rd Party | Vehicle | 157 | 10048 | 37.2457 | -121.0058 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 24-0011648 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | No | No | 1904646 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321930736658 | 20240117 | 1334 | 20240117 | 1600 | 2317680 | 146 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 292 | 37.5072 | -119.8354 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0011730 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904656 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 525123 | 20240117 | 1542 | 20240117 | 1901 | 2317893 | 199 | Distribution Circuit | 3rd Party | Vehicle | 4 | 796 | 37.2536 | -120.9979 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0011794 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1904666 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | TRANSFORMER | 320096828958 | 20240117 | 2310 | 20240118 | 34 | 2318130 | 84 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 840 | 37.2958 | -120.4665 | No | Fog;32-90 F |  |  | 24-0011939 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1904718 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320398022312 | 20240118 | 715 | 20240118 | 841 | 2318201 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 86 | 37.1126 | -120.3636 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0012016 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904759 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | RECLOSER | 9910 | 20240118 | 718 | 20240118 | 1226 | 2318205 | 308 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 553 | 56730 | 36.9918 | -120.6355 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0011974 | OH | Sus | 31681971 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1904732 | 0 | Non-EPSS | N | 2024 | GRD
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 2379 | 20240118 | 810 | 20240118 | 850 | 2318243 | 40 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 213 | 37.8278 | -121.0396 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0012023 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904765 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | TRANSFORMER | T428992 | 20240118 | 815 | 20240118 | 904 | 2318246 | 49 | Transformer only | Equipment Failure/Involved | Underground | 1 | 49 | 37.0476 | -120.8481 | No | Partly Cloudy-Fog;32-90 F | Fuse | Failed/Faulted | 24-0012044 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904789 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | MTR#1010282032 | 20240118 | 927 | 20240118 | 1149 | 2318324 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 142 | 36.8978 | -120.5435 | No | Overcast-Fog;32-90 F | Fuse | Burned Open | 24-0012170 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1904825 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 41891 | 20240118 | 1451 | 20240118 | 1807 | 2318577 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 196 | 37.2292 | -120.7796 | No | Overcast;32-90 F | Insulator | Broken | 24-0012268 | OH | Sus | 46164766 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1904847 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | SWITCH | 2979 | 20240118 | 1620 | 20240118 | 1748 | 2318628 | 88 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 1771 | 37.3513 | -120.5846 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0012167 | UG | Sus | 35524543 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1904855 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | TRANSFORMER | 320086129092 | 20240119 | 755 | 20240119 | 855 | 2318830 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 1140 | 37.2995 | -120.4697 | No | Clear;32-90 F | Secondary | Broken | 24-0012470 | OH | Sus | 46164881 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1904928 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | FUSE | 1927 | 20240119 | 910 | 20240119 | 1105 | 2319030 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 380 | 37.7973 | -121.0703 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0012536 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905051 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | OTHER | J10194 TWD T4573 | 20240119 | 1050 | 20240119 | 1217 | 2319111 | 87 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 1392 | 37.3533 | -120.5815 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0012491 | UG | Sus | 35524847 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905072 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 11737 | 20240119 | 1235 | 20240119 | 1347 | 2319173 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 144 | 37.5158 | -120.3648 | No | Clear;32-90 F |  |  | 24-0012690 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905111 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320590550575 | 20240119 | 1336 | 20240119 | 1819 | 2319214 | 283 | Transformer only | Equipment Failure/Involved | Underground | 1 | 283 | 37.8874 | -120.2967 | No | Overcast;32-90 F | Secondary | Broken | 24-0012777 | UG | Sus | 46166004 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905126 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 3888 | 20240120 | 11 | 20240120 | 715 | 2319507 | 424 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1414 | 36.6778 | -120.6624 | No | Partly Cloudy;32-90 F |  |  | 24-0012874 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905202 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | FUSE | 544633 | 20240120 | 36 | 20240120 | 931 | 2319511 | 535 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 11336 | 37.3184 | -121.0303 | No | Overcast-Drizzle;32-90 F | Elbow | Burned/flashed | 24-0012853 | UG | Sus | 46165996 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905190 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319084946240 | 20240120 | 800 | 20240120 | 1549 | 2319955 | 469 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 3752 | 37.7699 | -120.8176 | No | Overcast-Drizzle;32-90 F | Secondary | Burned Open | 24-0012969 | OH | Sus | 46166310 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905265 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | S721 | 20240120 | 853 | 20240120 | 1432 | 2319780 | 339 | Distribution Circuit | Animal | Bird found | 15 | 3437 | 37.7256 | -120.7885 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0012920 | OH | Sus | 46165999 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1905250 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 2052 | 20240120 | 2245 | 20240121 | 1500 | 2320485 | 975 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 2925 | 36.8584 | -120.3917 | No | Partly Cloudy;32-90 F |  |  | 24-0013114 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905369 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321648036719 | 20240121 | 11 | 20240121 | 845 | 2320268 | 514 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 514 | 37.5068 | -119.9322 | No | Overcast-Fog;32-90 F | Transformer (OH) | Broken | 24-0013050 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905320 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | TRANSFORMER | 318379029790 | 20240121 | 813 | 20240121 | 1509 | 2320319 | 416 | Distribution Circuit | Environmental/External | Lightning | 2 | 832 | 37.3169 | -121.0586 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0013076 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905343 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1647 | 20240121 | 1004 | 20240121 | 1921 | 2320383 | 557 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 5794 | 37.8209 | -120.7041 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0013083 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905347 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318352829848 | 20240121 | 1123 | 20240121 | 1604 | 2320409 | 281 | Transformer only | Environmental/External | Lightning | 1 | 281 | 37.3184 | -121.0675 | No | Overcast;32-90 F | Other | Failed/Faulted | 24-0013090 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905354 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | RECLOSER | 191286 | 20240121 | 1315 | 20240121 | 1912 | 2320436 | 357 | Distribution Circuit | 3rd Party | Vehicle | 92 | 32844 | 36.9744 | -120.0138 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0013101 | OH | Sus | 35525381 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905363 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7676 | 20240121 | 2053 | 20240121 | 2323 | 2320697 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1200 | 37.3244 | -120.3201 | No | Clear;32-90 F |  |  | 24-0013158 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905407 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 21427 | 20240121 | 2135 | 20240122 | 236 | 2320702 | 301 | Distribution Circuit | 3rd Party | Vehicle | 7 | 2059 | 37.9468 | -120.2705 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 24-0013151 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905401 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20240122 | 25 | 20240122 | 151 | 2320812 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 261 | 22446 | 37.0552 | -120.0295 | No | Overcast-Rain;32-90 F |  |  | 24-0013174 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905422 | 0 | EPSS Ckt | N | 2024 | A AND B
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20240122 | 208 | 20240125 | 1112 | 2320853 | 4864 | Distribution Circuit | Animal | Other | 261 | 17964 | 37.0552 | -120.0295 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0013180 | OH | Sus | 35525385 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905428 | 0 | EPSS Ckt | N | 2024 | B AND GROUND
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | FUSE | 9972 | 20240122 | 214 | 20240122 | 1430 | 2320856 | 736 | Distribution Circuit | Equipment Failure/Involved | Underground | 322 | 95627 | 37.0586 | -120.8222 | No | Overcast-Fog-Rain;32-90 F | Elbow | Broken | 24-0013193 | UG | Sus | 46166455 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905442 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320536928975 | 20240122 | 228 | 20240122 | 607 | 2320822 | 219 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 876 | 37.295 | -120.315 | No | Clear;32-90 F | Anchor or Guy | Deteriorated | 24-0013183 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905432 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | OTHER | WIRE DOWN 2 NW/OF 2439 | 20240122 | 710 | 20240122 | 1047 | 2320981 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 7926 | 38.0221 | -120.2723 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0013253 | OH | Sus | 46170220 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | Yes | 1905472 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | T9524 | 20240122 | 811 | 20240122 | 2202 | 2321038 | 717 | Distribution Circuit | Equipment Failure/Involved | Underground | 128 | 15080 | 37.73 | -120.9515 | No | Overcast-Fog-Heavy Rain;32-90 F | Transformer (UG) | Failed/Faulted | 24-0013241 | UG | Sus | 35525515 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905467 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 57879 | 20240122 | 817 | 20240122 | 925 | 2321060 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 68 | 37.2287 | -120.4518 | No | Overcast-Drizzle;32-90 F | Customer Equipment | Failed/Faulted | 24-0013290 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905499 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 320114544173 | 20240122 | 834 | 20240122 | 939 | 2321092 | 65 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 65 | 37.7133 | -120.4609 | No | Clear;32-90 F |  |  | 24-0013326 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1905534 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | T833 | 20240122 | 835 | 20240122 | 1053 | 2321076 | 138 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 138 | 37.7363 | -120.9316 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0013377 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905553 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318514048003 | 20240122 | 859 | 20240122 | 1234 | 2321118 | 215 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 215 | 37.8173 | -121.0155 | No | Clear;32-90 F | Fuse | Broken | 24-0013433 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905581 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | FUSE | 4685 | 20240122 | 1004 | 20240122 | 1439 | 2321242 | 275 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 20180 | 37.3165 | -120.4696 | No | Overcast-Fog-Heavy Rain;32-90 F | Elbow | Failed/Faulted | 24-0013369 | UG | Sus | 46170159 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905551 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | FUSE | S1693 | 20240122 | 1103 | 20240122 | 1450 | 2321321 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 150 | 34067 | 37.768 | -120.8372 | No | Overcast-Fog;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0013398 | OH | Sus | 46170440 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905566 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | OCB | 2107/2 | 20240122 | 1331 | 20240122 | 1345 | 2321482 | 14 | Distribution Circuit | 3rd Party | Metallic Balloon | 1030 | 14420 | 36.9236 | -119.8126 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0013485 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905600 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | RECLOSER | 9030 | 20240122 | 1347 | 20240122 | 1353 | 2321499 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 281 | 1686 | 37.7577 | -121.0494 | No | Overcast-Fog;32-90 F | Insulator | Burned/flashed | 24-0013497 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905605 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321142816477 | 20240122 | 1647 | 20240122 | 1903 | 2321654 | 136 | Transformer only | 3rd Party | Vehicle | 5 | 680 | 36.9523 | -120.1102 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0013574 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905628 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | S1903 | 20240122 | 1657 | 20240122 | 1824 | 2321702 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 87 | 37.7325 | -120.9593 | No | Overcast-Fog;32-90 F |  |  | 24-0013606 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905637 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | RECLOSER | 10530 | 20240122 | 2004 | 20240123 | 400 | 2321841 | 476 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 592 | 258552 | 37.3544 | -120.614 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0013624 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1905649 | 0 | Non-EPSS | N | 2024 | NA
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 6948 | 20240123 | 221 | 20240123 | 1302 | 2321926 | 641 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 5769 | 36.9809 | -120.4641 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Burned/flashed | 24-0013809 | OH | Sus | 31682255 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1905835 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | RECLOSER | 9100 | 20240123 | 1651 | 20240123 | 1815 | 2322558 | 84 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 663 | 55692 | 37.2435 | -121.0128 | No | Partly Cloudy;32-90 F |  |  | 24-0014083 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905896 | 0 | EPSS Ckt | N | 2024 | SGF
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20641 | 20240123 | 2208 | 20240124 | 722 | 2322668 | 554 | Distribution Circuit | 3rd Party | Vehicle | 12 | 6648 | 37.7249 | -120.8121 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0014150 | OH | Sus | 31682382 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1905945 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | OCB | 1104/2 | 20240124 | 641 | 20240124 | 829 | 2322774 | 108 | Distribution Circuit | Animal | Other | 169 | 18252 | 37.1847 | -120.2736 | No | Clear;32-90 F | Regulator | Burned/flashed | 24-0014173 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905956 | 0 | EPSS Ckt | N | 2024 | C PH & GRD
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 26389 | 20240124 | 658 | 20240124 | 1338 | 2322779 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 463 | 35375 | 37.9879 | -120.3884 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0014218 | OH | Sus | 31682384 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1905964 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 5033 | 20240124 | 804 | 20240124 | 950 | 2322850 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 778 | 37.3746 | -121.056 | No | Clear;32-90 F |  |  | 24-0014302 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906040 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L2183 | 20240124 | 1035 | 20240124 | 1125 | 2323037 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 50 | 37.9908 | -120.4797 | No | Overcast-Rain;32-90 F |  |  | 24-0014389 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906066 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | 20243 | 20240124 | 1104 | 20240124 | 1204 | 2323068 | 60 | Distribution Circuit | Animal | Bird found | 846 | 46249 | 37.9845 | -120.3796 | No | Overcast-Fog-Rain;32-90 F | Stepdown | Normal | 24-0014383 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906064 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321485939000 | 20240124 | 1217 | 20240124 | 1320 | 2323152 | 63 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 63 | 37.5681 | -119.9888 | No | Overcast-Drizzle;32-90 F |  |  | 24-0014493 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1906085 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | OCB | 1106/2 | 20240124 | 1730 | 20240125 | 356 | 2323392 | 626 | Distribution Circuit | 3rd Party | Vehicle | 373 | 65330 | 36.8862 | -120.6558 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0014684 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1906117 | 0 | EPSS Ckt | N | 2024 | C & GRD
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S1203 | 20240125 | 646 | 20240125 | 838 | 2323605 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 7056 | 37.8134 | -121.0341 | No | Clear;32-90 F |  |  | 24-0014854 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1906181 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRANSFORMER | 322559529820 | 20240125 | 706 | 20240125 | 722 | 2323582 | 16 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 16 | 37.3161 | -119.6203 | No | Overcast-Fog;32-90 F |  |  | 24-0014840 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1906178 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6648 | 20240125 | 829 | 20240125 | 1430 | 2323750 | 361 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 361 | 37.0326 | -120.0292 | No | Overcast-Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0014919 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1906297 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | JUMPER | BURNED OPEN JUMPER 1 W/OF 7526 | 20240125 | 1031 | 20240125 | 1110 | 2324023 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 275 | 7029 | 37.2992 | -120.4757 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Burned Open | 24-0015046 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1906380 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318356028594 | 20240125 | 1459 | 20240125 | 1505 | 2324209 | 6 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 6 | 37.2837 | -121.0657 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0015228 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1906427 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | JUMPER | OJ'S 1 W/OF MTR# 1009032897 | 20240125 | 1509 | 20240125 | 1659 | 2324223 | 110 | Distribution Circuit | 3rd Party | Vehicle | 1 | 110 | 36.9166 | -120.0379 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0015246 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1906432 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | RECLOSER | 3160 | 20240125 | 2340 | 20240126 | 317 | 2324435 | 217 | Distribution Circuit | 3rd Party | Vehicle | 135 | 8803 | 36.7225 | -120.3811 | No | Fog;32-90 F | Pole-Wood | Broken | 24-0015335 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1906498 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | RECLOSER | 3144 | 20240126 | 235 | 20240126 | 927 | 2324462 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 31726 | 37.9906 | -120.3839 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0015393 | OH | Sus | 31682468 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1906504 | 0 | EPSS Ckt | N | 2024 | B GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | 20013 | 20240126 | 411 | 20240126 | 1547 | 2324467 | 696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2768 | 37.8323 | -120.4867 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0015413 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906509 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 26922 | 20240126 | 1302 | 20240126 | 1411 | 2324965 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 1449 | 37.3473 | -121.0359 | No | Partly Cloudy;32-90 F |  |  | 24-0015667 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1906708 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 87895 | 20240126 | 1303 | 20240126 | 1421 | 2325040 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 390 | 37.1711 | -120.4151 | No | Partly Cloudy;32-90 F |  |  | 24-0015691 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1906713 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319724644900 | 20240126 | 1628 | 20240126 | 1730 | 2325206 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 62 | 37.7326 | -120.5964 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0015756 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1906734 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 9200 | 20240126 | 2320 | 20240127 | 1158 | 2325320 | 758 | Distribution Circuit | Animal | Bird found | 135 | 32570 | 37.229 | -120.4868 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0015786 | OH | Sus | 46173377 | CENTRAL VALLEY | JAN | Multi-Fault | 0 | No | Yes | No | 1906766 | 0 | Non-EPSS | N | 2024 | AC GRD
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | S1211 | 20240127 | 10 | 20240127 | 130 | 2325328 | 80 | Distribution Circuit | 3rd Party | Metallic Balloon | 155 | 12400 | 37.7254 | -120.9219 | No | Overcast-Fog;32-90 F | Jumper | Normal | 24-0015793 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906770 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 320761840731 | 20240127 | 839 | 20240127 | 1459 | 2325441 | 380 | Transformer only | 3rd Party | Other | 1 | 380 | 37.6187 | -120.2313 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0015846 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906841 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 394167 | 20240127 | 954 | 20240127 | 1055 | 2325523 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 122 | 37.0773 | -120.5327 | No | Overcast;32-90 F |  |  | 24-0015845 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906840 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | OCB | 2101/2 | 20240128 | 915 | 20240128 | 1017 | 2326302 | 62 | Distribution Circuit | Animal | Bird found | 3840 | 237324 | 37.5045 | -120.0077 | No | Partly Cloudy;32-90 F | Circuit Breaker | Normal | 24-0015949 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906921 | 0 | EPSS Ckt | N | 2024 | C GRD INST
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320611453723 | 20240128 | 1019 | 20240128 | 1439 | 2326335 | 260 | Transformer only | Equipment Failure/Involved | Underground | 3 | 780 | 37.9755 | -120.2888 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0015965 | UG | Sus | 46173702 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1906929 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 318996048042 | 20240128 | 2356 | 20240129 | 8 | 2326671 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 60 | 37.8185 | -120.8485 | No | Partly Cloudy-Fog;32-90 F | Fuse | Broken | 24-0016028 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906971 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 440120 | 20240129 | 212 | 20240129 | 358 | 2326778 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 318 | 37.3769 | -121.1035 | No | Clear;32-90 F |  |  | 24-0016032 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1906975 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20240129 | 227 | 20240129 | 346 | 2326781 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 150 | 11850 | 37.0679 | -119.9091 | No | Partly Cloudy;32-90 F |  |  | 24-0016031 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906974 | 0 | EPSS Ckt | N | 2024 | AB
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 2391 | 20240129 | 617 | 20240129 | 750 | 2326835 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 2791 | 37.7946 | -120.9508 | No | Clear;32-90 F |  |  | 24-0016064 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907015 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | OCB | 1103/2 | 20240129 | 727 | 20240129 | 853 | 2326887 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1033 | 50723 | 37.5792 | -121.2057 | No | Partly Cloudy;32-90 F |  |  | 24-0016051 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906998 | 0 | EPSS Ckt | N | 2024 | A & CN
YOSEMITE | YOSEMITE | PANOCHE-1102 | 253671102 | TRANSFORMER | 100000054178 | 20240129 | 950 | 20240129 | 1232 | 2327174 | 162 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 162 | 36.6752 | -120.5138 | No | Clear;32-90 F | Fuse | Broken | 24-0016233 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907217 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 24511 | 20240129 | 1232 | 20240129 | 1503 | 2327319 | 151 | Distribution Circuit | Animal | Bird found | 10 | 1510 | 36.6619 | -120.6761 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0016337 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1907258 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 27369 | 20240129 | 1618 | 20240130 | 220 | 2327532 | 602 | Distribution Circuit | 3rd Party | Vehicle | 2640 | 213283 | 36.9536 | -120.092 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0016379 | OH | Sus | 35526776 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907270 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | OTHER | T8271 TWD T8272 | 20240129 | 1645 | 20240129 | 1737 | 2327541 | 52 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 832 | 37.079 | -120.8306 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0016342 | UG | Sus | 35527005 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1907268 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1116 | 252761116 | FUSE | 5853 | 20240130 | 741 | 20240130 | 937 | 2327860 | 116 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 1625 | 36.8804 | -120.0106 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0016555 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907479 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319117346116 | 20240130 | 1310 | 20240130 | 1605 | 2328340 | 175 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 175 | 37.7659 | -120.8063 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0016772 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907556 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318565448130 | 20240130 | 1345 | 20240130 | 1422 | 2328372 | 37 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 148 | 37.8209 | -120.9976 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0016768 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907555 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 4665 | 20240130 | 1525 | 20240130 | 1723 | 2328451 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 708 | 37.5447 | -120.0949 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0016828 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1907569 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | OTHER | J25373 TWD T6748 | 20240130 | 1650 | 20240130 | 1924 | 2328523 | 154 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 308 | 37.0778 | -120.8278 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0016786 | UG | Sus | 35527214 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1907580 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 90035 | 20240130 | 2222 | 20240131 | 612 | 2328663 | 470 | Distribution Circuit | 3rd Party | Vehicle | 105 | 22486 | 37.9721 | -120.3316 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0016962 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1907634 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | OTHER | T14356 TWD T14357 | 20240130 | 2315 | 20240131 | 416 | 2328593 | 301 | Distribution Circuit | Equipment Failure/Involved | Underground | 43 | 12943 | 36.8422 | -120.4469 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0016913 | UG | Sus | 35527351 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1907616 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | RECLOSER | 9100 | 20240131 | 656 | 20240131 | 732 | 2328849 | 36 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 663 | 23868 | 37.2435 | -121.0128 | No | Partly Cloudy;32-90 F |  |  | 24-0017030 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907676 | 0 | EPSS Ckt | N | 2024 | SGF
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | 321187816596 | 20240131 | 837 | 20240131 | 1115 | 2329093 | 158 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 632 | 36.9555 | -120.0948 | No | Clear;32-90 F | Fuse | Broken | 24-0017232 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907857 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322891526254 | 20240131 | 1238 | 20240131 | 1555 | 2329832 | 197 | Transformer only | 3rd Party | Fire- house or bldg. | 2 | 394 | 37.2191 | -119.5079 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 24-0017396 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1907915 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S945 | 20240131 | 1342 | 20240131 | 1452 | 2329785 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 70 | 37.8276 | -120.9945 | No | Clear;32-90 F |  |  | 24-0017422 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907925 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | FUSE | 4171 | 20240131 | 1357 | 20240131 | 1452 | 2329810 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 1798 | 37.2887 | -120.4335 | No | Overcast;32-90 F |  |  | 24-0017429 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1907929 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 2381 | 20240131 | 1431 | 20240131 | 1440 | 2329841 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 72 | 37.8293 | -121.0249 | No | Overcast;32-90 F | Insulator | Broken | 24-0017401 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1907917 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 963185 | 20240131 | 1450 | 20240131 | 1730 | 2329863 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 480 | 37.0617 | -120.2882 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0017415 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1907922 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | OTHER | T7973 TWD T7975 | 20240131 | 1755 | 20240131 | 1830 | 2330164 | 35 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 560 | 37.3065 | -121.021 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0017452 | UG | Sus | 35527488 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1907989 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | RECLOSER | 9920 | 20240131 | 1757 | 20240201 | 1513 | 2330184 | 1276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 96374 | 37.1151 | -120.6384 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017574 | OH | Sus | 46176249 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1907991 | 0 | Non-EPSS | N | 2024 | C & GRD
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | RECLOSER | 90100 | 20240131 | 1838 | 20240131 | 2343 | 2330252 | 305 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 550 | 49799 | 37.827 | -120.9975 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017596 | OH | Sus | 31683188 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1908012 | 0 | Non-EPSS | N | 2024 | B AND GROUND
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | TRANSFORMER | 319629117632 | 20240131 | 1901 | 20240131 | 2209 | 2330298 | 188 | Transformer only | Unknown Cause | Patrol - found nothing | 15 | 2820 | 36.9844 | -120.6284 | No | Overcast-Drizzle;32-90 F |  |  | 24-0017720 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1908114 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10466 | 20240131 | 1907 | 20240131 | 2031 | 2330299 | 84 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 420 | 37.5129 | -119.8294 | No | Overcast-Drizzle;32-90 F |  |  | 24-0017642 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908047 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 21004 | 20240131 | 1913 | 20240201 | 138 | 2330318 | 385 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 3850 | 36.6918 | -120.6218 | No | Overcast-Drizzle;32-90 F |  |  | 24-0017746 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908143 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | JUMPER | 434305 | 20240131 | 1923 | 20240131 | 2130 | 2330331 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 495 | 61217 | 37.5603 | -121.1785 | No | Overcast-Rain-Strong Winds;32-90 F | Jumper | Broken | 24-0017627 | OH | Sus | 46176117 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1908035 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | 319634318280 | 20240131 | 2035 | 20240201 | 50 | 2330443 | 255 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 47 | 807 | 37.0018 | -120.6265 | No | Overcast-Drizzle;32-90 F | Jumper | Broken | 24-0017674 | OH | Sus | 46176130 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | No | No | 1908071 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 20240131 | 2054 | 20240131 | 2207 | 2330461 | 73 | Distribution Circuit | Vegetation | Tree - branch fell on line | 170 | 12410 | 37.5637 | -119.8544 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0017692 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908087 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 38882 | 20240131 | 2118 | 20240201 | 13 | 2330486 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 313 | 11611 | 37.7169 | -120.3056 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0017650 | OH | Sus | 35527478 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1908075 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10466 | 20240131 | 2129 | 20240201 | 410 | 2330501 | 401 | Distribution Circuit | Environmental/External | Water | 5 | 2005 | 37.5129 | -119.8294 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0017703 | OH | Sus | 46176162 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908097 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 6776 | 20240131 | 2336 | 20240201 | 513 | 2330721 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1011 | 37.1365 | -120.147 | No | Overcast-Drizzle;32-90 F | Woodpin | Broken | 24-0017742 | OH | Sus | 31683190 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908139 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 9460 | 20240201 | 3 | 20240201 | 915 | 2330682 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1309 | 153091 | 37.591 | -120.3071 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017732 | OH | Sus | 46176132 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1908128 | 0 | EPSS Ckt | N | 2024 | A&C
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7757 | 20240201 | 428 | 20240201 | 1145 | 2330790 | 437 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 7071 | 37.3465 | -120.9329 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0017866 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1908224 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | TRANSFORMER | 319127418614 | 20240201 | 701 | 20240201 | 1112 | 2330859 | 251 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 502 | 37.0108 | -120.7999 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0018000 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908300 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 25119 | 20240201 | 724 | 20240201 | 1413 | 2330959 | 409 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 6135 | 37.5236 | -120.3099 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0017836 | OH | Sus | 31682699 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1908196 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20240201 | 824 | 20240201 | 1324 | 2330979 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 469 | 93079 | 37.3391 | -119.585 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017844 | OH | Sus | 46176173 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1908202 | 0 | EPSS Ckt | N | 2024 | A AND B- GROUND
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320441041439 | 20240201 | 929 | 20240201 | 1151 | 2331112 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 142 | 37.6385 | -120.3479 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0018023 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908307 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | L1209 | 20240201 | 1346 | 20240201 | 1451 | 2331427 | 65 | Distribution Circuit | Animal | Bird found | 51 | 3338 | 37.9631 | -120.2909 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0018172 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1908346 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRIP-SAVER | 6697 | 20240201 | 1431 | 20240201 | 1551 | 2331486 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 179 | 14320 | 37.9607 | -120.4262 | No | Partly Cloudy;32-90 F |  |  | 24-0018227 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1908361 | 0 | EPSS Ckt | N | 2024 | A AND B PH
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318727345855 | 20240201 | 1706 | 20240201 | 2333 | 2331816 | 387 | Transformer only | Environmental/External | Lightning | 2 | 774 | 37.7584 | -120.9413 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018336 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908403 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 6797 | 20240201 | 1706 | 20240202 | 235 | 2331817 | 569 | Distribution Circuit | Environmental/External | Lightning | 24 | 6955 | 37.7584 | -120.9425 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018344 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1908411 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6846 | 20240201 | 1826 | 20240201 | 1910 | 2331899 | 44 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 18 | 792 | 37.0543 | -120.0759 | No | Overcast-Drizzle;32-90 F |  |  | 24-0018328 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908397 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | RECLOSER | 3630 | 20240202 | 255 | 20240202 | 1412 | 2332084 | 677 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 48005 | 36.6912 | -120.4598 | No | Partly Cloudy-Drizzle;32-90 F | Recloser | Failed/Faulted | 24-0018392 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908454 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318944844972 | 20240202 | 723 | 20240202 | 1025 | 2332245 | 182 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 182 | 37.7344 | -120.866 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0018556 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908594 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | TRANSFORMER | 320515219499 | 20240202 | 849 | 20240202 | 1048 | 2332289 | 119 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 119 | 37.0352 | -120.3231 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Broken | 24-0018581 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908601 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320514523896 | 20240202 | 1030 | 20240202 | 1037 | 2332381 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 7 | 37.1564 | -120.3243 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 24-0018568 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908598 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319692028404 | 20240202 | 1256 | 20240202 | 1343 | 2332578 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 47 | 37.2798 | -120.6072 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 24-0018712 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908638 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 10841 | 20240202 | 1322 | 20240202 | 1620 | 2332623 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 950 | 37.0276 | -120.8545 | No | Overcast-Drizzle;32-90 F |  |  | 24-0018812 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908683 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 57749 | 20240202 | 1528 | 20240202 | 1621 | 2332911 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 601 | 37.2175 | -120.4338 | No | Overcast;32-90 F |  |  | 24-0018824 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908689 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | FUSE | 8725 | 20240202 | 2114 | 20240202 | 2225 | 2333316 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 8236 | 37.3966 | -120.6127 | No | Overcast-Fog;32-90 F |  |  | 24-0018883 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1908745 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | SWITCH | 352740 | 20240203 | 421 | 20240203 | 551 | 2333402 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1561 | 81109 | 37.3384 | -119.6709 | No | Partly Cloudy;Below 32 F | Recloser | Malfunctioning | 24-0018899 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1908760 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 21843 | 20240203 | 1413 | 20240203 | 1518 | 2333739 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 650 | 37.9671 | -120.4344 | No | Partly Cloudy;32-90 F |  |  | 24-0018951 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1908857 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7013 | 20240204 | 205 | 20240204 | 854 | 2334221 | 409 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 117 | 17073 | 37.3301 | -120.6872 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0019099 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1908987 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320561227851 | 20240204 | 623 | 20240204 | 734 | 2334193 | 71 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 71 | 37.2651 | -120.307 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0019169 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1909058 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 21004 | 20240204 | 724 | 20240204 | 1407 | 2334896 | 403 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 4030 | 36.6918 | -120.6218 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F |  |  | 24-0019878 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909715 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 21059 | 20240204 | 745 | 20240206 | 1212 | 2335055 | 3147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 100704 | 37.5103 | -121.3234 | Yes | Clear;32-90 F |  |  | 24-0023327 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1912804 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | RECLOSER | 873156 | 20240204 | 839 | 20240204 | 1143 | 2335140 | 184 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 3820 | 37.2807 | -120.3237 | Yes | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0019310 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909196 | 0 | EPSS Ckt | N | 2024 | NA
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | FUSE | 3803 | 20240204 | 917 | 20240204 | 2338 | 2336126 | 861 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 24969 | 37.0538 | -121.0256 | Yes | Overcast-Fog-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020243 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1910071 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 2948 | 20240204 | 1134 | 20240204 | 1310 | 2338230 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2016 | 37.3209 | -119.6055 | Yes | Clear;32-90 F |  |  | 24-0019747 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909595 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 22181 | 20240204 | 1208 | 20240204 | 1255 | 2338837 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 987 | 37.9741 | -120.2639 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0019729 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909578 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 6429 | 20240204 | 1216 | 20240205 | 2330 | 2338989 | 2114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 54344 | 37.3476 | -121.0327 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0021408 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911242 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | RECLOSER | 3680 | 20240204 | 1222 | 20240205 | 2001 | 2339069 | 1899 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 43677 | 37.1002 | -120.9978 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020981 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1910802 | 0 | EPSS Ckt | N | 2024 | A PHASE & GRD
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 9583 | 20240204 | 1225 | 20240204 | 1348 | 2339133 | 83 | Distribution Circuit | Vegetation | Tree - branch fell on line | 307 | 25481 | 37.1007 | -121.0162 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019905 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909739 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | RECLOSER | 3130 | 20240204 | 1229 | 20240205 | 1537 | 2339186 | 1628 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 23088 | 37.1154 | -121.0347 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019708 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909557 | 0 | EPSS Ckt | N | 2024 | A & B
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 20205 | 20240204 | 1240 | 20240205 | 1515 | 2360787 | 1595 | Distribution Circuit | 3rd Party | Other | 3 | 4785 | 37.2782 | -120.9543 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0022344 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911997 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 21857 | 20240204 | 1241 | 20240204 | 1917 | 2339348 | 396 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 17424 | 36.996 | -119.9896 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020203 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1910028 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7756 | 20240204 | 1246 | 20240204 | 1757 | 2339382 | 311 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 6016 | 37.3454 | -120.9238 | Yes | Clear;32-90 F |  |  | 24-0020752 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910570 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 5778 | 20240204 | 1254 | 20240204 | 1620 | 2339482 | 206 | Distribution Circuit | Animal | Bird found | 14 | 2884 | 37.1418 | -120.2712 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 24-0020166 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909993 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | OCB | 1107/2 | 20240204 | 1257 | 20240204 | 2040 | 2339533 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3500 | 263453 | 36.9832 | -120.0335 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Annealed | 24-0019767 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1909615 | 0 | Non-EPSS | N | 2024 | A
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | RECLOSER | 9290 | 20240204 | 1304 | 20240204 | 1455 | 2339640 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 778 | 86358 | 37.7606 | -120.8173 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019786 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909638 | 0 | EPSS Ckt | N | 2024 | B- C
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | FUSE | 25547 | 20240204 | 1330 | 20240205 | 1924 | 2340133 | 1794 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 14352 | 37.3165 | -121.0493 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Lightning Arrestor | Broken | 24-0020986 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910808 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | RECLOSER | 245946 | 20240204 | 1335 | 20240204 | 2203 | 2340148 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 558 | 101096 | 36.9766 | -120.6265 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019869 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909707 | 0 | Non-EPSS | N | 2024 | B- C
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 4506 | 20240204 | 1339 | 20240204 | 1846 | 2339240 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 10479 | 37.3269 | -120.8603 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019891 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1909726 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | 319885216451 | 20240204 | 1339 | 20240205 | 250 | 2340203 | 791 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1582 | 36.9524 | -120.5411 | Yes | Strong Winds-Rain-Overcast;32-90 F | Transformer | Arcing | 24-0021420 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911255 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 3714 | 20240204 | 1342 | 20240205 | 1508 | 2340341 | 1526 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 91560 | 37.0459 | -120.5951 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021754 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1911510 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 7035 | 20240204 | 1344 | 20240205 | 1201 | 2340353 | 1337 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 12033 | 37.2728 | -120.5784 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022123 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911810 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 5527 | 20240204 | 1344 | 20240204 | 1804 | 2340325 | 260 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 6763 | 37.2518 | -120.4138 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0020613 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910434 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 10855 | 20240204 | 1345 | 20240204 | 2137 | 2342564 | 472 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 5192 | 36.9984 | -120.8643 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021129 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910952 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | RECLOSER | 4140 | 20240204 | 1349 | 20240204 | 1848 | 2340554 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 25415 | 37.2876 | -120.285 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019970 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909804 | 0 | EPSS Ckt | N | 2024 | NA
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | RECLOSER | 30980 | 20240204 | 1352 | 20240204 | 1635 | 2340487 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1168 | 190384 | 37.3044 | -120.4833 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0019938 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909769 | 0 | Non-EPSS | N | 2024 | A & B
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 8876 | 20240204 | 1352 | 20240204 | 1724 | 2340491 | 212 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 918 | 37.3202 | -120.4444 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020518 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910341 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 7834 | 20240204 | 1353 | 20240205 | 1310 | 2340549 | 1397 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 37216 | 37.3079 | -120.4578 | Yes | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0020274 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910103 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | RECLOSER | 11480 | 20240204 | 1354 | 20240205 | 1610 | 2340811 | 1576 | Distribution Circuit | Vegetation | Tree - branch fell on line | 531 | 165682 | 37.3158 | -120.4865 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0020407 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910234 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | RECLOSER | 9920 | 20240204 | 1354 | 20240206 | 1411 | 2340328 | 2897 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 134174 | 37.1151 | -120.6384 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019913 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1909747 | 0 | Non-EPSS | N | 2024 | B-C & GRD
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | FUSE | 23417 | 20240204 | 1355 | 20240204 | 1600 | 2340617 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 11256 | 37.0571 | -120.8225 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020179 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910005 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 27280 | 20240204 | 1355 | 20240204 | 1610 | 2340814 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1080 | 37.3177 | -120.3672 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020319 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910147 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 7818 | 20240204 | 1357 | 20240204 | 1707 | 2340742 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 7980 | 37.3017 | -120.4599 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020343 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910171 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 7145 | 20240204 | 1400 | 20240204 | 2301 | 2340857 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 78445 | 37.3328 | -120.4418 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020137 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1909966 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | RECLOSER | 9600 | 20240204 | 1402 | 20240205 | 141 | 2339228 | 699 | Distribution Circuit | Equipment Failure/Involved | Overhead | 196 | 137004 | 37.1244 | -121.0153 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019927 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1909759 | 0 | EPSS Ckt | N | 2024 | C GRD
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 4518 | 20240204 | 1403 | 20240204 | 1753 | 2340929 | 230 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 17020 | 37.2999 | -120.5777 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020661 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910482 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | FUSE | 21046 | 20240204 | 1407 | 20240204 | 1911 | 2340997 | 304 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 8516 | 37.4038 | -120.6148 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020795 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910614 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | OTHER | WIRE DOWN 5 E/OF 7091 | 20240204 | 1408 | 20240204 | 2110 | 2341025 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 386 | 162798 | 37.3676 | -120.6316 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020099 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | Yes | 1909928 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2059 | 20240204 | 1408 | 20240205 | 2102 | 2341032 | 1854 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 34378 | 38.0628 | -120.1847 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020154 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1909982 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7684 | 20240204 | 1411 | 20240205 | 748 | 2341098 | 1057 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 6336 | 37.4395 | -120.576 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021215 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911043 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | FUSE | 8643 | 20240204 | 1412 | 20240204 | 2145 | 2341191 | 453 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 128 | 57984 | 37.3966 | -120.6145 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021170 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910995 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRIP-SAVER | 7054 | 20240204 | 1413 | 20240205 | 1509 | 2341284 | 1496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 49190 | 37.346 | -120.7245 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021149 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910974 | 0 | Non-EPSS | N | 2024 | A- B
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7316 | 20240204 | 1418 | 20240205 | 1045 | 2341352 | 1227 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 17178 | 37.47 | -120.649 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021774 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911527 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | RECLOSER | 3040 | 20240204 | 1419 | 20240205 | 1935 | 2341626 | 1756 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 34818 | 37.0567 | -120.7501 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020410 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1910238 | 0 | Non-EPSS | N | 2024 | A- B- C
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 7318 | 20240204 | 1422 | 20240205 | 1730 | 2341425 | 1628 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 11396 | 37.4041 | -120.7116 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022498 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1912135 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 36849 | 20240204 | 1424 | 20240204 | 1900 | 2341467 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1380 | 37.9599 | -120.4149 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020198 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1910023 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 25873 | 20240204 | 1425 | 20240204 | 1632 | 2341533 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 3556 | 37.726 | -120.3186 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020366 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910194 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7257 | 20240204 | 1426 | 20240205 | 1400 | 2342108 | 1414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3773 | 37.2949 | -120.6149 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0021264 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911096 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 58637 | 20240204 | 1427 | 20240205 | 415 | 2341564 | 828 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 4140 | 37.3603 | -120.6822 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021468 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911303 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 11810 | 20240204 | 1428 | 20240204 | 2057 | 2341625 | 389 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 243 | 94527 | 37.3312 | -120.6346 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019998 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1909832 | 0 | Non-EPSS | N | 2024 | A- B- C
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | RECLOSER | 90490 | 20240204 | 1428 | 20240205 | 1010 | 2341272 | 1182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 15689 | 37.303 | -120.7639 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020013 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909847 | 0 | Non-EPSS | N | 2024 | B- C
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7544 | 20240204 | 1428 | 20240205 | 1045 | 2341608 | 1217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 45029 | 37.3387 | -120.76 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021800 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911548 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7546 | 20240204 | 1432 | 20240205 | 605 | 2341704 | 933 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 38253 | 37.3132 | -120.841 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021507 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911349 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | RECLOSER | 3640 | 20240204 | 1438 | 20240205 | 1848 | 2341883 | 1690 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 77010 | 37.1054 | -120.8361 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020820 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910639 | 0 | Non-EPSS | N | 2024 | A
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319729234096 | 20240204 | 1441 | 20240205 | 1912 | 2341934 | 1711 | Transformer only | Vegetation | Tree - fell into line | 4 | 6844 | 37.4367 | -120.5942 | Yes | Strong Winds-Rain-Overcast;32-90 F | Transformer | Broken- wire on ground | 24-0021206 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1911034 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | S477 | 20240204 | 1441 | 20240204 | 2030 | 2341966 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 931 | 37.2658 | -121.031 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020338 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910166 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | FUSE | 4501 | 20240204 | 1446 | 20240205 | 1631 | 2342109 | 1545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 146989 | 37.3271 | -120.9059 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021064 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910887 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | RECLOSER | 6926 | 20240204 | 1448 | 20240204 | 2000 | 2342242 | 312 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 205 | 63960 | 37.2459 | -121.0174 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020895 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910715 | 0 | EPSS Ckt | N | 2024 | A & C PHASE
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 7319 | 20240204 | 1452 | 20240204 | 2140 | 2342307 | 408 | Distribution Circuit | 3rd Party | Vehicle | 216 | 88128 | 37.3968 | -120.7055 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020360 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910188 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 318395931775 | 20240204 | 1453 | 20240205 | 406 | 2342264 | 793 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 7137 | 37.371 | -121.053 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 24-0021471 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911306 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | OCB | 1712/2 | 20240204 | 1459 | 20240204 | 1845 | 2342550 | 226 | Distribution Circuit | Vegetation | Tree - fell into line | 2171 | 234704 | 37.7688 | -120.9078 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0020141 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1909970 | 0 | Non-EPSS | N | 2024 | PH OC- BU RLY
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20240204 | 1501 | 20240204 | 1542 | 2342619 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 368 | 15088 | 37.9754 | -120.4464 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020156 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909984 | 0 | EPSS Ckt | N | 2024 | A & C
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318853446527 | 20240204 | 1503 | 20240205 | 203 | 2341361 | 660 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1320 | 37.7772 | -120.8977 | Yes | Clear-Strong Winds;32-90 F | Fuse | Failed/Faulted | 24-0021411 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911245 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1102 | 252261102 | FUSE | 19847 | 20240204 | 1506 | 20240205 | 1955 | s1911719 | 1729 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1729 | 37.3656 | -120.8325 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022001 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1911719 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | JUMPER | 53785 A PH BLOWN JMPR | 20240204 | 1507 | 20240205 | 820 | 2342661 | 1033 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 5165 | 37.0918 | -120.9255 | Yes | Overcast-Fog-Strong Winds;32-90 F | Jumper | Burned Open | 24-0021407 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1911241 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 1735 | 20240204 | 1519 | 20240204 | 1855 | 2343100 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 3240 | 37.7536 | -121.0421 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020796 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910615 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 9934 | 20240204 | 1521 | 20240206 | 411 | 2356719 | 2210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 11050 | 37.0421 | -120.9433 | Yes | Overcast-Fog-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0021472 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1911307 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 21004 | 20240204 | 1522 | 20240205 | 1220 | 2343091 | 1258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 12580 | 36.6918 | -120.6218 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021998 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911716 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 2277 | 20240204 | 1528 | 20240204 | 1853 | 2351360 | 205 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 820 | 37.7695 | -121.033 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020811 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910630 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20240204 | 1540 | 20240205 | 1443 | 2344386 | 1383 | Distribution Circuit | Vegetation | Tree - fell into line | 610 | 600145 | 37.8306 | -120.2367 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020287 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910116 | 0 | EPSS Ckt | N | 2024 | B & C
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | S403 | 20240204 | 1554 | 20240204 | 1749 | 2344868 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 81 | 9315 | 37.7593 | -121.0511 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020576 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910399 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320211051830 | 20240204 | 1555 | 20240205 | 517 | 2344767 | 802 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 802 | 37.9232 | -120.4271 | Yes | Overcast-Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Normal | 24-0021494 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911336 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 2147 | 20240204 | 1556 | 20240205 | 1031 | 2344860 | 1115 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 8920 | 37.3437 | -120.5792 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021773 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911526 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 9658 | 20240204 | 1601 | 20240205 | 1538 | 2345830 | 1417 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 3781 | 36.7949 | -120.3257 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0022311 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1911964 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | RECLOSER | 10460 | 20240204 | 1608 | 20240205 | 1646 | 2345540 | 1478 | Distribution Circuit | Vegetation | Tree - branch fell on line | 275 | 62470 | 37.3348 | -120.5811 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Transformer (OH) | Burned/flashed | 24-0020736 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910556 | 0 | Non-EPSS | N | 2024 | A- C- GRD
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 21116 | 20240204 | 1609 | 20240205 | 51 | 2346209 | 522 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 29232 | 37.3856 | -120.7607 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021355 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911189 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | RECLOSER | 90590 | 20240204 | 1613 | 20240205 | 1032 | 2346461 | 1099 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 61544 | 37.3624 | -121.0756 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021782 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911535 | 0 | EPSS Ckt | N | 2024 | A & C PHASE
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | FUSE | 19508 | 20240204 | 1614 | 20240205 | 1301 | 2346456 | 1247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 18705 | 37.0571 | -120.8716 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021401 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1911235 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 7444 | 20240204 | 1618 | 20240206 | 1529 | 2346107 | 2831 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 45296 | 37.1202 | -120.5379 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | On Ground | 24-0021399 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911232 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 23314 | 20240204 | 1623 | 20240205 | 212 | 2356341 | 589 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 589 | 37.7109 | -120.7611 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0021427 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911262 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 13359 | 20240204 | 1642 | 20240205 | 1045 | 2347138 | 1083 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 4332 | 37.4291 | -120.6187 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0021808 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1911555 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1105 | 254101105 | OCB | 1105/2 | 20240204 | 1644 | 20240204 | 2013 | 2357089 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1484 | 310156 | 37.1208 | -120.2505 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0021505 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | No | No | 1911348 | 0 | Non-EPSS | N | 2024 | A- B- C
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 801 | 20240204 | 1645 | 20240204 | 1738 | 2347254 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 137 | 7261 | 38.0509 | -120.4004 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020533 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910355 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 6441 | 20240204 | 1648 | 20240205 | 1041 | 2347455 | 1073 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 37729 | 37.7875 | -120.9977 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020961 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910781 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 320173012800 | 20240204 | 1651 | 20240205 | 2355 | 2347548 | 1864 | Transformer only | Vegetation | Tree - fell into line | 5 | 9320 | 36.8512 | -120.4423 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021275 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1911107 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 22502 | 20240204 | 1656 | 20240205 | 1926 | 2347754 | 1590 | Distribution Circuit | Vegetation | Tree - branch fell on line | 200 | 141480 | 37.3568 | -120.5968 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020790 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910608 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 100000003184 | 20240204 | 1659 | 20240205 | 1936 | 2348566 | 1597 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1597 | 37.323 | -121.0474 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 24-0022665 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912300 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | SWITCH | 6547 | 20240204 | 1700 | 20240204 | 1730 | 2347914 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 570 | 37.3346 | -121.0674 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020463 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1910289 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23223 | 20240204 | 1701 | 20240204 | 2159 | 2347932 | 298 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 23542 | 37.9785 | -120.3151 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021182 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911007 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | RECLOSER | 3214 | 20240204 | 1703 | 20240204 | 1910 | 2349299 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 220 | 27940 | 37.7904 | -120.8634 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0020632 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910451 | 0 | Non-EPSS | N | 2024 | A & C
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 2279 | 20240204 | 1703 | 20240204 | 1820 | 2348017 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 3080 | 37.7733 | -121.033 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0020697 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910517 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 25492 | 20240204 | 1708 | 20240205 | 740 | 2357062 | 872 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2616 | 37.7838 | -120.8673 | Yes | Overcast;32-90 F | Insulator | Broken | 24-0021503 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911346 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 2243 | 20240204 | 1714 | 20240205 | 1130 | 2348337 | 1096 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 4384 | 37.4244 | -120.6382 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0021892 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911627 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 1599 | 20240204 | 1714 | 20240205 | 328 | 2348246 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 7781 | 37.3007 | -121.0675 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 24-0021445 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911280 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | S1807 | 20240204 | 1714 | 20240205 | 826 | 2348338 | 912 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 17328 | 37.7597 | -120.8925 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0021584 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1911397 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | 64335 | 20240204 | 1730 | 20240205 | 351 | 2356612 | 621 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 3314 | 38.0213 | -120.2565 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0021455 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911290 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 667248 | 20240204 | 1732 | 20240205 | 2125 | 2349288 | 1673 | Distribution Circuit | Vegetation | Tree - fell into line | 2882 | 527666 | 38.049 | -120.2357 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020867 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1910685 | 0 | EPSS Ckt | N | 2024 | A & INST
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 8040 | 20240204 | 1732 | 20240205 | 217 | 2349301 | 525 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 131 | 68775 | 37.8999 | -120.5045 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021217 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1911045 | 0 | EPSS Ckt | N | 2024 | A-B-C TIME OC
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20240204 | 1736 | 20240205 | 1342 | 2350011 | 1206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 150 | 57576 | 37.8998 | -120.4541 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020966 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1910786 | 0 | EPSS Ckt | N | 2024 | B & TIME
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 21429 | 20240204 | 1736 | 20240205 | 1235 | 2354939 | 1139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 52394 | 37.8702 | -120.4332 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020966 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1910971 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 22181 | 20240204 | 1738 | 20240205 | 952 | 2349389 | 974 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 20454 | 37.9741 | -120.2639 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0021277 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911109 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 20240204 | 1741 | 20240205 | 146 | 2349462 | 485 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 17945 | 37.9718 | -120.2261 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0021376 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911209 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3717 | 20240204 | 1741 | 20240205 | 20 | 2348616 | 399 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2129 | 37.0399 | -120.5524 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0021402 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911236 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 20297 | 20240204 | 1751 | 20240205 | 2002 | 2349637 | 1571 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 95831 | 37.8646 | -120.2206 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021158 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910983 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | RECLOSER | 49704 | 20240204 | 1755 | 20240204 | 2058 | 2349943 | 183 | Distribution Circuit | Vegetation | Tree - branch fell on line | 298 | 54534 | 37.7767 | -120.817 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021027 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910850 | 0 | EPSS Ckt | N | 2024 | A & B PHASE
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319164544595 | 20240204 | 1811 | 20240205 | 357 | 2350378 | 586 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2930 | 37.7244 | -120.7901 | Yes | Clear-Strong Winds;32-90 F | Fuse | Failed/Faulted | 24-0021460 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911295 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 25106 | 20240204 | 1813 | 20240204 | 1931 | 2350500 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1404 | 37.6992 | -120.3346 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020865 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910683 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | L1457 | 20240204 | 1856 | 20240205 | 341 | 2351545 | 525 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6300 | 37.9018 | -120.4764 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021434 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911269 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | RECLOSER | 6318 | 20240204 | 1906 | 20240204 | 2133 | 2351906 | 147 | Distribution Circuit | Vegetation | Tree - branch fell on line | 414 | 60858 | 37.7777 | -120.8494 | Yes | Clear-Strong Winds;32-90 F | Transformer (OH) | Normal | 24-0021109 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1910932 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7756 | 20240204 | 1910 | 20240205 | 1519 | 2360469 | 1209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 23386 | 37.3454 | -120.9238 | Yes | Clear;32-90 F |  |  | 24-0022240 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911904 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 10922 | 20240204 | 1913 | 20240204 | 2146 | 2352166 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 918 | 37.3391 | -120.5178 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0021184 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911009 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 13079 | 20240204 | 1917 | 20240204 | 2036 | 2352247 | 79 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 50 | 3950 | 36.9965 | -120.0832 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020983 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1910804 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | RECLOSER | 90600 | 20240204 | 2026 | 20240206 | 1848 | 2353830 | 2782 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 292110 | 37.3618 | -121.0763 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020463 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1910806 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318556847295 | 20240204 | 2035 | 20240204 | 2106 | 2353759 | 31 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 186 | 37.7978 | -121.0006 | Yes | Partly Cloudy-Strong Winds;32-90 F | Secondary | Normal | 24-0020974 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1910794 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320076628533 | 20240204 | 2045 | 20240204 | 2059 | 2344406 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 112 | 37.2844 | -120.473 | Yes | Clear-Strong Winds;32-90 F | Other | Arcing | 24-0021061 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1910884 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | TAR FLAT-0401 | 163240401 | RECLOSER | 922858 | 20240204 | 2056 | 20240205 | 1650 | 2354284 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 55933 | 37.9843 | -120.3794 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0021120 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1910943 | 0 | EPSS Ckt | N | 2024 | C PHASE- GRD- INST
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 9547 | 20240204 | 2149 | 20240205 | 401 | 2355004 | 372 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 744 | 37.7708 | -120.9967 | Yes | Clear;32-90 F |  |  | 24-0021470 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911305 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 6913 | 20240204 | 2347 | 20240205 | 1354 | 2355800 | 847 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 12217 | 37.1117 | -120.2687 | Yes | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0021431 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911266 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | FUSE | 9864 | 20240205 | 5 | 20240205 | 1430 | 2355905 | 863 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 4315 | 36.7416 | -120.4779 | No | Partly Cloudy;32-90 F |  |  | 24-0022183 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911858 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321156818618 | 20240205 | 50 | 20240205 | 948 | 2354949 | 538 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 538 | 37.0109 | -120.1051 | No | Partly Cloudy-Drizzle;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0021375 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911208 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | T0664 | 20240205 | 237 | 20240205 | 1310 | 2356376 | 633 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1899 | 37.3304 | -120.5371 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0022032 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911746 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 3124 | 20240205 | 335 | 20240206 | 1635 | 2356573 | 2220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 13327 | 37.1384 | -120.6026 | No | Overcast-Fog-Drizzle;32-90 F | Other | Broken | 24-0022358 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912010 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 318394631796 | 20240205 | 350 | 20240205 | 438 | 2356628 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 144 | 37.3715 | -121.0535 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0021479 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911315 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | JUMPER | WIRE DOWN 5 S/OF CGC# 318495620935 | 20240205 | 532 | 20240205 | 1803 | 2356964 | 751 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 82948 | 37.0687 | -121.0163 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021514 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | Yes | 1911356 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320201253399 | 20240205 | 737 | 20240205 | 2146 | 2357553 | 849 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 849 | 37.9665 | -120.4311 | No | Overcast-Rain;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0021950 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1911678 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S945 | 20240205 | 739 | 20240205 | 1510 | 2357565 | 451 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 451 | 37.8276 | -120.9945 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0021959 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911687 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 778207 | 20240205 | 825 | 20240205 | 1545 | 2357943 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1320 | 37.8623 | -120.7758 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021778 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1911531 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7554 | 20240205 | 931 | 20240206 | 956 | 2359887 | 1465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2931 | 37.3025 | -120.7879 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0022035 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911748 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7343 | 20240205 | 1104 | 20240206 | 1031 | 2359111 | 1407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 40652 | 37.3601 | -120.8143 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0021858 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1911596 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | RECLOSER | 29612 | 20240205 | 1206 | 20240205 | 1304 | 2359456 | 58 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 568 | 32944 | 37.3585 | -120.8503 | No | Clear-Strong Winds;32-90 F | Insulator | Burned/flashed | 24-0021951 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1911679 | 0 | Non-EPSS | N | 2024 | ABC- TIME OC
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 2387 | 20240205 | 1222 | 20240205 | 1228 | 2359578 | 6 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 708 | 37.3822 | -120.7255 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0021968 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1911695 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | RECLOSER | 9000 | 20240205 | 1422 | 20240205 | 1431 | 2360295 | 9 | Distribution Circuit | Vegetation | Tree - branch fell on line | 973 | 8757 | 37.7937 | -120.9967 | No | Overcast;32-90 F | Conductor- Overhead | Arcing | 24-0022169 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1911847 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 5020 | 20240205 | 1551 | 20240205 | 1602 | 2360777 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1196 | 13156 | 37.2065 | -119.7142 | No | Overcast;32-90 F |  |  | 24-0022340 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911993 | 0 | EPSS Ckt | N | 2024 | A INST
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 3795 | 20240205 | 1643 | 20240205 | 1652 | 2361127 | 9 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 15 | 135 | 37.0084 | -120.7081 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0022430 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1912076 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | OCB | 1116/2 | 20240205 | 1746 | 20240205 | 1837 | 2361432 | 51 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 2052 | 86265 | 37.2732 | -120.4872 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0022556 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1912181 | 0 | Non-EPSS | N | 2024 | A- BTIME
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | OTHER | WIRE DOWN | 20240205 | 2021 | 20240205 | 2301 | 2362170 | 160 | Distribution Circuit | 3rd Party | Vehicle | 589 | 35874 | 37.79 | -120.9872 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022739 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | Yes | 1912374 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | SWITCH | 3035 | 20240205 | 2311 | 20240206 | 328 | 2362596 | 257 | Distribution Circuit | Equipment Failure/Involved | Overhead | 500 | 16444 | 37.0603 | -120.8624 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0022798 | OH | Sus | 35528425 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1912470 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322294426264 | 20240206 | 710 | 20240206 | 1133 | 2363145 | 263 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 526 | 37.2186 | -119.7117 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023017 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912599 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | TRANSFORMER | 318994743860 | 20240206 | 849 | 20240206 | 1010 | 2363466 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 243 | 37.7041 | -120.8484 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0023156 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912689 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20240206 | 1016 | 20240206 | 1731 | 2363830 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 688 | 180069 | 38.1888 | -120.0082 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 24-0023168 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912695 | 0 | EPSS Ckt | N | 2024 | B & GRD
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 550019 | 20240206 | 1043 | 20240206 | 1410 | 2363606 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 4140 | 37.8079 | -120.9969 | No | Clear;32-90 F | Insulator | Broken | 24-0023201 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1912714 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | T1745 | 20240206 | 1247 | 20240206 | 1319 | 2364214 | 32 | Transformer only | Equipment Failure/Involved | Underground | 11 | 352 | 37.396 | -120.6085 | No | Overcast-Rain;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0023423 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1912875 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 465 | 20240206 | 1335 | 20240206 | 1436 | 2364555 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 549 | 37.7854 | -120.8222 | No | Partly Cloudy;32-90 F |  |  | 24-0023468 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1912906 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320213719906 | 20240206 | 1432 | 20240206 | 1611 | 2364715 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 99 | 37.0461 | -120.4279 | No | Partly Cloudy-Drizzle;32-90 F | Fuse | Broken | 24-0023594 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913000 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | RECLOSER | 64194 | 20240206 | 1556 | 20240206 | 1805 | 2365005 | 129 | Distribution Circuit | Vegetation | Tree - branch fell on line | 58 | 6762 | 37.4231 | -120.6646 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0023674 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1913074 | 0 | Non-EPSS | N | 2024 | B- C
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317470036577 | 20240206 | 1900 | 20240207 | 1150 | 2365525 | 1010 | Transformer only | Unknown Cause | Patrol - not conducted | 7 | 7070 | 37.5019 | -121.3733 | No | Partly Cloudy;32-90 F |  |  | 24-0023751 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1913135 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319670031131 | 20240207 | 320 | 20240207 | 516 | 2366059 | 116 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1044 | 37.355 | -120.6144 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Burned Open | 24-0023943 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913302 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | TRANSFORMER | 318828543701 | 20240207 | 624 | 20240207 | 1136 | 2366165 | 312 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 312 | 37.6998 | -120.906 | No | Overcast-Fog;32-90 F | Transformer | Burned Open | 24-0024037 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913342 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | TRANSFORMER | 320975711310 | 20240207 | 807 | 20240207 | 1111 | 2366387 | 184 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 184 | 36.8094 | -120.1688 | No | Partly Cloudy;32-90 F |  |  | 24-0024165 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1913416 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | TRANSFORMER | 320138731801 | 20240207 | 825 | 20240207 | 1605 | 2366157 | 460 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1960 | 37.3743 | -120.4527 | No | Partly Cloudy-Fog;32-90 F | Secondary | Broken | 24-0023993 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1913323 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | TRIP-SAVER | 10480 | 20240207 | 859 | 20240207 | 1137 | 2367058 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 284 | 36.5744 | -120.4788 | No | Partly Cloudy;32-90 F |  |  | 24-0024189 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1913433 | 0 | Non-EPSS | N | 2024 | B & C PH
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6846 | 20240207 | 1043 | 20240207 | 1205 | 2366906 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1477 | 37.0543 | -120.0759 | No | Overcast;32-90 F | Lightning Arrestor | Broken | 24-0024258 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913474 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | TRANSFORMER | 415659045508 | 20240207 | 1122 | 20240208 | 1710 | 2367078 | 1788 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1788 | 36.5747 | -120.479 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0024198 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913436 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | SWITCH | 1578 | 20240207 | 1257 | 20240207 | 1443 | 2367338 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 106 | 36.9456 | -120.0493 | No | Overcast;32-90 F | Crossarm- Wood | Burned/flashed | 24-0024290 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1913493 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 863661 | 20240207 | 1322 | 20240207 | 1352 | 2367437 | 30 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 22 | 660 | 37.776 | -120.8475 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0024350 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913528 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | FUSE | 88322 | 20240207 | 1547 | 20240207 | 1720 | 2367967 | 93 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 104 | 9672 | 37.3606 | -120.5977 | No | Overcast-Rain;32-90 F |  |  | 24-0024533 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913623 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 318956019125 | 20240207 | 1640 | 20240207 | 1709 | 2368034 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 29 | 37.0243 | -120.8584 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0024584 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913655 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 10517 | 20240207 | 1709 | 20240207 | 1922 | 2368286 | 133 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 24 | 3192 | 37.4682 | -119.8825 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0024680 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913736 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 2071 | 20240207 | 1832 | 20240207 | 2207 | 2368573 | 215 | Distribution Circuit | Environmental/External | Ice or snow | 73 | 15695 | 37.8302 | -120.2039 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 24-0024904 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913934 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1321 | 20240207 | 1852 | 20240208 | 47 | 2368623 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 11005 | 37.7953 | -120.1228 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 24-0025275 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1914297 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | L1165 | 20240207 | 1948 | 20240207 | 2136 | 2368723 | 108 | Distribution Circuit | 3rd Party | Other | 22 | 2376 | 38.032 | -120.2249 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 24-0024878 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1913907 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23936 | 20240207 | 1952 | 20240208 | 55 | 2368733 | 303 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 909 | 37.7222 | -120.1193 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0025374 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1914395 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321961835880 | 20240207 | 1956 | 20240208 | 1011 | 2368749 | 855 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1710 | 37.4833 | -119.8252 | No | Overcast-Fog-Snow;Below 32 F | Connector or Splice (OH) | Broken | 24-0026134 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915067 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 4532 | 20240207 | 2003 | 20240208 | 934 | 2368761 | 811 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 5677 | 37.3325 | -120.4147 | No | Overcast-Rain;32-90 F |  |  | 24-0025187 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1914213 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | FUSE | 88322 | 20240207 | 2018 | 20240208 | 931 | 2368783 | 793 | Distribution Circuit | Equipment Failure/Involved | Underground | 104 | 29559 | 37.3606 | -120.5977 | No | Overcast;32-90 F | Elbow | Failed/Faulted | 24-0024738 | UG | Sus | 46176360 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913773 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 87889 | 20240207 | 2103 | 20240208 | 931 | 2368891 | 748 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5236 | 37.475 | -119.7725 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0026067 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915034 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321644933890 | 20240207 | 2110 | 20240209 | 955 | 2368800 | 2205 | Transformer only | Vegetation | Tree - fell into line | 1 | 2205 | 37.4316 | -119.9335 | No | Overcast-Fog-Rain;32-90 F | Service conductor | Broken- wire on object | 24-0024855 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1913885 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20240207 | 2320 | 20240208 | 1211 | 2369009 | 771 | Distribution Circuit | Environmental/External | Ice or snow | 162 | 124902 | 37.8183 | -120.0958 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025150 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1914179 | 0 | EPSS Ckt | N | 2024 | GRD & SGF
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 10295 | 20240207 | 2331 | 20240208 | 1927 | 2369017 | 1196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 127 | 42431 | 37.3168 | -119.5859 | No | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken | 24-0025468 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1914490 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 89099 | 20240208 | 3 | 20240208 | 1701 | 2369038 | 1018 | Distribution Circuit | Environmental/External | Ice or snow | 34 | 34612 | 37.2496 | -119.5654 | No | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken | 24-0025686 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1914707 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 513735 | 20240208 | 24 | 20240208 | 1740 | 2369045 | 1036 | Distribution Circuit | Environmental/External | Ice or snow | 37 | 38332 | 37.5325 | -119.9475 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025933 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1914963 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322141334635 | 20240208 | 610 | 20240208 | 1644 | 2369129 | 634 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 1268 | 37.448 | -119.7639 | No | Partly Cloudy-Fog;Below 32 F | Transformer | Failed/Faulted | 24-0026215 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915103 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 501771 | 20240208 | 611 | 20240208 | 642 | 2369126 | 31 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 4650 | 37.2319 | -119.4679 | No | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Normal | 24-0025945 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1914965 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2261 | 20240208 | 623 | 20240208 | 1148 | 2369132 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 34429 | 38.0594 | -120.1806 | No | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken | 24-0026031 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915013 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 2493 | 20240208 | 651 | 20240209 | 1035 | 2369155 | 1664 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9984 | 37.5386 | -119.9184 | No | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0026402 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1915190 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 5587 | 20240208 | 707 | 20240209 | 1212 | 2369461 | 1745 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 3490 | 37.3373 | -119.7669 | No | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0026047 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1915020 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3834 | 20240208 | 714 | 20240208 | 1413 | 2370250 | 419 | Distribution Circuit | Animal | Other | 9 | 3633 | 36.9238 | -120.6549 | No | Partly Cloudy-Fog;32-90 F | Jumper | Normal | 24-0026329 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915158 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 577693 | 20240208 | 737 | 20240209 | 1025 | 2369751 | 1608 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 1608 | 37.3452 | -119.7621 | No | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0026169 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1915078 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | OTHER | 10398 | 20240208 | 757 | 20240209 | 1407 | 2369251 | 1810 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 5430 | 37.4042 | -119.7667 | No | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0026508 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | Yes | Yes | 1915241 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4601 | 20240208 | 812 | 20240208 | 1600 | 2369307 | 468 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 16380 | 37.757 | -120.1145 | No | Partly Cloudy-Fog;Below 32 F |  |  | 24-0026478 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915221 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322829526228 | 20240208 | 839 | 20240208 | 1452 | 2369559 | 373 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 373 | 37.2178 | -119.5291 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0026418 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915193 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | OTHER | WIRE DOWN HOT SS/OF CGC#322236532945 | 20240208 | 854 | 20240209 | 845 | 2370367 | 1431 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 3781 | 37.4015 | -119.7287 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026385 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1915186 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320873956913 | 20240208 | 859 | 20240208 | 1017 | 2369452 | 78 | Transformer only | Environmental/External | Ice or snow | 3 | 234 | 38.0622 | -120.1969 | No | Partly Cloudy-Snow;32-90 F | Fuse | Normal | 24-0026143 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915072 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 10110 | 20240208 | 909 | 20240208 | 1817 | 2369463 | 548 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1068 | 286109 | 37.267 | -119.7114 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0026057 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915025 | 0 | EPSS Ckt | N | 2024 | B & C
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | LR 363884 | 20240208 | 921 | 20240208 | 1408 | 2369490 | 287 | Distribution Circuit | Environmental/External | Ice or snow | 70 | 20090 | 37.2317 | -119.4996 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0026337 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915163 | 0 | EPSS Ckt | N | 2024 | A & B
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 10295 | 20240208 | 933 | 20240208 | 1115 | 2369514 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 10914 | 37.3168 | -119.5859 | No | Partly Cloudy-Fog-Snow;Below 32 F |  |  | 24-0026181 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915084 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 2841 | 20240208 | 955 | 20240208 | 1316 | 2369554 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2410 | 37.5325 | -120.0518 | No | Overcast-Fog;32-90 F |  |  | 24-0026316 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915147 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 673480 | 20240208 | 956 | 20240208 | 1246 | 2369561 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 585 | 83106 | 37.288 | -119.5203 | No | Partly Cloudy;32-90 F |  |  | 24-0026108 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915053 | 0 | EPSS Ckt | N | 2024 | A- B- 51
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | S2243 | 20240208 | 1007 | 20240208 | 1205 | 2369596 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 241 | 28438 | 38.0383 | -120.2477 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0026248 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915118 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20240208 | 1139 | 20240208 | 1148 | 2369925 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 448 | 4032 | 37.8306 | -120.2367 | No | Partly Cloudy-Drizzle;32-90 F | Insulator | Broken | 24-0026224 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915104 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 23593 | 20240208 | 1159 | 20240208 | 1716 | 2370004 | 317 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1268 | 37.1581 | -120.87 | No | Partly Cloudy;32-90 F |  |  | 24-0026505 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915239 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 893393 | 20240208 | 1231 | 20240208 | 1444 | 2370103 | 133 | Distribution Circuit | Animal | Other | 7 | 931 | 37.0898 | -120.9076 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0026404 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915191 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | FUSE | 3803 | 20240208 | 1405 | 20240209 | 1139 | 2370332 | 1294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 37526 | 37.0538 | -121.0256 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0026359 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915178 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | TRANSFORMER | 318428730151 | 20240208 | 1431 | 20240208 | 1935 | 2370954 | 304 | Transformer only | Vegetation | Tree - fell into line | 1 | 304 | 37.3268 | -121.0415 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0026573 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915293 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 103437 | 20240208 | 2125 | 20240208 | 2206 | 2371000 | 41 | Distribution Circuit | Animal | Bird found | 266 | 10906 | 38.0127 | -120.3073 | No | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Normal | 24-0026749 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915464 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | OCB | 2101/2 | 20240209 | 1015 | 20240209 | 1424 | 2371476 | 249 | Distribution Circuit | 3rd Party | Vehicle | 5159 | 357668 | 37.2731 | -120.4872 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0026918 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | Yes | No | 1915558 | 0 | Non-EPSS | N | 2024 | A- B - C
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 320755936611 | 20240209 | 1024 | 20240209 | 1419 | 2371487 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 235 | 37.5066 | -120.2399 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0027011 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915598 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320099421437 | 20240209 | 1300 | 20240209 | 1412 | 2371805 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 72 | 37.0889 | -120.4656 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0027072 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915629 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 13099 | 20240209 | 1450 | 20240209 | 1600 | 2371981 | 70 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 22 | 1540 | 37.0908 | -120.2937 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0027125 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1915662 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | OCB | 2101/2 | 20240209 | 1619 | 20240210 | 241 | 2372132 | 622 | Distribution Circuit | 3rd Party | Vehicle | 5159 | 898870 | 37.2731 | -120.4872 | No | Partly Cloudy;32-90 F | Recloser | Broken- wire on ground | 24-0027137 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1915669 | 0 | Non-EPSS | N | 2024 | B & C
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 7150 | 20240209 | 1725 | 20240210 | 136 | 2372202 | 491 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 10134 | 37.5603 | -121.177 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027161 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1915684 | 0 | EPSS Ckt | N | 2024 | B- C- GRD
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320727256182 | 20240210 | 147 | 20240210 | 1401 | 2372435 | 734 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 1468 | 38.0429 | -120.248 | No | Clear;Below 32 F |  |  | 24-0027279 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915788 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 321962324797 | 20240210 | 1005 | 20240210 | 1014 | 2372572 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 9 | 37.1789 | -119.8261 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0027328 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915815 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20240211 | 1049 | 20240211 | 1257 | 2373255 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 19328 | 37.0679 | -119.9091 | No | Clear;32-90 F |  |  | 24-0027599 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | No | No | 1916027 | 0 | EPSS Ckt | N | 2024 | B & GRD
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 20240211 | 1737 | 20240211 | 2202 | 2373450 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 89 | 23585 | 37.7148 | -120.0964 | No | Clear;32-90 F |  |  | 24-0027654 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1916071 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320038438155 | 20240212 | 835 | 20240213 | 401 | 2373723 | 1166 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1166 | 37.5468 | -120.4895 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0027849 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916237 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | JUMPER | OJ'S 1 POLE N/OF CGC# 321197513684 | 20240212 | 1120 | 20240212 | 1310 | 2373936 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 110 | 36.8765 | -120.092 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0027869 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1916242 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 3799 | 20240212 | 1320 | 20240212 | 1515 | 2374090 | 115 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 15 | 1725 | 36.7699 | -120.3146 | No | Partly Cloudy;32-90 F |  |  | 24-0028013 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1916287 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1102 | 252091102 | RECLOSER | 520064 | 20240212 | 1425 | 20240212 | 1521 | 2374169 | 56 | Distribution Circuit | Vegetation | Tree - branch fell on line | 374 | 20944 | 37.0748 | -120.86 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0027990 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1916281 | 0 | Non-EPSS | N | 2024 | A- B- C
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | TRANSFORMER | 320685718555 | 20240212 | 1437 | 20240212 | 2149 | 2374181 | 432 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 432 | 37.0096 | -120.2662 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0028034 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916291 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | OCB | 1116/2 | 20240213 | 316 | 20240213 | 650 | 2374506 | 214 | Distribution Circuit | 3rd Party | Vehicle | 304 | 26779 | 37.2732 | -120.4872 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0028135 | OH | Sus | 35531134 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1916363 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319350831886 | 20240213 | 334 | 20240213 | 411 | 2374507 | 37 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 407 | 37.375 | -120.7242 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0028137 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1916365 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | RECLOSER | 4420 | 20240213 | 650 | 20240213 | 1124 | 2374560 | 274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 8283 | 37.2873 | -120.3791 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0028176 | OH | Sus | 46190178 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1916374 | 0 | EPSS Ckt | N | 2024 | A & GRD
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 10841 | 20240213 | 922 | 20240213 | 938 | 2374920 | 16 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 85 | 37.0276 | -120.8545 | No | Partly Cloudy;32-90 F |  |  | 24-0028243 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916499 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 26537 | 20240213 | 929 | 20240213 | 1545 | 2374818 | 376 | Distribution Circuit | Environmental/External | Lightning | 1 | 376 | 37.3299 | -120.9947 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0028356 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1916561 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | FUSE | 9803 | 20240213 | 944 | 20240213 | 1203 | 2374944 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 464 | 36.8217 | -120.4103 | No | Partly Cloudy;32-90 F |  |  | 24-0028353 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916559 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320462515684 | 20240213 | 953 | 20240213 | 1301 | 2374967 | 188 | Transformer only | Animal | Other | 1 | 188 | 36.932 | -120.3426 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0028402 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916576 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320081928004 | 20240213 | 1003 | 20240213 | 1045 | 2374983 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 168 | 37.2697 | -120.4711 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0028290 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916527 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319606330280 | 20240213 | 1134 | 20240213 | 2008 | 2375101 | 514 | Transformer only | 3rd Party | Contact with High Voltage- 3rd party | 2 | 1028 | 37.3312 | -120.6368 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0028372 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1916566 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1105 | 254101105 | TRANSFORMER | 320708722602 | 20240213 | 1221 | 20240213 | 1355 | 2375183 | 90 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 2694 | 37.1207 | -120.2582 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0028352 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1916558 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 53401 | 20240213 | 1340 | 20240213 | 1429 | 2375297 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 588 | 37.9655 | -120.4021 | No | Partly Cloudy;32-90 F |  |  | 24-0028451 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916596 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | TRANSFORMER | 415592651362 | 20240213 | 1351 | 20240213 | 2053 | 2375308 | 422 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 422 | 36.7343 | -120.5049 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0028559 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916609 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319432530813 | 20240213 | 1431 | 20240213 | 1738 | 2375268 | 187 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 374 | 37.3458 | -120.6952 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0028479 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916600 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319078246385 | 20240213 | 1614 | 20240213 | 2030 | 2375324 | 256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2722 | 37.7734 | -120.8197 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0028545 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916607 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | FUSE | 6959 | 20240213 | 1630 | 20240213 | 1813 | 2375463 | 103 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 618 | 36.8294 | -120.0832 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0028592 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916624 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 7454 | 20240213 | 1656 | 20240213 | 1928 | 2375482 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2384 | 37.2196 | -120.2151 | No | Clear;32-90 F |  |  | 24-0028599 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1916634 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 2391 | 20240214 | 459 | 20240214 | 953 | 2375772 | 294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 3242 | 37.7946 | -120.9508 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0028650 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916679 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320694554454 | 20240214 | 1255 | 20240214 | 1532 | 2376310 | 157 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 471 | 37.9955 | -120.26 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 24-0028952 | OH | Sus | 46190804 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916865 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 1993 | 20240214 | 1316 | 20240214 | 1716 | 2376324 | 240 | Distribution Circuit | Animal | Other | 3 | 504 | 36.9167 | -120.2918 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0029112 | OH | Sus | 46190836 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1916900 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 7075 | 20240214 | 1450 | 20240214 | 1551 | 2376195 | 61 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 61 | 37.5114 | -119.9938 | No | Overcast;32-90 F | Secondary | Broken | 24-0029075 | UG | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1916890 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318695347570 | 20240214 | 1825 | 20240214 | 2008 | 2376655 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 103 | 37.806 | -120.9528 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0029192 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1916925 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7994 | 20240215 | 56 | 20240215 | 104 | 2376815 | 8 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 13 | 37.5201 | -120.6073 | No | Overcast-Rain;32-90 F |  |  | 24-0029265 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1916983 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | RECLOSER | 9760 | 20240215 | 614 | 20240215 | 1450 | 2376897 | 516 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 30392 | 36.706 | -120.6196 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0029282 | OH | Sus | 46191100 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1917000 | 0 | EPSS Ckt | N | 2024 | A PH & GRD
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | TRANSFORMER | 318505323367 | 20240215 | 722 | 20240215 | 924 | 2376942 | 122 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 366 | 37.1402 | -121.0135 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0029370 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1917057 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20240215 | 839 | 20240215 | 953 | 2377002 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 688 | 50912 | 38.1888 | -120.0082 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0029346 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917041 | 0 | EPSS Ckt | N | 2024 | A PH & GRD
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319427432387 | 20240215 | 952 | 20240215 | 1737 | 2377092 | 465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1029 | 37.3893 | -120.6971 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0029413 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1917067 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1103 | 253671103 | SWITCH | 4837 | 20240215 | 1516 | 20240215 | 1522 | 2377404 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 32 | 192 | 36.6765 | -120.6217 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0029282 | OH | Sus | 46191100 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1917109 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | 318530527514 | 20240215 | 1854 | 20240216 | 532 | 2377602 | 638 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4466 | 37.2545 | -121.0058 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0029702 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917144 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 11810 | 20240215 | 2254 | 20240215 | 2356 | 2377697 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 243 | 15066 | 37.3312 | -120.6346 | No | Partly Cloudy;32-90 F |  |  | 24-0029726 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917171 | 0 | Non-EPSS | N | 2024 | B PH- SGF
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | S2605 | 20240216 | 1451 | 20240216 | 1641 | 2378376 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1210 | 37.7622 | -120.7857 | No | Clear;32-90 F |  |  | 24-0030068 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1917409 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | RECLOSER | 90170 | 20240216 | 2051 | 20240217 | 409 | 2378591 | 438 | Distribution Circuit | 3rd Party | Vehicle | 303 | 15926 | 37.0108 | -120.6372 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0030094 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1917428 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | JUMPER | HS JUMPERS @ CGC# 318886047685 | 20240217 | 1009 | 20240217 | 1112 | 2378790 | 63 | Distribution Circuit | Company Initiated | Other Circuits | 4 | 252 | 37.8089 | -120.8865 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0030164 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1917493 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 751914 | 20240217 | 1103 | 20240217 | 1200 | 2378837 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 115 | 6555 | 37.2927 | -119.5317 | No | Overcast;32-90 F |  |  | 24-0030182 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1917497 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320013821175 | 20240217 | 1416 | 20240217 | 1509 | 2378961 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 265 | 37.0821 | -120.4977 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 24-0030237 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917524 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318557947246 | 20240217 | 1852 | 20240217 | 2007 | 2379185 | 75 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 450 | 37.7965 | -121.0002 | No | Clear;32-90 F |  |  | 24-0030292 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917572 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 1835 | 20240217 | 2033 | 20240217 | 2158 | 2379256 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1445 | 37.7838 | -121.0525 | No | Overcast-Fog;32-90 F |  |  | 24-0030326 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1917605 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 24193 | 20240217 | 2214 | 20240217 | 2352 | 2379314 | 98 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 294 | 37.1202 | -120.4899 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0030349 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1917629 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | RECLOSER | 11540 | 20240217 | 2219 | 20240218 | 800 | 2379312 | 581 | Distribution Circuit | 3rd Party | Vehicle | 8 | 4648 | 36.9671 | -120.1285 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0030346 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1917626 | 0 | Non-EPSS | N | 2024 | C AND GROUND
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322408525807 | 20240218 | 950 | 20240218 | 1515 | 2379492 | 325 | Transformer only | Equipment Failure/Involved | Underground | 3 | 975 | 37.206 | -119.6733 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0030432 | UG | Sus | 46192727 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917685 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 852227 | 20240218 | 1342 | 20240218 | 2002 | 2379777 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 380 | 36.8804 | -119.9155 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0030476 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1917715 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 21297 | 20240218 | 1356 | 20240219 | 919 | 2379683 | 1163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 22097 | 37.3188 | -121.1094 | No | Clear;32-90 F |  |  | 24-0030593 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917833 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | 319676032292 | 20240218 | 1458 | 20240218 | 1739 | 2379749 | 161 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1449 | 37.387 | -120.6124 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0030484 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917722 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 248699 | 20240218 | 2306 | 20240219 | 550 | 2380198 | 404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 470 | 37.2745 | -120.3249 | No | Clear-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030580 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917820 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 13165 | 20240218 | 2332 | 20240219 | 622 | 2380210 | 410 | Distribution Circuit | Animal | Other | 11 | 1909 | 37.0069 | -119.9917 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 24-0030588 | OH | Sus | 46192783 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917828 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | JUMPER | BROKEN JUMPER ON 7554 POS 3 CUTOUT | 20240219 | 124 | 20240219 | 537 | 2380253 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 759 | 37.3025 | -120.7879 | No | Overcast-Fog-Rain;32-90 F | Jumper | Broken | 24-0030595 | OH | Sus | 46192784 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1917835 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 911059 | 20240219 | 223 | 20240221 | 1015 | 2380265 | 3352 | Distribution Circuit | Animal | Other | 6 | 4762 | 37.1267 | -120.1072 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Normal | 24-0030605 | OH | Sus | 35532357 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917845 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | MTR#1005002258 | 20240219 | 432 | 20240219 | 1058 | 2380287 | 386 | Transformer only | Environmental/External | Lightning | 1 | 386 | 37.2752 | -120.325 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030665 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917892 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 10398 | 20240219 | 547 | 20240219 | 919 | 2380352 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 636 | 37.4042 | -119.7667 | No | Clear;32-90 F |  |  | 24-0030649 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1917878 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 4717 | 20240219 | 729 | 20240219 | 1050 | 2380428 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3417 | 37.3484 | -120.5931 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0030753 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917964 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | FUSE | 6087 | 20240219 | 749 | 20240220 | 203 | 2380453 | 1094 | Distribution Circuit | Equipment Failure/Involved | Underground | 103 | 112682 | 36.9674 | -120.0762 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0030668 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917896 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | MTR#1009608352 | 20240219 | 841 | 20240219 | 1141 | 2380529 | 180 | Transformer only | Environmental/External | Lightning | 1 | 180 | 37.2748 | -120.325 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030675 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917901 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 6110 | 20240219 | 900 | 20240219 | 1738 | 2380560 | 518 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 66730 | 37.128 | -119.7352 | No | Overcast-Fog-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0030683 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1917910 | 0 | EPSS Ckt | N | 2024 | A & GRD
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | JUMPER | OJ'S E/OF MTR# 1010273086 | 20240219 | 904 | 20240219 | 1437 | 2380575 | 333 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 666 | 36.8876 | -120.1288 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Arcing | 24-0030686 | OH | Sus | 46192744 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1917914 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320118529299 | 20240219 | 945 | 20240219 | 1001 | 2380551 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 144 | 37.3054 | -120.459 | No | Partly Cloudy-Drizzle;32-90 F | Connector or Splice (OH) | Burned Open | 24-0030715 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1917933 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6577 | 20240219 | 953 | 20240219 | 2205 | 2380638 | 732 | Distribution Circuit | 3rd Party | Vehicle | 14 | 10248 | 36.8499 | -120.0192 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0030736 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1917950 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320508528318 | 20240219 | 1531 | 20240219 | 1918 | 2381741 | 227 | Transformer only | Environmental/External | Lightning | 2 | 454 | 37.2771 | -120.3249 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0031008 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918141 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | FUSE | 24519 | 20240219 | 1807 | 20240219 | 1940 | 2381953 | 93 | Distribution Circuit | Animal | Bird found | 298 | 27714 | 36.9554 | -120.0744 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0031058 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1918173 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | SWITCH | 23436 | 20240219 | 1908 | 20240219 | 1917 | 2382012 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 55 | 495 | 37.0846 | -119.7214 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0030683 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1918175 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | L461 | 20240219 | 1911 | 20240219 | 2245 | 2382018 | 214 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 12198 | 37.9901 | -120.4089 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0031080 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1918192 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 919060 | 20240219 | 2011 | 20240220 | 246 | 2382055 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 21303 | 37.9212 | -120.3506 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0031089 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1918199 | 0 | EPSS Ckt | N | 2024 | A AND B
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7684 | 20240220 | 7 | 20240220 | 143 | 2382335 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1728 | 37.4395 | -120.576 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0031150 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1918255 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319606330280 | 20240220 | 946 | 20240220 | 1358 | 2382728 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 504 | 37.3312 | -120.6368 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0031351 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918401 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320081928004 | 20240220 | 1029 | 20240220 | 1113 | 2382814 | 44 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 176 | 37.2697 | -120.4711 | No | Clear;32-90 F |  |  | 24-0031357 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1918403 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319322045095 | 20240220 | 1118 | 20240220 | 1249 | 2382871 | 91 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 91 | 37.7378 | -120.7353 | No | Clear;32-90 F |  |  | 24-0031435 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1918424 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 6475 | 20240220 | 1357 | 20240220 | 1645 | 2383074 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 4032 | 36.8953 | -119.811 | No | Overcast;32-90 F | Insulator | Broken | 24-0031558 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Three Phase Fault | 0 | No | No | No | 1918464 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 4532 | 20240220 | 1428 | 20240220 | 2154 | 2383200 | 446 | Distribution Circuit | 3rd Party | Aircraft- crop dusting | 7 | 3122 | 37.3325 | -120.4147 | No | Overcast-Drizzle-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0031611 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1918471 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 6762 | 20240220 | 1534 | 20240220 | 1636 | 2383152 | 62 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 3720 | 37.0255 | -120.1455 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0031622 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1918476 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | 22828 | 20240220 | 1553 | 20240220 | 1805 | 2383160 | 132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 516 | 37.7499 | -120.9055 | No | Overcast;32-90 F | Insulator | Broken | 24-0031596 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1918469 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | OCB | 2101/2 | 20240220 | 1603 | 20240220 | 1824 | 2383191 | 141 | Distribution Circuit | Environmental/External | Lightning | 5129 | 723189 | 37.2731 | -120.4872 | No | Overcast-Rain-Lightning;32-90 F | Fuse | Failed/Faulted | 24-0031617 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1918473 | 0 | Non-EPSS | N | 2024 | B&C TIME
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320090229523 | 20240220 | 1603 | 20240221 | 135 | 2383253 | 572 | Transformer only | Environmental/External | Lightning | 8 | 4576 | 37.3115 | -120.4687 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 24-0031617 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918485 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320091729508 | 20240220 | 1603 | 20240221 | 130 | 2383256 | 567 | Transformer only | Environmental/External | Lightning | 2 | 1134 | 37.311 | -120.4682 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 24-0031617 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918486 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320091729500 | 20240220 | 1603 | 20240221 | 127 | 2383260 | 564 | Transformer only | Environmental/External | Lightning | 15 | 8460 | 37.3108 | -120.4682 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0031617 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918487 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320089729500 | 20240220 | 1603 | 20240221 | 144 | 2383261 | 581 | Transformer only | Environmental/External | Lightning | 5 | 2905 | 37.3108 | -120.4689 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 24-0031617 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918488 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 21066 | 20240220 | 1607 | 20240221 | 320 | 2383193 | 673 | Distribution Circuit | Environmental/External | Lightning | 9 | 1417 | 37.5067 | -120.4212 | No | Overcast-Drizzle-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 24-0031650 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1918493 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 320030348568 | 20240220 | 1648 | 20240220 | 2151 | 2383240 | 303 | Transformer only | Environmental/External | Lightning | 1 | 303 | 37.8333 | -120.4907 | No | Overcast-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0031664 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918501 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1102 | 253671102 | OCB | 1102/2 | 20240220 | 2024 | 20240221 | 100 | 2383404 | 256 | Distribution Circuit | Animal | Other | 113 | 30471 | 36.6512 | -120.5803 | No | Overcast-Drizzle;32-90 F | Recloser | Burned/flashed | 24-0031688 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | No | No | 1918516 | 0 | Non-EPSS | N | 2024 | ABC- TIME OC
YOSEMITE | YOSEMITE | EL CAPITAN-1102 | 253881102 | FUSE | 320118330786 | 20240221 | 933 | 20240221 | 1606 | 2384002 | 393 | Distribution Circuit | Environmental/External | Lightning | 1 | 393 | 37.3467 | -120.4594 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0031985 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918797 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321324115246 | 20240221 | 1233 | 20240221 | 1304 | 2384322 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 31 | 36.9177 | -120.0478 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0032100 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1918823 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | TRANSFORMER | 320158217156 | 20240221 | 1551 | 20240221 | 1718 | 2384492 | 87 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 87 | 36.9715 | -120.4482 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0032245 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1918855 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 319028548713 | 20240221 | 1707 | 20240221 | 1728 | 2384565 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 21 | 37.8371 | -120.8377 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0032285 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1918864 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | JUMPER | S715 #2 JPR | 20240222 | 302 | 20240222 | 959 | 2384786 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2919 | 37.7619 | -120.8135 | No | Clear;32-90 F | Jumper | Burned Open | 24-0032368 | OH | Sus | 46193553 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1918936 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320270627325 | 20240222 | 956 | 20240222 | 1248 | 2385156 | 172 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 172 | 37.2512 | -120.4065 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0032505 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919114 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 757051 | 20240223 | 523 | 20240223 | 1220 | 2385823 | 417 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1251 | 36.8874 | -120.3059 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0032970 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1919390 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320130322704 | 20240223 | 811 | 20240223 | 1301 | 2385914 | 290 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 580 | 37.1238 | -120.4554 | No | Overcast;32-90 F | Secondary | Broken | 24-0033081 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919530 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 26748 | 20240223 | 924 | 20240223 | 1205 | 2385854 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 161 | 37.8569 | -120.914 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0033113 | OH | Sus | 31684894 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1919558 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 21765 | 20240223 | 1010 | 20240223 | 1410 | 2386387 | 240 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 960 | 36.8674 | -120.4553 | No | Overcast;32-90 F |  |  | 24-0033302 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1919617 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318708845071 | 20240223 | 1051 | 20240223 | 1302 | 2386184 | 131 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 2096 | 37.7371 | -120.9475 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0033159 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1919574 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | OTHER | J18462 TWD T87266 | 20240223 | 1540 | 20240223 | 1700 | 2386442 | 80 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 1680 | 36.9181 | -119.7984 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0033278 | UG | Sus | 35533297 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1919629 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | SWITCH | 2858 | 20240223 | 2228 | 20240223 | 2242 | 2386605 | 14 | Distribution Circuit | 3rd Party | Customer Equipment | 41 | 574 | 36.9766 | -120.0842 | No | Partly Cloudy;32-90 F | Customer Equipment | Normal | 24-0033425 | UG | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1919681 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | SWITCH | 461753 | 20240224 | 715 | 20240224 | 1750 | 2386656 | 635 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 635 | 36.8013 | -120.5302 | No | Partly Cloudy-Fog;32-90 F | Customer Equipment | Normal | 24-0032119 | OH | Sus | 46126800 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1919701 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321515414803 | 20240224 | 853 | 20240224 | 904 | 2386677 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 11 | 36.9054 | -119.9837 | No | Partly Cloudy-Fog;32-90 F | Fuse | Failed/Faulted | 24-0033460 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919741 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320874446004 | 20240224 | 1520 | 20240224 | 2145 | 2386851 | 385 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 770 | 37.7661 | -120.1982 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0033535 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919791 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318800546360 | 20240224 | 1609 | 20240224 | 1747 | 2387011 | 98 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 98 | 37.7724 | -120.9159 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0033539 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1919795 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 351615 | 20240224 | 2012 | 20240224 | 2208 | 2387117 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1624 | 36.9117 | -120.4452 | No | Clear;32-90 F |  |  | 24-0033573 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1919837 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | FUSE | 3285 | 20240225 | 1013 | 20240225 | 1425 | 2387364 | 252 | Distribution Circuit | Animal | Bird found | 11 | 2772 | 37.1536 | -121.0791 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0033642 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1919904 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | JUMPER | 6 POLES SS/OF CGC# 317821838587 | 20240225 | 1718 | 20240225 | 2214 | 2387546 | 296 | Distribution Circuit | 3rd Party | Vehicle | 2 | 592 | 37.5538 | -121.2505 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0033656 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1919915 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20240225 | 1724 | 20240226 | 1232 | 2387545 | 1148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 19516 | 37.1863 | -120.6348 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0033667 | OH | Sus | 46199783 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1919917 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 953431 | 20240226 | 823 | 20240226 | 1556 | 2387697 | 453 | Distribution Circuit | Equipment Failure/Involved | Underground | 63 | 28539 | 37.6222 | -120.2787 | No | Partly Cloudy;32-90 F | Customer Equipment | Failed/Faulted | 24-0033736 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1920028 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319718537344 | 20240226 | 1539 | 20240226 | 1714 | 2388310 | 95 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 95 | 37.5249 | -120.5982 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0034089 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920222 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7028 | 20240227 | 235 | 20240227 | 426 | 2388600 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 962 | 37.2994 | -120.6948 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0034153 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920264 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 2102 | 20240227 | 954 | 20240227 | 1052 | 2388941 | 58 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 193 | 36.8603 | -120.1102 | No | Clear;32-90 F |  |  | 24-0034318 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920478 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | T4607 | 20240227 | 1013 | 20240227 | 1143 | 2388849 | 90 | Transformer only | Equipment Failure/Involved | Underground | 8 | 720 | 37.7341 | -120.9554 | No | Clear;32-90 F | Secondary | Burned Open | 24-0034254 | UG | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1920417 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | 318400827430 | 20240227 | 1104 | 20240227 | 1645 | 2389013 | 341 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 341 | 37.2526 | -121.0502 | No | Clear;32-90 F |  |  | 24-0034390 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920499 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319822432727 | 20240227 | 1142 | 20240227 | 1624 | 2389029 | 282 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 282 | 37.3992 | -120.562 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0034360 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920491 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 924387 | 20240227 | 1642 | 20240227 | 1750 | 2389354 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 204 | 37.2454 | -121.0537 | No | Clear;32-90 F |  |  | 24-0034601 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920554 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | SWITCH | 38524 | 20240228 | 1124 | 20240228 | 1400 | 2390029 | 156 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 376 | 12326 | 36.96 | -120.1025 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0034891 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1920823 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | OCB | 2109/2 | 20240228 | 1800 | 20240229 | 14 | 2390360 | 374 | Distribution Circuit | Equipment Failure/Involved | Underground | 4597 | 505743 | 37.3359 | -120.5055 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0035144 | UG | Sus | 46200698 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1920887 | 0 | Non-EPSS | N | 2024 | C & GRD
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 4320 | 20240229 | 708 | 20240229 | 1630 | 2390587 | 562 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 123 | 18068 | 37.2283 | -120.4881 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0035231 | OH | Sus | 46201042 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1920940 | 0 | Non-EPSS | N | 2024 | B GRD
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6609 | 20240229 | 1614 | 20240229 | 1630 | 2391450 | 16 | Distribution Circuit | 3rd Party | Kite | 5 | 80 | 36.8692 | -120.1477 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0035709 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1921194 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | OCB | 2103/2 | 20240301 | 401 | 20240301 | 953 | 2391868 | 351 | Distribution Circuit | Animal | Other | 5 | 1755 | 37.2274 | -119.6906 | Yes | Overcast-Fog-Rain;32-90 F | Sectionalizer | Failed/Faulted | 24-0035971 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921282 | 0 | EPSS Ckt | N | 2024 | ABC- TIME OC
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRIP-SAVER | 7905 | 20240301 | 428 | 20240301 | 545 | 2391752 | 77 | Distribution Circuit | Animal | Other | 11 | 847 | 37.5163 | -120.3696 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0035837 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921260 | 0 | EPSS Ckt | N | 2024 | B & C
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | TRANSFORMER | 415772048441 | 20240301 | 832 | 20240301 | 1107 | 2391863 | 155 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1240 | 36.6552 | -120.4426 | Yes | Overcast-Drizzle;32-90 F | Fuse | Broken | 24-0036030 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921299 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | OTHER | T473490 TWD T782795 | 20240301 | 928 | 20240301 | 1023 | 2391901 | 55 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 275 | 36.9127 | -119.8205 | Yes | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0035873 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1921280 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 320705110986 | 20240301 | 930 | 20240301 | 1401 | 2391905 | 271 | Transformer only | 3rd Party | Vehicle | 1 | 271 | 36.8008 | -120.2601 | Yes | Overcast-Drizzle;32-90 F | Anchor or Guy | Broken | 24-0036151 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921336 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | TRANSFORMER | 319020220833 | 20240301 | 1015 | 20240301 | 1542 | 2391936 | 327 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 4251 | 37.0716 | -120.8368 | Yes | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0036268 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1921383 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | JUMPER | OJ TWD CGC 318985145936 | 20240301 | 1031 | 20240301 | 1208 | 2391953 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1746 | 37.7609 | -120.8523 | Yes | Overcast;32-90 F | Connector or Splice (OH) | Broken | 24-0036014 | OH | Sus | 46201965 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1921293 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6577 | 20240301 | 1050 | 20240301 | 1214 | 2391977 | 84 | Distribution Circuit | Animal | Other | 9 | 784 | 36.8499 | -120.0192 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0036067 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921307 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L1227 | 20240301 | 1056 | 20240301 | 1142 | 2391984 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 46 | 37.9327 | -120.2534 | Yes | Overcast-Rain;32-90 F |  |  | 24-0036061 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921304 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | RECLOSER | 389784 | 20240301 | 1141 | 20240301 | 1642 | 2392027 | 301 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3612 | 37.15 | -120.5739 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036065 | OH | Sus | 46202145 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1921305 | 0 | Non-EPSS | N | 2024 | C PH- GROUND- TIME OC
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 100000039540 | 20240301 | 1320 | 20240301 | 1549 | 2392189 | 149 | Distribution Circuit | 3rd Party | Vehicle | 2 | 298 | 37.0475 | -120.6097 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0036135 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1921332 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9280 | 20240301 | 1356 | 20240301 | 1805 | 2392248 | 249 | Distribution Circuit | Environmental/External | Ice or snow | 1535 | 190793 | 38.1994 | -120.0195 | Yes | Overcast-Rain;32-90 F | Other | Broken | 24-0036156 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921339 | 0 | EPSS Ckt | N | 2024 | SGF
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 88393 | 20240301 | 1413 | 20240301 | 1930 | 2392273 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6023 | 37.8379 | -120.2303 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036232 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921367 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | FUSE | 2876 | 20240301 | 1542 | 20240301 | 1613 | 2392441 | 31 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 775 | 37.0248 | -120.0619 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0036257 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921378 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321523737906 | 20240301 | 1601 | 20240301 | 2002 | 2392564 | 241 | Transformer only | Environmental/External | Lightning | 1 | 241 | 37.5392 | -119.9763 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0036319 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921399 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4572 | 20240301 | 1603 | 20240301 | 1640 | 2392495 | 37 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 49 | 1813 | 37.5217 | -119.9394 | Yes | Overcast-Fog-Rain-Lightning;32-90 F |  |  | 24-0036277 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921386 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 90035 | 20240301 | 1653 | 20240301 | 2210 | 2392548 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 4827 | 37.9721 | -120.3316 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 24-0036322 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921400 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 4569 | 20240301 | 1714 | 20240301 | 1755 | 2392580 | 41 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 574 | 37.4791 | -119.8688 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0036333 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921405 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9280 | 20240301 | 1812 | 20240302 | 1603 | 2392753 | 1311 | Distribution Circuit | Environmental/External | Ice or snow | 1536 | 925712 | 38.1994 | -120.0195 | Yes | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036374 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921423 | 0 | EPSS Ckt | N | 2024 | SGF
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321523737815 | 20240301 | 1848 | 20240302 | 1059 | 2392858 | 971 | Transformer only | Environmental/External | Lightning | 1 | 971 | 37.5365 | -119.9762 | Yes | Overcast-Fog-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0036452 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921497 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | 21523 | 20240301 | 2229 | 20240304 | 1628 | 2396211 | 3959 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 190032 | 38.2378 | -119.993 | Yes | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036573 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1922142 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 10720 | 20240301 | 2252 | 20240303 | 1724 | 2393857 | 2552 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 266764 | 38.1995 | -120.0203 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036573 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1921612 | 0 | EPSS Ckt | N | 2024 | B- C
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320900857002 | 20240301 | 2322 | 20240302 | 44 | 2393982 | 82 | Transformer only | Environmental/External | Ice or snow | 9 | 738 | 38.0651 | -120.1879 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Fuse | Normal | 24-0036626 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921667 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | 21003 | 20240301 | 2340 | 20240303 | 1524 | 2395399 | 2384 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 317410 | 38.1883 | -119.9994 | Yes | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037012 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921959 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 693441 | 20240301 | 2340 | 20240303 | 1552 | 2395405 | 2412 | Distribution Circuit | Vegetation | Tree - fell into line | 344 | 712191 | 38.1877 | -120.0025 | Yes | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036601 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921961 | 0 | EPSS Ckt | N | 2024 | B/C
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | L1293 | 20240301 | 2340 | 20240304 | 1455 | s1922151 | 3795 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 53130 | 38.1907 | -120.0003 | Yes | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037012 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1922151 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | JUMPER | WIRE DOWN @ 24764 QUARTZ AVE | 20240302 | 36 | 20240302 | 1255 | 2394112 | 739 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 62341 | 38.0708 | -120.1741 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036658 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | Yes | 1921702 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 20299 | 20240302 | 39 | 20240302 | 1350 | 2394118 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 58955 | 37.8652 | -120.2186 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0036662 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921707 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 902949 | 20240302 | 40 | 20240303 | 1322 | 2394119 | 2202 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 37638 | 38.0887 | -120.1946 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0036934 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921910 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | T2465 | 20240302 | 53 | 20240302 | 1920 | 2394150 | 1107 | Distribution Circuit | 3rd Party | Vehicle | 23 | 6341 | 37.9472 | -120.3156 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Transformer (UG) | Broken | 24-0036968 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921932 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 321047457999 | 20240302 | 123 | 20240302 | 1039 | 2394097 | 556 | Transformer only | Vegetation | Tree - fell into line | 23 | 12788 | 38.0923 | -120.1366 | No | Strong Winds-Rain-Overcast-Fog;32-90 F | Transformer | Broken- wire on ground | 24-0036641 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | Yes | No | 1921685 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | OCB | 1119/2 | 20240302 | 131 | 20240302 | 1242 | 2394191 | 671 | Distribution Circuit | 3rd Party | Vehicle | 2070 | 106031 | 36.9232 | -120.0551 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036640 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1921683 | 0 | Non-EPSS | N | 2024 | A- B- GRD
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1729 | 20240302 | 154 | 20240302 | 1210 | 2394210 | 616 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 52360 | 37.9076 | -120.2932 | No | Overcast-Fog-Rain-Lightning-Strong Winds;32-90 F |  |  | 24-0036887 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921881 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | JUMPER | OJ 1/W/OF 25026 | 20240302 | 158 | 20240302 | 852 | 2394222 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 7890 | 37.3387 | -120.7838 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036648 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921692 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2057 | 20240302 | 245 | 20240302 | 1844 | 2394246 | 959 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 96569 | 38.0646 | -120.1848 | No | Overcast-Fog-Snow-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036680 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921724 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20240302 | 252 | 20240302 | 1620 | 2394250 | 808 | Distribution Circuit | Vegetation | Tree - fell into line | 1314 | 693379 | 38.0063 | -120.3474 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036653 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921697 | 0 | EPSS Ckt | N | 2024 | B- GRD
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 10268 | 20240302 | 257 | 20240302 | 1945 | 2394251 | 1008 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4428 | 37.7952 | -120.1793 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036841 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1921851 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 20240302 | 315 | 20240302 | 1618 | 2394281 | 783 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 20205 | 37.7148 | -120.0964 | No | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036674 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921719 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 20361 | 20240302 | 318 | 20240303 | 1335 | 2394278 | 2057 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 13773 | 37.9919 | -120.4396 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036754 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921784 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | L1123 | 20240302 | 403 | 20240302 | 1917 | 2394316 | 914 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 94142 | 38.1975 | -120.0126 | No | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036765 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1921792 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | JUMPER | OJ 1 N/OF CGC#321404261831 | 20240302 | 403 | 20240304 | 1215 | 2395396 | 3372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 171972 | 38.1978 | -120.0123 | No | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken | 24-0036765 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1921958 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | 4183 | 20240302 | 555 | 20240302 | 750 | 2394386 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 575 | 37.7623 | -120.7749 | No | Clear;32-90 F |  |  | 24-0036721 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921758 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 19697 | 20240302 | 640 | 20240302 | 1430 | 2394429 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 812 | 37.948 | -120.4136 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0036738 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921772 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 27330 | 20240302 | 659 | 20240302 | 1307 | 2394457 | 368 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 736 | 37.8323 | -120.2135 | No | Overcast-Fog;32-90 F |  |  | 24-0036908 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921894 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | S1273 | 20240302 | 800 | 20240302 | 1044 | 2394517 | 164 | Distribution Circuit | Animal | Squirrel | 32 | 5248 | 38.003 | -120.31 | No | Overcast-Fog-Snow;32-90 F | Transformer (OH) | Normal | 24-0036835 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921845 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321826335776 | 20240302 | 823 | 20240302 | 1455 | 2394684 | 392 | Transformer only | Environmental/External | Lightning | 1 | 392 | 37.4806 | -119.8722 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Burned/flashed | 24-0036824 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921836 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321828835755 | 20240302 | 825 | 20240302 | 1515 | 2394685 | 410 | Transformer only | Environmental/External | Lightning | 1 | 410 | 37.4804 | -119.8714 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Burned/flashed | 24-0036822 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921835 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320818349714 | 20240302 | 1015 | 20240303 | 1300 | 2394679 | 1605 | Transformer only | Vegetation | Tree - fell into line | 1 | 1605 | 37.8652 | -120.2175 | No | Overcast-Fog-Rain;32-90 F | Service conductor | Broken- wire on ground | 24-0036869 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921867 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | L1209 | 20240302 | 1052 | 20240302 | 1208 | 2394723 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 5852 | 37.9631 | -120.2909 | No | Overcast-Rain;32-90 F |  |  | 24-0036881 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921878 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321614633995 | 20240302 | 1109 | 20240302 | 1615 | 2394776 | 306 | Transformer only | Vegetation | Tree - fell into line | 2 | 612 | 37.432 | -119.9446 | No | Overcast-Drizzle;32-90 F | Secondary | Broken- wire on ground | 24-0036867 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1921866 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320950257230 | 20240302 | 1442 | 20240302 | 1451 | 2395128 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 27 | 38.0719 | -120.172 | No | Overcast-Fog;32-90 F | Transformer (OH) | Normal | 24-0036966 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921930 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 14407 | 20240302 | 1943 | 20240302 | 2136 | 2395559 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 678 | 37.1367 | -120.962 | No | Overcast-Drizzle;32-90 F |  |  | 24-0037074 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922017 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 911059 | 20240302 | 2152 | 20240302 | 2249 | 2395641 | 57 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 228 | 37.1267 | -120.1072 | No | Overcast-Rain;32-90 F |  |  | 24-0037086 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922029 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320666048460 | 20240303 | 130 | 20240303 | 1444 | 2395683 | 794 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3445 | 37.8322 | -120.2697 | No | Overcast-Fog;32-90 F | Transformer (OH) |  | 24-0037100 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922044 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11615 | 20240303 | 306 | 20240303 | 500 | 2395693 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 532 | 37.2328 | -120.3386 | No | Overcast-Drizzle;32-90 F |  |  | 24-0037107 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922051 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | FUSE | 11676 | 20240303 | 651 | 20240303 | 833 | 2395767 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 2448 | 37.2311 | -120.8771 | No | Overcast-Fog;32-90 F |  |  | 24-0037143 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922075 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20240303 | 1006 | 20240303 | 1329 | 2395929 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 259 | 49805 | 37.5694 | -120.1177 | No | Overcast;32-90 F | PGs- Kearneys | Deteriorated | 24-0037171 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922098 | 0 | EPSS Ckt | N | 2024 | A- B- TIME
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | L1707 | 20240303 | 1656 | 20240304 | 1247 | 2396274 | 1191 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 33348 | 38.1872 | -120.0021 | No | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037244 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1922157 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 961465 | 20240303 | 2253 | 20240304 | 6 | 2396393 | 73 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 146 | 37.1568 | -120.5216 | No | Overcast-Drizzle;32-90 F |  |  | 24-0037335 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922235 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | TRANSFORMER | 318556048715 | 20240304 | 10 | 20240304 | 122 | 2396398 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 216 | 37.8366 | -121.0012 | No | Partly Cloudy-Fog;32-90 F | Fuse | Broken | 24-0037338 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922238 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20240304 | 12 | 20240304 | 1526 | 2396399 | 914 | Distribution Circuit | Environmental/External | Ice or snow | 688 | 628832 | 38.1888 | -120.0082 | No | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037336 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1922236 | 0 | EPSS Ckt | N | 2024 | B GRD TIME
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | TRANSFORMER | 320635614362 | 20240304 | 927 | 20240304 | 1056 | 2396624 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 89 | 36.8935 | -120.2824 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0037500 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922297 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 8717 | 20240304 | 935 | 20240304 | 1033 | 2396637 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 464 | 37.3121 | -120.4828 | No | Partly Cloudy;32-90 F |  |  | 24-0037488 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922293 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 5861 | 20240304 | 1145 | 20240304 | 1440 | 2396772 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 175 | 36.849 | -119.9741 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0037651 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922333 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 10720 | 20240304 | 1312 | 20240304 | 1322 | 2396863 | 10 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 107 | 1070 | 38.1995 | -120.0203 | No | Overcast;32-90 F |  |  | 24-0037608 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922318 | 0 | EPSS Ckt | N | 2024 | B & C
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320600454577 | 20240304 | 1442 | 20240304 | 1823 | 2396931 | 221 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 221 | 37.9985 | -120.2931 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0037710 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922347 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320061921864 | 20240304 | 1622 | 20240304 | 1752 | 2397027 | 90 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 90 | 37.1007 | -120.4788 | No | Overcast;32-90 F |  |  | 24-0037767 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1922358 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | RECLOSER | 9140 | 20240304 | 1651 | 20240305 | 532 | 2397051 | 761 | Distribution Circuit | 3rd Party | Vehicle | 121 | 8221 | 37.3244 | -121.0007 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0037748 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1922356 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318566430458 | 20240304 | 1748 | 20240305 | 443 | 2397109 | 655 | Transformer only | Animal | Bird found | 1 | 655 | 37.3353 | -120.9941 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0037782 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922368 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | TRANSFORMER | 415237050388 | 20240305 | 739 | 20240305 | 1424 | 2397359 | 405 | Transformer only | Environmental/External | Lightning | 1 | 405 | 36.7062 | -120.6261 | No | Partly Cloudy;32-90 F | Other | Failed/Faulted | 24-0038139 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922597 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 100000001072 | 20240305 | 1046 | 20240305 | 2015 | 2397960 | 569 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1707 | 37.8007 | -120.9782 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0038389 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922665 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | TRANSFORMER | 321065012105 | 20240305 | 1244 | 20240305 | 1440 | 2397685 | 116 | Transformer only | Animal | Other | 1 | 116 | 36.8318 | -120.1377 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0038281 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1922631 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 7488 | 20240305 | 1335 | 20240305 | 1516 | 2397796 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 2502 | 37.7548 | -120.8325 | No | Clear;32-90 F |  |  | 24-0038291 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922637 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 6346 | 20240305 | 1746 | 20240306 | 629 | 2397970 | 763 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2119 | 37.0029 | -120.436 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0038485 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922756 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 10163 | 20240306 | 605 | 20240306 | 732 | 2398137 | 87 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 2436 | 37.096 | -119.7675 | No | Partly Cloudy;32-90 F |  |  | 24-0038551 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922791 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | OTHER | J10904 TWD J10905 | 20240306 | 850 | 20240306 | 900 | s1940099 | 10 | Distribution Circuit | Company Initiated | Personnel- company | 50 | 500 | 37.3079 | -120.601 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 24-0033178 | UG | Sus | 35506999 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1940099 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 13210 | 20240306 | 856 | 20240306 | 1022 | 2398267 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 5621 | 36.929 | -119.8941 | No | Partly Cloudy;32-90 F |  |  | 24-0038660 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922924 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 6609 | 20240306 | 902 | 20240306 | 1455 | 2398280 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1177 | 36.8692 | -120.1477 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0038734 | OH | Sus | 31685769 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922938 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 59225 | 20240306 | 932 | 20240306 | 1526 | 2398359 | 354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2124 | 37.9855 | -120.2646 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0038650 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1922917 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318384026308 | 20240306 | 1020 | 20240306 | 1325 | 2398410 | 185 | Transformer only | Animal | Bird found | 1 | 185 | 37.2208 | -121.0563 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0038782 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922947 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319526736899 | 20240306 | 1243 | 20240306 | 1344 | 2398543 | 61 | Transformer only | Animal | Other | 1 | 61 | 37.514 | -120.6637 | No | Clear;32-90 F | Transformer (OH) |  | 24-0038802 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922949 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 11585 | 20240306 | 1320 | 20240306 | 1425 | 2398571 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 130 | 37.2051 | -120.2708 | No | Clear;32-90 F |  |  | 24-0038828 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922956 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320916956922 | 20240306 | 1329 | 20240306 | 1454 | 2398575 | 85 | Transformer only | Environmental/External | Ice or snow | 7 | 595 | 38.0629 | -120.1823 | No | Partly Cloudy-Drizzle;32-90 F | Transformer | Normal | 24-0038874 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922971 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | OTHER | J25219 TWD T8759 | 20240306 | 1449 | 20240306 | 1605 | 2398644 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 2356 | 37.0681 | -120.8312 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0038788 | UG | Sus | 35535865 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1922966 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321514837508 | 20240306 | 1559 | 20240307 | 148 | 2398699 | 589 | Transformer only | Environmental/External | Lightning | 3 | 1767 | 37.5283 | -119.9783 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0038963 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1923008 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | JUMPER | BURNED OPEN JUMPER | 20240306 | 1633 | 20240306 | 2145 | 2398729 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 6929 | 37.2601 | -120.7263 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0038956 | OH | Sus | 46204063 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1923001 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 24459 | 20240306 | 1814 | 20240306 | 2156 | 2398802 | 222 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2886 | 37.9505 | -120.3021 | No | Partly Cloudy;32-90 F |  |  | 24-0039007 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923048 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 9806 | 20240306 | 1847 | 20240307 | 432 | 2398814 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 8190 | 36.8558 | -120.4177 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0039018 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923054 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 2059 | 20240306 | 2003 | 20240307 | 34 | 2398838 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 11653 | 38.0628 | -120.1847 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0038968 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923013 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 1589 | 20240307 | 1116 | 20240307 | 1210 | 2399326 | 54 | Distribution Circuit | 3rd Party | Metallic Balloon | 176 | 9504 | 36.9233 | -119.8762 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0039259 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923266 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 2837 | 20240307 | 1438 | 20240307 | 1856 | 2399480 | 258 | Distribution Circuit | Animal | Bird found | 1 | 258 | 36.923 | -119.8299 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0039439 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923307 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319742230661 | 20240308 | 130 | 20240308 | 1120 | 2399752 | 590 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4130 | 37.3421 | -120.5885 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0039601 | OH | Sus | 35535934 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1923392 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 11534 | 20240308 | 753 | 20240308 | 957 | 2399860 | 124 | Distribution Circuit | 3rd Party | Gun Shot | 8 | 992 | 37.4534 | -120.6493 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0039646 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923414 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | 8269 | 20240308 | 1024 | 20240308 | 1302 | 2400094 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1422 | 37.8439 | -121.0147 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0039738 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923550 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 10319 | 20240308 | 1114 | 20240308 | 1225 | 2400149 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1231 | 37.3326 | -119.6558 | No | Clear;32-90 F |  |  | 24-0039785 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1923566 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | JUMPER | OJ 3 SPANS S/OF CGC # 319473231133 | 20240308 | 1442 | 20240308 | 1750 | 2400299 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 188 | 37.3539 | -120.6822 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0039908 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1923597 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 319789523783 | 20240308 | 1552 | 20240308 | 2022 | 2400358 | 270 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 270 | 37.1536 | -120.5732 | No | Clear;32-90 F |  |  | 24-0040016 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1923632 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319213732294 | 20240308 | 1651 | 20240308 | 2126 | 2400502 | 275 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 275 | 37.3857 | -120.7713 | No | Clear;32-90 F |  |  | 24-0040039 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1923656 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | S2215 | 20240308 | 1829 | 20240308 | 2200 | 2400448 | 211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2743 | 37.9871 | -120.3314 | No | Clear;32-90 F |  |  | 24-0040042 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923658 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 321020757337 | 20240309 | 902 | 20240309 | 1450 | 2400678 | 348 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 696 | 38.0744 | -120.1466 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0040091 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1923751 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 91141 | 20240309 | 1827 | 20240309 | 1924 | 2400985 | 57 | Distribution Circuit | 3rd Party | Vehicle | 3 | 171 | 37.3458 | -120.6525 | No | Partly Cloudy;32-90 F | Anchor or Guy | Normal | 24-0040140 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923794 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | OCB | 1110/2 | 20240309 | 2222 | 20240310 | 422 | 2401045 | 360 | Distribution Circuit | 3rd Party | Vehicle | 1034 | 108790 | 37.1847 | -120.2736 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0040174 | OH | Sus | 35536426 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923830 | 0 | EPSS Ckt | N | 2024 | A & C
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 6755 | 20240311 | 235 | 20240311 | 440 | 2401348 | 125 | Distribution Circuit | Animal | Bird found | 3 | 375 | 36.9817 | -120.1379 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0040246 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1923910 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | TRANSFORMER | 321977513092 | 20240311 | 752 | 20240311 | 1314 | 2401388 | 322 | Transformer only | Animal | Other | 2 | 644 | 36.8568 | -119.8245 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0040436 | OH | Sus | 46210441 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924101 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | JUMPER | OJ @ MTR# 1010433820 | 20240311 | 931 | 20240311 | 1202 | 2401588 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2340 | 36.8809 | -120.6722 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0040412 | OH | Sus | 46210444 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924093 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319141647281 | 20240311 | 1209 | 20240311 | 1525 | 2401752 | 196 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 196 | 37.7988 | -120.7988 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0040523 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924130 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 81675 | 20240311 | 1215 | 20240311 | 1314 | 2401753 | 59 | Distribution Circuit | Animal | Other | 1 | 59 | 36.8526 | -119.8227 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0040481 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1924118 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7887 | 20240311 | 1241 | 20240311 | 1352 | 2401774 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 710 | 37.3267 | -120.2518 | No | Clear;32-90 F |  |  | 24-0040529 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1924131 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319289131885 | 20240311 | 1325 | 20240311 | 1528 | 2401817 | 123 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 123 | 37.375 | -120.7456 | No | Clear;32-90 F |  |  | 24-0040607 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1924152 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | RECLOSER | 5870 | 20240311 | 1539 | 20240312 | 148 | 2402077 | 609 | Distribution Circuit | 3rd Party | Other | 33 | 13331 | 36.8075 | -120.152 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0040653 | OH | Sus | 46210665 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1924163 | 0 | Non-EPSS | N | 2024 | A- B- C
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | OTHER | 19036 | 20240312 | 741 | 20240312 | 1456 | 2402371 | 435 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 91 | 39585 | 37.0525 | -120.8679 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0040842 | UG | Sus | 31686252 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924354 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | TRANSFORMER | 320530316858 | 20240312 | 1225 | 20240312 | 1255 | 2402743 | 30 | Transformer only | Animal | Bird found | 1 | 30 | 36.9633 | -120.3186 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0041015 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1924409 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319625131590 | 20240312 | 1406 | 20240312 | 1554 | 2402817 | 108 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 108 | 37.3676 | -120.6299 | No | Overcast;32-90 F |  |  | 24-0041166 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1924441 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 6607 | 20240312 | 1531 | 20240312 | 1735 | 2402871 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 5828 | 37.0982 | -120.4358 | No | Partly Cloudy;32-90 F |  |  | 24-0041190 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1924450 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 6062 | 20240312 | 1536 | 20240312 | 1948 | 2402881 | 252 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 2016 | 36.8803 | -120.2933 | No | Partly Cloudy;32-90 F |  |  | 24-0041224 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1924463 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | JUMPER | L&B JUMPERS 1 P N/O CGC# 321260116455 | 20240312 | 1748 | 20240312 | 2036 | 2402917 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2688 | 36.9514 | -120.0703 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0041187 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1924449 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 26924 | 20240312 | 1848 | 20240312 | 2240 | 2402963 | 232 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1392 | 37.344 | -121.0314 | No | Clear;32-90 F |  |  | 24-0041257 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1924493 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320283054835 | 20240313 | 648 | 20240313 | 933 | 2403154 | 165 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 495 | 38.0054 | -120.403 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0041318 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924518 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | OCB | 1713/2 | 20240313 | 648 | 20240313 | 1419 | 2403155 | 451 | Distribution Circuit | 3rd Party | Vehicle | 2699 | 60450 | 37.7688 | -120.9078 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0041297 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1924510 | 0 | Non-EPSS | N | 2024 | B & GRD
YOSEMITE | STANISLAUS | PINECREST-0401 | 163160401 | FUSE | 1863 | 20240313 | 859 | 20240313 | 1540 | 2403296 | 401 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 30075 | 38.1899 | -119.987 | No | Clear;Below 32 F | Pole-Wood | Broken | 24-0041364 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1924603 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318512747576 | 20240313 | 906 | 20240313 | 1125 | 2403338 | 139 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 139 | 37.8055 | -121.0158 | No | Clear;32-90 F | Fuse | Broken | 24-0041462 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924696 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319659137226 | 20240313 | 1116 | 20240313 | 1533 | 2403404 | 257 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 257 | 37.5279 | -120.6168 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0041484 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924704 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | S1805 | 20240313 | 1151 | 20240313 | 1325 | 2403528 | 94 | Distribution Circuit | 3rd Party | Metallic Balloon | 91 | 8527 | 37.8384 | -121.005 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041526 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924719 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318381126420 | 20240313 | 1322 | 20240313 | 1825 | 2403506 | 303 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 303 | 37.2239 | -121.0572 | No | Clear;32-90 F | Other | Malfunctioning | 24-0041568 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924728 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320348227191 | 20240313 | 1323 | 20240313 | 1430 | 2403604 | 67 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 268 | 37.2476 | -120.3803 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0041599 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924736 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320144813008 | 20240313 | 1335 | 20240313 | 1443 | 2403623 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 476 | 36.857 | -120.452 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0041547 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1924721 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 5404 | 20240313 | 1546 | 20240314 | 355 | 2403820 | 729 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 4374 | 37.0586 | -120.4734 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0041702 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1924765 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | FUSE | 2447 | 20240313 | 1748 | 20240313 | 1940 | 2403849 | 112 | Distribution Circuit | Animal | Bird found | 2 | 224 | 37.0667 | -120.8385 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041739 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1924786 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 3429 | 20240313 | 2351 | 20240314 | 2200 | 2403979 | 1329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 4432 | 36.7358 | -120.7124 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0041906 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924942 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | TRANSFORMER | 320661516162 | 20240314 | 39 | 20240314 | 538 | 2403808 | 299 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 299 | 36.9443 | -120.2735 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0041791 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1924822 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 21059 | 20240314 | 535 | 20240314 | 1102 | 2404122 | 327 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 6979 | 37.5103 | -121.3234 | No | Clear;32-90 F |  |  | 24-0042110 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925114 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 6110 | 20240314 | 731 | 20240314 | 858 | 2404235 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 5494 | 37.128 | -119.7352 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041850 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1924862 | 0 | EPSS Ckt | N | 2024 | A & B
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320281654867 | 20240314 | 847 | 20240314 | 928 | 2404424 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 164 | 38.0075 | -120.4035 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0041957 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925025 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320609828723 | 20240314 | 917 | 20240314 | 1223 | 2404510 | 186 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 186 | 37.2876 | -120.2901 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0042004 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925056 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321325520085 | 20240314 | 921 | 20240314 | 1521 | 2404524 | 360 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 360 | 37.0509 | -120.0473 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0042031 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925073 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320481016225 | 20240314 | 923 | 20240314 | 1509 | 2404534 | 346 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 346 | 36.9454 | -120.3358 | No | Clear;32-90 F | Bushing | Broken | 24-0042301 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925194 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | TRANSFORMER | 318996518350 | 20240314 | 946 | 20240314 | 1403 | 2404591 | 257 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 257 | 37.0037 | -120.8446 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0042289 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925190 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 321892315492 | 20240314 | 950 | 20240314 | 1227 | 2404598 | 157 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 157 | 36.923 | -119.8536 | No | Clear;32-90 F | Fuse | Broken | 24-0042149 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925135 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321181019950 | 20240314 | 1003 | 20240314 | 1658 | 2404664 | 415 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 830 | 37.0472 | -120.097 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0042193 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925158 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318877129784 | 20240314 | 1033 | 20240314 | 1414 | 2404776 | 221 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 663 | 37.3151 | -120.8876 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0042107 | OH | Sus | 31686490 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925112 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | FUSE | 20333 | 20240314 | 1034 | 20240314 | 1306 | 2404780 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 13224 | 38.1986 | -120.0087 | No | Clear-Strong Winds;32-90 F |  |  | 24-0042172 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925147 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20240314 | 1108 | 20240314 | 1217 | 2404874 | 69 | Distribution Circuit | Vegetation | Tree - branch fell on line | 688 | 47472 | 38.1888 | -120.0082 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0042064 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1925089 | 0 | EPSS Ckt | N | 2024 | ABC TIME
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 25873 | 20240314 | 1109 | 20240314 | 1408 | 2404870 | 179 | Distribution Circuit | Company Initiated | Improper Construction | 28 | 5012 | 37.726 | -120.3186 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042173 | OH | Sus | 46211578 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925149 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | TRANSFORMER | 318479824377 | 20240314 | 1202 | 20240314 | 1734 | 2405017 | 332 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 664 | 37.168 | -121.0226 | No | Clear;32-90 F | Fuse | Broken | 24-0042416 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925237 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317470036890 | 20240314 | 1210 | 20240314 | 1708 | 2405176 | 298 | Transformer only | Unknown Cause | Patrol - not conducted | 5 | 1490 | 37.5105 | -121.3739 | No | Clear;32-90 F |  |  | 24-0042397 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1925223 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317467836839 | 20240314 | 1210 | 20240314 | 1710 | 2405177 | 300 | Transformer only | Unknown Cause | Patrol - not conducted | 5 | 1500 | 37.509 | -121.3742 | No | Clear;32-90 F |  |  | 24-0042398 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1925224 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320861656775 | 20240314 | 1528 | 20240314 | 1630 | 2405331 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 186 | 38.0592 | -120.2014 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0042391 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925220 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 20240314 | 1712 | 20240314 | 1839 | 2405426 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 14790 | 37.5637 | -119.8544 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042426 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1925244 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | T5502 | 20240314 | 1759 | 20240314 | 1812 | 2405451 | 13 | Transformer only | Equipment Failure/Involved | Underground | 8 | 104 | 37.7308 | -120.9223 | No | Clear;32-90 F | Secondary | Broken | 24-0042414 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925235 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRIP-SAVER | 10342 | 20240314 | 2013 | 20240314 | 2145 | 2405514 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 7084 | 37.2706 | -119.5342 | No | Clear;32-90 F |  |  | 24-0042461 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925257 | 0 | EPSS Ckt | N | 2024 | A & C
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | OTHER | WIRE DOWN 8 POLES SS OF 5663 | 20240314 | 2154 | 20240315 | 1028 | 2405551 | 754 | Distribution Circuit | Vegetation | Tree - branch fell on line | 585 | 212876 | 37.3227 | -119.5419 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0042494 | OH | Sus | 46211866 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1925291 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20240314 | 2239 | 20240315 | 713 | 2405564 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 470 | 81740 | 37.3391 | -119.585 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0042491 | OH | Sus | 46211864 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925288 | 0 | EPSS Ckt | N | 2024 | A & B
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 34426 | 20240314 | 2345 | 20240315 | 1658 | 2405593 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 564 | 274660 | 37.9661 | -120.2384 | No | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0042507 | OH | Sus | 46211865 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1925298 | 0 | EPSS Ckt | N | 2024 | B & GRD
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 20240314 | 2352 | 20240315 | 1217 | 2405597 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 272 | 168362 | 38.03 | -120.2447 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0042508 | OH | Sus | 46211869 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1925299 | 0 | EPSS Ckt | N | 2024 | A B C & GRD
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 823548 | 20240315 | 40 | 20240315 | 1507 | s1925319 | 867 | Distribution Circuit | Vegetation | Tree - fell into line | 841 | 268830 | 38.0441 | -120.248 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0042511 | OH | Sus | 46211794 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1925319 | 0 | EPSS Ckt | N | 2024 | C &CGR
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 493841 | 20240315 | 52 | 20240315 | 509 | 2405624 | 257 | Distribution Circuit | Vegetation | Tree - branch fell on line | 348 | 89436 | 37.9988 | -120.2322 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0042523 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925316 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320801954299 | 20240315 | 607 | 20240315 | 1420 | 2405674 | 493 | Transformer only | Vegetation | Tree - fell into line | 3 | 1479 | 37.9912 | -120.2226 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0042532 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925324 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 24262 | 20240315 | 649 | 20240315 | 816 | 2405707 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 8526 | 37.3334 | -120.5501 | No | Clear;32-90 F |  |  | 24-0042595 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925382 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | TRANSFORMER | 319976020310 | 20240315 | 853 | 20240315 | 906 | 2405775 | 13 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 13 | 37.0581 | -120.5107 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0042632 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925459 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321301013755 | 20240315 | 930 | 20240315 | 1208 | 2406046 | 158 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 158 | 36.8766 | -120.056 | No | Clear;32-90 F |  |  | 24-0042754 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1925547 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10614 | 20240315 | 934 | 20240315 | 1121 | 2406057 | 107 | Distribution Circuit | 3rd Party | Vehicle | 100 | 10700 | 37.1828 | -119.791 | No | Clear;32-90 F | Secondary | Broken | 24-0042713 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925530 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 5133 | 20240315 | 1149 | 20240315 | 1415 | 2406406 | 146 | Distribution Circuit | Animal | Other | 16 | 2382 | 37.0202 | -119.9655 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042786 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925563 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | SWITCH | 4224 | 20240315 | 1217 | 20240315 | 1927 | 2406416 | 430 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 12040 | 37.464 | -120.5372 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on object | 24-0042743 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | Yes | No | 1925542 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318587947138 | 20240315 | 1227 | 20240315 | 1325 | 2406192 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 522 | 37.7936 | -120.9899 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0042840 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925588 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | RECLOSER | 90040 | 20240315 | 1338 | 20240315 | 2133 | 2406614 | 475 | Distribution Circuit | 3rd Party | Vehicle | 574 | 69450 | 36.927 | -120.0195 | No | Clear;32-90 F | Fuse | Broken | 24-0042845 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1925590 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | OTHER | J22784 TWD T7228 | 20240315 | 1445 | 20240315 | 1531 | 2406709 | 46 | Distribution Circuit | Equipment Failure/Involved | Underground | 85 | 3910 | 36.7672 | -120.3838 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0042793 | UG | Sus | 35537890 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925610 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321462263260 | 20240315 | 1512 | 20240315 | 2007 | 2406570 | 295 | Transformer only | Vegetation | Tree - fell into line | 3 | 885 | 38.2374 | -119.9926 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0042948 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925623 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | TRANSFORMER | 322849129103 | 20240315 | 1642 | 20240316 | 358 | 2406819 | 676 | Transformer only | Vegetation | Tree - fell into line | 5 | 3380 | 37.2961 | -119.5214 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0043005 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925649 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321813315296 | 20240315 | 1710 | 20240315 | 2341 | 2406836 | 391 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1173 | 36.9177 | -119.881 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043009 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1925652 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320056928850 | 20240315 | 2104 | 20240315 | 2115 | 2406951 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 28 | 308 | 37.2931 | -120.4799 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0043035 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925672 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 25738 | 20240315 | 2153 | 20240316 | 32 | 2406985 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1431 | 37.7005 | -120.6963 | No | Clear;32-90 F |  |  | 24-0043062 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925700 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 13413 | 20240316 | 745 | 20240316 | 950 | 2407058 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 625 | 36.9331 | -120.8192 | No | Clear;32-90 F |  |  | 24-0043103 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925784 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | JUMPER | BURNT OPEN JUMPER | 20240316 | 944 | 20240316 | 1108 | 2407198 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 420 | 37.2696 | -121.0407 | No | Clear;32-90 F | Jumper | Burned Open | 24-0043112 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1925790 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 21469 | 20240316 | 1555 | 20240317 | 521 | 2407393 | 806 | Distribution Circuit | 3rd Party | Vehicle | 173 | 46150 | 37.9647 | -120.2848 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0043165 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1925828 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | S767 | 20240317 | 45 | 20240317 | 531 | 2407582 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2860 | 37.7184 | -120.619 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0043215 | OH | Sus | 46212761 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1925882 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | OCB | 1105/2 | 20240317 | 333 | 20240317 | 1008 | 2407605 | 211 | Distribution Circuit | Equipment Failure/Involved | Underground | 4367 | 735913 | 37.3359 | -120.5054 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0043216 | UG | Sus | 46212762 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | No | No | 1925883 | 0 | Non-EPSS | N | 2024 | B- C- GRD- TIME OC
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20240317 | 1031 | 20240317 | 1849 | 2407712 | 498 | Distribution Circuit | Animal | Bird found | 151 | 26898 | 37.0679 | -119.9091 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0043244 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925926 | 0 | EPSS Ckt | N | 2024 | A- B
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | RECLOSER | 658906 | 20240317 | 1148 | 20240318 | 12 | 2407734 | 744 | Distribution Circuit | Company Initiated | Coordination failure | 3 | 2232 | 36.8222 | -120.3051 | No | Clear;32-90 F | Recloser | Normal | 24-0023131 | OH | Sus | 46082902 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925928 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 321139620345 | 20240318 | 1109 | 20240318 | 1118 | 2408202 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 9 | 37.0582 | -120.1107 | No | Clear;32-90 F | Fuse | Broken | 24-0043535 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926267 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319654537635 | 20240318 | 1241 | 20240318 | 1449 | 2408470 | 128 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 128 | 37.5334 | -120.62 | No | Clear;32-90 F |  |  | 24-0043595 | OH | Sus | 46213224 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926303 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PINECREST-0401 | 163160401 | FUSE | 1863 | 20240318 | 1346 | 20240318 | 2120 | 2408419 | 454 | Distribution Circuit | Vegetation | Tree - grew into line | 75 | 34050 | 38.1899 | -119.987 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0043614 | OH | Sus | 46213153 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1926310 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1101 | 162671101 | TRANSFORMER | 317859238886 | 20240318 | 1538 | 20240318 | 1552 | 2408574 | 14 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 14 | 37.5657 | -121.2398 | No | Clear;32-90 F |  |  | 24-0043705 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1926338 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 27343 | 20240318 | 1619 | 20240318 | 1837 | 2408761 | 138 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 276 | 37.824 | -119.9633 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0043760 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1926358 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 62845 | 20240318 | 1929 | 20240319 | 201 | 2408827 | 392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1086 | 38.0427 | -120.3995 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043798 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1926384 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20240318 | 2303 | 20240319 | 534 | 2408884 | 391 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 4434 | 37.1863 | -120.6348 | No | Clear;32-90 F |  |  | 24-0043853 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926423 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 754579 | 20240319 | 612 | 20240319 | 734 | 2408942 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 492 | 37.2347 | -120.2708 | No | Clear;32-90 F |  |  | 24-0043874 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1926437 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318886829722 | 20240319 | 810 | 20240319 | 927 | 2409008 | 77 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 154 | 37.3134 | -120.8844 | No | Clear;32-90 F |  |  | 24-0043964 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1926580 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 320024423080 | 20240319 | 1108 | 20240319 | 1400 | 2409350 | 172 | Transformer only | 3rd Party | Vehicle | 2 | 344 | 37.1339 | -120.4922 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0044095 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926641 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 26354 | 20240319 | 1207 | 20240319 | 1257 | 2409370 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 250 | 38.0227 | -120.3798 | No | Clear;32-90 F | Bushing | Broken | 24-0044093 | OH | Sus | 31687058 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1926640 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320655512005 | 20240319 | 1237 | 20240319 | 1314 | 2409311 | 37 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 37 | 36.8294 | -120.277 | No | Clear;32-90 F |  |  | 24-0044143 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1926657 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9908 | 20240319 | 1238 | 20240319 | 1442 | 2409399 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1984 | 36.6469 | -120.3868 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0044124 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1926651 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322062125014 | 20240319 | 1347 | 20240319 | 1611 | 2409463 | 144 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 144 | 37.1847 | -119.7917 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0044162 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1926663 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | JUMPER | OJ 4 POLES SS OF CGC# 318938319155 | 20240319 | 1441 | 20240319 | 1540 | 2409494 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 59 | 37.0275 | -120.8691 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0044191 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1926670 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20240319 | 1457 | 20240320 | 0 | 2409520 | 543 | Distribution Circuit | Equipment Failure/Involved | Overhead | 262 | 24792 | 37.0552 | -120.0295 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0044265 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | No | No | 1926680 | 0 | EPSS Ckt | N | 2024 | ABC GND
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320946044845 | 20240319 | 1615 | 20240320 | 9 | 2409574 | 474 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 474 | 37.7329 | -120.1739 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044306 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926688 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321774818333 | 20240320 | 743 | 20240320 | 910 | 2409906 | 87 | Transformer only | Animal | Other | 1 | 87 | 37.0021 | -119.893 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0044493 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926886 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 23486 | 20240320 | 750 | 20240320 | 1010 | 2409920 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 840 | 37.0399 | -120.6718 | No | Clear;32-90 F |  |  | 24-0044538 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926923 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321305512125 | 20240320 | 1231 | 20240320 | 1558 | 2410345 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 414 | 36.8333 | -120.0549 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044712 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926988 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | JUMPER | OPEN JUMPERS 2 POLES SS OF CGC#100000071013 | 20240320 | 1538 | 20240320 | 1757 | 2410475 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 139 | 37.2907 | -120.8226 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0044792 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1927010 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | TRANSFORMER | 100000085149 | 20240320 | 1645 | 20240320 | 2024 | 2410523 | 219 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 219 | 37.1338 | -120.6009 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0044907 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927047 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319617030504 | 20240320 | 1726 | 20240320 | 1919 | 2410548 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 113 | 37.3376 | -120.6328 | No | Clear;32-90 F | Fuse | Broken | 24-0044901 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927042 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | TRANSFORMER | 415619352401 | 20240320 | 1921 | 20240321 | 233 | 2410579 | 432 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 432 | 36.7634 | -120.4964 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0044902 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1927043 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 5774 | 20240321 | 742 | 20240321 | 910 | 2410972 | 88 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 440 | 36.851 | -120.0283 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0045065 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927175 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | T772289 | 20240321 | 930 | 20240321 | 1502 | 2411089 | 332 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 3652 | 37.3246 | -120.5293 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0045091 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927187 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | T1623 | 20240321 | 1128 | 20240321 | 1212 | 2411175 | 44 | Transformer only | Equipment Failure/Involved | Underground | 15 | 660 | 37.3653 | -120.6254 | No | Clear;32-90 F | Bus | Arcing | 24-0045141 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1927196 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | RECLOSER | 5590 | 20240321 | 1132 | 20240321 | 1716 | 2411180 | 344 | Distribution Circuit | 3rd Party | Vehicle | 50 | 17200 | 36.9345 | -120.2107 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0045152 | OH | Sus | 35539033 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1927197 | 0 | Non-EPSS | N | 2024 | A & B
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | OCB | 1713/2 | 20240322 | 637 | 20240322 | 712 | 2411562 | 35 | Distribution Circuit | 3rd Party | Vehicle | 508 | 17780 | 37.7688 | -120.9078 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0045374 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1927293 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | FUSE | 23784 | 20240322 | 730 | 20240322 | 824 | 2411587 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 54 | 37.26 | -121.0212 | No | Partly Cloudy;32-90 F |  |  | 24-0045443 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927323 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | T2193 | 20240322 | 1541 | 20240323 | 241 | 2412194 | 660 | Distribution Circuit | Equipment Failure/Involved | Underground | 93 | 15804 | 36.9593 | -120.0917 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0045806 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927556 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319735250387 | 20240322 | 2006 | 20240322 | 2145 | 2412375 | 99 | Transformer only | Vegetation | Other ground vegetation | 5 | 495 | 37.8841 | -120.5927 | No | Clear-Lightning;32-90 F | Fuse | Failed/Faulted | 24-0045846 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927584 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 20133 | 20240322 | 2208 | 20240323 | 1002 | 2412451 | 714 | Distribution Circuit | 3rd Party | Vehicle | 62 | 18964 | 37.7519 | -120.8399 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0045881 | UG | Sus | 35539443 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927617 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 8814 | 20240323 | 17 | 20240323 | 1910 | 2412976 | 1133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 3399 | 37.1408 | -120.4464 | No | Overcast-Rain;32-90 F |  |  | 24-0046090 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927797 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 6062 | 20240323 | 24 | 20240323 | 1300 | 2412500 | 756 | Distribution Circuit | Animal | Other | 8 | 1855 | 36.8803 | -120.2933 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0045900 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1927636 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | 2111 | 20240323 | 58 | 20240323 | 415 | 2412508 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1051 | 37.7401 | -120.7644 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0045909 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927645 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 9616 | 20240323 | 145 | 20240323 | 530 | 2412527 | 225 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1575 | 36.7638 | -120.6031 | No | Overcast-Rain;32-90 F |  |  | 24-0045924 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927660 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | OCB | 1101/2 | 20240323 | 209 | 20240323 | 934 | 2412534 | 445 | Distribution Circuit | Animal | Bird found | 79 | 33285 | 36.6512 | -120.5803 | No | Overcast-Rain;32-90 F | Recloser | Burned/flashed | 24-0045915 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1927651 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11615 | 20240323 | 250 | 20240323 | 1514 | 2412543 | 744 | Distribution Circuit | Environmental/External | Lightning | 7 | 3900 | 37.2328 | -120.3386 | No | Overcast-Rain;32-90 F | Lightning Arrestor | Burned/flashed | 24-0045913 | OH | Sus | 31687724 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927649 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20240323 | 345 | 20240323 | 439 | 2412559 | 54 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 262 | 14148 | 37.0552 | -120.0295 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0045910 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927646 | 0 | EPSS Ckt | N | 2024 | AB
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | T1684 | 20240323 | 538 | 20240323 | 940 | 2412577 | 242 | Transformer only | Equipment Failure/Involved | Underground | 7 | 1694 | 37.2992 | -120.5084 | No | Overcast-Rain;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0045916 | UG | Sus | 46215432 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927652 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | FUSE | 9508 | 20240323 | 917 | 20240323 | 1200 | 2412698 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 544 | 36.8068 | -120.7142 | No | Partly Cloudy;32-90 F |  |  | 24-0046009 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927735 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | RECLOSER | 90490 | 20240323 | 941 | 20240323 | 2236 | 2412720 | 775 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 36640 | 37.303 | -120.7639 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0045954 | OH | Sus | 46215609 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1927706 | 0 | Non-EPSS | N | 2024 | B GRD
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | TRANSFORMER | 414943253664 | 20240323 | 1200 | 20240323 | 2055 | 2412840 | 535 | Transformer only | Animal | Other | 1 | 535 | 36.7952 | -120.729 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Contaminated | 24-0046010 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1927736 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | TRANSFORMER | 415649051885 | 20240323 | 1313 | 20240323 | 2315 | 2412876 | 602 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 602 | 36.7489 | -120.4874 | No | Overcast-Drizzle;32-90 F | Other | Malfunctioning | 24-0046030 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927752 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318768546780 | 20240323 | 1429 | 20240323 | 1933 | 2412922 | 304 | Transformer only | Environmental/External | Lightning | 3 | 912 | 37.7839 | -120.9272 | No | Clear-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0046057 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927766 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | JUMPER | OJ 1/E/OF 698511 | 20240323 | 1513 | 20240323 | 1705 | 2412950 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1012 | 37.2904 | -120.7222 | No | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 24-0046071 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1927775 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 21992 | 20240323 | 1747 | 20240324 | 1130 | 2412930 | 1063 | Distribution Circuit | Environmental/External | Lightning | 8 | 4137 | 36.749 | -120.3535 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0046086 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927793 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | TRANSFORMER | 320501618851 | 20240324 | 702 | 20240324 | 811 | 2413274 | 69 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 69 | 37.0173 | -120.3285 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 24-0046147 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927858 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 5502 | 20240324 | 1246 | 20240324 | 1625 | 2413417 | 219 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 81 | 17739 | 37.2961 | -119.5213 | No | Overcast-Drizzle;32-90 F |  |  | 24-0046215 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927910 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320539230549 | 20240324 | 1515 | 20240324 | 2222 | 2413492 | 427 | Transformer only | Environmental/External | Lightning | 1 | 427 | 37.3387 | -120.3134 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0046227 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927918 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321410021650 | 20240324 | 1912 | 20240324 | 2051 | 2413584 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 99 | 37.0938 | -120.0189 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0046241 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927933 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 47441 | 20240325 | 336 | 20240325 | 908 | 2414006 | 332 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 664 | 37.1786 | -120.4155 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0046390 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1928124 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 320730619627 | 20240325 | 807 | 20240325 | 1456 | 2413819 | 409 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 409 | 37.0387 | -120.25 | No | Partly Cloudy;32-90 F |  |  | 24-0046419 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928155 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 13122 | 20240325 | 817 | 20240325 | 1012 | 2413844 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 4255 | 37.0093 | -119.8844 | No | Partly Cloudy;32-90 F |  |  | 24-0046432 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928165 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 91827 | 20240325 | 841 | 20240325 | 1600 | 2413890 | 439 | Distribution Circuit | Animal | Bird found | 7 | 3073 | 37.1503 | -120.1019 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0046641 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1928216 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319155544475 | 20240325 | 1024 | 20240325 | 1620 | 2414111 | 356 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 356 | 37.721 | -120.7931 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0046460 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928172 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | FUSE | 6245 | 20240325 | 1127 | 20240325 | 1515 | 2414186 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 684 | 37.0098 | -120.2921 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0046494 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1928179 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320014019786 | 20240325 | 1316 | 20240325 | 1622 | 2414194 | 186 | Transformer only | Vegetation | Other ground vegetation | 1 | 186 | 37.0436 | -120.4972 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0046603 | OH | Sus | 46216243 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928207 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1645 | 20240325 | 1317 | 20240325 | 1510 | 2414292 | 113 | Distribution Circuit | Animal | Bird found | 60 | 6780 | 37.8202 | -120.6777 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0046581 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1928204 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318593947041 | 20240325 | 1327 | 20240325 | 1737 | 2414301 | 250 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3000 | 37.7909 | -120.9878 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0046623 | OH | Sus | 31687995 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928211 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 169700 | 20240326 | 100 | 20240326 | 306 | 2414566 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1507 | 186843 | 37.8364 | -120.2605 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 24-0046734 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1928265 | 0 | EPSS Ckt | N | 2024 | ABC
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | TRANSFORMER | 320843818318 | 20240326 | 858 | 20240326 | 1128 | 2415143 | 150 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 150 | 37.0028 | -120.2113 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0046903 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928483 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | TRANSFORMER | 321056516635 | 20240326 | 932 | 20240326 | 1405 | 2415460 | 273 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 273 | 36.9568 | -120.1383 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0046921 | OH | Sus | 31688816 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928489 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 321004548525 | 20240326 | 1100 | 20240326 | 1120 | 2415546 | 20 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 20 | 37.8314 | -120.1554 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0046911 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928487 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 5556 | 20240326 | 1109 | 20240326 | 1202 | 2415573 | 53 | Distribution Circuit | Animal | Squirrel | 15 | 795 | 36.9239 | -119.8722 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0046934 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928498 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | SWITCH | 23146 | 20240326 | 1227 | 20240326 | 1330 | 2415649 | 63 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 441 | 36.7817 | -120.3598 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0046946 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1928503 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | TRANSFORMER | 320147622624 | 20240326 | 1406 | 20240326 | 1625 | 2415775 | 139 | Transformer only | Animal | Bird found | 2 | 278 | 37.1206 | -120.107 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0047027 | OH | Sus | 46216525 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928531 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 24859 | 20240326 | 1531 | 20240326 | 1708 | 2415829 | 97 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 3880 | 37.9906 | -120.4076 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0047098 | UG | Sus | 31688931 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928543 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | OTHER | T6563 TWD T6564 | 20240326 | 1642 | 20240326 | 1718 | 2415884 | 36 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 936 | 36.7502 | -120.3894 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0046965 | UG | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1928546 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | SWITCH | 4732 | 20240327 | 217 | 20240327 | 228 | 2416139 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 40 | 440 | 37.9928 | -120.4057 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 24-0047098 | OH | Sus | 31688931 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1928643 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320544730739 | 20240327 | 818 | 20240327 | 1240 | 2416260 | 262 | Transformer only | Environmental/External | Lightning | 1 | 262 | 37.3438 | -120.3115 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0047334 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928780 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1116 | 252761116 | FUSE | 5848 | 20240327 | 1023 | 20240327 | 1133 | 2416466 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 980 | 36.9239 | -120.0332 | No | Clear;32-90 F | Fuse | Burned Open | 24-0047430 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1928819 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 27103 | 20240327 | 1313 | 20240327 | 1411 | 2416595 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 2901 | 38.0006 | -120.275 | No | Overcast;32-90 F |  |  | 24-0047537 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928858 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 6985 | 20240327 | 1431 | 20240327 | 1525 | 2416655 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 162 | 36.8876 | -120.0919 | No | Clear;32-90 F |  |  | 24-0047606 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1928872 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | L2151 | 20240327 | 1538 | 20240327 | 1655 | 2416702 | 77 | Distribution Circuit | Animal | Squirrel | 23 | 1771 | 37.9716 | -120.3266 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0047670 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928886 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | TRANSFORMER | 318952820256 | 20240328 | 403 | 20240328 | 507 | 2416958 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 192 | 37.0555 | -120.8595 | No | Overcast;32-90 F | Fuse | Broken | 24-0047750 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928956 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | TRANSFORMER | 318952820274 | 20240328 | 403 | 20240328 | 508 | 2416959 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 910 | 37.056 | -120.8595 | No | Overcast;32-90 F | Fuse | Broken | 24-0047751 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928957 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | SECTIONALIZER | 11240 | 20240328 | 412 | 20240328 | 730 | 2416961 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 9108 | 36.7853 | -120.3737 | No | Overcast;32-90 F |  |  | 24-0047764 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928967 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | OCB | 1102/2 | 20240328 | 529 | 20240328 | 801 | 2416975 | 152 | Distribution Circuit | Animal | Other | 324 | 38900 | 37.1208 | -120.473 | No | Overcast;32-90 F | Regulator | Burned/flashed | 24-0047753 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1928959 | 0 | Non-EPSS | N | 2024 | A & B
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 24352 | 20240328 | 709 | 20240328 | 804 | 2417012 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 477 | 37.2235 | -121.0309 | No | Partly Cloudy;32-90 F |  |  | 24-0047799 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1928992 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 100000058874 | 20240328 | 721 | 20240328 | 835 | 2417022 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 148 | 37.1564 | -120.3921 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 24-0047824 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929037 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 6926 | 20240328 | 805 | 20240328 | 859 | 2417062 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 378 | 37.0619 | -120.3113 | No | Partly Cloudy;32-90 F |  |  | 24-0047831 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929057 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20643 | 20240328 | 845 | 20240328 | 937 | 2417160 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 52 | 37.7426 | -120.824 | No | Partly Cloudy;32-90 F |  |  | 24-0047843 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929096 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S291 | 20240328 | 931 | 20240328 | 1041 | 2417262 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 140 | 37.7877 | -120.8174 | No | Partly Cloudy;32-90 F |  |  | 24-0047849 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929108 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 6454 | 20240328 | 1226 | 20240328 | 1324 | 2417433 | 58 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 25 | 1470 | 37.0692 | -120.1933 | No | Partly Cloudy;32-90 F |  |  | 24-0048011 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929179 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | FUSE | 24838 | 20240328 | 1405 | 20240328 | 1609 | 2417500 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 248 | 37.1272 | -120.3585 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 24-0048035 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1929189 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 2781 | 20240328 | 2007 | 20240328 | 2105 | 2417683 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 406 | 37.1203 | -120.4825 | No | Overcast;32-90 F |  |  | 24-0048177 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929226 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321587334896 | 20240329 | 224 | 20240329 | 1005 | 2417767 | 461 | Transformer only | Vegetation | Tree - fell into line | 3 | 1383 | 37.4556 | -119.9545 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0048216 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929282 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 64566 | 20240329 | 1723 | 20240329 | 2111 | 2418412 | 228 | Distribution Circuit | 3rd Party | Vehicle | 87 | 19836 | 37.346 | -120.6332 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0048550 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1929457 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 20127 | 20240329 | 1835 | 20240330 | 1642 | 2418473 | 1327 | Distribution Circuit | Equipment Failure/Involved | Underground | 90 | 27903 | 37.7358 | -120.9543 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 24-0048583 | UG | Sus | 46218350 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929470 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 8927 | 20240329 | 1934 | 20240330 | 342 | 2418515 | 488 | Distribution Circuit | 3rd Party | Vehicle | 17 | 8070 | 37.707 | -120.793 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0048596 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1929480 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 14407 | 20240329 | 2108 | 20240329 | 2200 | 2418509 | 52 | Distribution Circuit | Animal | Other | 6 | 312 | 37.1367 | -120.962 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 24-0048627 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929513 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 13102 | 20240329 | 2129 | 20240329 | 2317 | 2418586 | 108 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 10 | 1080 | 37.0798 | -120.2954 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0048635 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929518 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | OCB | 1104/2 | 20240329 | 2142 | 20240330 | 542 | 2418592 | 480 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1562 | 366243 | 36.9832 | -120.0336 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0048605 | OH | Sus | 35540904 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1929489 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | RECLOSER | 12140 | 20240330 | 535 | 20240330 | 1114 | 2418801 | 339 | Distribution Circuit | Animal | Other | 52 | 8128 | 36.737 | -120.6573 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0048661 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1929541 | 0 | EPSS Ckt | N | 2024 | A-B-C
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | TRANSFORMER | 320322017793 | 20240330 | 956 | 20240330 | 1350 | 2418961 | 234 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 468 | 36.9889 | -120.3907 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048735 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929594 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 6110 | 20240330 | 1148 | 20240330 | 1625 | 2419014 | 277 | Distribution Circuit | Animal | Bird found | 170 | 40120 | 37.128 | -119.7352 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048759 | OH | Sus | 31689236 | CENTRAL VALLEY | MAR | Multi-Fault | 0 | No | Yes | No | 1929605 | 0 | EPSS Ckt | N | 2024 | A-B-C & GRD
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320766355938 | 20240330 | 1158 | 20240330 | 1259 | 2419030 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 305 | 38.0363 | -120.2351 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0048792 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929615 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | TRANSFORMER | 320935719157 | 20240330 | 1242 | 20240330 | 1406 | 2419054 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 252 | 37.0256 | -120.1806 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048809 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929627 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 3332 | 20240330 | 1435 | 20240330 | 1706 | 2419121 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 806 | 37.1434 | -120.6018 | No | Overcast;32-90 F |  |  | 24-0048829 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929644 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20240330 | 1818 | 20240330 | 1900 | 2419214 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 262 | 11004 | 37.0552 | -120.0295 | No | Partly Cloudy;32-90 F |  |  | 24-0048842 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929655 | 0 | EPSS Ckt | N | 2024 | A PH & GRD
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6748 | 20240331 | 433 | 20240331 | 702 | 2419389 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3822 | 36.9084 | -120.1375 | No | Partly Cloudy;32-90 F |  |  | 24-0048886 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929699 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20240331 | 643 | 20240331 | 845 | 2419430 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 3660 | 37.9913 | -120.4128 | No | Overcast;32-90 F |  |  | 24-0048897 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929707 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 21249 | 20240331 | 713 | 20240331 | 1050 | 2419436 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 6510 | 37.7329 | -120.8395 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048891 | OH | Sus | 46218560 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1929702 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 922991 | 20240331 | 855 | 20240401 | 1118 | 2419490 | 1518 | Distribution Circuit | 3rd Party | Other | 5 | 3285 | 37.3313 | -120.7649 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0048908 | OH | Sus | 46218484 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929717 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 8717 | 20240331 | 925 | 20240331 | 1136 | 2419469 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1048 | 37.3121 | -120.4828 | No | Partly Cloudy;32-90 F |  |  | 24-0048917 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929727 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | FUSE | 2877 | 20240331 | 1147 | 20240331 | 1320 | 2419513 | 93 | Distribution Circuit | Animal | Other | 42 | 3906 | 37.0206 | -120.0614 | No | Partly Cloudy;32-90 F | Anchor or Guy | Normal | 24-0048922 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1929732 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 9607 | 20240331 | 1253 | 20240331 | 1400 | 2419533 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 335 | 37.0998 | -120.8452 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0048925 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1929735 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320449854217 | 20240331 | 1832 | 20240331 | 1839 | 2419673 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 7 | 37.9888 | -120.3447 | No | Partly Cloudy-Drizzle-Lightning;32-90 F | Fuse | Broken | 24-0048937 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929752 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 6799 | 20240331 | 2031 | 20240401 | 249 | 2419734 | 378 | Distribution Circuit | Environmental/External | Lightning | 17 | 6426 | 37.7503 | -120.9409 | No | Overcast;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0048961 | OH | Sus | 31689263 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1929779 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | 20943 | 20240331 | 2033 | 20240401 | 653 | 2419737 | 620 | Distribution Circuit | Environmental/External | Lightning | 58 | 35960 | 37.7318 | -120.9313 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048949 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1929766 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | OTHER | 1 PH 1 SPAN WIRE DOWN | 20240331 | 2236 | 20240401 | 1452 | 2419754 | 976 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 5856 | 36.9256 | -120.7966 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048971 | OH | Sus | 46218507 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1929789 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | RECLOSER | 90170 | 20240401 | 1039 | 20240401 | 2054 | 2420146 | 615 | Distribution Circuit | 3rd Party | Vehicle | 303 | 135826 | 37.0108 | -120.6372 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0049097 | OH | Sus | 31689370 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1929953 | 0 | Non-EPSS | N | 2024 | A-B & GRD
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320546230587 | 20240401 | 1229 | 20240401 | 1545 | 2420259 | 196 | Transformer only | Environmental/External | Lightning | 1 | 196 | 37.3397 | -120.311 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0049239 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1929994 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 13207 | 20240401 | 1259 | 20240401 | 1355 | 2420282 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 2520 | 36.9338 | -119.894 | No | Clear;32-90 F |  |  | 24-0049246 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1929995 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRIP-SAVER | 7054 | 20240401 | 1435 | 20240401 | 2208 | 2420341 | 453 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 61 | 5744 | 37.346 | -120.7245 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0049327 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1930012 | 0 | Non-EPSS | N | 2024 | A&B
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | SWITCH | 2172 | 20240401 | 2105 | 20240401 | 2114 | 2420520 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 31 | 279 | 37.0508 | -120.7079 | No | Clear;32-90 F | Other | Normal | 24-0049097 | OH | Sus | 31689370 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930046 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 19349 | 20240401 | 2128 | 20240401 | 2142 | 2420529 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 103 | 1442 | 37.0529 | -120.6718 | No | Clear;32-90 F | Other | Normal | 24-0049097 | OH | Sus | 31689370 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930049 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | S1299 | 20240402 | 131 | 20240402 | 323 | 2420584 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 6160 | 37.9777 | -120.3168 | No | Clear;32-90 F |  |  | 24-0049458 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930091 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | 319658614610 | 20240402 | 720 | 20240402 | 1445 | 2420672 | 445 | Transformer only | Animal | Bird found | 1 | 445 | 36.9006 | -120.618 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0049637 | OH | Sus | 46219366 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930290 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 5128 | 20240402 | 745 | 20240402 | 911 | 2420690 | 86 | Distribution Circuit | Animal | Other | 1 | 86 | 36.8536 | -119.8156 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0049654 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930294 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 81675 | 20240402 | 1153 | 20240402 | 1321 | s1930306 | 88 | Distribution Circuit | Animal | Other | 1 | 88 | 36.8526 | -119.8227 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0049654 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930306 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320151013379 | 20240402 | 1214 | 20240402 | 1258 | 2420691 | 44 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 132 | 36.8677 | -120.4497 | No | Clear;32-90 F |  |  | 24-0049708 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1930313 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 619809 | 20240402 | 1242 | 20240402 | 1358 | 2421089 | 76 | Distribution Circuit | Animal | Other | 6 | 456 | 37.1994 | -120.1489 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0049756 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1930326 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | FUSE | 3704 | 20240402 | 1448 | 20240402 | 2247 | 2421262 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 479 | 36.6025 | -120.5325 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0049923 | OH | Sus | 46219591 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930354 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320348511963 | 20240402 | 1923 | 20240402 | 2358 | 2421297 | 275 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 550 | 36.8281 | -120.3815 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0049943 | OH | Sus | 46219530 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930367 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321646115445 | 20240402 | 2044 | 20240402 | 2114 | 2421282 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 60 | 36.9221 | -119.9381 | No | Clear;32-90 F | Secondary | Broken | 24-0049954 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930379 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 3736 | 20240403 | 624 | 20240403 | 900 | 2421457 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1041 | 36.792 | -120.2592 | No | Clear;32-90 F |  |  | 24-0050060 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930498 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | TRANSFORMER | 320247417156 | 20240403 | 732 | 20240403 | 1122 | 2421484 | 230 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 230 | 36.9707 | -120.4165 | No | Partly Cloudy;32-90 F |  |  | 24-0050142 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1930604 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 25945 | 20240403 | 755 | 20240403 | 937 | 2421502 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 476 | 37.1416 | -120.311 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0050091 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930577 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 56266 | 20240403 | 820 | 20240403 | 936 | 2421541 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 152 | 37.8865 | -120.9292 | No | Fog;32-90 F |  |  | 24-0050073 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930540 | 0 | EPSS Ckt | N | 2024 | B & G
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318617027320 | 20240403 | 1041 | 20240403 | 1144 | 2421740 | 63 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 63 | 37.2493 | -120.9762 | No | Clear;32-90 F |  |  | 24-0050202 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1930619 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | JUMPER | OJ'S AT CGC# 319312529500 | 20240403 | 1540 | 20240403 | 1925 | 2421931 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 675 | 37.3095 | -120.7377 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0050319 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930643 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | OTHER | J22713 TWD T7406 | 20240403 | 1657 | 20240403 | 1738 | s1930661 | 41 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 492 | 37.0843 | -120.8305 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0050295 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930661 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | SWITCH | 504259 | 20240403 | 1911 | 20240404 | 218 | 2422053 | 427 | Distribution Circuit | 3rd Party | Vehicle | 364 | 144948 | 37.4669 | -119.8835 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0050431 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930684 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PINECREST-0401 | 163160401 | FUSE | 1863 | 20240403 | 1933 | 20240404 | 1139 | 2422091 | 966 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 19624 | 38.1899 | -119.987 | No | Overcast;32-90 F | Secondary | Burned Open | 24-0050436 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930688 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7322 | 20240404 | 626 | 20240404 | 807 | 2422202 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1515 | 37.4779 | -120.5849 | No | Partly Cloudy;32-90 F |  |  | 24-0050502 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930746 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1103 | 253671103 | RECLOSER | 724590 | 20240404 | 800 | 20240404 | 1151 | 2422253 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 5360 | 36.6482 | -120.623 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0050522 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930757 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318937530235 | 20240404 | 952 | 20240404 | 1455 | 2422380 | 303 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 303 | 37.328 | -120.8666 | No | Overcast;32-90 F | Jumper | Broken | 24-0050656 | OH | Sus | 31689677 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930839 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320611529864 | 20240404 | 1049 | 20240404 | 1143 | 2422424 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 54 | 37.3186 | -120.2885 | No | Overcast;32-90 F | Fuse | Broken | 24-0050723 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930850 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | 20373 | 20240404 | 1112 | 20240404 | 1230 | 2422444 | 78 | Distribution Circuit | 3rd Party | Metallic Balloon | 172 | 13416 | 37.7987 | -120.9874 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0050724 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930851 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20240404 | 1214 | 20240405 | 244 | 2422487 | 870 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 14790 | 37.1863 | -120.6348 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0050792 | OH | Sus | 46220598 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1930864 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | OCB | 1102/2 | 20240404 | 1247 | 20240404 | 1442 | 2422519 | 115 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1848 | 206684 | 37.5231 | -120.3304 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0050783 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930860 | 0 | EPSS Ckt | N | 2024 | B & C TIME
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | RECLOSER | 5050 | 20240404 | 1325 | 20240404 | 1416 | 2422547 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 1224 | 37.1589 | -120.1712 | No | Overcast;32-90 F |  |  | 24-0050818 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1930873 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 320903849033 | 20240404 | 1340 | 20240405 | 225 | 2422565 | 765 | Distribution Circuit | Environmental/External | Lightning | 26 | 14203 | 37.8462 | -120.188 | No | Overcast-Fog-Drizzle-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051010 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930939 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | RECLOSER | 257152 | 20240404 | 1356 | 20240404 | 1736 | 2422585 | 220 | Distribution Circuit | Animal | Other | 38 | 8360 | 37.1634 | -120.1016 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 24-0050849 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1930886 | 0 | EPSS Ckt | N | 2024 | ABC
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320897048885 | 20240404 | 1416 | 20240404 | 2250 | 2422605 | 514 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2570 | 37.8423 | -120.1907 | No | Overcast-Fog-Snow-Lightning;Below 32 F | Transformer (OH) | Failed/Faulted | 24-0050975 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930919 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | L1667 | 20240404 | 1505 | 20240404 | 2039 | 2423083 | 334 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 334 | 37.806 | -120.5455 | No | Partly Cloudy;32-90 F |  |  | 24-0051047 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930967 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320193522429 | 20240404 | 1512 | 20240404 | 1813 | 2422803 | 181 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 181 | 37.1164 | -120.4344 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 24-0051014 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930942 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320085329332 | 20240404 | 1534 | 20240404 | 1930 | 2422626 | 236 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2596 | 37.3063 | -120.4705 | No | Overcast-Rain;32-90 F | Secondary | Broken | 24-0050963 | OH | Sus | 31689761 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930911 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 3714 | 20240404 | 1643 | 20240404 | 2152 | 2423123 | 309 | Distribution Circuit | Environmental/External | Lightning | 60 | 7389 | 37.0459 | -120.5951 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 24-0051022 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930948 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 2077 | 20240404 | 1706 | 20240404 | 2200 | 2423050 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1470 | 37.5333 | -121.1402 | No | Clear;32-90 F |  |  | 24-0051078 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931001 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320231354278 | 20240404 | 1833 | 20240404 | 2240 | 2422883 | 247 | Transformer only | Environmental/External | Lightning | 2 | 494 | 37.9904 | -120.4203 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051032 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930953 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 20084 | 20240404 | 1930 | 20240405 | 355 | 2423149 | 505 | Distribution Circuit | Equipment Failure/Involved | Underground | 59 | 8459 | 37.9498 | -120.2813 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0051057 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930974 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 10207 | 20240404 | 2034 | 20240405 | 1319 | 2423185 | 1005 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 44220 | 37.2984 | -119.6169 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051062 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1930982 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318742045565 | 20240405 | 34 | 20240405 | 550 | 2423288 | 316 | Transformer only | Environmental/External | Lightning | 3 | 948 | 37.7503 | -120.9363 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051095 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931020 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 2841 | 20240405 | 35 | 20240405 | 259 | 2423319 | 144 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 36 | 5184 | 37.5325 | -120.0518 | No | Overcast-Drizzle;32-90 F |  |  | 24-0051110 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931037 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 20209 | 20240405 | 151 | 20240405 | 506 | 2423341 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 5460 | 38.0181 | -120.3123 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0051120 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931047 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L879 | 20240405 | 202 | 20240405 | 1937 | 2424099 | 1055 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 15825 | 38.0394 | -120.3454 | No | Partly Cloudy;32-90 F |  |  | 24-0051618 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931381 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | INTERRUPTER | 14190 | 20240405 | 224 | 20240405 | 644 | 2423353 | 260 | Distribution Circuit | Equipment Failure/Involved | Underground | 926 | 240760 | 37.3217 | -120.4783 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Burned/flashed | 24-0051111 | UG | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | No | No | 1931038 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 363884 | 20240405 | 405 | 20240405 | 650 | 2423377 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 11550 | 37.2327 | -119.4996 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0051119 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931046 | 0 | EPSS Ckt | N | 2024 | B & C
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 5554 | 20240405 | 419 | 20240405 | 737 | 2423384 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2772 | 37.5398 | -119.6551 | No | Overcast-Snow;Below 32 F |  |  | 24-0051151 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931065 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L2073 | 20240405 | 438 | 20240405 | 2054 | 2424740 | 976 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 9760 | 38.02 | -120.3864 | No | Overcast-Fog-Snow;32-90 F | Pole-Wood | Normal | 24-0051585 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931358 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20240405 | 459 | 20240406 | 1259 | 2423415 | 1920 | Distribution Circuit | Vegetation | Tree - fell into line | 1140 | 961052 | 38.0063 | -120.3474 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051121 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1931048 | 0 | EPSS Ckt | N | 2024 | B & C
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 87303 | 20240405 | 459 | 20240406 | 1312 | 2423728 | 1933 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3866 | 38.0218 | -120.3828 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051193 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | Yes | No | 1931114 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 20807 | 20240405 | 459 | 20240405 | 1713 | 2424000 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 16148 | 38.0343 | -120.3706 | No | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 24-0051317 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | Yes | No | 1931229 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | JUMPER | 52327 HS JMPRS | 20240405 | 459 | 20240405 | 2045 | 2424154 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5676 | 38.0214 | -120.3832 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051437 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931272 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 515539 | 20240405 | 459 | 20240406 | 1040 | 2424179 | 1781 | Distribution Circuit | Vegetation | Tree - branch fell on line | 108 | 192348 | 38.0418 | -120.3863 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051455 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931279 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | JUMPER | OJ 1 SPAN SS OF CGC#320325055995 | 20240405 | 459 | 20240406 | 1935 | 2425275 | 2316 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 13896 | 38.0384 | -120.3884 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 24-0051759 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1931530 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320294056013 | 20240405 | 459 | 20240406 | 1321 | s1931542 | 1942 | Transformer only | Vegetation | Tree - fell into line | 5 | 9710 | 38.0384 | -120.3991 | No | Overcast-Fog-Snow;Below 32 F | Secondary | Broken | 24-0051121 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1931542 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20240405 | 502 | 20240405 | 2239 | 2423638 | 1057 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 29596 | 37.9913 | -120.4128 | No | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Broken | 24-0051665 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931429 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320271652996 | 20240405 | 504 | 20240406 | 2027 | 2423903 | 2363 | Transformer only | Environmental/External | Ice or snow | 1 | 2363 | 37.9553 | -120.4068 | No | Overcast;32-90 F | Transformer | Broken- wire on ground | 24-0051754 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931528 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 20361 | 20240405 | 504 | 20240405 | 1929 | 2423471 | 865 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 19454 | 37.9919 | -120.4396 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051521 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931316 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | L347 | 20240405 | 510 | 20240406 | 1545 | 2424737 | 2075 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 105825 | 38.0366 | -120.4258 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051123 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931356 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320238155667 | 20240405 | 512 | 20240406 | 1701 | 2425107 | 2149 | Transformer only | Vegetation | Tree - fell into line | 13 | 27937 | 38.0288 | -120.4187 | No | Overcast-Fog-Snow;32-90 F | Secondary | Broken- wire on ground | 24-0051123 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1931462 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 799924 | 20240405 | 513 | 20240406 | 1223 | 2423485 | 1870 | Distribution Circuit | Vegetation | Tree - fell into line | 389 | 646356 | 38.0052 | -120.4062 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051123 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1931050 | 0 | EPSS Ckt | N | 2024 | A- B- C
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320231354278 | 20240405 | 513 | 20240406 | 1030 | 2424967 | 1757 | Transformer only | Vegetation | Tree - fell into line | 2 | 3514 | 37.9904 | -120.4203 | No | Overcast;32-90 F | Transformer (OH) | Broken | 24-0051664 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931428 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 26392 | 20240405 | 519 | 20240406 | 1649 | 2423645 | 2130 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 34080 | 37.987 | -120.3889 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051776 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931541 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | SWITCH | 7118 | 20240405 | 528 | 20240406 | 1727 | 2424037 | 2159 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 79853 | 37.9811 | -120.382 | No | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on object | 24-0051347 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | Yes | No | 1931240 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 25688 | 20240405 | 528 | 20240406 | 1337 | 2425004 | 1929 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 45588 | 37.9829 | -120.3829 | No | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051676 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1931443 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 26366 | 20240405 | 536 | 20240406 | 1600 | 2424845 | 2064 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10320 | 38.0097 | -120.4178 | No | Overcast;32-90 F | Secondary | Broken | 24-0051622 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1931386 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 26367 | 20240405 | 536 | 20240406 | 1839 | 2424892 | 2223 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6669 | 38.0113 | -120.419 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0051123 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931401 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320256754900 | 20240405 | 536 | 20240406 | 1429 | 2425139 | 1973 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 7892 | 38.008 | -120.4126 | No | Overcast;32-90 F | Secondary | Normal | 24-0051704 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931479 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320217555005 | 20240405 | 536 | 20240406 | 1557 | 2425196 | 2061 | Transformer only | Environmental/External | Ice or snow | 1 | 2061 | 38.0122 | -120.4233 | No | Overcast;32-90 F | Transformer | Broken- wire on ground | 24-0051123 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | Yes | No | 1931507 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320219754788 | 20240405 | 536 | 20240406 | 1603 | 2425207 | 2067 | Transformer only | Vegetation | Tree - fell into line | 2 | 4134 | 38.0051 | -120.4245 | No | Overcast;32-90 F | Service conductor | Broken | 24-0051733 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1931512 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 1673 | 20240405 | 536 | 20240406 | 1753 | 2425253 | 2177 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 15239 | 38.0115 | -120.4183 | No | Overcast;32-90 F | Other | Broken | 24-0051123 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1931525 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | SWITCH | 122091 | 20240405 | 537 | 20240406 | 1559 | 2425232 | 2062 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 28205 | 38.0139 | -120.4164 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051123 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | Yes | No | 1931519 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 143831 | 20240405 | 538 | 20240406 | 1914 | 2423515 | 2256 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17999 | 37.9551 | -120.3278 | No | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken | 24-0051744 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931520 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 26357 | 20240405 | 539 | 20240405 | 2151 | 2424805 | 972 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 53460 | 37.9834 | -120.3871 | No | Overcast-Snow;32-90 F | Crossarm- Wood | Broken | 24-0051606 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931373 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320322653714 | 20240405 | 551 | 20240406 | 1415 | 2425121 | 1944 | Transformer only | Vegetation | Tree - fell into line | 10 | 19440 | 37.9754 | -120.3892 | No | Snow-Overcast-Fog;Below 32 F | Transformer | Broken- wire on ground | 24-0051694 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931470 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320346453880 | 20240405 | 552 | 20240406 | 1800 | 2423529 | 2168 | Transformer only | Vegetation | Tree - fell into line | 8 | 17344 | 37.9797 | -120.3806 | No | Snow-Overcast;32-90 F | Transformer | Failed/Faulted | 24-0051708 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931483 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | OTHER | 5959 | 20240405 | 604 | 20240405 | 1050 | 2423648 | 286 | Distribution Circuit | Environmental/External | Ice or snow | 18 | 5148 | 38.0357 | -120.3995 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051194 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | Yes | 1931119 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 258550 | 20240405 | 623 | 20240405 | 1713 | 2423551 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 2568 | 389797 | 37.8844 | -120.3058 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051135 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1931059 | 0 | EPSS Ckt | N | 2024 | SGF
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7704 | 20240405 | 636 | 20240405 | 918 | 2423560 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1782 | 37.2655 | -120.3256 | No | Clear;32-90 F |  |  | 24-0051230 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931181 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 363884 | 20240405 | 722 | 20240405 | 1404 | 2423607 | 402 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 28140 | 37.2327 | -119.4996 | No | Overcast-Fog-Snow;32-90 F | Other | Broken | 24-0051156 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931069 | 0 | EPSS Ckt | N | 2024 | A & B
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | TRANSFORMER | 318512048725 | 20240405 | 730 | 20240405 | 1110 | 2423612 | 220 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 660 | 37.837 | -121.0163 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0051220 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931170 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 44839 | 20240405 | 756 | 20240406 | 1520 | 2423647 | 1884 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3768 | 38.005 | -120.4371 | No | Overcast-Drizzle;32-90 F |  |  | 24-0051797 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931553 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 21435 | 20240405 | 809 | 20240405 | 1041 | 2423670 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 136 | 20672 | 37.967 | -120.4336 | No | Overcast-Drizzle;32-90 F |  |  | 24-0051312 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931225 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L2155 | 20240405 | 823 | 20240406 | 1005 | 2423693 | 1542 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 24672 | 37.9492 | -120.2562 | No | Overcast-Fog-Snow;32-90 F |  |  | 24-0051720 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931501 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320532454076 | 20240405 | 825 | 20240405 | 1800 | 2423622 | 575 | Transformer only | Vegetation | Tree - fell into line | 4 | 2300 | 37.985 | -120.3169 | No | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Failed/Faulted | 24-0051456 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931280 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 20329 | 20240405 | 828 | 20240406 | 1434 | 2423700 | 1806 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 41538 | 38.0185 | -120.2184 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0051789 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931547 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 90374 | 20240405 | 840 | 20240406 | 1506 | 2423585 | 1826 | Distribution Circuit | Equipment Failure/Involved | Overhead | 226 | 133826 | 37.9595 | -120.403 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0051198 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931124 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1843 | 20240405 | 859 | 20240406 | 1812 | 2423804 | 1993 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 117064 | 37.9482 | -120.3903 | No | Overcast-Fog-Snow;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051644 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931408 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320278053310 | 20240405 | 901 | 20240406 | 1328 | 2424767 | 1707 | Transformer only | Environmental/External | Ice or snow | 2 | 3414 | 37.9643 | -120.4036 | No | Snow-Overcast-Fog;Below 32 F | Transformer | Failed/Faulted | 24-0051591 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931362 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 20240405 | 912 | 20240406 | 7 | 2423866 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 27495 | 37.7148 | -120.0964 | No | Overcast-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0051467 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931287 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 1617 | 20240405 | 921 | 20240405 | 1109 | 2423841 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 3273 | 37.3122 | -119.6203 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0051273 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931206 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 6504 | 20240405 | 926 | 20240405 | 1234 | 2423859 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 11280 | 36.9531 | -120.0861 | No | Overcast;32-90 F |  |  | 24-0051403 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931258 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5596 | 20240405 | 1013 | 20240405 | 1328 | 2423956 | 195 | Distribution Circuit | Environmental/External | Ice or snow | 270 | 52650 | 37.2119 | -119.5538 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken | 24-0051338 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931234 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320190153441 | 20240405 | 1127 | 20240405 | 1800 | 2423630 | 393 | Transformer only | Vegetation | Tree - fell into line | 2 | 786 | 37.9676 | -120.4352 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0051388 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931250 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRIP-SAVER | 5722 | 20240405 | 1145 | 20240405 | 1410 | 2424066 | 145 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 23 | 3332 | 37.3158 | -119.6086 | No | Overcast-Fog;32-90 F |  |  | 24-0051484 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931298 | 1 | EPSS Ckt | N | 2024 | A
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | SWITCH | 5663 | 20240405 | 1259 | 20240405 | 1338 | 2424159 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 358 | 13962 | 37.3271 | -119.5462 | No | Overcast-Snow;32-90 F |  |  | 24-0051443 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931274 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 24353 | 20240405 | 1323 | 20240405 | 1635 | 2424180 | 192 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2304 | 37.2166 | -121.0309 | No | Partly Cloudy;32-90 F |  |  | 24-0051566 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931343 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | RECLOSER | 90350 | 20240405 | 1351 | 20240405 | 2258 | 2424218 | 547 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1749 | 139806 | 37.307 | -120.4985 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0051490 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931301 | 0 | Non-EPSS | N | 2024 | A GRD
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | RECLOSER | 9600 | 20240405 | 1353 | 20240405 | 1740 | 2424224 | 227 | Distribution Circuit | 3rd Party | Vehicle | 197 | 21655 | 37.1245 | -121.0153 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0051477 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931293 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 2254 | 20240405 | 1432 | 20240405 | 1649 | 2424101 | 137 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 6165 | 37.3174 | -119.6067 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0051502 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931304 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRANSFORMER | 322590529650 | 20240405 | 1443 | 20240405 | 1807 | 2424282 | 204 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 816 | 37.3114 | -119.61 | No | Overcast-Rain;32-90 F | Service conductor | Broken- wire on ground | 24-0051528 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931320 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 6765 | 20240405 | 1500 | 20240405 | 2204 | 2424200 | 424 | Distribution Circuit | 3rd Party | Vehicle | 55 | 23320 | 37.0181 | -120.1459 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0051518 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931312 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320323853992 | 20240405 | 1636 | 20240406 | 1427 | 2424823 | 1311 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 19665 | 37.9826 | -120.3884 | No | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken | 24-0051611 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931375 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319565231111 | 20240405 | 1707 | 20240405 | 1735 | 2424638 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 56 | 37.3542 | -120.6504 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0051589 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931360 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319248131304 | 20240405 | 1719 | 20240405 | 1808 | 2424719 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 49 | 37.3588 | -120.7598 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0051602 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931370 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320319556292 | 20240405 | 1725 | 20240405 | 1749 | 2424736 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 48 | 38.0462 | -120.39 | No | Partly Cloudy;32-90 F | Secondary | Contaminated | 24-0051582 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931354 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | FUSE | 1641 | 20240405 | 1736 | 20240406 | 900 | 2424748 | 924 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 25 | 23100 | 38.0047 | -120.3856 | No | Partly Cloudy;32-90 F |  |  | 24-0051703 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931478 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23936 | 20240405 | 1745 | 20240405 | 2114 | 2424768 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 627 | 37.7222 | -120.1193 | No | Partly Cloudy;32-90 F |  |  | 24-0051646 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931410 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 53159 | 20240405 | 1829 | 20240407 | 1116 | 2424816 | 2447 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2447 | 37.9643 | -120.4048 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0051741 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1931518 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 4893 | 20240405 | 1933 | 20240405 | 1944 | 2423531 | 11 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 396 | 37.9596 | -120.4296 | No | Overcast-Snow;32-90 F | Transformer (OH) | Broken | 24-0051619 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931382 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | TAR FLAT-0401 | 163240401 | FUSE | 464057 | 20240405 | 1945 | 20240406 | 1057 | 2424867 | 912 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2736 | 37.9913 | -120.3791 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0051739 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931517 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 26356 | 20240405 | 2339 | 20240406 | 1815 | 2425102 | 1116 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4464 | 38.0339 | -120.3804 | No | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051812 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931562 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | RECLOSER | 10960 | 20240406 | 455 | 20240406 | 826 | 2425014 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3439 | 272077 | 37.3307 | -120.4693 | No | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051679 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1931447 | 0 | Non-EPSS | N | 2024 | BC GRD
YOSEMITE | STANISLAUS | TAR FLAT-0401 | 163240401 | TRANSFORMER | 320366054275 | 20240406 | 519 | 20240406 | 1853 | 2425331 | 814 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1628 | 37.9907 | -120.3729 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051796 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | Yes | Yes | 1931552 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | L319 | 20240406 | 635 | 20240406 | 2014 | 2425353 | 819 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 4003 | 37.9947 | -120.4172 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051799 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931555 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 6504 | 20240406 | 841 | 20240406 | 1024 | 2425123 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 6180 | 36.9531 | -120.0861 | No | Clear;32-90 F |  |  | 24-0051727 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931506 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 318983617372 | 20240406 | 907 | 20240406 | 1121 | 2425144 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 134 | 36.9769 | -120.849 | No | Clear;32-90 F | Fuse | Broken | 24-0051746 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931522 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 19684 | 20240406 | 1016 | 20240406 | 1306 | 2425200 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 4080 | 37.9526 | -120.3906 | No | Clear;32-90 F |  |  | 24-0051772 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931538 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | FUSE | 10839 | 20240406 | 1119 | 20240406 | 1207 | 2425240 | 48 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 768 | 37.0352 | -120.8494 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0051757 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931529 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320237554949 | 20240406 | 1201 | 20240406 | 1217 | 2424866 | 16 | Transformer only | Vegetation | Tree - fell into line | 5 | 80 | 38.0096 | -120.4188 | No | Overcast;32-90 F | Service conductor | Broken | 24-0051627 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931391 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320210755363 | 20240406 | 1201 | 20240406 | 1826 | 2425198 | 385 | Transformer only | Vegetation | Tree - fell into line | 2 | 770 | 38.0209 | -120.4279 | No | Overcast;32-90 F | Service conductor | Broken | 24-0051729 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931508 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320487152911 | 20240406 | 1224 | 20240406 | 1857 | 2425251 | 393 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 786 | 37.9534 | -120.3321 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051768 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931536 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 6335 | 20240406 | 1253 | 20240406 | 1426 | 2425290 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 372 | 36.9534 | -119.7845 | No | Clear;32-90 F |  |  | 24-0051786 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931545 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 751459 | 20240406 | 1615 | 20240407 | 901 | 2425383 | 1006 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 4024 | 38.038 | -120.4269 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0051810 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931560 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320371256507 | 20240406 | 1652 | 20240407 | 1014 | 2425395 | 1042 | Transformer only | Environmental/External | Ice or snow | 1 | 1042 | 38.0516 | -120.3751 | No | Partly Cloudy;32-90 F | Transformer | Contaminated | 24-0051816 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931563 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | S1405 | 20240407 | 56 | 20240407 | 439 | 2425529 | 223 | Distribution Circuit | Vegetation | Other ground vegetation | 25 | 5652 | 37.7956 | -120.8246 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0051854 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931595 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 19689 | 20240407 | 613 | 20240407 | 827 | 2425558 | 134 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 670 | 37.9372 | -120.3842 | No | Clear;32-90 F |  |  | 24-0051866 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931609 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L2627 | 20240407 | 626 | 20240407 | 732 | 2425562 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 1386 | 37.9706 | -120.448 | No | Clear;32-90 F |  |  | 24-0051860 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931603 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320349153957 | 20240407 | 930 | 20240407 | 1130 | 2425639 | 120 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 600 | 37.9818 | -120.3799 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0051874 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931624 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320278453456 | 20240407 | 1123 | 20240407 | 1214 | 2425643 | 51 | Transformer only | Vegetation | Tree - fell into line | 4 | 204 | 37.9681 | -120.4043 | No | Clear;32-90 F | Service conductor | Bent or Twisted | 24-0051883 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931636 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 4733 | 20240407 | 1206 | 20240407 | 1355 | 2425682 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 653 | 37.3225 | -120.451 | No | Clear;32-90 F |  |  | 24-0051890 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931645 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 460215 | 20240407 | 1710 | 20240407 | 1811 | 2425785 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1098 | 37.9547 | -120.3303 | No | Partly Cloudy;32-90 F |  |  | 24-0051908 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931656 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 176489 | 20240408 | 740 | 20240408 | 845 | 2425956 | 65 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 95 | 6175 | 37.3234 | -119.605 | No | Clear;32-90 F |  |  | 24-0052000 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931772 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | TRANSFORMER | 415570149490 | 20240408 | 1026 | 20240408 | 1215 | 2426196 | 109 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 109 | 36.682 | -120.5116 | No | Clear;32-90 F | Fuse | Broken | 24-0052167 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931900 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | TRANSFORMER | 415013751120 | 20240408 | 1050 | 20240408 | 1119 | 2426229 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 29 | 36.7257 | -120.7029 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0052086 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931872 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 26365 | 20240408 | 1247 | 20240408 | 1505 | 2426323 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 966 | 38.0076 | -120.4119 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0052172 | OH | Sus | 31690017 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1931901 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | SWITCH | 5446 | 20240408 | 1444 | 20240408 | 1603 | 2426406 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2082 | 164478 | 37.2502 | -119.5611 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0052195 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1931904 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 23875 | 20240408 | 2330 | 20240409 | 1116 | 2426649 | 706 | Distribution Circuit | Equipment Failure/Involved | Underground | 155 | 35411 | 37.7744 | -120.8459 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0052399 | UG | Sus | 46222144 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932028 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | JUMPER | 6007 | 20240408 | 2357 | 20240410 | 512 | 2427467 | 1755 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3510 | 37.0697 | -120.4735 | No | Clear;32-90 F | Jumper | Burned Open | 24-0052894 | OH | Sus | 46222678 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1932321 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7999 | 20240409 | 554 | 20240409 | 754 | 2426688 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 120 | 37.5228 | -120.5787 | No | Clear;32-90 F |  |  | 24-0052473 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932091 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 322401030803 | 20240409 | 821 | 20240409 | 1058 | 2426759 | 157 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 314 | 37.3433 | -119.6745 | No | Clear;32-90 F | Service conductor | Broken | 24-0052464 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932079 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321106016034 | 20240409 | 910 | 20240409 | 1054 | 2426866 | 104 | Transformer only | Animal | Other | 1 | 104 | 36.9397 | -120.1216 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0052569 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932216 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 53957 | 20240409 | 930 | 20240409 | 1045 | 2426925 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 3652 | 38.0333 | -120.4031 | No | Clear;32-90 F |  |  | 24-0052554 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932211 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319263031709 | 20240409 | 942 | 20240409 | 1818 | 2426937 | 516 | Distribution Circuit | Environmental/External | Lightning | 1 | 516 | 37.3694 | -120.7542 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0052579 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932221 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | T4614 | 20240409 | 944 | 20240409 | 1012 | 2426939 | 28 | Transformer only | Equipment Failure/Involved | Underground | 14 | 392 | 37.7592 | -120.8717 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0052527 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932197 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 1199 | 20240409 | 1151 | 20240409 | 1412 | 2427134 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 6627 | 37.3313 | -121.097 | No | Clear;32-90 F |  |  | 24-0052666 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932253 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319670031131 | 20240409 | 1155 | 20240409 | 1219 | 2427045 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 216 | 37.355 | -120.6144 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0052614 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932241 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | OTHER | J13399 TWD T3746 | 20240409 | 1618 | 20240409 | 1902 | 2427322 | 164 | Distribution Circuit | Equipment Failure/Involved | Underground | 41 | 2968 | 36.9868 | -120.0741 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0052760 | UG | Sus | 35543107 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932277 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320274154244 | 20240409 | 1651 | 20240409 | 1730 | 2427347 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 78 | 37.99 | -120.4061 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0052805 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932278 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | L817 | 20240409 | 1702 | 20240412 | 1244 | 2427282 | 4062 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 20310 | 37.9807 | -120.3921 | No | Clear;32-90 F | Customer Equipment | Broken | 24-0052755 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932269 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L2183 | 20240410 | 854 | 20240410 | 950 | 2427645 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 56 | 37.9908 | -120.4797 | No | Clear;32-90 F |  |  | 24-0053034 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932486 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 2199 | 20240410 | 1012 | 20240410 | 1143 | 2427772 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 364 | 37.151 | -120.6376 | No | Clear;32-90 F |  |  | 24-0053070 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932520 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 2081 | 20240410 | 1019 | 20240410 | 1114 | 2427779 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 165 | 37.7762 | -120.8073 | No | Partly Cloudy;32-90 F |  |  | 24-0053044 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932498 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 929199 | 20240410 | 1045 | 20240410 | 1210 | 2427799 | 85 | Distribution Circuit | Animal | Other | 2 | 170 | 37.3399 | -120.279 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0053093 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932531 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 100000055638 | 20240410 | 1243 | 20240410 | 1550 | 2427830 | 187 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 187 | 38.0113 | -120.4042 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0053112 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932535 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 320072011727 | 20240410 | 1354 | 20240410 | 1655 | 2427944 | 181 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 362 | 36.8214 | -120.4762 | No | Clear;32-90 F | Transformer | Normal | 24-0053271 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932554 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321399717073 | 20240410 | 1503 | 20240410 | 1630 | 2427989 | 87 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 174 | 36.9677 | -120.0219 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0053274 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932555 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 319703325130 | 20240410 | 1623 | 20240410 | 2015 | 2427935 | 232 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 232 | 37.1908 | -120.6051 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0053281 | OH | Sus | 31690071 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932561 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | JUMPER | OJ @ CGC 321466261792 | 20240410 | 1654 | 20240410 | 1856 | 2428059 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 366 | 38.196 | -119.9905 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0053279 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932559 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | JUMPER | OJ 3 POLES S/OF CGC # 323023126726 | 20240410 | 2312 | 20240411 | 206 | 2428173 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 11136 | 37.2291 | -119.4612 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0053341 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932594 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 809495 | 20240411 | 1200 | 20240411 | 2150 | 2428637 | 590 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2660 | 37.7579 | -121.0738 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0053587 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932814 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321764934702 | 20240411 | 1413 | 20240411 | 1714 | 2428718 | 181 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 181 | 37.4496 | -119.8923 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0053682 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932834 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 3343 | 20240411 | 1441 | 20240411 | 1644 | 2428749 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2091 | 37.9458 | -120.8437 | No | Clear;32-90 F |  |  | 24-0053699 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932835 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | JUMPER | UNMAPPED FUCO 93889 | 20240411 | 1700 | 20240412 | 1 | 2428836 | 421 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 421 | 37.5319 | -120.4412 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0053787 | OH | Sus | 31690076 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932859 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | JUMPER | BURNT 'A' PHASE JUMPER @ 21018 OPEN | 20240411 | 1825 | 20240412 | 331 | 2428876 | 546 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2730 | 37.1858 | -120.5155 | No | Clear;32-90 F |  |  | 24-0053834 | OH | Sus | 46227776 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932917 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | TRANSFORMER | T7126 | 20240411 | 1828 | 20240412 | 324 | 2428878 | 536 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 8322 | 37.0672 | -120.8232 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0053795 | UG | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932882 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20643 | 20240411 | 2321 | 20240412 | 58 | 2429044 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 97 | 37.7426 | -120.824 | No | Clear;32-90 F |  |  | 24-0053842 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1932922 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 778665 | 20240412 | 345 | 20240412 | 721 | 2429072 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1297 | 37.2299 | -120.7025 | No | Clear;32-90 F |  |  | 24-0053887 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932950 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | TRANSFORMER | 319226019975 | 20240412 | 803 | 20240412 | 1140 | 2429162 | 217 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 217 | 37.0479 | -120.7657 | No | Clear;32-90 F |  |  | 24-0054088 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1933120 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | TRANSFORMER | 322252418920 | 20240412 | 1201 | 20240412 | 1346 | 2429481 | 105 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 105 | 37.0186 | -119.7297 | No | Clear;32-90 F |  |  | 24-0054142 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1933137 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | OCB | 1101/2 | 20240412 | 1246 | 20240412 | 1253 | 2429520 | 7 | Distribution Circuit | 3rd Party | Other | 565 | 3955 | 37.3635 | -120.7607 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0054091 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933122 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 318478630218 | 20240412 | 1249 | 20240412 | 1617 | 2429526 | 208 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 416 | 37.3287 | -121.024 | No | Clear;32-90 F | Fuse | Broken | 24-0054217 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933169 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | S1651 | 20240412 | 1343 | 20240412 | 1433 | 2429595 | 50 | Distribution Circuit | Animal | Squirrel | 1 | 50 | 37.9709 | -120.2808 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0054167 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933149 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321521733771 | 20240412 | 1520 | 20240412 | 1543 | 2429498 | 23 | Transformer only | Equipment Failure/Involved | Underground | 1 | 23 | 37.4251 | -119.9762 | No | Clear;32-90 F | Secondary | Broken | 24-0054198 | UG | Sus | 46228566 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933161 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 21167 | 20240412 | 1746 | 20240412 | 1950 | 2429910 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1116 | 37.7955 | -120.8254 | No | Clear;32-90 F |  |  | 24-0054278 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933201 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 25364 | 20240412 | 1813 | 20240412 | 2240 | 2429926 | 267 | Distribution Circuit | Animal | Bird found | 3 | 801 | 37.762 | -120.9691 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0054306 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933234 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1102 | 252091102 | FUSE | 3092 | 20240412 | 1857 | 20240412 | 2004 | 2429947 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 737 | 37.0644 | -120.8785 | No | Clear;32-90 F |  |  | 24-0054277 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933200 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 21004 | 20240412 | 2127 | 20240413 | 45 | 2430001 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1980 | 36.6918 | -120.6218 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0054313 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933241 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | FUSE | 1641 | 20240413 | 622 | 20240413 | 858 | 2430145 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3900 | 38.0047 | -120.3856 | No | Overcast;32-90 F |  |  | 24-0054362 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933281 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | RECLOSER | 5570 | 20240413 | 1249 | 20240413 | 2230 | 2430343 | 581 | Distribution Circuit | Equipment Failure/Involved | Overhead | 437 | 56369 | 37.0543 | -120.3521 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Burned/flashed | 24-0054466 | OH | Sus | 31690515 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | No | No | 1933350 | 0 | Non-EPSS | N | 2024 | A AND B- SGF
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318647545885 | 20240413 | 1253 | 20240413 | 1815 | 2430350 | 322 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 322 | 37.7593 | -120.969 | No | Overcast-Rain;32-90 F | Transformer (OH) | Leaking | 24-0054435 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933323 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | TRANSFORMER | 320131029848 | 20240413 | 1328 | 20240413 | 1402 | 2430264 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 170 | 37.3205 | -120.4547 | No | Partly Cloudy-Rain;32-90 F | Secondary | Broken | 24-0054439 | OH | Sus | 46228510 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933327 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | FUSE | 5591 | 20240413 | 1331 | 20240413 | 1534 | 2430392 | 123 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 85 | 10455 | 37.0287 | -119.7252 | No | Overcast-Rain;32-90 F |  |  | 24-0054502 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933370 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319735450486 | 20240413 | 1400 | 20240413 | 1548 | 2430503 | 108 | Transformer only | Animal | Other | 2 | 216 | 37.8866 | -120.5926 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Normal | 24-0054518 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933380 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5680 | 20240413 | 1401 | 20240413 | 1925 | 2430484 | 324 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 262 | 49246 | 37.0552 | -120.0295 | No | Overcast-Rain;32-90 F |  |  | 24-0054519 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933382 | 0 | EPSS Ckt | N | 2024 | C PH AND GROUND
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 321020557323 | 20240413 | 1702 | 20240413 | 2245 | 2430776 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 343 | 38.074 | -120.1467 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0054556 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933420 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L2075 | 20240413 | 1911 | 20240413 | 2113 | 2430910 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1098 | 38.0207 | -120.3837 | No | Overcast;32-90 F |  |  | 24-0054573 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933436 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 8517 | 20240413 | 2317 | 20240414 | 210 | 2430993 | 173 | Distribution Circuit | Animal | Bird found | 4 | 692 | 37.9448 | -120.8894 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0054616 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933483 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 9010 | 20240414 | 343 | 20240414 | 739 | 2431038 | 236 | Distribution Circuit | Animal | Other | 240 | 56640 | 37.5385 | -121.2044 | No | Overcast-Fog;32-90 F | Recloser | Burned/flashed | 24-0054618 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | No | No | 1933485 | 0 | EPSS Ckt | N | 2024 | B C GRD MTT
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 14252 | 20240414 | 434 | 20240414 | 1333 | 2431042 | 539 | Distribution Circuit | Equipment Failure/Involved | Underground | 193 | 38113 | 37.3008 | -120.4836 | No | Overcast-Rain;32-90 F | Elbow | Failed/Faulted | 24-0054628 | UG | Sus | 46228761 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933495 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321476518292 | 20240414 | 1411 | 20240414 | 1621 | 2431322 | 130 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 260 | 37.0011 | -119.9954 | No | Partly Cloudy;32-90 F |  |  | 24-0054715 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1933578 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | S1791 | 20240415 | 1010 | 20240415 | 1125 | 2431809 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1125 | 37.904 | -120.4541 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0054862 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933771 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321595214464 | 20240415 | 1301 | 20240415 | 1814 | 2431975 | 313 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 313 | 36.8959 | -119.9565 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0055045 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933839 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 99295 | 20240416 | 19 | 20240416 | 216 | 2432306 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3042 | 37.5445 | -120.4624 | No | Clear;32-90 F |  |  | 24-0055234 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933939 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | TRANSFORMER | 318841629729 | 20240416 | 402 | 20240416 | 848 | 2432320 | 286 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 858 | 37.3135 | -120.8997 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0055238 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1933943 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | FUSE | 3812 | 20240416 | 1110 | 20240416 | 1137 | 2432674 | 27 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 1782 | 37.0619 | -120.832 | No | Clear;32-90 F | Fuse | Broken | 24-0055337 | OH | Sus | 46229240 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934132 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | SWITCH | 540 | 20240416 | 1306 | 20240416 | 1317 | 2432753 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 66 | 726 | 37.0639 | -120.8308 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0055337 | UG | Sus | 46229240 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1934161 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | S1839 | 20240416 | 1438 | 20240416 | 1757 | 2432826 | 199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 3184 | 37.8494 | -120.9982 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0055543 | OH | Sus | 31690953 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1934187 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 154291 | 20240416 | 1450 | 20240416 | 1654 | 2432836 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 124 | 37.2371 | -120.6541 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0055544 | OH | Sus | 31690952 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1934190 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 21794 | 20240416 | 1456 | 20240416 | 2115 | 2432841 | 379 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 379 | 37.7106 | -120.6686 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0055539 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934184 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | OTHER | T809889 TWD T257111 | 20240416 | 1516 | 20240416 | 1604 | 2432858 | 48 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 576 | 36.964 | -120.0381 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0045157 | UG | Sus | 35315884 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1934195 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | TRANSFORMER | 415269656083 | 20240416 | 1714 | 20240416 | 1734 | 2432822 | 20 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 20 | 36.8621 | -120.6183 | No | Clear;32-90 F |  |  | 24-0055604 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1934214 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 23058 | 20240416 | 1724 | 20240416 | 1922 | 2432940 | 118 | Distribution Circuit | 3rd Party | Other | 12 | 1416 | 36.9987 | -120.5989 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0055616 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1934224 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | RECLOSER | 3800 | 20240416 | 2037 | 20240417 | 201 | 2433038 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 19764 | 37.0575 | -120.9266 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0055631 | OH | Sus | 31690955 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1934234 | 0 | EPSS Ckt | N | 2024 | A GRD MTT
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 318809044905 | 20240417 | 705 | 20240417 | 1438 | 2433242 | 453 | Distribution Circuit | 3rd Party | Vehicle | 1991 | 12393 | 37.7326 | -120.9126 | No | Fog;32-90 F | Pole-Wood | Broken | 24-0055794 | OH | Sus | 35545852 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934400 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | TRANSFORMER | 414981053040 | 20240417 | 733 | 20240417 | 1027 | 2433148 | 174 | Transformer only | Animal | Bird found | 1 | 174 | 36.7775 | -120.7156 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0055845 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934492 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319667733579 | 20240417 | 744 | 20240417 | 856 | 2433155 | 72 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 72 | 37.4224 | -120.6149 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0055801 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1934411 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 11585 | 20240417 | 1035 | 20240417 | 1122 | 2433412 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 94 | 37.2051 | -120.2708 | No | Clear;32-90 F |  |  | 24-0055873 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934505 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319526736899 | 20240417 | 1046 | 20240417 | 1228 | 2433434 | 102 | Transformer only | Animal | Other | 1 | 102 | 37.514 | -120.6637 | No | Clear;32-90 F | Transformer (OH) |  | 24-0055930 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934518 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | TRANSFORMER | 414904555160 | 20240417 | 1105 | 20240417 | 1153 | 2433270 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 48 | 36.8359 | -120.7426 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0055911 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934512 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | JUMPER | BLOWN INSERT AT T3138 | 20240417 | 1755 | 20240418 | 439 | 2433772 | 537 | Distribution Circuit | Equipment Failure/Involved | Overhead | 452 | 75726 | 37.2298 | -120.2506 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0056106 | OH | Sus | 35546229 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934583 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | TRANSFORMER | 320138731801 | 20240417 | 1810 | 20240417 | 1817 | 2433761 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 14 | 37.3743 | -120.4527 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0056107 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934577 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 37357 | 20240418 | 353 | 20240418 | 641 | 2433897 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 7935 | 37.4265 | -120.6639 | No | Fog;32-90 F |  |  | 24-0056188 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1934649 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | TRANSFORMER | 322057915069 | 20240418 | 626 | 20240418 | 840 | 2433938 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 134 | 36.9116 | -119.7981 | No | Clear;32-90 F | Fuse | Broken | 24-0056238 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934699 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320299226382 | 20240418 | 1157 | 20240418 | 1240 | 2434146 | 43 | Transformer only | Animal | Other | 1 | 43 | 37.2253 | -120.3987 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0056392 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934754 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | 20453 | 20240418 | 1230 | 20240418 | 1408 | 2434165 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 294 | 37.7396 | -120.8814 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0056363 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934748 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 3759 | 20240419 | 223 | 20240419 | 1356 | 2434496 | 693 | Distribution Circuit | Equipment Failure/Involved | Underground | 199 | 97911 | 37.3645 | -120.5958 | No | Partly Cloudy;32-90 F | Elbow | Failed/Faulted | 24-0056676 | UG | Sus | 46231357 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934842 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10338 | 20240419 | 915 | 20240419 | 1137 | 2434715 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2840 | 37.2814 | -119.6699 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0056750 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934917 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 24884 | 20240419 | 922 | 20240419 | 1010 | 2434779 | 48 | Distribution Circuit | Equipment Failure/Involved | Underground | 121 | 5808 | 37.0829 | -120.837 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0056426 | UG | Sus | 35546351 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934969 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | TRANSFORMER | 321248321765 | 20240419 | 1012 | 20240419 | 1152 | 2434837 | 100 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 100 | 37.097 | -120.0738 | No | Clear;32-90 F | Fuse | Broken | 24-0056884 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935020 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 6793 | 20240419 | 1105 | 20240419 | 1315 | 2434890 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 5200 | 37.7405 | -120.9588 | No | Clear;32-90 F |  |  | 24-0056903 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935026 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320576543434 | 20240419 | 1159 | 20240419 | 1830 | 2434920 | 391 | Transformer only | Environmental/External | Lightning | 1 | 391 | 37.6964 | -120.3006 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057008 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935053 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320766553918 | 20240419 | 1345 | 20240419 | 1502 | 2435081 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 231 | 37.981 | -120.2352 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0056971 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935039 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | TRANSFORMER | 415967952163 | 20240419 | 1542 | 20240419 | 1746 | 2435160 | 124 | Transformer only | 3rd Party | Customer Equipment | 16 | 1984 | 36.7582 | -120.3771 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 24-0057066 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1935068 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 6413 | 20240419 | 2020 | 20240419 | 2115 | 2435280 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 220 | 37.7401 | -120.8022 | No | Clear;32-90 F |  |  | 24-0057080 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935081 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 320755936611 | 20240420 | 733 | 20240420 | 1659 | 2435373 | 566 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 566 | 37.5066 | -120.2399 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057180 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935215 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | L817 | 20240420 | 852 | 20240420 | 1334 | 2435435 | 282 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 1410 | 37.9807 | -120.3921 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0057130 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1935172 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 6573 | 20240420 | 858 | 20240420 | 1014 | 2435441 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1368 | 36.8684 | -120.083 | No | Clear;32-90 F |  |  | 24-0057139 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935192 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | SWITCH | 67545 | 20240420 | 901 | 20240420 | 1515 | 2435440 | 374 | Distribution Circuit | 3rd Party | Vehicle | 30 | 11220 | 36.923 | -120.0558 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0057111 | OH | Sus | 35546872 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935175 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 8822 | 20240420 | 1206 | 20240420 | 1312 | 2435515 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 308 | 37.1773 | -120.4919 | No | Clear;32-90 F |  |  | 24-0057171 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935212 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318486046585 | 20240420 | 1252 | 20240420 | 2000 | 2435507 | 428 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 428 | 37.7788 | -121.0249 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057172 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935213 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | RECLOSER | 30980 | 20240420 | 1524 | 20240420 | 2303 | 2435578 | 459 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1171 | 34917 | 37.3044 | -120.4833 | No | Clear;32-90 F | Secondary | Broken- wire on object | 24-0057194 | OH | Sus | 46232014 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935225 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7306 | 20240420 | 1622 | 20240420 | 1750 | 2435606 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 792 | 37.5134 | -120.5116 | No | Clear;32-90 F |  |  | 24-0057214 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935231 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318780547570 | 20240420 | 1834 | 20240420 | 2004 | 2435642 | 90 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 180 | 37.8057 | -120.9226 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0057236 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935241 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 4587 | 20240420 | 1838 | 20240420 | 1932 | 2435641 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 648 | 37.1927 | -120.4879 | No | Clear;32-90 F |  |  | 24-0057233 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935238 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S1249 | 20240420 | 2018 | 20240420 | 2105 | 2435671 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1160 | 37.7834 | -120.8622 | No | Clear;32-90 F |  |  | 24-0057240 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935247 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 9539 | 20240421 | 141 | 20240421 | 255 | 2435726 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1135 | 37.7875 | -121.0102 | No | Clear;32-90 F |  |  | 24-0057271 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935273 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 63502 | 20240421 | 551 | 20240421 | 927 | 2435755 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 359 | 77544 | 38.0456 | -120.3921 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0057274 | OH | Sus | 31691580 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1935277 | 0 | EPSS Ckt | N | 2024 | C PH & GRD
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 11585 | 20240421 | 555 | 20240421 | 820 | 2435756 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 290 | 37.2051 | -120.2708 | No | Clear;32-90 F |  |  | 24-0057286 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935290 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 4926 | 20240421 | 2050 | 20240421 | 2150 | 2435987 | 60 | Distribution Circuit | Animal | Bird found | 41 | 2460 | 37.3281 | -120.7423 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0057341 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935347 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | OCB | 1110/2 | 20240422 | 927 | 20240422 | 1137 | 2436367 | 130 | Distribution Circuit | Animal | Bird found | 1038 | 119860 | 37.1847 | -120.2736 | No | Clear;32-90 F | Recloser | Failed/Faulted | 24-0057456 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935489 | 0 | EPSS Ckt | N | 2024 | A & GRD
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 3705 | 20240422 | 1010 | 20240422 | 1401 | 2436457 | 231 | Distribution Circuit | 3rd Party | Vehicle | 27 | 6237 | 37.0002 | -120.8551 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0057538 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1935536 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20643 | 20240422 | 1031 | 20240422 | 1121 | 2436530 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 50 | 37.7426 | -120.824 | No | Clear;32-90 F |  |  | 24-0057543 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935537 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321647814162 | 20240422 | 1124 | 20240422 | 1410 | 2436581 | 166 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 166 | 36.8876 | -119.9378 | No | Clear;32-90 F | Fuse | Burned Open | 24-0057661 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935575 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319488028868 | 20240422 | 1310 | 20240422 | 1630 | 2436673 | 200 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 400 | 37.2928 | -120.6779 | No | Clear;32-90 F | Secondary | Broken | 24-0057609 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935566 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319342530833 | 20240422 | 1425 | 20240422 | 1945 | 2436734 | 320 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 640 | 37.346 | -120.7275 | No | Clear;32-90 F |  |  | 24-0057764 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935618 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319663730806 | 20240422 | 1522 | 20240422 | 1900 | 2436786 | 218 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1526 | 37.3462 | -120.6165 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057708 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935596 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | OTHER | T7123 TWD T7124 | 20240422 | 1527 | 20240422 | 1610 | 2436795 | 43 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 516 | 37.0679 | -120.8241 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0057658 | UG | Sus | 35547334 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935594 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | TRANSFORMER | 320116129064 | 20240422 | 1606 | 20240422 | 2205 | 2436823 | 359 | Transformer only | Vegetation | Tree - fell into line | 10 | 3590 | 37.2988 | -120.4599 | No | Clear;32-90 F | Secondary | Broken | 24-0057728 | OH | Sus | 31691686 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935601 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321647814162 | 20240422 | 1758 | 20240422 | 2255 | 2436881 | 297 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 297 | 36.8876 | -119.9378 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057777 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935634 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 10764 | 20240423 | 604 | 20240423 | 710 | 2437090 | 66 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 924 | 37.1658 | -119.7547 | No | Clear;32-90 F |  |  | 24-0057838 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935665 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 4913 | 20240423 | 936 | 20240423 | 1134 | 2437327 | 118 | Distribution Circuit | 3rd Party | Vehicle | 7 | 826 | 37.3866 | -120.7597 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0057989 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1935819 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | TRANSFORMER | 318945646189 | 20240423 | 1258 | 20240423 | 1408 | 2437496 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 140 | 37.7679 | -120.8658 | No | Clear;32-90 F | Secondary | Broken | 24-0058050 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935838 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20240423 | 1338 | 20240423 | 1532 | 2437591 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 17214 | 37.0679 | -119.9091 | No | Clear;32-90 F |  |  | 24-0058152 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935870 | 0 | EPSS Ckt | N | 2024 | B & GRD
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320237523340 | 20240423 | 1339 | 20240423 | 1532 | 2437537 | 113 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 113 | 37.1417 | -120.4193 | No | Clear;32-90 F |  |  | 24-0058175 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1935876 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 23517 | 20240424 | 440 | 20240424 | 1108 | 2437822 | 388 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1164 | 36.8806 | -119.8482 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0058284 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1935933 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | S2159 | 20240424 | 523 | 20240424 | 630 | 2437845 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2144 | 37.7511 | -120.9036 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0058294 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1935943 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321324419443 | 20240424 | 730 | 20240425 | 658 | 2437858 | 1408 | Transformer only | Animal | Bird found | 1 | 1408 | 37.0332 | -120.0472 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0058533 | OH | Sus | 46233818 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936150 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 850821 | 20240424 | 837 | 20240424 | 951 | 2437928 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 839 | 37.0178 | -120.4373 | No | Overcast;32-90 F |  |  | 24-0058407 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936107 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 100000021682 | 20240424 | 1137 | 20240424 | 1151 | 2438020 | 14 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 14 | 37.5829 | -120.5145 | No | Clear;32-90 F |  |  | 24-0058491 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1936134 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319226546624 | 20240424 | 1800 | 20240424 | 2100 | 2438455 | 180 | Transformer only | Company Initiated | Personnel- company | 7 | 1260 | 37.7805 | -120.7689 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Contaminated | 24-0058680 | UG | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936190 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 281135 | 20240425 | 1313 | 20240425 | 1500 | 2439021 | 107 | Distribution Circuit | Animal | Other | 3 | 321 | 37.0392 | -119.9744 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0059029 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936465 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | FUSE | 161941 | 20240425 | 1414 | 20240425 | 1802 | 2439055 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 456 | 36.6479 | -120.541 | No | Partly Cloudy;32-90 F |  |  | 24-0059100 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936493 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 402242 | 20240425 | 1503 | 20240425 | 1650 | 2439093 | 107 | Distribution Circuit | 3rd Party | Other | 178 | 19046 | 37.0542 | -120.031 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0059028 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936464 | 0 | EPSS Ckt | N | 2024 | AB
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319533226309 | 20240425 | 1620 | 20240425 | 1708 | 2439074 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 48 | 37.2225 | -120.6612 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059072 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936475 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3863 | 20240425 | 1635 | 20240425 | 1654 | 2439155 | 19 | Distribution Circuit | 3rd Party | Other | 21 | 399 | 36.9825 | -120.5904 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0059074 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936477 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | JUMPER | OJS 1 N/OF CGC 1006954288 | 20240425 | 1720 | 20240425 | 1916 | 2439169 | 116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 232 | 37.1062 | -120.4097 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059088 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936482 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 10613 | 20240425 | 2047 | 20240425 | 2345 | 2439286 | 178 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 8 | 1424 | 37.333 | -119.6116 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 24-0059108 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936504 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | T0481 | 20240426 | 116 | 20240426 | 303 | 2439276 | 107 | Transformer only | Equipment Failure/Involved | Underground | 18 | 1926 | 37.3587 | -120.614 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0059153 | UG | Sus | 46234890 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936556 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 27211 | 20240426 | 559 | 20240426 | 833 | 2439589 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1386 | 37.7552 | -121.0271 | No | Partly Cloudy;32-90 F |  |  | 24-0059211 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936636 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | JUMPER | BURNT JUMPER CTR PHASE | 20240426 | 722 | 20240426 | 854 | 2439582 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 1977 | 37.0583 | -120.8539 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0059209 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1936633 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 2857 | 20240426 | 928 | 20240426 | 1110 | 2439678 | 102 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 272 | 36.8764 | -120.1104 | No | Overcast;32-90 F |  |  | 24-0059287 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936718 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 1695 | 20240426 | 1131 | 20240426 | 1329 | 2439789 | 118 | Distribution Circuit | Animal | Other | 60 | 7080 | 37.9734 | -120.4612 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0059357 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936749 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1116 | 252761116 | TRANSFORMER | 321416213633 | 20240426 | 1357 | 20240426 | 1513 | 2439909 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 152 | 36.873 | -120.0163 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0059426 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936767 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 321147433328 | 20240426 | 1748 | 20240426 | 2159 | 2440117 | 251 | Transformer only | Environmental/External | Lightning | 1 | 251 | 37.4153 | -120.1079 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059501 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936816 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7309 | 20240426 | 1802 | 20240426 | 2310 | 2440139 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 1218 | 37.4913 | -120.629 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0059513 | OH | Sus | 31692360 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936824 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320112713257 | 20240426 | 1828 | 20240426 | 2255 | 2440068 | 267 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1602 | 36.8639 | -120.4624 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0059504 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936819 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 786213 | 20240427 | 314 | 20240427 | 431 | 2440362 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 719 | 37.0907 | -120.2971 | No | Partly Cloudy;32-90 F |  |  | 24-0059579 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936893 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 5987 | 20240427 | 417 | 20240427 | 546 | 2440365 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1157 | 37.0544 | -120.2878 | No | Partly Cloudy;32-90 F |  |  | 24-0059583 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936896 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 100000033277 | 20240427 | 751 | 20240427 | 1554 | 2440392 | 483 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 483 | 37.8032 | -120.9418 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059599 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936944 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 786213 | 20240427 | 952 | 20240427 | 1324 | 2440491 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2968 | 37.0907 | -120.2971 | No | Partly Cloudy;32-90 F |  |  | 24-0059643 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936979 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 19088 | 20240427 | 957 | 20240427 | 1221 | 2440570 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 288 | 37.3279 | -120.8666 | No | Clear;32-90 F |  |  | 24-0059625 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936968 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 22697 | 20240427 | 1012 | 20240427 | 1440 | 2440435 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 1324 | 37.845 | -120.9322 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0059604 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936953 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321467019911 | 20240427 | 1440 | 20240427 | 1540 | 2440650 | 60 | Transformer only | 3rd Party | Customer Equipment | 4 | 240 | 37.0461 | -119.9987 | No | Partly Cloudy;32-90 F | Customer Equipment | Bent or Twisted | 24-0059674 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936997 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319468048025 | 20240427 | 1446 | 20240427 | 1853 | 2440729 | 247 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 247 | 37.8191 | -120.6853 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059677 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936999 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | JUMPER | 3943 BURNT OPEN JUMPER | 20240427 | 1813 | 20240427 | 1955 | 2440796 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 714 | 37.1058 | -121.0665 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0059696 | OH | Sus | 0 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1937015 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | JUMPER | OJ 1 N/OF CGC 322614829152 | 20240427 | 2044 | 20240427 | 2327 | 2440827 | 163 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 326 | 37.2983 | -119.6019 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0059697 | OH | Sus | 46235667 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1937017 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 454509 | 20240427 | 2321 | 20240428 | 1024 | 2440872 | 663 | Distribution Circuit | 3rd Party | Vehicle | 5 | 3315 | 37.3118 | -120.4152 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0059730 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937052 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 19343 | 20240428 | 37 | 20240428 | 405 | 2440864 | 208 | Distribution Circuit | 3rd Party | Vehicle | 44 | 9152 | 37.3439 | -120.5961 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0059722 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1937044 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 4652 | 20240428 | 208 | 20240428 | 2105 | 2440885 | 1137 | Distribution Circuit | Equipment Failure/Involved | Underground | 201 | 73552 | 37.3247 | -120.4693 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0059734 | UG | Sus | 46235860 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937056 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320305022310 | 20240428 | 645 | 20240428 | 802 | 2440922 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 77 | 37.1127 | -120.3963 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0059745 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937069 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320796249638 | 20240428 | 813 | 20240428 | 1006 | 2440943 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 113 | 37.8632 | -120.2251 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0059760 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937088 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | FUSE | 226873 | 20240428 | 1027 | 20240428 | 1145 | 2441013 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1170 | 37.0697 | -120.8124 | No | Clear;32-90 F |  |  | 24-0059764 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937092 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 3708 | 20240428 | 1637 | 20240428 | 1753 | 2441133 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 811 | 37.0595 | -120.9129 | No | Clear;32-90 F |  |  | 24-0059794 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937116 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | RECLOSER | 187702 | 20240429 | 21 | 20240429 | 1100 | 2441243 | 519 | Distribution Circuit | Equipment Failure/Involved | Overhead | 196 | 40237 | 37.3599 | -120.8525 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 24-0059819 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937139 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | OTHER | T14282 TWD T14281 | 20240429 | 214 | 20240429 | 253 | 2441251 | 39 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 117 | 37.0924 | -121.0245 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0059825 | UG | Sus | 35549080 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1937141 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321773217381 | 20240429 | 642 | 20240429 | 810 | 2441309 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 176 | 36.9756 | -119.8936 | No | Clear;32-90 F | Fuse | Broken | 24-0059862 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937187 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 7717 | 20240429 | 1014 | 20240429 | 1114 | 2441616 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 660 | 37.1996 | -120.2163 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0059956 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937316 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321768734963 | 20240429 | 1043 | 20240429 | 1400 | 2441629 | 197 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 197 | 37.456 | -119.891 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059967 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937322 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319705938170 | 20240429 | 1319 | 20240429 | 1430 | 2441782 | 71 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 71 | 37.5481 | -120.6032 | No | Clear;32-90 F |  |  | 24-0060077 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1937369 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | L349 | 20240429 | 1507 | 20240429 | 1653 | 2441915 | 106 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 3604 | 37.9602 | -120.4251 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0060098 | OH | Sus | 46236207 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1937375 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 5889 | 20240429 | 1721 | 20240429 | 1829 | 2441997 | 68 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 28 | 1904 | 37.04 | -120.1093 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0060165 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937411 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319147544380 | 20240430 | 527 | 20240430 | 958 | 2442199 | 271 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 271 | 37.7183 | -120.7957 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0060263 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937506 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 6607 | 20240430 | 653 | 20240430 | 845 | 2442197 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 3586 | 37.0982 | -120.4358 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Broken | 24-0060304 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937587 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 655583 | 20240430 | 813 | 20240501 | 1315 | 2442278 | 1742 | Distribution Circuit | Animal | Bird found | 1 | 1742 | 37.1268 | -120.0436 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0060381 | OH | Sus | 46236520 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937699 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321280419350 | 20240430 | 845 | 20240430 | 1009 | 2442383 | 84 | Transformer only | Unknown Cause | Patrol - not conducted | 3 | 252 | 37.0308 | -120.0626 | No | Clear;32-90 F |  |  | 24-0060355 | OH | Sus | 0 | CENTRAL VALLEY | APR | None | 0 | No | No | No | 1937689 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 90448 | 20240430 | 948 | 20240430 | 1456 | 2442777 | 308 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 308 | 37.0433 | -120.0293 | No | Clear-Drizzle;32-90 F |  |  | 24-0060562 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937763 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319662330813 | 20240430 | 1138 | 20240430 | 1558 | 2442656 | 260 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 260 | 37.3464 | -120.6171 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0060529 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937749 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | RECLOSER | 3400 | 20240430 | 1159 | 20240430 | 2039 | 2442675 | 520 | Distribution Circuit | 3rd Party | Vehicle | 286 | 40477 | 36.9816 | -120.5941 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0060500 | OH | Sus | 31692553 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1937742 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6577 | 20240430 | 1321 | 20240430 | 1444 | 2442769 | 83 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 775 | 36.8499 | -120.0192 | No | Clear;32-90 F |  |  | 24-0060558 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937761 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320312922442 | 20240430 | 1814 | 20240430 | 1821 | 2442925 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 7 | 37.1161 | -120.3936 | No | Clear;32-90 F | Fuse | Broken | 24-0060632 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937779 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | TRANSFORMER | 319797225080 | 20240501 | 717 | 20240501 | 756 | 2443068 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 117 | 37.1891 | -120.5706 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0060740 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1937844 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | OTHER | J22759 TWD T7726 | 20240501 | 736 | 20240501 | 845 | 2443097 | 69 | Distribution Circuit | Equipment Failure/Involved | Underground | 60 | 4140 | 37.081 | -120.8434 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0059026 | UG | Sus | 35548467 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1937837 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 23037 | 20240501 | 806 | 20240501 | 908 | 2443248 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 62 | 37.0909 | -120.483 | No | Clear;32-90 F |  |  | 24-0060780 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1937954 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318740246475 | 20240501 | 857 | 20240501 | 1043 | 2443245 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 106 | 37.7754 | -120.9367 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0060779 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1937952 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319434132434 | 20240501 | 923 | 20240501 | 1015 | 2443269 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 52 | 37.3907 | -120.6936 | No | Clear;32-90 F | Jumper | Broken | 24-0060836 | OH | Sus | 46236754 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938003 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | JUMPER | BURNED OJ 2 E/OF CGC# 318358332313 | 20240501 | 1040 | 20240501 | 1321 | 2443353 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 322 | 37.3855 | -121.0652 | No | Clear;32-90 F | Jumper | Burned Open | 24-0060861 | OH | Sus | 46236850 | CENTRAL VALLEY | MAY | Open Circuit | 0 | No | No | No | 1938011 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | TRANSFORMER | 320118125975 | 20240501 | 1102 | 20240501 | 1153 | 2443376 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 51 | 37.2141 | -120.4609 | No | Clear;32-90 F | Fuse | Broken | 24-0060893 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938021 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | T3876 | 20240501 | 1420 | 20240502 | 9 | 2443586 | 589 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 1658 | 37.3236 | -120.8209 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0061059 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938091 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | S707 | 20240501 | 1800 | 20240501 | 1850 | 2443781 | 50 | Distribution Circuit | Animal | Bird found | 9 | 450 | 37.8573 | -120.9714 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0061087 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938108 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 659827 | 20240502 | 600 | 20240502 | 1119 | 2443861 | 319 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1276 | 37.154 | -120.2744 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0061171 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938173 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | S707 | 20240502 | 1026 | 20240502 | 1136 | 2444256 | 70 | Distribution Circuit | Animal | Bird found | 9 | 630 | 37.8573 | -120.9714 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0061284 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938356 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | TRANSFORMER | 322944826368 | 20240502 | 1157 | 20240502 | 1445 | 2444266 | 168 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 336 | 37.2215 | -119.4891 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0061356 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938391 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318622429973 | 20240502 | 1252 | 20240502 | 1518 | 2444179 | 146 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 146 | 37.3222 | -120.9747 | No | Clear;32-90 F | Other | Failed/Faulted | 24-0061329 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938378 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | 9119 | 20240502 | 1315 | 20240502 | 1430 | 2444378 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 225 | 37.9793 | -120.3728 | No | Clear;32-90 F |  |  | 24-0061368 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938394 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321419621146 | 20240502 | 1426 | 20240502 | 1436 | 2444289 | 10 | Transformer only | Animal | Other | 1 | 10 | 37.0794 | -120.0143 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0061398 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938397 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319748933520 | 20240502 | 1614 | 20240502 | 2321 | 2444462 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1708 | 37.4207 | -120.5874 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0061475 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938419 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | SWITCH | 5326 | 20240502 | 1731 | 20240502 | 2204 | 2444506 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 85722 | 36.9717 | -120.0656 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0061335 | OH | Sus | 31692778 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1938420 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | L1209 | 20240502 | 2014 | 20240502 | 2201 | 2444572 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 8239 | 37.9631 | -120.2909 | No | Clear;32-90 F |  |  | 24-0061510 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938444 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6577 | 20240503 | 125 | 20240503 | 309 | 2444654 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 971 | 36.8499 | -120.0192 | No | Clear;32-90 F | Fuse | Broken | 24-0061553 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1938497 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 21742 | 20240503 | 558 | 20240503 | 831 | 2444678 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 7038 | 37.6385 | -120.3479 | No | Clear;32-90 F |  |  | 24-0061586 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938520 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | RECLOSER | 5450 | 20240503 | 750 | 20240503 | 1257 | 2444723 | 195 | Distribution Circuit | 3rd Party | Vehicle | 173 | 22083 | 37.0401 | -120.2544 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0061585 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938519 | 0 | Non-EPSS | N | 2024 | A- B- GRD
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 321822315093 | 20240503 | 953 | 20240503 | 1700 | 2445165 | 427 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 427 | 36.9121 | -119.8778 | No | Clear;32-90 F |  |  | 24-0061868 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1938727 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | RECLOSER | 187702 | 20240503 | 1224 | 20240503 | 1230 | 2445085 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 600 | 37.3599 | -120.8525 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0054205 | OH | Sus | 35018628 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938697 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | RECLOSER | 11640 | 20240503 | 1415 | 20240503 | 2122 | 2445153 | 427 | Distribution Circuit | Equipment Failure/Involved | Underground | 1175 | 67313 | 37.0618 | -120.8332 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0061808 | UG | Sus | 46238274 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938711 | 0 | Non-EPSS | N | 2024 | A- GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | L467 | 20240503 | 2045 | 20240504 | 337 | 2445365 | 412 | Distribution Circuit | Animal | Other | 137 | 56444 | 37.8868 | -120.5956 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0061948 | OH | Sus | 31693042 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938806 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | SECTIONALIZER | 11230 | 20240503 | 2143 | 20240503 | 2207 | 2445388 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 1872 | 37.0474 | -120.8265 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0061808 | OH | Sus | 46238274 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1938766 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | RECLOSER | 187702 | 20240503 | 2356 | 20240504 | 936 | 2445432 | 580 | Distribution Circuit | Equipment Failure/Involved | Overhead | 196 | 68752 | 37.3599 | -120.8525 | No | Clear;32-90 F | Insulator | Broken | 24-0061953 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938811 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320518630314 | 20240504 | 716 | 20240504 | 838 | 2445537 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 82 | 37.3322 | -120.3203 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0061981 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1938841 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 787527 | 20240504 | 1227 | 20240504 | 1912 | 2445783 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1192 | 37.9188 | -120.8776 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0062197 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938975 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 1599 | 20240504 | 1317 | 20240507 | 851 | 2445820 | 4054 | Distribution Circuit | Animal | Other | 23 | 6892 | 37.3034 | -121.0675 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0062121 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1938921 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7994 | 20240504 | 1323 | 20240504 | 1444 | 2445819 | 81 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 405 | 37.5201 | -120.6073 | No | Overcast;32-90 F |  |  | 24-0062108 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938915 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 4618 | 20240504 | 1352 | 20240504 | 1720 | 2445844 | 208 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 2286 | 37.4886 | -120.0413 | No | Overcast-Rain;32-90 F |  |  | 24-0062164 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938944 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 151918 | 20240504 | 1359 | 20240504 | 1640 | 2445856 | 161 | Distribution Circuit | Animal | Other | 2896 | 466256 | 37.4926 | -119.9657 | No | Overcast-Heavy Rain;32-90 F | Cutout- fuse holder | Normal | 24-0062103 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | No | No | 1938911 | 0 | EPSS Ckt | N | 2024 | AC TIME
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 11585 | 20240504 | 1417 | 20240505 | 1210 | 2445866 | 1313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2627 | 37.2051 | -120.2708 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0062188 | OH | Sus | 31692699 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938966 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 9703 | 20240504 | 1443 | 20240504 | 2004 | 2446044 | 321 | Distribution Circuit | Animal | Bird found | 22 | 7062 | 36.9152 | -120.7285 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Normal | 24-0062220 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1938997 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 19038 | 20240504 | 1522 | 20240504 | 1954 | 2445910 | 272 | Distribution Circuit | Animal | Other | 32 | 8704 | 37.2011 | -119.6879 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 24-0062213 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938990 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322427525284 | 20240504 | 1522 | 20240504 | 2046 | 2445952 | 324 | Transformer only | Vegetation | Other ground vegetation | 1 | 324 | 37.1916 | -119.6673 | No | Overcast-Rain;32-90 F | Fuse | Burned Open | 24-0062237 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939011 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6854 | 20240504 | 1636 | 20240506 | 1052 | 2445969 | 2536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 4516 | 37.0725 | -120.0748 | No | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Broken | 24-0062215 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1938992 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1101 | 162671101 | OTHER | 8627 | 20240504 | 1711 | 20240505 | 155 | 2446018 | 524 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 61 | 19224 | 37.559 | -121.209 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on object | 24-0062173 | OH | Sus | 35550712 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | Yes | 1938952 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322494231167 | 20240504 | 1716 | 20240505 | 1244 | 2446041 | 1168 | Transformer only | Vegetation | Other ground vegetation | 1 | 1168 | 37.3528 | -119.6424 | No | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Burned/flashed | 24-0062202 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938981 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 88295 | 20240504 | 2120 | 20240505 | 1000 | 2446197 | 760 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 13680 | 37.4946 | -119.8555 | No | Clear;32-90 F | Insulator | Broken | 24-0062271 | OH | Sus | 31693140 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939044 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 182315 | 20240504 | 2249 | 20240505 | 222 | 2446224 | 213 | Distribution Circuit | Animal | Bird found | 8 | 1705 | 37.3307 | -120.2882 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0062296 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939062 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 6757 | 20240505 | 141 | 20240505 | 1019 | 2446248 | 518 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3626 | 37.808 | -120.7218 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0062287 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939056 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 823548 | 20240505 | 449 | 20240505 | 536 | 2446270 | 47 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 839 | 39433 | 38.0441 | -120.248 | No | Overcast-Fog;Below 32 F |  |  | 24-0062305 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939070 | 0 | EPSS Ckt | N | 2024 | A & C
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321092717783 | 20240505 | 524 | 20240505 | 653 | 2446276 | 89 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 89 | 36.9883 | -120.1266 | No | Partly Cloudy;32-90 F |  |  | 24-0062309 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939075 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | 6821 | 20240505 | 553 | 20240505 | 1204 | 2446283 | 371 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 16695 | 38.0554 | -120.2748 | No | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0062321 | OH | Sus | 31693161 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1939086 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321459014975 | 20240505 | 653 | 20240505 | 726 | 2446296 | 33 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 33 | 36.9104 | -120.0016 | No | Partly Cloudy;32-90 F |  |  | 24-0062315 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939080 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 321424235535 | 20240505 | 1621 | 20240505 | 1738 | 2446548 | 77 | Transformer only | Animal | Other | 1 | 77 | 37.4748 | -120.0083 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0062403 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939159 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 99295 | 20240505 | 2130 | 20240506 | 8 | 2446609 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 4108 | 37.5445 | -120.4624 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0062437 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939187 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 11517 | 20240506 | 545 | 20240506 | 746 | 2446658 | 121 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 161 | 37.4799 | -120.5037 | No | Clear;32-90 F |  |  | 24-0062464 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939214 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | TRANSFORMER | 100000020443 | 20240506 | 1047 | 20240506 | 1208 | 2447099 | 81 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 81 | 37.1793 | -120.9767 | No | Clear;32-90 F |  |  | 24-0062645 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939401 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRANSFORMER | 320538020594 | 20240506 | 1152 | 20240506 | 2151 | 2447172 | 599 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1797 | 37.0652 | -120.3152 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062663 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939408 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | TRANSFORMER | 415164556041 | 20240506 | 1357 | 20240506 | 1500 | 2447230 | 63 | Transformer only | Animal | Other | 1 | 63 | 36.8609 | -120.654 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0062698 | OH | Sus | 46239280 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939413 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1102 | 254421102 | FUSE | 10017 | 20240506 | 1617 | 20240506 | 1732 | 2447333 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 2025 | 37.3228 | -119.6628 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0062734 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939421 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319742650481 | 20240506 | 1717 | 20240506 | 1826 | 2447419 | 69 | Transformer only | Animal | Other | 3 | 207 | 37.8864 | -120.5898 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 24-0062784 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939433 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 6705 | 20240506 | 1920 | 20240507 | 337 | 2447475 | 497 | Distribution Circuit | 3rd Party | Gun Shot | 8 | 3976 | 36.8799 | -120.2643 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0062838 | OH | Sus | 46239274 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1939479 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 7552 | 20240507 | 822 | 20240507 | 949 | 2447667 | 87 | Distribution Circuit | 3rd Party | Vehicle | 5 | 435 | 37.1199 | -120.4285 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0062944 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939614 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321717016510 | 20240507 | 1133 | 20240507 | 1900 | 2447922 | 447 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 3 | 1341 | 36.952 | -119.9129 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0063072 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1939673 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L2073 | 20240507 | 1317 | 20240507 | 1412 | 2447998 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 550 | 38.02 | -120.3864 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0063110 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939691 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | TRANSFORMER | 318489323510 | 20240507 | 1334 | 20240507 | 1625 | 2447619 | 171 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 171 | 37.1444 | -121.019 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0063131 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939699 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | JUMPER | JPRS 1 S/OF MTR# 1010594026 | 20240507 | 1430 | 20240507 | 1620 | 2448047 | 110 | Distribution Circuit | 3rd Party | Vehicle | 2 | 220 | 37.02 | -120.5633 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0063163 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939708 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321388761669 | 20240507 | 1520 | 20240507 | 1755 | 2448101 | 155 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 930 | 38.1931 | -120.0177 | No | Clear;32-90 F | Fuse | Normal | 24-0063277 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939752 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | OTHER | WIRE DOWN @ 6683 | 20240507 | 1613 | 20240507 | 2257 | 2448197 | 404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 27381 | 37.0576 | -119.7297 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0063272 | OH | Sus | 46239644 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | Yes | 1939750 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | FUSE | 840701 | 20240507 | 2346 | 20240508 | 1431 | 2448308 | 885 | Distribution Circuit | Animal | Other | 13 | 2493 | 37.3623 | -121.1033 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 24-0063377 | OH | Sus | 35551162 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939854 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 26964 | 20240508 | 321 | 20240508 | 532 | 2448337 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1310 | 37.8523 | -120.1886 | No | Clear;32-90 F |  |  | 24-0063383 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939863 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | STANISLAUS-1702 | 162821702 | JUMPER | OJ 8SP N/W/OF CGC #320431259717 | 20240508 | 915 | 20240508 | 1059 | 2448546 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 104 | 38.1434 | -120.3551 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0063471 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939970 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | SECTIONALIZER | 11831 | 20240508 | 931 | 20240509 | 943 | 2448939 | 1452 | Distribution Circuit | 3rd Party | Vehicle | 3 | 3827 | 37.0874 | -120.2566 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0063714 | OH | Sus | 35551474 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1940076 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | TRANSFORMER | 321112024290 | 20240508 | 953 | 20240508 | 1330 | 2448634 | 217 | Transformer only | Animal | Bird found | 2 | 434 | 37.1681 | -120.12 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0063689 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940071 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319921137750 | 20240508 | 1014 | 20240508 | 1027 | 2448564 | 13 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 13 | 37.5364 | -120.5285 | No | Clear;32-90 F |  |  | 24-0063535 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1940022 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1104 | 253401104 | TRANSFORMER | 415486450353 | 20240508 | 1108 | 20240508 | 1117 | 2448505 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 9 | 36.7057 | -120.5408 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0063597 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940044 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | TRANSFORMER | 100000026142 | 20240508 | 1111 | 20240508 | 1148 | 2448801 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 37 | 36.6616 | -120.4694 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0063630 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940052 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1103 | 255391103 | TRANSFORMER | 320846816918 | 20240508 | 1238 | 20240508 | 1425 | 2448676 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 107 | 36.9647 | -120.2112 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0063687 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940070 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | RECLOSER | 9090 | 20240509 | 238 | 20240509 | 1149 | 2449343 | 551 | Distribution Circuit | 3rd Party | Vehicle | 347 | 79968 | 37.096 | -120.9254 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0063973 | OH | Sus | 35551833 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1940195 | 0 | EPSS Ckt | N | 2024 | B & GRD
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319588329120 | 20240509 | 635 | 20240509 | 1212 | 2449469 | 337 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 337 | 37.2995 | -120.6426 | No | Clear;32-90 F | Secondary | Broken | 24-0064033 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940241 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318514747566 | 20240509 | 815 | 20240509 | 955 | 2449461 | 100 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 200 | 37.8052 | -121.0152 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0064026 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940235 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | OCB | 1701/2 | 20240509 | 919 | 20240509 | 925 | 2449621 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2640 | 15840 | 37.9742 | -120.3199 | No | Clear;32-90 F |  |  | 24-0064093 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1940325 | 0 | EPSS Ckt | N | 2024 | AB
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321405913354 | 20240509 | 1108 | 20240509 | 1338 | 2449811 | 150 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 150 | 36.8658 | -120.0204 | No | Clear;32-90 F |  |  | 24-0064283 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1940427 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1104 | 253401104 | TRANSFORMER | 100000000175 | 20240509 | 1126 | 20240509 | 1424 | 2449821 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 178 | 36.7199 | -120.5496 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0064324 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940442 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6648 | 20240509 | 1424 | 20240509 | 1558 | 2449952 | 94 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 94 | 37.0326 | -120.0292 | No | Clear;32-90 F |  |  | 24-0064382 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940457 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321285819353 | 20240509 | 1645 | 20240509 | 2046 | 2450054 | 241 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 482 | 37.0309 | -120.0608 | No | Clear;32-90 F | Fuse | Broken | 24-0064468 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940495 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 888664 | 20240509 | 1839 | 20240509 | 2125 | 2450138 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 775 | 36.8439 | -120.0556 | No | Clear;32-90 F |  |  | 24-0064477 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940511 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | OCB | 1703/2 | 20240509 | 2327 | 20240510 | 1022 | 2450260 | 655 | Distribution Circuit | 3rd Party | Vehicle | 3118 | 507413 | 37.9799 | -120.4136 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 24-0064498 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1940531 | 0 | EPSS Ckt | N | 2024 | A- B- C- TIME
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319406530014 | 20240510 | 645 | 20240510 | 1230 | 2450315 | 345 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 345 | 37.3241 | -120.7051 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0064570 | OH | Sus | 46245180 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940584 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | TRANSFORMER | 318826043690 | 20240510 | 952 | 20240510 | 1025 | 2450535 | 33 | Transformer only | Vegetation | Tree - grew into line | 2 | 66 | 37.6991 | -120.9065 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0064602 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940666 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319663730806 | 20240510 | 1405 | 20240510 | 2030 | 2450971 | 385 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2695 | 37.3462 | -120.6165 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0064835 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940764 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 1532 | 20240510 | 1512 | 20240511 | 204 | 2451039 | 652 | Distribution Circuit | 3rd Party | Vehicle | 208 | 51115 | 37.8674 | -120.8795 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0064827 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | Yes | No | 1940760 | 0 | EPSS Ckt | N | 2024 | A- B- GR
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | L2091 | 20240510 | 1605 | 20240510 | 2259 | 2451065 | 414 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1242 | 37.964 | -120.3618 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0064837 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940766 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318845023200 | 20240510 | 1658 | 20240510 | 1901 | 2451118 | 123 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 123 | 37.1364 | -120.8971 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0064872 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940780 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | JUMPER | TSB ES/OF CGC# 320611755029 | 20240510 | 1713 | 20240510 | 2032 | 2450977 | 199 | Distribution Circuit | Animal | Other | 8 | 1592 | 38.0109 | -120.2883 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0064785 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940745 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | TRANSFORMER | T4907 | 20240510 | 1930 | 20240511 | 139 | 2451184 | 369 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 4059 | 37.0601 | -120.8129 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0064882 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940789 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 4193 | 20240510 | 2127 | 20240511 | 2 | 2451215 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 620 | 37.8311 | -120.8692 | No | Clear;32-90 F |  |  | 24-0064914 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1940830 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | TRANSFORMER | T39117 | 20240510 | 2316 | 20240511 | 1721 | 2451245 | 1085 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 16689 | 36.9219 | -119.8011 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0064917 | UG | Sus | 35552341 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940833 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | FUSE | 19972 | 20240511 | 20 | 20240511 | 137 | 2451252 | 77 | Distribution Circuit | Equipment Failure/Involved | Underground | 99 | 7623 | 37.0606 | -120.8138 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0064915 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940831 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 5841 | 20240511 | 955 | 20240511 | 1245 | 2451417 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1700 | 37.7762 | -120.7898 | No | Clear;32-90 F |  |  | 24-0064983 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1940894 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 21133 | 20240511 | 1510 | 20240511 | 1622 | 2451604 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1152 | 36.9232 | -119.9215 | No | Clear;32-90 F |  |  | 24-0065062 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1940931 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 7557 | 20240511 | 1637 | 20240511 | 1720 | 2451639 | 43 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 1204 | 37.3506 | -120.6171 | No | Clear;Above 90 |  |  | 24-0065065 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1940935 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | FUSE | 3837 | 20240511 | 2327 | 20240512 | 1020 | 2451789 | 653 | Distribution Circuit | 3rd Party | Vehicle | 17 | 11101 | 36.9094 | -120.5433 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0065125 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1940993 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | S929 | 20240511 | 2348 | 20240512 | 225 | 2451792 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1727 | 37.9444 | -120.8246 | No | Clear;32-90 F |  |  | 24-0065127 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1940995 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | FUSE | 9799 | 20240512 | 329 | 20240512 | 1143 | 2451842 | 494 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6916 | 36.9091 | -120.4796 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0065152 | OH | Sus | 46246183 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1941021 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1102 | 254421102 | TRANSFORMER | 322449529995 | 20240512 | 507 | 20240512 | 1740 | 2451989 | 753 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 753 | 37.3207 | -119.6586 | No | Clear;32-90 F | Secondary | Burned Open | 24-0065175 | OH | Sus | 46246162 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941037 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | FUSE | S1755 | 20240512 | 647 | 20240512 | 1243 | 2451945 | 356 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 9436 | 37.758 | -120.8581 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0065138 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941007 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | OTHER | WIRE DOWN 1 POLE S/OF CGC 319088331435 | 20240512 | 1532 | 20240512 | 2113 | 2452096 | 341 | Distribution Circuit | 3rd Party | Metallic Balloon | 945 | 16389 | 37.3604 | -120.8144 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0065193 | OH | Sus | 31693924 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | Yes | 1941048 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 9010 | 20240512 | 2232 | 20240513 | 441 | 2452261 | 369 | Distribution Circuit | 3rd Party | Vehicle | 240 | 29372 | 37.5385 | -121.2044 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0065242 | OH | Sus | 35552482 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941097 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20240513 | 536 | 20240513 | 605 | 2452284 | 29 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 17 | 493 | 37.1863 | -120.6348 | No | Clear;32-90 F |  |  | 24-0065258 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941111 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319897734936 | 20240513 | 904 | 20240513 | 1005 | 2452475 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 61 | 37.4603 | -120.5358 | No | Clear;32-90 F |  |  | 24-0065357 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1941267 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 7746 | 20240513 | 933 | 20240513 | 1020 | 2452531 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 376 | 37.1419 | -120.4644 | No | Clear;32-90 F |  |  | 24-0065364 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941275 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319838036008 | 20240513 | 1114 | 20240513 | 1430 | 2452647 | 196 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 392 | 37.489 | -120.557 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0065389 | OH | Sus | 31694078 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941298 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 6036 | 20240513 | 1246 | 20240513 | 2104 | 2452731 | 498 | Distribution Circuit | 3rd Party | Vehicle | 24 | 11952 | 36.9254 | -119.9394 | No | Clear-Drizzle;32-90 F | Pole-Wood | Broken- wire on object | 24-0065443 | OH | Sus | 35552765 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1941329 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | RECLOSER | 149636 | 20240513 | 1442 | 20240514 | 29 | 2452861 | 551 | Distribution Circuit | 3rd Party | Vehicle | 2342 | 130699 | 37.2733 | -120.5259 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0065504 | OH | Sus | 46246564 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | Yes | No | 1941347 | 0 | Non-EPSS | N | 2024 | ABC- GRD- SGF TIME OC
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 13233 | 20240513 | 1706 | 20240513 | 1812 | 2452990 | 64 | Distribution Circuit | 3rd Party | Metallic Balloon | 109 | 6976 | 36.9385 | -120.0583 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0065578 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941378 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | TRANSFORMER | 318645749508 | 20240513 | 1712 | 20240514 | 144 | 2453099 | 512 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 512 | 37.8589 | -120.9698 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0065604 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941397 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRIP-SAVER | 2553 | 20240513 | 1723 | 20240513 | 2209 | 2452999 | 286 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 20512 | 37.9918 | -120.4016 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0065579 | OH | Sus | 46246530 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941379 | 0 | EPSS Ckt | N | 2024 | A & B
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 866636 | 20240513 | 1821 | 20240513 | 2257 | 2453032 | 276 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 276 | 37.8055 | -120.7589 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0065580 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941380 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 6775 | 20240514 | 853 | 20240514 | 1120 | 2453318 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1079 | 37.1343 | -120.1605 | No | Clear;32-90 F |  |  | 24-0065809 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941603 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320476816882 | 20240514 | 1110 | 20240514 | 1227 | 2453522 | 77 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 77 | 36.9635 | -120.3371 | No | Clear;32-90 F |  |  | 24-0065859 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1941627 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | OCB | 1105/2 | 20240514 | 1512 | 20240514 | 1956 | 2453733 | 284 | Distribution Circuit | 3rd Party | Vehicle | 2125 | 140972 | 36.9834 | -120.8198 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0065975 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941646 | 0 | Non-EPSS | N | 2024 | A & C
YOSEMITE | YOSEMITE | PANOCHE-1101 | 253671101 | TRIP-SAVER | 10480 | 20240514 | 1521 | 20240514 | 2240 | 2453967 | 439 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 439 | 36.5744 | -120.4788 | No | Clear;32-90 F |  |  | 24-0066068 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941705 | 1 | Non-EPSS | N | 2024 | A
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | OTHER | J25848 TWD T14218 | 20240514 | 1526 | 20240514 | 1653 | 2453741 | 87 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 1305 | 37.2511 | -121.0026 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0065781 | UG | Sus | 35552929 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941649 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | OCB | 1101/2 | 20240514 | 1607 | 20240514 | 2331 | 2453753 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1684 | 35049 | 37.253 | -121.013 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0065992 | OH | Sus | 46246995 | CENTRAL VALLEY | MAY | Force Out | 0 | No | Yes | Yes | 1941654 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | 20335 | 20240514 | 1632 | 20240514 | 1737 | 2453784 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 1755 | 38.0291 | -120.2586 | No | Clear;32-90 F |  |  | 24-0066026 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941666 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 100000010918 | 20240514 | 2015 | 20240515 | 136 | 2453916 | 321 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 321 | 37.9181 | -120.8898 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0066044 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941678 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 9650 | 20240514 | 2110 | 20240514 | 2359 | 2453930 | 169 | Distribution Circuit | Animal | Other | 70 | 10094 | 37.3021 | -120.6354 | No | Partly Cloudy;32-90 F | Capacitor | Normal | 24-0066051 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941689 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | RECLOSER | 999258 | 20240515 | 37 | 20240515 | 1036 | 2453979 | 599 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 12071 | 37.1542 | -121.0608 | No | Clear;32-90 F |  |  | 24-0066073 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1941712 | 0 | EPSS Ckt | Y | 2024 | B & C
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | OTHER | T7389 TWD T7388 | 20240515 | 39 | 20240515 | 142 | 2453981 | 63 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 1323 | 37.0515 | -120.8637 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0066008 | UG | Sus | 35553142 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941713 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 3695 | 20240515 | 101 | 20240515 | 545 | 2453982 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 379 | 36.7054 | -120.3868 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0066080 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941723 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 11517 | 20240515 | 852 | 20240515 | 910 | 2454169 | 18 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 24 | 37.4799 | -120.5037 | No | Clear;32-90 F |  |  | 24-0066220 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941886 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | JUMPER | OJ'S 1 E/OF 7019 | 20240515 | 1442 | 20240515 | 1908 | 2454516 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 18354 | 37.393 | -120.6103 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0066441 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941954 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | S1829 | 20240515 | 1557 | 20240515 | 2159 | 2460533 | 362 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 39096 | 37.5629 | -121.1796 | No | Clear;32-90 F |  |  | 24-0066715 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1942054 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321278916710 | 20240515 | 1617 | 20240515 | 2350 | 2454580 | 453 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 8154 | 36.9584 | -120.0638 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0066569 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941975 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | RECLOSER | 11430 | 20240515 | 2152 | 20240515 | 2359 | 2454690 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1269 | 161163 | 36.9537 | -120.0626 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0066656 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942031 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 8289 | 20240516 | 309 | 20240516 | 1345 | s1942042 | 636 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 8268 | 37.7293 | -120.9405 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0066693 | UG | Sus | 31694290 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942042 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | RECLOSER | 90580 | 20240516 | 550 | 20240516 | 918 | 2460425 | 208 | Distribution Circuit | 3rd Party | Vehicle | 622 | 45610 | 37.3312 | -120.6134 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0066622 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942026 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320892711412 | 20240516 | 1252 | 20240516 | 1415 | 2460700 | 83 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 83 | 36.8122 | -120.1967 | No | Clear;32-90 F |  |  | 24-0066890 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1942115 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320950512229 | 20240516 | 1329 | 20240516 | 1450 | 2460735 | 81 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 81 | 36.8346 | -120.1765 | No | Clear;32-90 F |  |  | 24-0066913 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1942125 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7952 | 20240516 | 2134 | 20240516 | 2319 | 2461126 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1995 | 37.2665 | -120.6704 | No | Clear;32-90 F |  |  | 24-0067036 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1942207 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | TEMP | 20240517 | 537 | 20240517 | 733 | 2461193 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1472 | 37.9248 | -120.5269 | No | Clear;32-90 F |  |  | 24-0067070 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1942232 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 91473 | 20240517 | 807 | 20240517 | 1316 | 2461331 | 309 | Distribution Circuit | 3rd Party | Vehicle | 27 | 8343 | 38.0619 | -120.187 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0067165 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1942366 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | TRANSFORMER | 100000011494 | 20240517 | 1023 | 20240517 | 1225 | 2461422 | 122 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 122 | 37.3743 | -121.0566 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0067199 | OH | Sus | 46247677 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942388 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | RECLOSER | 30980 | 20240517 | 1701 | 20240518 | 500 | 2461842 | 719 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1171 | 87425 | 37.3044 | -120.4833 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0067396 | OH | Sus | 35554042 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942448 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11615 | 20240518 | 150 | 20240518 | 255 | 2462007 | 65 | Distribution Circuit | 3rd Party | Vehicle | 7 | 455 | 37.2328 | -120.3386 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0067449 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1942495 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322124225615 | 20240518 | 700 | 20240518 | 1150 | 2462117 | 290 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 870 | 37.2016 | -119.7706 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0067474 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1942539 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | TRANSFORMER | 319047518680 | 20240518 | 809 | 20240518 | 1110 | 2462067 | 181 | Transformer only | 3rd Party | Vehicle | 1 | 181 | 37.0128 | -120.8272 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0067467 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942518 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | RECLOSER | 90600 | 20240518 | 858 | 20240518 | 1012 | 2462124 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 105 | 7150 | 37.3618 | -121.0763 | No | Clear;32-90 F |  |  | 24-0067479 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942545 | 0 | EPSS Ckt | N | 2024 | A GRD
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | FUSE | 91512 | 20240518 | 1536 | 20240518 | 1659 | 2462301 | 83 | Distribution Circuit | 3rd Party | Metallic Balloon | 130 | 10790 | 37.3606 | -120.594 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0067546 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1942588 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 6694 | 20240519 | 520 | 20240519 | 750 | 2462461 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 750 | 37.0792 | -120.4737 | No | Partly Cloudy;32-90 F |  |  | 24-0067607 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1942634 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | SECTIONALIZER | 10810 | 20240519 | 803 | 20240519 | 957 | 2462506 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 5130 | 37.5363 | -120.5166 | No | Clear;32-90 F |  |  | 24-0067614 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1942655 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | FUSE | 11676 | 20240519 | 1511 | 20240519 | 1825 | 2462667 | 194 | Distribution Circuit | 3rd Party | Metallic Balloon | 10 | 1940 | 37.2311 | -120.8771 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0067647 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1942682 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 69153 | 20240520 | 809 | 20240520 | 1217 | 2462962 | 248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 248 | 37.3603 | -120.6728 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0067748 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942776 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | TRANSFORMER | 318387125038 | 20240520 | 910 | 20240520 | 1023 | 2462949 | 73 | Transformer only | Animal | Other | 1 | 73 | 37.1864 | -121.054 | No | Clear;32-90 F | Bushing | Normal | 24-0067838 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942889 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | TRANSFORMER | 321227116601 | 20240520 | 925 | 20240520 | 1014 | 2463096 | 49 | Transformer only | Unknown Cause | Patrol - not conducted | 11 | 539 | 36.9556 | -120.0814 | No | Clear;32-90 F |  |  | 24-0067848 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1942896 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 100000015212 | 20240520 | 1035 | 20240520 | 1112 | 2463187 | 37 | Transformer only | Animal | Other | 1 | 37 | 37.3343 | -120.2866 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0067869 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942906 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319657931011 | 20240520 | 1054 | 20240520 | 1339 | 2463207 | 165 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 6 | 990 | 37.3518 | -120.6185 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0067868 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1942904 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318564146390 | 20240520 | 1450 | 20240520 | 2101 | 2463470 | 371 | Transformer only | 3rd Party | Vehicle | 4 | 1484 | 37.7731 | -120.9978 | No | Clear;32-90 F | Secondary | Broken | 24-0068033 | OH | Sus | 31694783 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1942953 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 6413 | 20240520 | 1737 | 20240520 | 1804 | 2463639 | 27 | Distribution Circuit | Animal | Other | 4 | 108 | 37.7401 | -120.8022 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0068073 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942974 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | RECLOSER | 3630 | 20240520 | 1906 | 20240521 | 456 | 2463644 | 590 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 93 | 30256 | 36.6912 | -120.4598 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0068078 | OH | Sus | 35554702 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | Yes | No | 1942978 | 0 | Non-EPSS | N | 2024 | A B
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | TRANSFORMER | 322486720222 | 20240520 | 2011 | 20240520 | 2140 | 2463663 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 178 | 37.0518 | -119.6489 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0068081 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942983 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 1257 | 20240521 | 604 | 20240521 | 1132 | 2463939 | 328 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1304 | 127250 | 38.039 | -120.3833 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0068138 | OH | Sus | 31694880 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | Yes | 1943037 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318969045317 | 20240521 | 930 | 20240521 | 1711 | 2464167 | 461 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 922 | 37.744 | -120.8578 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0068264 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943195 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | RECLOSER | 2850 | 20240521 | 1007 | 20240521 | 1017 | 2464221 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 78 | 728 | 36.6403 | -120.3884 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0068078 | OH | Sus | 35554702 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1943183 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320085515918 | 20240521 | 1121 | 20240521 | 1324 | 2464292 | 123 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 123 | 36.9371 | -120.4722 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0068383 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943226 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1102 | 253671102 | RECLOSER | 681764 | 20240521 | 1335 | 20240521 | 1603 | 2464377 | 148 | Distribution Circuit | Company Initiated | Operating error | 52 | 5246 | 36.6267 | -120.4606 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0068374 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1943222 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 659827 | 20240522 | 950 | 20240522 | 1507 | 2465085 | 317 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1268 | 37.154 | -120.2744 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0068734 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1943502 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 9203 | 20240522 | 1154 | 20240522 | 1300 | 2465142 | 66 | Distribution Circuit | 3rd Party | Vehicle | 49 | 3234 | 37.2302 | -120.9942 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0068798 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1943526 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10315 | 20240522 | 1343 | 20240522 | 1620 | 2465209 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2512 | 37.4684 | -119.7375 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0068826 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1943535 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 19648 | 20240522 | 1624 | 20240522 | 2220 | 2465343 | 356 | Distribution Circuit | 3rd Party | Vehicle | 2 | 712 | 37.9989 | -120.2332 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0068952 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1943556 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319865229469 | 20240522 | 1701 | 20240522 | 1844 | 2465340 | 103 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 103 | 37.3083 | -120.5464 | No | Clear;32-90 F |  |  | 24-0068974 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1943565 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23248 | 20240523 | 641 | 20240523 | 930 | 2465549 | 169 | Distribution Circuit | Animal | Bird found | 13 | 1261 | 37.9986 | -120.2942 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0069084 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943653 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | FUSE | 6768 | 20240523 | 738 | 20240523 | 904 | 2465571 | 86 | Distribution Circuit | Animal | Bird found | 16 | 1376 | 36.9379 | -120.0025 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0069109 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1943700 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 318902544985 | 20240523 | 911 | 20240523 | 953 | 2465690 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 42 | 37.7345 | -120.8806 | No | Clear;32-90 F | Secondary | Broken | 24-0069115 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1943720 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 90090 | 20240523 | 916 | 20240523 | 1606 | 2465714 | 410 | Distribution Circuit | 3rd Party | Vehicle | 2103 | 225235 | 37.9028 | -120.4538 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0069124 | OH | Sus | 35555390 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1943741 | 0 | EPSS Ckt | N | 2024 | ABC
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6575 | 20240523 | 1134 | 20240523 | 1228 | 2465894 | 54 | Distribution Circuit | Animal | Other | 19 | 1026 | 36.8512 | -120.0464 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0069242 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1943824 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 184241 | 20240523 | 1252 | 20240523 | 1441 | 2465959 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 109 | 36.88 | -120.2011 | No | Clear;32-90 F |  |  | 24-0069306 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943836 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 13210 | 20240523 | 1328 | 20240524 | 113 | 2466023 | 705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 69090 | 36.929 | -119.8941 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0069422 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1943863 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | S1369 | 20240523 | 1845 | 20240523 | 2000 | 2466172 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 2625 | 37.9354 | -120.4431 | No | Clear;32-90 F |  |  | 24-0069434 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1943871 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | FUSE | 8643 | 20240523 | 2348 | 20240524 | 739 | 2466282 | 471 | Distribution Circuit | 3rd Party | Vehicle | 128 | 60288 | 37.3966 | -120.6145 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0069481 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | Yes | No | 1943915 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | OTHER | WIRE DOWN 1 PH MID SPAN S/OF CGC#321567915146 | 20240524 | 51 | 20240524 | 916 | 2466299 | 505 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 40238 | 36.9133 | -119.964 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0069490 | OH | Sus | 46250843 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | Yes | 1943919 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | FUSE | 23173 | 20240524 | 516 | 20240524 | 728 | 2466316 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1056 | 36.8828 | -120.4916 | No | Partly Cloudy;32-90 F |  |  | 24-0069517 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1943930 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 27390 | 20240524 | 949 | 20240524 | 1908 | 2466582 | 559 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1118 | 36.7564 | -120.3891 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0069667 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944040 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 86913 | 20240524 | 1118 | 20240524 | 1210 | 2466606 | 52 | Distribution Circuit | 3rd Party | Metallic Balloon | 46 | 2392 | 36.9659 | -120.0495 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0069757 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944059 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | SWITCH | 22953 | 20240524 | 1154 | 20240524 | 1618 | 2466618 | 264 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 1848 | 38.0317 | -120.3789 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0069718 | OH | Sus | 46250851 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944051 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | JUMPER | OJ 2SP N/OF CGC #318370725790 | 20240524 | 1207 | 20240524 | 1648 | 2466593 | 281 | Distribution Circuit | 3rd Party | Vehicle | 1 | 281 | 37.208 | -121.0606 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0069755 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944058 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320812111233 | 20240524 | 1319 | 20240524 | 1430 | 2466693 | 71 | Transformer only | Animal | Other | 1 | 71 | 36.8074 | -120.2241 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0069846 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1944084 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | RECLOSER | 406044 | 20240524 | 1434 | 20240524 | 1532 | 2466735 | 58 | Distribution Circuit | 3rd Party | Other | 47 | 2726 | 37.0703 | -120.184 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0069847 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944085 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | JUMPER | OJ 1 POLE SW OF CGC#320924921076 | 20240524 | 2032 | 20240524 | 2240 | 2466952 | 128 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 384 | 37.0783 | -120.1839 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0069914 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944114 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322310827695 | 20240524 | 2347 | 20240525 | 527 | 2467050 | 340 | Transformer only | Equipment Failure/Involved | Underground | 2 | 680 | 37.2588 | -119.7075 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0069935 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944145 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | FUSE | 6626 | 20240525 | 36 | 20240525 | 449 | 2467083 | 253 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 5060 | 37.047 | -120.3855 | No | Partly Cloudy;32-90 F |  |  | 24-0069951 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944162 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | OCB | 1106/2 | 20240525 | 327 | 20240525 | 453 | 2467231 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 374 | 32164 | 36.8862 | -120.6558 | No | Partly Cloudy;32-90 F |  |  | 24-0069945 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | No | No | 1944155 | 0 | EPSS Ckt | N | 2024 | A- B & GRD TIME
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 3736 | 20240525 | 521 | 20240525 | 720 | 2467272 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 794 | 36.792 | -120.2592 | No | Clear;32-90 F |  |  | 24-0069962 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944168 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319710630745 | 20240525 | 750 | 20240525 | 823 | 2467289 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 429 | 37.3446 | -120.6004 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0069960 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944167 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | FUSE | 20491 | 20240525 | 828 | 20240525 | 931 | 2467328 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1135 | 37.1877 | -121.0117 | No | Clear;32-90 F |  |  | 24-0069980 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944191 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10330 | 20240525 | 935 | 20240525 | 1043 | 2467379 | 68 | Distribution Circuit | Company Initiated | Personnel- company | 1538 | 103476 | 37.2507 | -119.5619 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0069982 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944193 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11622 | 20240525 | 1058 | 20240525 | 1653 | 2467438 | 355 | Distribution Circuit | Animal | Bird found | 13 | 1733 | 37.2074 | -120.3357 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0069999 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944206 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 363884 | 20240525 | 1332 | 20240525 | 1357 | 2467515 | 25 | Distribution Circuit | 3rd Party | Customer Equipment | 70 | 1750 | 37.2327 | -119.4996 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 24-0070011 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944212 | 0 | EPSS Ckt | N | 2024 | TIME
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | FUSE | 914969 | 20240526 | 202 | 20240526 | 718 | 2467694 | 316 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 4 | 1264 | 36.9864 | -120.088 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0070055 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944254 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 10748 | 20240526 | 233 | 20240526 | 1315 | 2467698 | 642 | Distribution Circuit | 3rd Party | Vehicle | 30 | 19260 | 37.2435 | -119.543 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0070059 | OH | Sus | 31695341 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1944259 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | S1319 | 20240526 | 733 | 20240526 | 916 | 2467733 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 8450 | 37.2457 | -121.0058 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0070075 | OH | Sus | 46251822 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944271 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L2183 | 20240526 | 943 | 20240526 | 1256 | 2467780 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 193 | 37.9908 | -120.4797 | No | Clear;32-90 F |  |  | 24-0070110 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | No | No | 1944294 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | OCB | 1102/2 | 20240526 | 1022 | 20240527 | 34 | 2467802 | 852 | Distribution Circuit | 3rd Party | Vehicle | 63 | 13636 | 36.9678 | -120.2031 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0070090 | OH | Sus | 35556042 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1944284 | 0 | Non-EPSS | N | 2024 | PH- GRD
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | SWITCH | 1806 | 20240526 | 1257 | 20240526 | 1633 | 2467951 | 216 | Distribution Circuit | Company Initiated | Improper Construction | 18 | 3888 | 37.3123 | -120.455 | No | Clear;32-90 F | Secondary | Normal | 24-0070119 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944304 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319584031202 | 20240526 | 1406 | 20240526 | 1806 | 2467866 | 240 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 480 | 37.3567 | -120.6446 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0070132 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944309 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | TRANSFORMER | 318511948499 | 20240526 | 1651 | 20240526 | 1708 | 2467939 | 17 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 17 | 37.831 | -121.0161 | No | Clear;32-90 F |  |  | 24-0070134 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1944311 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 318858019382 | 20240526 | 1748 | 20240526 | 1922 | 2467981 | 94 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 376 | 37.0311 | -120.8918 | No | Clear;32-90 F |  |  | 24-0070139 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1944316 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 4521 | 20240527 | 144 | 20240527 | 334 | 2468044 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 660 | 37.3243 | -120.311 | No | Clear;32-90 F |  |  | 24-0070164 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944339 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | INTERRUPTER | 14190 | 20240527 | 602 | 20240527 | 728 | 2468077 | 86 | Distribution Circuit | Animal | Bird found | 926 | 55846 | 37.3217 | -120.4783 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070174 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944350 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 21245 | 20240527 | 605 | 20240527 | 705 | 2468080 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 240 | 37.7184 | -120.8473 | No | Clear;32-90 F |  |  | 24-0070176 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944352 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 24529 | 20240527 | 727 | 20240527 | 1051 | 2468113 | 204 | Distribution Circuit | Animal | Bird found | 2056 | 82629 | 37.2933 | -120.4651 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0070182 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944355 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | JUMPER | OPEN JUMPERS 4 POLES N/OF CGC#320495118796 | 20240527 | 841 | 20240527 | 1034 | 2468120 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 226 | 37.018 | -120.3304 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0070186 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944359 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318522729772 | 20240527 | 907 | 20240527 | 1258 | 2468128 | 231 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 231 | 37.3165 | -121.0088 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070189 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944365 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10040 | 20240527 | 1017 | 20240527 | 1404 | 2468174 | 227 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 430 | 97610 | 37.3104 | -119.5846 | No | Clear-Drizzle;32-90 F |  |  | 24-0070200 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944370 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 415726351626 | 20240527 | 1918 | 20240528 | 155 | 2468388 | 397 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1588 | 36.7417 | -120.4597 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070261 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944423 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 363884 | 20240527 | 2033 | 20240527 | 2114 | 2468420 | 41 | Distribution Circuit | 3rd Party | Customer Equipment | 70 | 2870 | 37.2327 | -119.4996 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 24-0070260 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944422 | 0 | EPSS Ckt | N | 2024 | C
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319205929140 | 20240527 | 2034 | 20240527 | 2050 | 2468380 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 16 | 37.298 | -120.774 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0070258 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944421 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 11900 | 20240528 | 640 | 20240528 | 733 | 2468495 | 53 | Distribution Circuit | Animal | Bird found | 222 | 11766 | 37.334 | -119.6447 | No | Clear;32-90 F | Bushing | Normal | 24-0070298 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944458 | 0 | EPSS Ckt | Y | 2024 | AB INST
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | RECLOSER | 9910 | 20240528 | 1259 | 20240528 | 1500 | 2468963 | 121 | Distribution Circuit | 3rd Party | Vehicle | 556 | 24618 | 36.9918 | -120.6355 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0070561 | OH | Sus | 31695385 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | Yes | No | 1944660 | 0 | Non-EPSS | N | 2024 | A GRD
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320196022565 | 20240528 | 1303 | 20240528 | 1349 | 2468974 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 46 | 37.1202 | -120.4338 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0070584 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944666 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 9650 | 20240528 | 1935 | 20240528 | 2122 | 2469346 | 107 | Distribution Circuit | Company Initiated | Personnel- company | 70 | 7490 | 37.3021 | -120.6354 | No | Clear;32-90 F | Generator | Normal | 24-0070723 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944717 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | TRANSFORMER | 319964731077 | 20240528 | 2024 | 20240528 | 2218 | 2469375 | 114 | Transformer only | Vegetation | Tree - fell into line | 1 | 114 | 37.3544 | -120.5119 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0070751 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944746 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 20005 | 20240529 | 446 | 20240529 | 549 | 2469450 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1071 | 37.7587 | -120.931 | No | Clear;32-90 F |  |  | 24-0070773 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944762 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | FUSE | 8648 | 20240529 | 707 | 20240529 | 758 | 2469496 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 102 | 37.4328 | -120.577 | No | Clear;32-90 F |  |  | 24-0070815 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944787 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321779417259 | 20240529 | 945 | 20240529 | 1157 | 2469716 | 132 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 264 | 36.9724 | -119.8915 | No | Clear-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070926 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944940 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | FUSE | 26868 | 20240529 | 1004 | 20240529 | 1036 | 2469754 | 32 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 1387 | 37.2869 | -120.4334 | No | Clear;32-90 F |  |  | 24-0070884 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944928 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320637730722 | 20240529 | 1112 | 20240529 | 1231 | 2469796 | 79 | Transformer only | Animal | Other | 1 | 79 | 37.3421 | -120.2794 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0070945 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1944949 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319669330919 | 20240529 | 1330 | 20240529 | 1849 | 2469937 | 319 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 4147 | 37.3493 | -120.6147 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070978 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944965 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 6622 | 20240529 | 1411 | 20240529 | 1507 | 2470010 | 56 | Distribution Circuit | Animal | Bird found | 15 | 840 | 37.0326 | -120.4029 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071033 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1944984 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319492548275 | 20240529 | 1416 | 20240529 | 2255 | 2470072 | 519 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 519 | 37.8255 | -120.6774 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0071133 | OH | Sus | 31695394 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945030 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7754 | 20240529 | 1523 | 20240529 | 1708 | 2470087 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1155 | 37.3482 | -120.8886 | No | Clear;32-90 F |  |  | 24-0071114 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1945011 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 320872336150 | 20240529 | 1524 | 20240530 | 50 | 2470088 | 566 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 566 | 37.4873 | -120.1973 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0071116 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945013 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 263072 | 20240529 | 1555 | 20240529 | 2003 | 2470138 | 248 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 353 | 87544 | 37.9489 | -120.4255 | No | Clear;32-90 F |  |  | 24-0071093 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1945002 | 0 | EPSS Ckt | N | 2024 | AB INST
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 10680 | 20240529 | 2001 | 20240529 | 2035 | 2470386 | 34 | Distribution Circuit | Company Initiated | Personnel- company | 687 | 23358 | 37.3451 | -120.6327 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0071134 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945032 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | FUSE | 20205 | 20240529 | 2033 | 20240529 | 2126 | 2470412 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 159 | 37.2782 | -120.9543 | No | Clear;32-90 F |  |  | 24-0071145 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945040 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | FUSE | 6487 | 20240529 | 2053 | 20240530 | 145 | 2470456 | 292 | Distribution Circuit | Equipment Failure/Involved | Underground | 66 | 16432 | 36.9801 | -120.0561 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0071180 | UG | Sus | 31695558 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945072 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7327 | 20240530 | 607 | 20240530 | 850 | 2470534 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 489 | 37.4725 | -120.6031 | No | Clear;32-90 F |  |  | 24-0071265 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1945154 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 37282 | 20240530 | 1059 | 20240530 | 1156 | 2470862 | 57 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 2132 | 119919 | 37.462 | -119.9483 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071365 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1945262 | 0 | EPSS Ckt | Y | 2024 | A AND C PH
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320165529499 | 20240530 | 1335 | 20240530 | 1442 | 2470989 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 268 | 37.3106 | -120.4428 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0071466 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945305 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6306 | 20240530 | 1414 | 20240530 | 1645 | 2471063 | 151 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 151 | 37.0734 | -119.9695 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071496 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945310 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | TRANSFORMER | 319555716708 | 20240530 | 1453 | 20240531 | 108 | 2471085 | 615 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 886 | 36.9588 | -120.6535 | No | Clear;32-90 F | Other | Leaking | 24-0071545 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945319 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320063554450 | 20240530 | 1527 | 20240530 | 1542 | 2471104 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 30 | 37.9963 | -120.4781 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0071555 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945325 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | RECLOSER | 11700 | 20240530 | 1611 | 20240530 | 1814 | 2471129 | 123 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 90 | 11070 | 36.88 | -120.2185 | No | Clear;Above 90 | Regulator | Burned/flashed | 24-0071577 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945327 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 320233745134 | 20240530 | 1745 | 20240530 | 1800 | 2471169 | 15 | Transformer only | Vegetation | Tree - bark fell into line | 1 | 15 | 37.74 | -120.4243 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0071596 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945336 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | INTERRUPTER | 14420 | 20240530 | 1933 | 20240531 | 1108 | 2471262 | 935 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 9863 | 37.302 | -120.4829 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0071632 | UG | Sus | 46253620 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945363 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320164029517 | 20240530 | 2040 | 20240530 | 2146 | 2471299 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 198 | 37.3111 | -120.4433 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0071631 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945362 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | TAR FLAT-0401 | 163240401 | TRANSFORMER | 320346754079 | 20240530 | 2207 | 20240531 | 205 | 2471353 | 238 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2856 | 37.9853 | -120.3807 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0071682 | OH | Sus | 31695880 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945403 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321273316713 | 20240530 | 2252 | 20240531 | 201 | 2471358 | 189 | Transformer only | 3rd Party | Fire- house or bldg. | 17 | 3213 | 36.9585 | -120.0657 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0071673 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945394 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318871331068 | 20240531 | 916 | 20240531 | 955 | 2471470 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 39 | 37.3504 | -120.8902 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0071838 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945549 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | SWITCH | 944951 | 20240531 | 1308 | 20240531 | 1347 | 2471898 | 39 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 39 | 37.0103 | -119.8096 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0071938 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945597 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319486028574 | 20240531 | 1322 | 20240531 | 1418 | 2471906 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 56 | 37.2842 | -120.6776 | No | Clear;Above 90 | Fuse | Broken | 24-0071997 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945619 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 158761 | 20240531 | 1725 | 20240601 | 525 | 2472099 | 720 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 9 | 6480 | 36.8657 | -119.9356 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 24-0072067 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945646 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 11862 | 20240531 | 1905 | 20240601 | 913 | 2472163 | 848 | Distribution Circuit | Equipment Failure/Involved | Underground | 107 | 90736 | 37.286 | -120.4912 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0072089 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945655 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | TRANSFORMER | 321947521265 | 20240531 | 2125 | 20240531 | 2325 | 2472237 | 120 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 240 | 37.082 | -119.8327 | No | Clear;32-90 F |  |  | 24-0072113 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1945684 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 19875 | 20240531 | 2332 | 20240601 | 18 | 2472274 | 46 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 92 | 37.3351 | -120.7602 | No | Clear;32-90 F |  |  | 24-0072116 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1945685 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | FUSE | 20205 | 20240601 | 255 | 20240601 | 537 | 2472305 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 324 | 37.2782 | -120.9543 | No | Clear;32-90 F |  |  | 24-0072123 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945692 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 5857 | 20240601 | 515 | 20240601 | 650 | 2472325 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1425 | 36.8659 | -119.9109 | No | Clear;32-90 F |  |  | 24-0072130 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1945696 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 6493 | 20240601 | 656 | 20240601 | 919 | 2472340 | 143 | Distribution Circuit | Animal | Other | 7 | 1001 | 36.8354 | -120.2731 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0072151 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945732 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319713530860 | 20240601 | 916 | 20240601 | 931 | 2472427 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 60 | 37.3478 | -120.5995 | No | Clear;32-90 F | Secondary | Normal | 24-0072148 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945730 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318842922625 | 20240601 | 1429 | 20240601 | 1518 | 2472587 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 147 | 37.1201 | -120.8978 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0072195 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1945763 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319775230401 | 20240601 | 1540 | 20240601 | 1700 | 2472628 | 80 | Transformer only | 3rd Party | Vehicle | 3 | 240 | 37.3351 | -120.5773 | No | Clear;Above 90 | Secondary | Broken | 24-0072222 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1945781 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319775230401 | 20240601 | 1540 | 20240601 | 2243 | 2472952 | 423 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1269 | 37.3351 | -120.5773 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0072253 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1945810 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | S255 | 20240602 | 103 | 20240602 | 808 | 2473018 | 425 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 143 | 60775 | 37.7699 | -120.9412 | No | Clear;32-90 F |  |  | 24-0072297 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1945863 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | JUMPER | LR 2990 #2 SS JUMPER | 20240602 | 620 | 20240602 | 1101 | 2473063 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 11802 | 37.1065 | -120.8349 | No | Clear;32-90 F | Jumper | Burned Open | 24-0072301 | OH | Sus | 46254144 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1945869 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 25296 | 20240602 | 655 | 20240602 | 900 | 2473115 | 125 | Distribution Circuit | Animal | Bird found | 3 | 375 | 37.7781 | -120.9139 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0072307 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1945873 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 319945421515 | 20240602 | 1041 | 20240602 | 1225 | 2473147 | 104 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 104 | 37.0909 | -120.5212 | No | Partly Cloudy;32-90 F |  |  | 24-0072323 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1945891 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 24354 | 20240602 | 1059 | 20240602 | 1208 | 2473161 | 69 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 184 | 37.3554 | -121.0037 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0072322 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945890 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 7404 | 20240602 | 1540 | 20240602 | 1615 | 2473255 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 47 | 37.0971 | -120.5195 | No | Partly Cloudy;32-90 F |  |  | 24-0072343 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945904 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321812618239 | 20240602 | 1912 | 20240602 | 2023 | 2473343 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 284 | 36.9995 | -119.88 | No | Clear;32-90 F | Fuse | Broken | 24-0072361 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1945923 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | JUMPER | JMPRS 4 POLES E/OF SW 5358 | 20240603 | 840 | 20240603 | 1138 | s1946006 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 356 | 37 | -120.2072 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0072434 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946006 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 64455 | 20240603 | 917 | 20240603 | 1238 | 2473923 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 804 | 37.4562 | -119.8973 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0072484 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946093 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 90090 | 20240603 | 1021 | 20240603 | 1423 | 2474025 | 242 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2103 | 508926 | 37.9028 | -120.4538 | No | Partly Cloudy;32-90 F |  |  | 24-0072514 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946124 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | T5425 | 20240603 | 1603 | 20240603 | 1633 | 2474280 | 30 | Transformer only | Equipment Failure/Involved | Underground | 10 | 300 | 37.7895 | -121.0093 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0072733 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946202 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10040 | 20240603 | 1619 | 20240604 | 103 | 2474354 | 524 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 430 | 185120 | 37.3104 | -119.5846 | No | Partly Cloudy;32-90 F |  |  | 24-0072725 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946199 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | FUSE | 320199528669 | 20240603 | 1726 | 20240603 | 1812 | 2474426 | 46 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 92 | 37.2878 | -120.4311 | No | Partly Cloudy;32-90 F |  |  | 24-0072754 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1946216 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | TRANSFORMER | 318524522714 | 20240603 | 1826 | 20240604 | 208 | 2474462 | 462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 462 | 37.1224 | -121.0059 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0072758 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946219 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320187420714 | 20240603 | 1904 | 20240603 | 2000 | 2474492 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 112 | 37.0689 | -120.4367 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0072765 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946226 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | JUMPER | OJS 1 N/OF 19327 | 20240603 | 2124 | 20240604 | 146 | 2474504 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 11216 | 37.3535 | -120.601 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0072771 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946230 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | RECLOSER | 9660 | 20240603 | 2136 | 20240604 | 208 | 2474529 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 7888 | 37.1224 | -121.015 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0072759 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946242 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6638 | 20240604 | 112 | 20240604 | 237 | 2474559 | 85 | Distribution Circuit | Animal | Bird found | 103 | 8755 | 37.0402 | -119.9896 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0072797 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946255 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319430248055 | 20240604 | 828 | 20240604 | 1232 | 2474637 | 244 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 244 | 37.8197 | -120.6984 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0072896 | OH | Sus | 31696240 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946393 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | JUMPER | OJ N/OF CGC#320146054210 | 20240604 | 904 | 20240604 | 1238 | 2474765 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 428 | 37.9894 | -120.4506 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0072888 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946368 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | TRANSFORMER | 320153518603 | 20240604 | 1016 | 20240604 | 1615 | 2475145 | 359 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 359 | 37.0108 | -120.4478 | No | Clear;32-90 F | Transformer (OH) | Arcing | 24-0073087 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946485 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321312420421 | 20240604 | 1344 | 20240604 | 2051 | 2475173 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 427 | 37.0598 | -120.0518 | No | Clear-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073169 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946504 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 1735 | 20240604 | 1452 | 20240604 | 1553 | 2475243 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 915 | 37.7536 | -121.0421 | No | Clear;Above 90 |  |  | 24-0073224 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1946524 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319663730806 | 20240604 | 1549 | 20240604 | 1918 | 2475296 | 209 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1463 | 37.3462 | -120.6165 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0073250 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946534 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | OTHER | WIRE DOWN #3 PHASE | 20240604 | 2032 | 20240605 | 227 | 2475631 | 355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2566 | 54827 | 37.1153 | -120.744 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0073311 | OH | Sus | 31696050 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | Yes | 1946580 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | T8232 | 20240604 | 2157 | 20240605 | 454 | 2475665 | 417 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 6830 | 37.3049 | -121.032 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0073356 | UG | Sus | 35558215 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946626 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | 319581519376 | 20240604 | 2202 | 20240604 | 2241 | 2475672 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 39 | 37.0318 | -120.6447 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0073341 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946612 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | S1961 | 20240604 | 2214 | 20240605 | 736 | 2475678 | 562 | Distribution Circuit | Equipment Failure/Involved | Underground | 214 | 61933 | 37.7583 | -120.8743 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0073340 | UG | Sus | 35558325 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1946611 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | SWITCH | 66932 | 20240605 | 120 | 20240605 | 309 | 2475731 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 6322 | 37.0543 | -120.4039 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0073347 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946627 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | RECLOSER | 5030 | 20240605 | 326 | 20240605 | 342 | 2475755 | 16 | Distribution Circuit | Company Initiated | Return Circuit Normal | 44 | 704 | 37.0544 | -120.4718 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0073347 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946637 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20240605 | 753 | 20240605 | 1128 | 2475834 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 582 | 125130 | 38.0085 | -120.3034 | No | Clear;32-90 F |  |  | 24-0073419 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946665 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322180527995 | 20240605 | 825 | 20240605 | 1312 | 2475893 | 287 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 287 | 37.2671 | -119.7514 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0073432 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946701 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320199120186 | 20240605 | 858 | 20240605 | 1202 | 2475966 | 184 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 184 | 37.0544 | -120.4325 | No | Clear;32-90 F |  |  | 24-0073595 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1946833 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322587132014 | 20240605 | 920 | 20240605 | 939 | 2476016 | 19 | Transformer only | Vegetation | Tree - grew into line | 1 | 19 | 37.376 | -119.6101 | No | Clear;32-90 F | Secondary | Normal | 24-0073461 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946766 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 27249 | 20240605 | 1015 | 20240605 | 1155 | 2476106 | 100 | Distribution Circuit | 3rd Party | Metallic Balloon | 1 | 100 | 37.74 | -120.974 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073579 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1946829 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | 21109 | 20240605 | 1553 | 20240606 | 56 | 2476491 | 543 | Distribution Circuit | 3rd Party | Vehicle | 1 | 543 | 37.7548 | -120.887 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 24-0073760 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1946903 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 321017919753 | 20240605 | 1735 | 20240605 | 2330 | 2476569 | 355 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 355 | 37.0414 | -120.1516 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0073825 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946948 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 11516 | 20240605 | 1819 | 20240605 | 1937 | 2476664 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 858 | 37.3004 | -120.4474 | No | Clear;Above 90 |  |  | 24-0073820 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1946945 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | T6736 | 20240605 | 1936 | 20240606 | 449 | 2476873 | 553 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 10122 | 37.2595 | -121.0141 | No | Clear;Above 90 | Other | Failed/Faulted | 24-0073882 | UG | Sus | 35558662 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947000 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | TRANSFORMER | 321307115937 | 20240605 | 1945 | 20240605 | 2139 | 2476879 | 114 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1368 | 36.937 | -120.0537 | No | Clear;Above 90 | Fuse | Broken | 24-0073867 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946986 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | SWITCH | 1582 | 20240605 | 2002 | 20240606 | 425 | 2476904 | 503 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 14084 | 37.775 | -120.8451 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0073862 | UG | Sus | 46255599 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1947023 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20240605 | 2019 | 20240606 | 243 | 2476957 | 384 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 688 | 243159 | 38.1888 | -120.0082 | No | Clear;32-90 F |  |  | 24-0073841 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1946963 | 0 | EPSS Ckt | Y | 2024 | AC
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319243630600 | 20240605 | 2105 | 20240606 | 240 | 2477053 | 335 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 335 | 37.3397 | -120.7614 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073900 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947011 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | RECLOSER | 92709 | 20240605 | 2157 | 20240606 | 136 | 2477141 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 711 | 64097 | 37.058 | -120.8173 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0073908 | OH | Sus | 31696341 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1947018 | 0 | Non-EPSS | N | 2024 | C- SGF
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | RECLOSER | 9740 | 20240606 | 39 | 20240606 | 1228 | 2477238 | 709 | Distribution Circuit | Equipment Failure/Involved | Underground | 1546 | 230981 | 37.282 | -120.4877 | No | Clear;32-90 F | Elbow | Broken | 24-0073919 | UG | Sus | 46255888 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947029 | 0 | Non-EPSS | N | 2024 | C- GRD
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | RECLOSER | 935396 | 20240606 | 314 | 20240606 | 932 | 2477298 | 378 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 156 | 58968 | 37.0158 | -119.7296 | No | Clear;32-90 F |  |  | 24-0073937 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947047 | 0 | EPSS Ckt | Y | 2024 | B- C
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320080829023 | 20240606 | 325 | 20240606 | 825 | 2477292 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 5400 | 37.2977 | -120.4716 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0073939 | OH | Sus | 46255887 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947048 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20240606 | 729 | 20240606 | 1142 | 2477415 | 253 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 582 | 147246 | 38.0085 | -120.3034 | No | Clear;32-90 F |  |  | 24-0073976 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947070 | 0 | EPSS Ckt | Y | 2024 | GRD- SGF & DCD
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 320856619417 | 20240606 | 956 | 20240606 | 1111 | 2477691 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 75 | 37.0329 | -120.2076 | No | Clear;Above 90 | Fuse | Failed/Faulted | 24-0074103 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947214 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | TRANSFORMER | 321451715989 | 20240606 | 1209 | 20240606 | 1919 | 2477888 | 430 | Transformer only | 3rd Party | Contact with High Voltage- 3rd party | 2 | 860 | 36.9379 | -120.0038 | No | Clear-Drizzle;Above 90 | Transformer (OH) | Failed/Faulted | 24-0074222 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947256 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 318584050520 | 20240606 | 1219 | 20240606 | 1536 | 2477893 | 197 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 197 | 37.8865 | -120.9916 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0074156 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947235 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 20133 | 20240606 | 1518 | 20240607 | 18 | 2478106 | 540 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 13384 | 37.7519 | -120.8399 | No | Clear;Above 90 | Conductor- Underground | Deteriorated | 24-0074314 | UG | Sus | 35558489 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947281 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320524128941 | 20240606 | 1932 | 20240606 | 2024 | 2478570 | 52 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 572 | 37.2941 | -120.3193 | No | Clear;Above 90 |  |  | 24-0074420 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1947336 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 9650 | 20240606 | 1951 | 20240606 | 2135 | 2478604 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 7280 | 37.3021 | -120.6354 | No | Clear;Above 90 | Insulator | Broken | 24-0074403 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947327 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | T909 | 20240606 | 2051 | 20240607 | 341 | 2478636 | 410 | Distribution Circuit | Equipment Failure/Involved | Underground | 69 | 9060 | 37.7595 | -120.873 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0074427 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947364 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 3332 | 20240607 | 127 | 20240607 | 1303 | 2478770 | 696 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 7 | 4872 | 37.1434 | -120.6018 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0074488 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947399 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 5556 | 20240607 | 710 | 20240607 | 757 | 2478850 | 47 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 15 | 705 | 36.9239 | -119.8722 | No | Clear;32-90 F |  |  | 24-0074524 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947419 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319228545030 | 20240607 | 746 | 20240607 | 1357 | 2478847 | 371 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 371 | 37.7363 | -120.7678 | No | Clear;32-90 F |  |  | 24-0074536 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1947439 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 7746 | 20240607 | 805 | 20240607 | 908 | 2478925 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 504 | 37.1419 | -120.4644 | No | Partly Cloudy;32-90 F |  |  | 24-0074587 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947499 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 318995146363 | 20240607 | 822 | 20240607 | 1608 | 2478960 | 466 | Transformer only | Animal | Bird found | 6 | 2796 | 37.7728 | -120.8487 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0074606 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947521 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318378226780 | 20240607 | 924 | 20240607 | 1318 | 2478883 | 234 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 234 | 37.2348 | -121.058 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074585 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947495 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 20240607 | 943 | 20240607 | 1429 | 2479077 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1877 | 273011 | 37.8308 | -120.2369 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074596 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947508 | 0 | EPSS Ckt | Y | 2024 | A & GRD
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | S255 | 20240607 | 1241 | 20240607 | 1355 | 2479304 | 74 | Distribution Circuit | Animal | Bird found | 145 | 10730 | 37.7699 | -120.9412 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0074753 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947566 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | TRANSFORMER | 319738430850 | 20240607 | 1624 | 20240607 | 2342 | 2479576 | 438 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2190 | 37.3476 | -120.59 | No | Clear;Above 90 | Transformer (OH) | Broken | 24-0074846 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947600 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | RECLOSER | 562202 | 20240607 | 2025 | 20240607 | 2136 | 2479750 | 71 | Distribution Circuit | 3rd Party | Metallic Balloon | 663 | 36068 | 37.2435 | -121.0128 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0074862 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947614 | 0 | EPSS Ckt | Y | 2024 | A- C
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | RECLOSER | 977268 | 20240608 | 711 | 20240608 | 936 | 2479899 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 254 | 27758 | 36.8803 | -119.9699 | No | Clear;32-90 F |  |  | 24-0074926 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947679 | 0 | Non-EPSS | N | 2024 | GRD & SGF
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321510720466 | 20240608 | 1502 | 20240608 | 1548 | 2480211 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 92 | 37.0615 | -119.9837 | No | Partly Cloudy;Above 90 | Fuse | Failed/Faulted | 24-0074994 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947745 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | JUMPER | 26904 #2 LD SIDE JMPRER BLOWN | 20240608 | 1634 | 20240608 | 1949 | 2480254 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 19500 | 37.2969 | -120.4935 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0075003 | OH | Sus | 46257681 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947750 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321863218370 | 20240608 | 1643 | 20240608 | 2243 | 2480145 | 360 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1440 | 37.0032 | -119.8633 | No | Partly Cloudy;Above 90 | Transformer (OH) | Broken | 24-0075000 | OH | Sus | 46257590 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947747 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 43347 | 20240608 | 2005 | 20240608 | 2321 | 2480309 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1176 | 37.4413 | -119.8944 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0075046 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1947795 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRANSFORMER | 320651322568 | 20240608 | 2026 | 20240609 | 642 | 2480313 | 616 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1232 | 37.1206 | -120.2772 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0075029 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947775 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 6277 | 20240609 | 13 | 20240609 | 914 | 2480365 | 541 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 26509 | 37.1183 | -120.2767 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0075050 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947801 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 65477 | 20240609 | 244 | 20240609 | 644 | 2480388 | 182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 2548 | 37.1202 | -120.2772 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0075051 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1947802 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | FUSE | 6946 | 20240609 | 419 | 20240609 | 535 | 2480392 | 76 | Distribution Circuit | Animal | Bird found | 11 | 701 | 37.0547 | -120.4283 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0075056 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947811 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | RECLOSER | 11700 | 20240609 | 2207 | 20240610 | 844 | 2480731 | 637 | Distribution Circuit | 3rd Party | Vehicle | 90 | 32578 | 36.88 | -120.2185 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0075174 | OH | Sus | 35559343 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1947917 | 0 | Non-EPSS | N | 2024 | A- B- C
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 5480 | 20240610 | 826 | 20240610 | 1210 | 2481044 | 224 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1155 | 192346 | 37.3755 | -119.6292 | No | Clear;32-90 F |  |  | 24-0075225 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1947990 | 0 | EPSS Ckt | Y | 2024 | B C MTT
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7258 | 20240610 | 853 | 20240610 | 1355 | 2481111 | 302 | Distribution Circuit | 3rd Party | Vehicle | 20 | 6040 | 37.303 | -120.7908 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0075260 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1948069 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 19893 | 20240610 | 1006 | 20240610 | 1128 | 2481235 | 82 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 82 | 37.1037 | -121.0162 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0075259 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948068 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319573629307 | 20240610 | 1101 | 20240610 | 1210 | 2481338 | 69 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 138 | 37.3046 | -120.6478 | No | Clear;32-90 F | Fuse | Burned Open | 24-0075323 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948110 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 100000011676 | 20240610 | 1120 | 20240610 | 1342 | 2481174 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 142 | 36.9988 | -120.8551 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0075327 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948112 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319810741403 | 20240610 | 1403 | 20240610 | 1440 | 2481534 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 74 | 37.6385 | -120.5643 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0075383 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948133 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 53691 | 20240610 | 1408 | 20240610 | 1450 | 2481529 | 42 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 42 | 37.1019 | -121.0212 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0075381 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948131 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319427047955 | 20240610 | 1442 | 20240610 | 1642 | 2481604 | 120 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 120 | 37.8166 | -120.6994 | No | Clear;Above 90 | Bushing | Broken | 24-0075421 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948147 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | L399 | 20240610 | 1747 | 20240611 | 604 | 2481720 | 737 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 17373 | 37.9932 | -120.4098 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0075501 | UG | Sus | 46262077 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948175 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | T684 | 20240610 | 1902 | 20240611 | 539 | 2481856 | 637 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 8469 | 37.7925 | -120.9838 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0075514 | UG | Sus | 46262183 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948211 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | FUSE | 7654 | 20240610 | 2030 | 20240610 | 2113 | 2481829 | 43 | Distribution Circuit | Animal | Bird found | 182 | 7826 | 37.3334 | -120.5408 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0075518 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1948183 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 424839 | 20240610 | 2114 | 20240611 | 638 | 2481842 | 564 | Distribution Circuit | 3rd Party | Vehicle | 55 | 31020 | 37.2111 | -119.5262 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0075558 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | Yes | No | 1948215 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | RECLOSER | 84280 | 20240611 | 615 | 20240611 | 836 | 2481921 | 141 | Distribution Circuit | Animal | Bird found | 23 | 2561 | 37.013 | -120.9431 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0075583 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1948237 | 0 | EPSS Ckt | Y | 2024 | A & C INST
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 3186 | 20240611 | 1116 | 20240611 | 1807 | 2482277 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1264 | 113784 | 37.8624 | -120.2266 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0075736 | OH | Sus | 35559856 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948434 | 0 | EPSS Ckt | Y | 2024 | B & GRD
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318782548360 | 20240611 | 1131 | 20240611 | 1218 | 2482297 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 94 | 37.8276 | -120.9222 | No | Clear;32-90 F | Fuse | Broken | 24-0075777 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948456 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 9010 | 20240611 | 1408 | 20240611 | 2122 | 2482439 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 240 | 67960 | 37.5385 | -121.2044 | No | Clear;Above 90 | Insulator | Broken | 24-0075853 | OH | Sus | 31696864 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1948474 | 0 | EPSS Ckt | N | 2024 | ABC
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | TRANSFORMER | 321218514104 | 20240611 | 1505 | 20240611 | 2245 | 2482482 | 460 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 460 | 36.8873 | -120.085 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0075907 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948484 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10316 | 20240611 | 1625 | 20240611 | 1812 | 2482586 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 4066 | 37.4659 | -119.7355 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0075948 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948500 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 9650 | 20240611 | 2014 | 20240611 | 2256 | 2482789 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 11340 | 37.3021 | -120.6354 | No | Clear;Above 90 |  |  | 24-0076002 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948539 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 2113 | 20240612 | 134 | 20240612 | 922 | 2482952 | 463 | Distribution Circuit | 3rd Party | Vehicle | 497 | 19484 | 36.8808 | -120.1286 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0076047 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1948575 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | JUMPER | OJ'S 4 POLES N/OF CGC# 321354611621 | 20240612 | 851 | 20240612 | 1316 | 2483024 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 530 | 36.8221 | -120.0381 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0076125 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948652 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10040 | 20240612 | 1140 | 20240612 | 1546 | 2483591 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 430 | 105780 | 37.3104 | -119.5846 | No | Clear;32-90 F |  |  | 24-0076235 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948765 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 3844 | 20240612 | 1313 | 20240612 | 1451 | 2483710 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 980 | 36.8916 | -120.6724 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0076286 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948787 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | OCB | 1110/2 | 20240612 | 1528 | 20240612 | 2011 | 2483824 | 283 | Distribution Circuit | Animal | Bird found | 720 | 186048 | 37.0139 | -120.9447 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0076386 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1948808 | 0 | EPSS Ckt | Y | 2024 | B & C
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 5133 | 20240612 | 1541 | 20240612 | 2028 | 2483834 | 287 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 4683 | 37.0202 | -119.9655 | No | Clear-Drizzle;Above 90 |  |  | 24-0076446 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948840 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321472218626 | 20240612 | 2136 | 20240612 | 2238 | 2484066 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 310 | 37.0108 | -119.9976 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0076486 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948877 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | TRANSFORMER | 320813325906 | 20240613 | 805 | 20240613 | 1241 | 2484236 | 276 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 276 | 37.2111 | -120.2201 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0076642 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949067 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | TRANSFORMER | 318468329873 | 20240613 | 923 | 20240613 | 1034 | 2484366 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 355 | 37.3192 | -121.0277 | No | Clear;32-90 F | Secondary | Broken | 24-0076575 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949007 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 8289 | 20240613 | 931 | 20240613 | 1438 | 2484422 | 307 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 3991 | 37.7293 | -120.9405 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0076592 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949032 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 576504 | 20240613 | 1018 | 20240613 | 1206 | 2484491 | 108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 609 | 65772 | 38.0492 | -120.2341 | No | Clear;32-90 F | Secondary | Normal | 24-0076654 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949071 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | OTHER | BROKEN JMPR 6P SS 9644 | 20240613 | 1119 | 20240613 | 1504 | 2484587 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 5002 | 36.7289 | -120.3149 | No | Clear;32-90 F | Jumper | Broken | 24-0076688 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1949096 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | RECLOSER | 9600 | 20240613 | 1143 | 20240613 | 2030 | 2484609 | 527 | Distribution Circuit | 3rd Party | Vehicle | 196 | 16157 | 37.1245 | -121.0153 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0076700 | OH | Sus | 35560353 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | Yes | No | 1949100 | 0 | EPSS Ckt | N | 2024 | A- B- GRD
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | TRANSFORMER | 100000008945 | 20240613 | 1238 | 20240613 | 1406 | 2484657 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 88 | 36.6649 | -120.3698 | No | Clear;Above 90 | Fuse | Broken | 24-0076804 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949130 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 278740 | 20240613 | 1356 | 20240613 | 1511 | 2484752 | 75 | Distribution Circuit | Animal | Squirrel | 1891 | 132257 | 37.9881 | -120.2845 | No | Clear;32-90 F | Recloser | Normal | 24-0076795 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949126 | 0 | EPSS Ckt | Y | 2024 | B & C- INST
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 319204231103 | 20240613 | 1526 | 20240613 | 2212 | 2484819 | 406 | Transformer only | 3rd Party | Customer Equipment | 3 | 1218 | 37.3533 | -120.775 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0076876 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1949141 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | SWITCH | 8223SW | 20240613 | 2307 | 20240614 | 212 | 2485067 | 185 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 1011 | 37.7941 | -120.9841 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0076942 | UG | Sus | 35560343 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949195 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | FUSE | 20205 | 20240614 | 413 | 20240614 | 553 | 2485123 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 200 | 37.2782 | -120.9543 | No | Clear;32-90 F |  |  | 24-0076967 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949220 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 7276 | 20240614 | 848 | 20240614 | 947 | 2485325 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 590 | 37.3019 | -120.4799 | No | Clear;32-90 F |  |  | 24-0077044 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949344 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 10110 | 20240614 | 930 | 20240614 | 1507 | 2485440 | 337 | Distribution Circuit | 3rd Party | Vehicle | 1069 | 60613 | 37.267 | -119.7114 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0077042 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949339 | 0 | EPSS Ckt | Y | 2024 | A & B
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | FUSE | 402873 | 20240614 | 1256 | 20240614 | 1410 | 2485675 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 148 | 37.009 | -120.0735 | No | Clear;Above 90 |  |  | 24-0077183 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949414 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 20240614 | 1352 | 20240614 | 1958 | 2485701 | 366 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 906 | 196362 | 37.6313 | -120.1536 | No | Clear;32-90 F |  |  | 24-0077174 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949413 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 27216 | 20240614 | 1505 | 20240614 | 1725 | 2485761 | 140 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 700 | 36.9099 | -120.6547 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0077226 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949427 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 263072 | 20240614 | 1609 | 20240614 | 1817 | 2485807 | 128 | Distribution Circuit | Company Initiated | Personnel- company | 353 | 45184 | 37.9489 | -120.4255 | No | Clear;32-90 F | Recloser | Normal | 24-0077248 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949431 | 0 | EPSS Ckt | Y | 2024 | A & B
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | FUSE | 402873 | 20240614 | 1704 | 20240614 | 1903 | 2485917 | 119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 357 | 37.009 | -120.0735 | No | Clear;Above 90 | Lightning Arrestor | Failed/Faulted | 24-0077282 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949447 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 319110447003 | 20240614 | 1931 | 20240614 | 2114 | 2486005 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 103 | 37.7911 | -120.8077 | No | Clear;32-90 F | Fuse | Broken | 24-0077290 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949458 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 20240614 | 1939 | 20240615 | 649 | 2485996 | 670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1877 | 395681 | 37.8308 | -120.2369 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0077284 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949448 | 0 | EPSS Ckt | Y | 2024 | AB
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 263072 | 20240614 | 2011 | 20240614 | 2148 | 2486018 | 97 | Distribution Circuit | Company Initiated | Personnel- company | 353 | 34241 | 37.9489 | -120.4255 | No | Clear;32-90 F | Recloser | Normal | 24-0077286 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949452 | 0 | EPSS Ckt | Y | 2024 | A GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 263072 | 20240614 | 2207 | 20240614 | 2336 | 2486148 | 89 | Distribution Circuit | Company Initiated | Personnel- company | 353 | 31417 | 37.9489 | -120.4255 | No | Clear;32-90 F | Recloser | Normal | 24-0077309 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949474 | 0 | EPSS Ckt | Y | 2024 | C INST
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 2177 | 20240615 | 4 | 20240615 | 140 | 2486195 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 640 | 37.0549 | -120.6718 | No | Clear;32-90 F |  |  | 24-0077320 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949488 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 1769 | 20240615 | 433 | 20240615 | 620 | 2486237 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 5885 | 37.7878 | -120.8601 | No | Clear;32-90 F |  |  | 24-0077327 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949493 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 90356 | 20240615 | 755 | 20240615 | 2043 | 2486289 | 768 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 16888 | 37.2198 | -119.9043 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0077338 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949508 | 0 | EPSS Ckt | Y | 2024 | C & GRD INST
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 25157 | 20240615 | 1340 | 20240615 | 1620 | 2486522 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 4320 | 36.7544 | -120.3869 | No | Clear;32-90 F |  |  | 24-0077398 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949562 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | OTHER | T6681 TWD T6759 | 20240615 | 1544 | 20240615 | 1853 | 2486599 | 189 | Distribution Circuit | Equipment Failure/Involved | Underground | 77 | 4998 | 37.058 | -120.8109 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0077371 | UG | Sus | 35560944 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949560 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | RECLOSER | 935396 | 20240615 | 1758 | 20240616 | 824 | 2486668 | 866 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 156 | 101087 | 37.0158 | -119.7296 | No | Clear;32-90 F |  |  | 24-0077406 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949569 | 0 | EPSS Ckt | Y | 2024 | AB INST
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318534327533 | 20240615 | 1811 | 20240616 | 213 | 2486602 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 6266 | 37.255 | -121.0045 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0077418 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949581 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20240615 | 1829 | 20240615 | 2143 | 2486695 | 194 | Distribution Circuit | Animal | Other | 151 | 29294 | 37.0679 | -119.9091 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0077413 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949575 | 0 | EPSS Ckt | N | 2024 | A GRD
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | JUMPER | COIS @ T4910 TWD T4911 | 20240615 | 1952 | 20240615 | 2120 | 2486749 | 88 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 4752 | 37.0591 | -120.8141 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0077368 | UG | Sus | 35560943 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949580 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 7007 | 20240615 | 2228 | 20240616 | 103 | 2486809 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 414 | 37.0928 | -120.5543 | No | Clear;32-90 F |  |  | 24-0077443 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949603 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | RECLOSER | 52144 | 20240616 | 901 | 20240616 | 1737 | 2486914 | 516 | Distribution Circuit | 3rd Party | Metallic Balloon | 215 | 20018 | 37.1133 | -120.1655 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0077460 | OH | Sus | 46264240 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1949619 | 0 | Non-EPSS | N | 2024 | B & GRD
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20240616 | 1436 | 20240616 | 1633 | 2487057 | 117 | Distribution Circuit | 3rd Party | Metallic Balloon | 683 | 79911 | 37.9574 | -120.3132 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077495 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949649 | 0 | EPSS Ckt | Y | 2024 | A & B INST
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | RECLOSER | 9920 | 20240616 | 1704 | 20240617 | 825 | 2487112 | 921 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 92 | 55624 | 37.1151 | -120.6384 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0077504 | OH | Sus | 35561061 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949658 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6575 | 20240617 | 335 | 20240617 | 613 | 2487354 | 158 | Distribution Circuit | 3rd Party | Metallic Balloon | 19 | 3002 | 36.8512 | -120.0464 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077565 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949709 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322720730083 | 20240617 | 809 | 20240617 | 954 | 2487458 | 105 | Transformer only | Vegetation | Other ground vegetation | 3 | 315 | 37.323 | -119.5655 | No | Clear;32-90 F | Transformer | Normal | 24-0077617 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949790 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4405 | 20240617 | 855 | 20240617 | 924 | 2487555 | 29 | Distribution Circuit | Company Initiated | Return Circuit Normal | 38 | 1102 | 37.1859 | -120.6656 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077504 | OH | Sus | 35561061 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949776 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 1995 | 20240617 | 1001 | 20240617 | 1202 | 2487679 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 2299 | 38.0517 | -120.3669 | No | Clear;32-90 F | Insulator | Broken | 24-0077633 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949832 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320406025233 | 20240617 | 1335 | 20240617 | 1412 | 2487946 | 37 | Transformer only | Animal | Other | 1 | 37 | 37.1937 | -120.3614 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0077743 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949908 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320082329058 | 20240617 | 1441 | 20240617 | 1949 | 2487988 | 308 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 7084 | 37.2986 | -120.471 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0077772 | OH | Sus | 31697575 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949919 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10133 | 20240617 | 1533 | 20240617 | 2005 | 2487928 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3536 | 37.3763 | -119.6686 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on object | 24-0077791 | OH | Sus | 31697447 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | Yes | No | 1949923 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | OTHER | T14290 TWD J26072 | 20240617 | 1626 | 20240617 | 1748 | 2488170 | 82 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 2870 | 37.0892 | -121.0226 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0077750 | UG | Sus | 35561115 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949935 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | FUSE | 10853 | 20240617 | 1633 | 20240618 | 342 | 2488188 | 669 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1785 | 36.991 | -120.8375 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0077890 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949996 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 7834 | 20240617 | 1721 | 20240617 | 2139 | 2488448 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6873 | 37.3079 | -120.4578 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077851 | OH | Sus | 46264710 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949961 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | OCB | 1712/2 | 20240617 | 1723 | 20240617 | 2125 | 2488490 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 2196 | 195054 | 37.7688 | -120.9078 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0077840 | OH | Sus | 31697658 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1949952 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318593526605 | 20240617 | 1809 | 20240617 | 2013 | 2488534 | 124 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 372 | 37.2297 | -120.9841 | No | Clear;32-90 F | Transformer (OH) |  | 24-0077874 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949979 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | JUMPER | 22006 | 20240617 | 1811 | 20240617 | 2259 | 2488537 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 864 | 37.1856 | -120.596 | No | Partly Cloudy;32-90 F | Jumper | Burned/flashed | 24-0077884 | OH | Sus | 46264682 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1949990 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | OCB | 1704/2 | 20240617 | 1858 | 20240618 | 539 | 2488570 | 641 | Distribution Circuit | 3rd Party | Vehicle | 463 | 147591 | 37.8561 | -120.9446 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0077859 | OH | Sus | 35561219 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | Yes | No | 1949965 | 0 | Non-EPSS | N | 2024 | AC GRD TIME
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 9200 | 20240617 | 2017 | 20240617 | 2035 | 2488631 | 18 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 136 | 2448 | 37.229 | -120.4868 | No | Overcast;32-90 F | Fuse | Normal | 24-0077873 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1949978 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | SWITCH | 3403 | 20240617 | 2215 | 20240617 | 2235 | 2488675 | 20 | Distribution Circuit | Company Initiated | Return Circuit Normal | 868 | 10808 | 37.8271 | -120.9609 | No | Clear;32-90 F | Crossarm- Wood | Normal | 24-0077840 | OH | Sus | 31697658 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1950015 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | TRANSFORMER | 318982520524 | 20240617 | 2243 | 20240618 | 128 | 2488714 | 165 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 330 | 37.0629 | -120.8493 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0077914 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950019 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 5270 | 20240617 | 2335 | 20240618 | 424 | 2488785 | 289 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 43639 | 37.0679 | -119.9091 | No | Clear;32-90 F |  |  | 24-0077933 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950043 | 0 | EPSS Ckt | N | 2024 | B GRD
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | TRANSFORMER | 320603811746 | 20240618 | 1107 | 20240618 | 1445 | 2489265 | 218 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 218 | 36.8218 | -120.295 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0078242 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950269 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 20240618 | 1221 | 20240618 | 1339 | 2489315 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 2808 | 37.5512 | -119.9231 | No | Clear;32-90 F | Other | Broken | 24-0078148 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950240 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | JUMPER | OJ 2 POLES S/OF CGC#320167212924 | 20240618 | 1742 | 20240618 | 2113 | 2489568 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 4431 | 36.854 | -120.4445 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0078298 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950291 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 3403 | 20240618 | 2059 | 20240618 | 2145 | 2489649 | 46 | Distribution Circuit | Animal | Bird found | 5 | 245 | 37.1828 | -120.9308 | No | Clear;32-90 F | Fuse | Broken | 24-0078323 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950312 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 85002 | 20240619 | 1704 | 20240619 | 1911 | 2490191 | 127 | Distribution Circuit | Animal | Bird found | 557 | 61289 | 37.6445 | -120.3119 | No | Clear;32-90 F | Bushing | Normal | 24-0078514 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950480 | 0 | EPSS Ckt | Y | 2024 | C
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | TRANSFORMER | 321073815470 | 20240619 | 2120 | 20240619 | 2245 | 2490304 | 85 | Transformer only | Vegetation | Tree - fell into line | 2 | 170 | 36.9245 | -120.1333 | No | Clear;32-90 F | Secondary | Normal | 24-0078552 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950516 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 5133 | 20240620 | 329 | 20240620 | 600 | 2490371 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 7399 | 37.0202 | -119.9655 | No | Clear;32-90 F |  |  | 24-0078567 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1950538 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319184745430 | 20240620 | 1031 | 20240620 | 1822 | 2490761 | 471 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 471 | 37.7473 | -120.7806 | No | Clear;32-90 F |  |  | 24-0078662 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1950599 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | TRANSFORMER | 321182311743 | 20240620 | 1148 | 20240620 | 1347 | 2490815 | 119 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 119 | 36.8228 | -120.0969 | No | Clear;32-90 F |  |  | 24-0078751 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1950629 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320756055702 | 20240620 | 1150 | 20240620 | 1246 | 2490819 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 224 | 38.0295 | -120.2387 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0078694 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950615 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320288050214 | 20240620 | 1403 | 20240620 | 1522 | 2490914 | 79 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 79 | 37.8789 | -120.4014 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0078750 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950628 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320466141673 | 20240620 | 1412 | 20240620 | 1455 | 2490931 | 43 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 43 | 37.6449 | -120.3394 | No | Clear;32-90 F | Fuse | Broken | 24-0078761 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950631 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 100000001644 | 20240620 | 1539 | 20240620 | 1800 | 2490920 | 141 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 141 | 37.7693 | -120.9326 | No | Clear;32-90 F | Jumper | Broken | 24-0078793 | OH | Sus | 46265815 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950646 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 7875 | 20240620 | 1725 | 20240621 | 155 | 2491048 | 510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 5882 | 37.3529 | -120.6583 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0078820 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950657 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 5987 | 20240620 | 1802 | 20240621 | 18 | 2491076 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1612 | 37.0544 | -120.2878 | No | Clear;32-90 F | Jumper | Burned Open | 24-0078841 | OH | Sus | 31697556 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950673 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 320355011520 | 20240620 | 1953 | 20240620 | 2038 | 2490952 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 90 | 36.816 | -120.3797 | No | Clear;32-90 F | Fuse | Broken | 24-0078844 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950676 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321225918209 | 20240621 | 848 | 20240621 | 1120 | 2491489 | 152 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 304 | 36.9997 | -120.0813 | No | Clear;32-90 F |  |  | 24-0079091 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1950901 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | RECLOSER | 4140 | 20240621 | 910 | 20240621 | 1537 | 2491552 | 387 | Distribution Circuit | 3rd Party | Vehicle | 85 | 32895 | 37.2876 | -120.285 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0079013 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | Yes | No | 1950863 | 0 | EPSS Ckt | N | 2024 | UNKNOWN
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 5672 | 20240621 | 950 | 20240621 | 1321 | 2491629 | 211 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 76 | 16036 | 37.3237 | -119.7782 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079019 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950865 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 6453 | 20240621 | 1240 | 20240621 | 1417 | 2491882 | 97 | Distribution Circuit | Animal | Bird found | 6 | 582 | 37.04 | -120.2205 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0079213 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950941 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1112 | 252761112 | FUSE | 5439 | 20240621 | 1316 | 20240621 | 1436 | 2491932 | 80 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 80 | 36.924 | -120.0809 | No | Clear;32-90 F |  |  | 24-0079215 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950942 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 8000 | 20240621 | 1329 | 20240621 | 1504 | 2491930 | 95 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1150 | 83536 | 38.0083 | -120.301 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079174 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950935 | 0 | EPSS Ckt | Y | 2024 | A PH- & GRD
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 23593 | 20240621 | 1558 | 20240621 | 2344 | 2492214 | 466 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1864 | 37.1581 | -120.87 | No | Clear;Above 90 |  |  | 24-0079341 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1950986 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 319554016847 | 20240621 | 1643 | 20240621 | 1957 | 2492069 | 194 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 10 | 1802 | 36.9626 | -120.6542 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079292 | OH | Sus | 31697907 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950950 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320207029896 | 20240621 | 1858 | 20240622 | 222 | 2492191 | 444 | Transformer only | Vegetation | Tree - grew into line | 1 | 444 | 37.3216 | -120.4285 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0079339 | OH | Sus | 31697909 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1950984 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | 318537227656 | 20240621 | 2251 | 20240621 | 2326 | 2492198 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 665 | 37.2584 | -121.0036 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0079338 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950983 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | S1405 | 20240622 | 808 | 20240622 | 952 | 2492355 | 104 | Distribution Circuit | Vegetation | Other ground vegetation | 25 | 2636 | 37.7956 | -120.8246 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0079372 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951023 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 4958 | 20240622 | 944 | 20240623 | 2140 | 2492411 | 2156 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 2156 | 37.2877 | -120.4877 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0079453 | UG | Sus | 46267724 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951077 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1103 | 253671103 | OCB | 1103/2 | 20240622 | 948 | 20240622 | 1801 | 2492417 | 493 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 130 | 7794 | 36.6512 | -120.5803 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0079381 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951036 | 0 | EPSS Ckt | N | 2024 | A & B
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | SWITCH | 9390 | 20240622 | 955 | 20240622 | 1725 | 2492424 | 450 | Distribution Circuit | 3rd Party | Vehicle | 100 | 16449 | 37.4836 | -120.5303 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0079383 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951037 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | SWITCH | 78448 | 20240622 | 1058 | 20240622 | 1106 | 2492372 | 8 | Distribution Circuit | Animal | Bird found | 155 | 1240 | 37.0197 | -119.7297 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0079397 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951048 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 20240622 | 1929 | 20240623 | 205 | 2492728 | 396 | Distribution Circuit | Company Initiated | Personnel- company | 306 | 104948 | 37.6769 | -119.7776 | No | Clear;Above 90 | Recloser | Normal | 24-0079463 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | Yes | No | No | 1951083 | 0 | EPSS Ckt | Y | 2024 | C INST
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320065128861 | 20240622 | 2010 | 20240623 | 148 | 2492750 | 338 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 5070 | 37.2933 | -120.4771 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079477 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951091 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 11509 | 20240622 | 2146 | 20240622 | 2205 | 2492787 | 19 | Distribution Circuit | 3rd Party | Vehicle | 30 | 570 | 37.3103 | -120.4445 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0079491 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951101 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 39256 | 20240623 | 553 | 20240623 | 829 | 2492857 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 525 | 81900 | 37.9571 | -120.3087 | No | Clear;32-90 F |  |  | 24-0079501 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951118 | 0 | EPSS Ckt | Y | 2024 | B- INST
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 10110 | 20240623 | 1241 | 20240624 | 346 | 2492985 | 905 | Distribution Circuit | 3rd Party | Vehicle | 1069 | 146933 | 37.267 | -119.7114 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 24-0079535 | OH | Sus | 46267805 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | Yes | No | 1951157 | 0 | EPSS Ckt | Y | 2024 | A & B- INST OC
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | FUSE | 3868 | 20240623 | 1520 | 20240623 | 1829 | 2493031 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 129 | 21288 | 37.3216 | -120.4871 | No | Clear;Above 90 |  |  | 24-0079549 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951167 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320085629002 | 20240623 | 1557 | 20240624 | 137 | 2493042 | 580 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 6380 | 37.2971 | -120.4699 | No | Clear;32-90 F | Secondary | Burned Open | 24-0079588 | OH | Sus | 31698268 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951204 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320543728323 | 20240623 | 1918 | 20240624 | 548 | 2493153 | 630 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 630 | 37.2769 | -120.3129 | No | Clear;Above 90 | Transformer (OH) | Deteriorated | 24-0079602 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951216 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | RECLOSER | 5490 | 20240623 | 1959 | 20240623 | 2217 | 2493186 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1556 | 204010 | 37.3399 | -119.6754 | No | Clear;32-90 F |  |  | 24-0079576 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951193 | 0 | EPSS Ckt | Y | 2024 | A B
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10040 | 20240623 | 2148 | 20240624 | 934 | 2493219 | 706 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 430 | 303580 | 37.3104 | -119.5846 | No | Clear;32-90 F |  |  | 24-0079584 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951200 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 7903 | 20240624 | 744 | 20240624 | 923 | 2493384 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 396 | 37.5647 | -120.437 | No | Clear;32-90 F |  |  | 24-0079683 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951339 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 313549 | 20240624 | 809 | 20240624 | 1112 | 2493722 | 183 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 610 | 36.8368 | -120.001 | No | Clear;32-90 F |  |  | 24-0079729 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951392 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | TRANSFORMER | 320961917398 | 20240624 | 811 | 20240624 | 1107 | 2493418 | 176 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 176 | 36.9776 | -120.1716 | No | Clear;32-90 F |  |  | 24-0079731 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1951395 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1111 | 252421111 | TRANSFORMER | 320451921789 | 20240624 | 831 | 20240624 | 1605 | 2493457 | 454 | Transformer only | 3rd Party | Customer Equipment | 1 | 454 | 37.0982 | -120.3457 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079915 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951504 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320379038525 | 20240624 | 831 | 20240624 | 1016 | 2493455 | 105 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 105 | 37.5573 | -120.3703 | No | Clear;32-90 F |  |  | 24-0079706 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1951369 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | OCB | 2101/2 | 20240624 | 948 | 20240624 | 1323 | 2493640 | 215 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5157 | 340308 | 37.2731 | -120.4872 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0079702 | OH | Sus | 46268164 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | Yes | No | 1951364 | 0 | Non-EPSS | N | 2024 | SET A
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 10703 | 20240624 | 1005 | 20240624 | 1210 | 2493646 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1375 | 37.7197 | -120.2041 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0079699 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951367 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | TRANSFORMER | 321179912789 | 20240624 | 1257 | 20240624 | 1758 | 2493873 | 301 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 301 | 36.8512 | -120.0979 | No | Clear-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079863 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951467 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | TRANSFORMER | 321190112789 | 20240624 | 1308 | 20240624 | 1937 | 2493885 | 389 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1167 | 36.8512 | -120.0943 | No | Partly Cloudy-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079882 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951481 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | FUSE | 13267 | 20240624 | 1310 | 20240624 | 1545 | 2493889 | 155 | Distribution Circuit | Environmental/External | Lightning | 37 | 5735 | 36.9602 | -120.0713 | No | Clear-Lightning;Above 90 | Fuse | Failed/Faulted | 24-0079893 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951486 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 5977 | 20240624 | 1315 | 20240625 | 328 | 2493897 | 853 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 16492 | 36.9576 | -120.0922 | No | Partly Cloudy-Lightning;Above 90 | Transformer (UG) | Failed/Faulted | 24-0079902 | UG | Sus | 35562593 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951494 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | INTERRUPTER | 13426 | 20240624 | 1315 | 20240624 | 1504 | 2493939 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 14473 | 36.9799 | -120.0742 | No | Partly Cloudy-Lightning;Above 90 |  |  | 24-0079816 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1951440 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 6092 | 20240624 | 1317 | 20240624 | 1524 | 2493911 | 127 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 237 | 30099 | 36.9603 | -120.0926 | No | Clear-Lightning;Above 90 |  |  | 24-0079883 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951482 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 6864 | 20240624 | 1320 | 20240626 | 221 | 2493917 | 2221 | Distribution Circuit | Environmental/External | Lightning | 15 | 10194 | 36.8784 | -119.9249 | No | Clear;Above 90 | Lightning Arrestor | Burned/flashed | 24-0080023 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951589 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 13085 | 20240624 | 1320 | 20240624 | 1746 | 2493922 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1596 | 36.9967 | -120.0915 | No | Clear-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079947 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951522 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321196418186 | 20240624 | 1320 | 20240624 | 2010 | 2494598 | 410 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 820 | 36.999 | -120.0915 | No | Clear-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079947 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951524 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321196418208 | 20240624 | 1326 | 20240624 | 2033 | 2494597 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 854 | 36.9996 | -120.0915 | No | Clear-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079947 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951523 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6643 | 20240624 | 1333 | 20240625 | 1154 | 2493931 | 1341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4606 | 37.0035 | -120.0288 | No | Clear-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0080004 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1951576 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321383418104 | 20240624 | 1335 | 20240625 | 47 | 2493934 | 672 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 1344 | 36.9961 | -120.027 | No | Clear-Lightning;Above 90 |  |  | 24-0080073 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1951629 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 13072 | 20240624 | 1356 | 20240625 | 1732 | 2493973 | 1656 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 11592 | 36.9963 | -120.0503 | No | Clear-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0080069 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1951625 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 905960 | 20240624 | 1412 | 20240624 | 1809 | 2494052 | 237 | Distribution Circuit | Environmental/External | Lightning | 2629 | 525528 | 37.2274 | -119.7103 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0079848 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951461 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | RECLOSER | 5010 | 20240624 | 1427 | 20240625 | 1145 | 2494126 | 1278 | Distribution Circuit | Animal | Other | 90 | 42168 | 37.1618 | -120.1722 | No | Partly Cloudy-Lightning;Above 90 | Transformer (OH) | Normal | 24-0079898 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1951491 | 0 | EPSS Ckt | Y | 2024 | A & B- G
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 4553 | 20240624 | 1440 | 20240624 | 2041 | 2494166 | 361 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 35378 | 37.4215 | -119.9663 | No | Partly Cloudy-Lightning;Above 90 |  |  | 24-0079937 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951515 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | TRANSFORMER | 321235017454 | 20240624 | 1518 | 20240624 | 2241 | 2494366 | 443 | Transformer only | Environmental/External | Lightning | 4 | 1772 | 36.9788 | -120.0786 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0079999 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951571 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20240624 | 1525 | 20240624 | 1940 | 2494382 | 255 | Distribution Circuit | Environmental/External | Lightning | 259 | 66045 | 37.5694 | -120.1177 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 24-0079890 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Multi-Fault | 0 | No | No | No | 1951485 | 0 | EPSS Ckt | Y | 2024 | ABC G
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 24472 | 20240624 | 1535 | 20240625 | 303 | 2494364 | 688 | Distribution Circuit | Environmental/External | Lightning | 30 | 20640 | 36.9667 | -120.0548 | No | Clear;Above 90 | Pole-Wood | Burned/flashed | 24-0079904 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951496 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 278740 | 20240624 | 1536 | 20240624 | 1703 | 2494396 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1894 | 164778 | 37.9881 | -120.2845 | No | Clear;Above 90 |  |  | 24-0079894 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951487 | 0 | EPSS Ckt | Y | 2024 | GRD / SGF / DCD
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319830948944 | 20240624 | 1539 | 20240625 | 448 | 2494664 | 789 | Transformer only | Environmental/External | Lightning | 1 | 789 | 37.8448 | -120.5574 | No | Clear;Above 90 | Transformer | Burned/flashed | 24-0080013 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951582 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | T2374 | 20240624 | 1544 | 20240625 | 1416 | 2494407 | 1352 | Distribution Circuit | Environmental/External | Lightning | 221 | 35683 | 36.9611 | -120.0926 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0080009 | UG | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951581 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | 1807 | 20240624 | 1544 | 20240625 | 1009 | 2494404 | 1105 | Distribution Circuit | Environmental/External | Lightning | 7 | 3823 | 37.8101 | -120.5457 | No | Partly Cloudy-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0080057 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1951617 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | TRANSFORMER | 321232417501 | 20240624 | 1549 | 20240624 | 2340 | 2494414 | 471 | Transformer only | Environmental/External | Lightning | 6 | 2826 | 36.9801 | -120.0795 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079987 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951554 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321260716836 | 20240624 | 1602 | 20240625 | 116 | 2494851 | 554 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3324 | 36.962 | -120.07 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0080089 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951646 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20240624 | 1604 | 20240625 | 11 | 2494480 | 487 | Distribution Circuit | Environmental/External | Lightning | 611 | 70201 | 37.8306 | -120.2367 | No | Partly Cloudy-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079914 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1951503 | 0 | EPSS Ckt | Y | 2024 | A-B-C
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321256916844 | 20240624 | 1604 | 20240625 | 225 | 2494853 | 621 | Transformer only | Environmental/External | Lightning | 5 | 3105 | 36.9622 | -120.0713 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0080084 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951641 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321260716873 | 20240624 | 1607 | 20240625 | 48 | 2494852 | 521 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2084 | 36.9627 | -120.07 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0080088 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951645 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321260716812 | 20240624 | 1612 | 20240625 | 1638 | 2494850 | 1466 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 7330 | 36.9613 | -120.07 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0080091 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951648 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10040 | 20240624 | 1730 | 20240624 | 1834 | 2494570 | 64 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 430 | 27520 | 37.3104 | -119.5846 | No | Clear;32-90 F |  |  | 24-0079942 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951519 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321532334480 | 20240624 | 1844 | 20240625 | 317 | 2494406 | 513 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 513 | 37.4444 | -119.9727 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0080049 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951610 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319822148950 | 20240624 | 1907 | 20240625 | 336 | 2494665 | 509 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1018 | 37.845 | -120.5606 | No | Clear;Above 90 | Transformer | Burned/flashed | 24-0080022 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951588 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319354932122 | 20240624 | 1928 | 20240625 | 0 | 2494729 | 272 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 2448 | 37.3815 | -120.7228 | No | Clear;Above 90 | Connector or Splice (OH) | Broken- wire on ground | 24-0080016 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | Yes | No | 1951585 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | 321186316756 | 20240624 | 1936 | 20240625 | 105 | 2494582 | 329 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 658 | 36.96 | -120.0952 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079993 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951560 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | L817 | 20240624 | 1950 | 20240624 | 2015 | 2494698 | 25 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 125 | 37.9807 | -120.3921 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0079995 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951567 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | JUMPER | WIRE DOWN HOT 1 SPAN N/OF 6113 | 20240624 | 2002 | 20240625 | 443 | 2494706 | 521 | Distribution Circuit | 3rd Party | Vehicle | 28 | 14588 | 37.0763 | -120.2657 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0080027 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | Yes | 1951593 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 320847237662 | 20240624 | 2012 | 20240625 | 5 | 2494709 | 233 | Transformer only | Environmental/External | Lightning | 1 | 233 | 37.5346 | -120.2065 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0080007 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951579 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | S403 | 20240625 | 44 | 20240625 | 252 | 2494835 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 10240 | 37.7593 | -121.0511 | No | Clear;32-90 F |  |  | 24-0080102 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951659 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 905960 | 20240625 | 145 | 20240625 | 1045 | 2494875 | 540 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2629 | 1327706 | 37.2274 | -119.7103 | No | Partly Cloudy;32-90 F |  |  | 24-0080087 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951644 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 7903 | 20240625 | 508 | 20240625 | 755 | 2494902 | 167 | Distribution Circuit | 3rd Party | Vehicle | 4 | 668 | 37.5647 | -120.437 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0080143 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951688 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 7425 | 20240625 | 541 | 20240625 | 1158 | 2494912 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1217 | 37.315 | -119.9691 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0080155 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951701 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | FUSE | 5258 | 20240625 | 939 | 20240626 | 220 | 2495228 | 1001 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2552 | 36.976 | -120.1101 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0080506 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1951948 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | 1807 | 20240625 | 1150 | 20240625 | 1833 | 2495405 | 403 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2819 | 37.8101 | -120.5457 | No | Partly Cloudy;Above 90 |  |  | 24-0080487 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951944 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 23043 | 20240625 | 1413 | 20240625 | 1504 | 2495579 | 51 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 153 | 37.0729 | -120.4735 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0080438 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1951930 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | TRANSFORMER | 320621423747 | 20240625 | 1642 | 20240625 | 2241 | 2495710 | 359 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 359 | 37.1516 | -120.2878 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0080528 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951962 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | OCB | 2102/2 | 20240625 | 1858 | 20240626 | 1601 | 2495885 | 1263 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1602 | 267096 | 37.2274 | -119.6906 | No | Clear;Above 90 | Connector or Splice (OH) | Broken- wire on ground | 24-0080544 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | Yes | No | 1951968 | 0 | EPSS Ckt | Y | 2024 | B C INST
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | FUSE | 23154 | 20240626 | 207 | 20240626 | 504 | 2496053 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1062 | 36.8212 | -120.5121 | No | Clear;32-90 F |  |  | 24-0080646 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952032 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 23045 | 20240626 | 451 | 20240626 | 1308 | 2496081 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 693 | 37.0473 | -120.4735 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0080676 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952041 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322205328355 | 20240626 | 854 | 20240626 | 1051 | 2496403 | 117 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 117 | 37.2767 | -119.7434 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0080725 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1952120 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 1532 | 20240626 | 1034 | 20240626 | 2030 | 2496616 | 596 | Distribution Circuit | 3rd Party | Vehicle | 210 | 35224 | 37.8674 | -120.8795 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0080841 | OH | Sus | 35563143 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952210 | 0 | EPSS Ckt | Y | 2024 | BC
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | OCB | 1104/2 | 20240626 | 1118 | 20240626 | 1650 | 2496687 | 332 | Distribution Circuit | 3rd Party | Vehicle | 2038 | 55636 | 36.9832 | -120.0336 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0080842 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1952211 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320079828985 | 20240626 | 1814 | 20240627 | 914 | 2497129 | 900 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 24576 | 37.2966 | -120.4719 | No | Clear;Above 90 | Secondary | Broken- wire on ground | 24-0081050 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1952274 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 691467 | 20240627 | 451 | 20240627 | 615 | 2497330 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 420 | 36.9959 | -120.0467 | No | Clear;32-90 F |  |  | 24-0081134 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952340 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 100000009598 | 20240627 | 737 | 20240627 | 1330 | 2497374 | 353 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1412 | 36.9964 | -120.0465 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0081226 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952465 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 1589 | 20240627 | 851 | 20240627 | 930 | 2497478 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 2286 | 36.9233 | -119.8762 | No | Clear;32-90 F |  |  | 24-0081237 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952473 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320291822084 | 20240627 | 853 | 20240627 | 1043 | 2497479 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 110 | 37.1066 | -120.4008 | No | Clear;32-90 F | Fuse | Broken | 24-0081290 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952496 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 6110 | 20240627 | 924 | 20240627 | 1305 | 2497545 | 221 | Distribution Circuit | Animal | Bird found | 169 | 22629 | 37.128 | -119.7352 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0081225 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952463 | 0 | EPSS Ckt | Y | 2024 | AB INST
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | FUSE | 6447 | 20240627 | 929 | 20240627 | 1035 | 2497554 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 660 | 37.021 | -119.794 | No | Clear;32-90 F |  |  | 24-0081258 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952488 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 884549 | 20240627 | 1125 | 20240627 | 1328 | 2497669 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 246 | 37.7802 | -120.7195 | No | Clear;32-90 F |  |  | 24-0081389 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952525 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320085629002 | 20240627 | 1309 | 20240627 | 1328 | 2497759 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 209 | 37.2971 | -120.4699 | No | Clear;Above 90 | Secondary | Deteriorated | 24-0081379 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1952522 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 69633 | 20240627 | 1441 | 20240627 | 1945 | 2497815 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1216 | 37.783 | -120.7591 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0081437 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1952533 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | 1807 | 20240627 | 1811 | 20240628 | 528 | 2498169 | 677 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4556 | 37.8101 | -120.5457 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0081615 | OH | Sus | 35563506 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952665 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1102 | 252531102 | RECLOSER | 1102/2 | 20240627 | 1951 | 20240627 | 2319 | 2498003 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 261 | 54288 | 37.2537 | -119.5192 | No | Clear;32-90 F |  |  | 24-0081529 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952571 | 0 | EPSS Ckt | Y | 2024 | A & B INST OC
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 9040 | 20240627 | 2048 | 20240627 | 2119 | 2498036 | 31 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 351 | 10881 | 37.2602 | -120.4878 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0081541 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1952581 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7258 | 20240627 | 2214 | 20240628 | 840 | 2498113 | 626 | Distribution Circuit | Animal | Bird found | 20 | 4787 | 37.303 | -120.7908 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0081609 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952657 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1102 | 254101102 | JUMPER | 22608 HIGH SIDE JMPR | 20240627 | 2225 | 20240628 | 438 | 2498119 | 373 | Distribution Circuit | 3rd Party | Vehicle | 85 | 31705 | 37.1274 | -120.2306 | No | Clear;32-90 F | Jumper | Broken | 24-0081613 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Open Circuit | 0 | No | No | No | 1952662 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319775430168 | 20240628 | 511 | 20240628 | 1222 | 2498212 | 431 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 431 | 37.3284 | -120.5774 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0081640 | OH | Sus | 31698217 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1952682 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320318654170 | 20240628 | 856 | 20240628 | 915 | 2498386 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 133 | 37.9878 | -120.3904 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0081694 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1952747 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 6609 | 20240628 | 1004 | 20240628 | 1109 | 2498487 | 65 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 217 | 36.8692 | -120.1477 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 24-0081783 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952822 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20240628 | 1119 | 20240628 | 1309 | 2498579 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 196 | 21560 | 37.8998 | -120.4541 | No | Clear;32-90 F | Insulator | Broken | 24-0081779 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952821 | 0 | EPSS Ckt | Y | 2024 | A- C
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321816717260 | 20240628 | 1238 | 20240628 | 1331 | 2498652 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 212 | 36.9724 | -119.8789 | No | Clear;Above 90 | Transformer (OH) | Leaking | 24-0081809 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1952846 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320426116118 | 20240628 | 2206 | 20240628 | 2330 | 2498817 | 84 | Transformer only | 3rd Party | Vehicle | 1 | 84 | 36.9457 | -120.3546 | No | Clear;32-90 F | Secondary | Broken | 24-0081989 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1952926 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7544 | 20240628 | 2351 | 20240629 | 124 | 2499065 | 93 | Distribution Circuit | 3rd Party | Vehicle | 37 | 3441 | 37.3387 | -120.76 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0082001 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952938 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | TRANSFORMER | 415933652388 | 20240629 | 220 | 20240629 | 1404 | 2499079 | 704 | Transformer only | Equipment Failure/Involved | Underground | 3 | 2112 | 36.7647 | -120.3888 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0082008 | UG | Sus | 31698359 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952948 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 47488 | 20240629 | 520 | 20240629 | 914 | 2499104 | 234 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 589 | 98772 | 37.9655 | -120.2508 | No | Clear;32-90 F |  |  | 24-0082006 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952946 | 0 | EPSS Ckt | Y | 2024 | A & B
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | S1919 | 20240629 | 531 | 20240629 | 834 | 2499108 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 6954 | 37.7457 | -120.8497 | No | Clear;32-90 F |  |  | 24-0082011 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952951 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 25409 | 20240629 | 655 | 20240629 | 1137 | 2499124 | 282 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 3384 | 37.7571 | -121.014 | No | Clear;32-90 F |  |  | 24-0082035 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1952978 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | 319614617952 | 20240629 | 946 | 20240629 | 1610 | 2499245 | 384 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 768 | 36.9932 | -120.6336 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0082057 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952992 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | 1807 | 20240629 | 1148 | 20240629 | 1815 | 2499310 | 387 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2709 | 37.8101 | -120.5457 | No | Clear;Above 90 |  |  | 24-0082096 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1953018 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | S1919 | 20240629 | 1958 | 20240629 | 2157 | 2499525 | 119 | Distribution Circuit | Animal | Bird found | 38 | 4522 | 37.7457 | -120.8497 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082125 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1953045 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | FUSE | 1568 | 20240630 | 108 | 20240630 | 340 | 2499565 | 152 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 912 | 36.9347 | -120.0639 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0082147 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1953069 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 23593 | 20240630 | 416 | 20240630 | 636 | 2499584 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 560 | 37.1581 | -120.87 | No | Clear;32-90 F |  |  | 24-0082160 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1953079 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 21094 | 20240630 | 1737 | 20240630 | 1849 | 2499956 | 72 | Distribution Circuit | Animal | Bird found | 124 | 8928 | 37.3385 | -119.6418 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0082232 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1953145 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | RECLOSER | 4420 | 20240630 | 1837 | 20240701 | 342 | 2500031 | 545 | Distribution Circuit | 3rd Party | Vehicle | 93 | 21903 | 37.2873 | -120.3791 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 24-0082237 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1953150 | 0 | EPSS Ckt | N | 2024 | B & GRD
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | RECLOSER | 935396 | 20240630 | 1910 | 20240701 | 210 | 2500140 | 420 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 156 | 49560 | 37.0158 | -119.7296 | No | Clear;Above 90 |  |  | 24-0082239 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1953152 | 0 | EPSS Ckt | Y | 2024 | A & B INST OC
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 9040 | 20240630 | 2048 | 20240630 | 2105 | 2500199 | 17 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 351 | 5967 | 37.2602 | -120.4878 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082249 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1953162 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | RECLOSER | 2850 | 20240630 | 2110 | 20240630 | 2337 | 2500206 | 147 | Distribution Circuit | 3rd Party | Vehicle | 26 | 3182 | 36.6403 | -120.3884 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0082252 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1953165 | 0 | Non-EPSS | N | 2024 | A & GRD
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | JUMPER | BURNT OJ N/OF CGC#320424717796 | 20240701 | 716 | 20240701 | 1249 | 2500843 | 333 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1998 | 36.989 | -120.3554 | No | Clear;32-90 F | Jumper | Burned Open | 24-0082521 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1953347 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | TRANSFORMER | 320641819681 | 20240701 | 810 | 20240701 | 1045 | 2500485 | 155 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 155 | 37.04 | -120.2794 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0082311 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953215 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319466044751 | 20240701 | 815 | 20240701 | 901 | 2500516 | 46 | Transformer only | Animal | Other | 1 | 46 | 37.7287 | -120.6854 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0082323 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953235 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 84944 | 20240701 | 823 | 20240701 | 1055 | 2500538 | 152 | Distribution Circuit | Animal | Bird found | 3087 | 469224 | 37.9525 | -120.3686 | No | Clear;32-90 F | Capacitor | Normal | 24-0082332 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | No | No | 1953245 | 0 | EPSS Ckt | Y | 2024 | A-B-GRD-INST
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | TRANSFORMER | 320001019253 | 20240701 | 1029 | 20240701 | 1227 | 2500713 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 118 | 37.0288 | -120.5018 | No | Clear;32-90 F | Fuse | Broken | 24-0082510 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953344 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318777545034 | 20240701 | 1250 | 20240701 | 1339 | 2500752 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 588 | 37.7361 | -120.9236 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0082481 | OH | Sus | 46271040 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953336 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 320049712533 | 20240701 | 1345 | 20240701 | 2130 | 2500819 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 465 | 36.8445 | -120.4848 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0082611 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953362 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | FUSE | 27329 | 20240701 | 1459 | 20240701 | 1625 | 2501056 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 86 | 37.3361 | -120.9034 | No | Clear;Above 90 |  |  | 24-0082660 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953377 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 7239 | 20240701 | 1702 | 20240701 | 1749 | 2501075 | 47 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 5922 | 37.3535 | -120.5959 | No | Clear;Above 90 | Fuse | Burned Open | 24-0082690 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953385 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 20240701 | 1848 | 20240701 | 2038 | 2501179 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 743 | 81730 | 37.4963 | -120.0432 | No | Clear;Above 90 |  |  | 24-0082706 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1953394 | 0 | EPSS Ckt | Y | 2024 | A & B INST OC
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320066528135 | 20240702 | 850 | 20240702 | 1028 | 2501683 | 98 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 392 | 37.2734 | -120.4764 | No | Clear-Heat Wave;32-90 F | Secondary | Broken- wire on ground | 24-0082871 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953539 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | SECTIONALIZER | 10810 | 20240702 | 902 | 20240702 | 1041 | 2501825 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 4455 | 37.5363 | -120.5166 | No | Clear-Heat Wave;32-90 F |  |  | 24-0082947 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1953589 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320474020930 | 20240702 | 1556 | 20240702 | 1740 | 2502380 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 208 | 37.0746 | -120.3379 | No | Clear-Heat Wave;Above 90 | Secondary | Broken | 24-0083203 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953672 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | TRANSFORMER | 321220218805 | 20240702 | 1736 | 20240702 | 1942 | 2502611 | 126 | Transformer only | Environmental/External | Fire- Forest/Grass | 2 | 252 | 37.0157 | -120.0834 | No | Partly Cloudy-Heat Wave;Above 90 | Conductor- Underground | Burned/flashed | 24-0083260 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953703 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319609632104 | 20240702 | 1835 | 20240702 | 2202 | 2502849 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 207 | 37.3817 | -120.6352 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083247 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953696 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | TRANSFORMER | 320130319000 | 20240702 | 1932 | 20240702 | 1944 | 2502920 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 24 | 37.0217 | -120.4557 | No | Clear-Heat Wave;32-90 F | Cutout- fuse holder | Broken | 24-0083267 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953708 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 22893 | 20240702 | 1948 | 20240702 | 2053 | 2503036 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 96 | 6240 | 36.8957 | -119.7943 | No | Partly Cloudy-Heat Wave;Above 90 |  |  | 24-0083310 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1953743 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | RECLOSER | 3400 | 20240702 | 2003 | 20240703 | 133 | 2503068 | 330 | Distribution Circuit | 3rd Party | Vehicle | 287 | 18900 | 36.9816 | -120.5941 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0083304 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1953739 | 0 | Non-EPSS | N | 2024 | GRD
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | T9333 | 20240702 | 2207 | 20240703 | 1231 | 2503224 | 864 | Distribution Circuit | Equipment Failure/Involved | Underground | 114 | 11927 | 37.3207 | -121.0097 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0083370 | UG | Sus | 35563398 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953787 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | FUSE | 14206C | 20240702 | 2303 | 20240703 | 1237 | 2503276 | 814 | Distribution Circuit | Equipment Failure/Involved | Underground | 64 | 52096 | 37.3166 | -120.4733 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0083371 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953788 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 306717 | 20240703 | 554 | 20240703 | 823 | 2503460 | 149 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1491 | 37.3713 | -120.6502 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0083437 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953880 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319695527911 | 20240703 | 950 | 20240703 | 1102 | 2503638 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 144 | 37.2663 | -120.6061 | No | Clear-Heat Wave;32-90 F | Secondary | Deteriorated | 24-0083483 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1953896 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320913112719 | 20240703 | 955 | 20240703 | 1559 | 2503647 | 364 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 5 | 1601 | 36.8485 | -120.1885 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Broken- wire on ground | 24-0083511 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1953904 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | JUMPER | 1675 LD SIDE JMPR BURNED OPEN | 20240703 | 1031 | 20240703 | 1127 | 2503702 | 56 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 3640 | 37.2747 | -120.5784 | No | Clear-Heat Wave;Above 90 | Jumper | Burned Open | 24-0083514 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1953905 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | 1807 | 20240703 | 1319 | 20240703 | 1750 | 2503822 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1897 | 37.8101 | -120.5457 | No | Clear-Heat Wave;Above 90 | Insulator | Failed/Faulted | 24-0083682 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1953940 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | RECLOSER | 3430 | 20240703 | 1413 | 20240703 | 1627 | 2503871 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 104 | 13841 | 36.7781 | -120.4001 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083637 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953928 | 0 | Non-EPSS | N | 2024 | GRD
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 22939 | 20240703 | 1517 | 20240703 | 1636 | 2503936 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 316 | 37.1998 | -120.2584 | No | Clear;32-90 F |  |  | 24-0083731 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1953954 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | RECLOSER | 191286 | 20240704 | 528 | 20240704 | 614 | 2504704 | 46 | Distribution Circuit | 3rd Party | Vehicle | 93 | 4278 | 36.9744 | -120.0138 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0083927 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954097 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7327 | 20240704 | 1056 | 20240704 | 1224 | 2504966 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 264 | 37.4725 | -120.6031 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084008 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954143 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 20240704 | 1844 | 20240704 | 2046 | 2505407 | 122 | Distribution Circuit | Company Initiated | Personnel- company | 306 | 37332 | 37.6769 | -119.7776 | No | Clear-Heat Wave;Above 90 | Recloser | Normal | 24-0084099 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954184 | 0 | EPSS Ckt | Y | 2024 | C PHASE- INST OC- DCD
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4572 | 20240704 | 1848 | 20240706 | 1706 | 2505408 | 2725 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3739 | 261687 | 37.5217 | -119.9394 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Burned/flashed | 24-0084100 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 4630882 | No | No | No | 1954185 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 44555 | 20240704 | 1927 | 20240704 | 2121 | 2505433 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 382 | 37.9697 | -120.331 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084116 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954199 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 20240704 | 2052 | 20240704 | 2253 | 2505481 | 121 | Distribution Circuit | Company Initiated | Personnel- company | 306 | 31598 | 37.6769 | -119.7776 | No | Clear;Above 90 | Recloser | Normal | 24-0084099 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954205 | 0 | EPSS Ckt | Y | 2024 | C PHASE- INST OC- DCD
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | SWITCH | 241564 | 20240704 | 2054 | 20240706 | 930 | 2506950 | 2196 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 21 | 5660 | 37.4872 | -119.9618 | No | Clear;Above 90 | Secondary | Burned/flashed | 24-0084100 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 27846 | No | No | No | 1954421 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 23853 | 20240705 | 45 | 20240705 | 149 | 2505641 | 64 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 13 | 831 | 37.4975 | -119.9791 | No | Clear;32-90 F |  |  | 24-0084176 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954261 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 8882 | 20240705 | 208 | 20240705 | 320 | 2505657 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1080 | 37.3005 | -120.8333 | No | Clear;32-90 F |  |  | 24-0084182 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954268 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 20799 | 20240705 | 322 | 20240705 | 421 | 2505660 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 59 | 37.7841 | -120.9688 | No | Clear;32-90 F |  |  | 24-0084186 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954271 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321279019211 | 20240705 | 744 | 20240705 | 1443 | 2505755 | 419 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1257 | 37.0269 | -120.0631 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084258 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954307 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 5691 | 20240705 | 837 | 20240705 | 1006 | 2505814 | 89 | Distribution Circuit | Animal | Bird found | 5 | 416 | 37.6566 | -120.5642 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Normal | 24-0084266 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954313 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 952535 | 20240705 | 946 | 20240705 | 1055 | 2505874 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 138 | 37.2285 | -120.471 | No | Clear;32-90 F |  |  | 24-0084286 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954324 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | JUMPER | OJS @ CGC 321279719217 | 20240705 | 1020 | 20240705 | 1443 | 2505913 | 263 | Distribution Circuit | 3rd Party | Vehicle | 3 | 789 | 37.027 | -120.0629 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Broken | 24-0084276 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954318 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320693853714 | 20240705 | 1112 | 20240705 | 1131 | 2505953 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 38 | 37.9754 | -120.2596 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Leaking | 24-0084290 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954327 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7544 | 20240705 | 1229 | 20240705 | 1325 | 2506016 | 56 | Distribution Circuit | 3rd Party | Vehicle | 25 | 1382 | 37.3387 | -120.76 | No | Clear-Heat Wave;Above 90 | Anchor or Guy | Broken | 24-0084331 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954352 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 100000058934 | 20240705 | 1238 | 20240705 | 1615 | 2505986 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 217 | 36.9109 | -120.0831 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0084337 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954353 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | RECLOSER | 11870 | 20240705 | 1340 | 20240705 | 2005 | 2506080 | 385 | Distribution Circuit | 3rd Party | Vehicle | 771 | 40323 | 36.9658 | -120.1284 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Broken- wire on ground | 24-0084338 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1954354 | 0 | Non-EPSS | N | 2024 | B GRD
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 8263 | 20240705 | 1346 | 20240705 | 2223 | 2506083 | 517 | Distribution Circuit | Equipment Failure/Involved | Underground | 125 | 31455 | 37.7309 | -120.9435 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Burned/flashed | 24-0084372 | UG | Sus | 46269426 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954374 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318902549170 | 20240705 | 1629 | 20240706 | 49 | 2506277 | 500 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 500 | 37.8495 | -120.8808 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084409 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954390 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | TRANSFORMER | 318982020452 | 20240705 | 1718 | 20240705 | 2200 | 2506327 | 282 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1128 | 37.061 | -120.8494 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Broken | 24-0084423 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954400 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20240705 | 1815 | 20240705 | 2012 | 2506470 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1006 | 117702 | 37.8473 | -120.2023 | No | Clear-Heat Wave;Above 90 | Regulator | Malfunctioning | 24-0084418 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954396 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | SWITCH | S111 | 20240705 | 1841 | 20240705 | 1952 | 2506103 | 71 | Distribution Circuit | Equipment Failure/Involved | Overhead | 331 | 23501 | 37.7935 | -120.9256 | No | Clear-Heat Wave;Above 90 | Insulator | Broken | 24-0084347 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954360 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | TRANSFORMER | 320704022403 | 20240705 | 2009 | 20240705 | 2050 | 2506409 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 451 | 37.1152 | -120.2599 | No | Clear-Heat Wave;Above 90 | Secondary | Broken | 24-0084436 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954412 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320079828985 | 20240705 | 2021 | 20240705 | 2044 | 2506595 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 276 | 37.2966 | -120.4719 | No | Clear;Above 90 | Secondary | Broken- wire on ground | 24-0084452 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954427 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | JUMPER | JMPRS 2 POLES SS OF CGC#320400249270 | 20240705 | 2030 | 20240705 | 2114 | 2506592 | 44 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 44 | 37.8531 | -120.3604 | No | Clear-Heat Wave;Above 90 | Other | Burned/flashed | 24-0084451 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954425 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 25730 | 20240705 | 2122 | 20240705 | 2314 | 2507132 | 112 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 224 | 37.3286 | -120.8328 | No | Clear;32-90 F | Metering Equipment | Burned/flashed | 24-0084488 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954461 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | RECLOSER | 9630 | 20240706 | 3 | 20240706 | 714 | 2507238 | 431 | Distribution Circuit | 3rd Party | Vehicle | 452 | 39148 | 37.2274 | -120.2709 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0084496 | OH | Sus | 35564828 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954471 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | OCB | 1104/2 | 20240706 | 250 | 20240706 | 1516 | 2507264 | 746 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1003 | 163352 | 37.0856 | -121.0132 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0084509 | OH | Sus | 35563391 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954485 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 25795 | 20240706 | 309 | 20240706 | 1244 | 2507268 | 575 | Distribution Circuit | Equipment Failure/Involved | Underground | 79 | 40409 | 37.0478 | -120.8824 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0084518 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1954494 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | L1719 | 20240706 | 400 | 20240706 | 859 | 2507283 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 28405 | 37.9765 | -120.3659 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0084514 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1954490 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 26747 | 20240706 | 703 | 20240706 | 820 | 2507377 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1078 | 37.8569 | -120.9195 | No | Clear;32-90 F |  |  | 24-0084539 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954506 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322251527295 | 20240706 | 858 | 20240706 | 1058 | 2507397 | 120 | Transformer only | Vegetation | Tree - grew into line | 3 | 360 | 37.2478 | -119.7271 | No | Clear-Heat Wave;32-90 F | Secondary | Normal | 24-0084552 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954510 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | TRANSFORMER | T551 | 20240706 | 1059 | 20240706 | 1236 | 2507520 | 97 | Transformer only | Equipment Failure/Involved | Underground | 11 | 1067 | 37.3209 | -121.0304 | No | Clear;32-90 F | Secondary | Burned Open | 24-0084593 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954521 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320474020930 | 20240706 | 1217 | 20240706 | 1515 | 2507561 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 356 | 37.0746 | -120.3379 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084600 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954522 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | 319685332174 | 20240706 | 1516 | 20240706 | 1522 | 2507641 | 6 | Transformer only | Equipment Failure/Involved | Overhead | 34 | 204 | 37.3838 | -120.6092 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Broken | 24-0084621 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1954534 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 916436 | 20240706 | 1646 | 20240707 | 1352 | 2507772 | 1266 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 459 | 92402 | 37.7217 | -120.2738 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Burned/flashed | 24-0084653 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954553 | 0 | EPSS Ckt | Y | 2024 | AB
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | FUSE | 6103 | 20240706 | 1737 | 20240706 | 1828 | 2507872 | 51 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 189 | 9627 | 36.9603 | -120.0836 | No | Overcast-Heat Wave;Above 90 |  |  | 24-0084678 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954574 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1949 | 20240706 | 1748 | 20240706 | 2242 | 2507886 | 294 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 157 | 46158 | 37.8529 | -120.1659 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Normal | 24-0084663 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954560 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | FUSE | 23263 | 20240706 | 1802 | 20240706 | 2049 | 2507940 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 2056 | 37.3138 | -120.4925 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084681 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954578 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | 318514727724 | 20240706 | 1804 | 20240706 | 1847 | 2507947 | 43 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 559 | 37.2602 | -121.0113 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084696 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1954594 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318851546445 | 20240706 | 1809 | 20240706 | 1838 | 2507806 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 87 | 37.7746 | -120.8982 | No | Clear-Heat Wave;Above 90 | Connector or Splice (OH) | Broken | 24-0084670 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954566 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 84944 | 20240706 | 1827 | 20240706 | 1937 | 2508152 | 70 | Distribution Circuit | Company Initiated | Personnel- company | 2928 | 190014 | 37.9525 | -120.3686 | No | Clear-Heat Wave;Above 90 | Recloser | Normal | 24-0084694 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954592 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318549426325 | 20240706 | 1849 | 20240706 | 2110 | 2508225 | 141 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 141 | 37.2219 | -120.9992 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084711 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954611 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 278740 | 20240706 | 1925 | 20240706 | 2008 | 2508293 | 43 | Distribution Circuit | Company Initiated | Coordination failure | 1893 | 81399 | 37.9881 | -120.2845 | No | Clear-Heat Wave;Above 90 | Recloser | Normal | 24-0084705 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954605 | 0 | EPSS Ckt | Y | 2024 | G- SGF- DCD
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | RECLOSER | 90050 | 20240706 | 2027 | 20240706 | 2056 | -2508347 | 29 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 753 | 21837 | 36.9244 | -119.9125 | No | Clear;Above 90 | Regulator | Burned/flashed | 24-0084717 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954622 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 6064 | 20240706 | 2030 | 20240706 | 2335 | 2508376 | 185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 387 | 71595 | 37.9603 | -120.3771 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084722 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954623 | 0 | EPSS Ckt | Y | 2024 | B & GRD
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320117613335 | 20240706 | 2157 | 20240707 | 408 | 2508510 | 371 | Transformer only | Equipment Failure/Involved | Overhead | 42 | 15582 | 36.8665 | -120.4608 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084797 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954695 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 264976 | 20240707 | 12 | 20240707 | 1512 | 2508582 | 900 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 14334 | 37.0732 | -120.0297 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084791 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954689 | 0 | EPSS Ckt | Y | 2024 | A & B INST OC
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | FUSE | 3868 | 20240707 | 42 | 20240707 | 141 | 2508599 | 59 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 129 | 7611 | 37.3216 | -120.4871 | No | Clear;32-90 F |  |  | 24-0084795 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954693 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | TRANSFORMER | T0294 | 20240707 | 205 | 20240707 | 1227 | 2508628 | 622 | Distribution Circuit | Equipment Failure/Involved | Underground | 121 | 14080 | 37.3212 | -120.491 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0084800 | UG | Sus | 35563393 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954699 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 26929 | 20240707 | 634 | 20240707 | 848 | 2508748 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 938 | 37.333 | -121.0186 | No | Clear;32-90 F |  |  | 24-0084827 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954722 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 318912018122 | 20240707 | 926 | 20240707 | 1023 | 2508821 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 57 | 36.9973 | -120.8734 | No | Clear-Heat Wave;Above 90 | Cutout- fuse holder | Failed/Faulted | 24-0084844 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954732 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322285525330 | 20240707 | 1040 | 20240707 | 1234 | 2508830 | 114 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 342 | 37.1932 | -119.7156 | No | Clear-Heat Wave;Above 90 | Service conductor | Broken- wire on ground | 24-0084843 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954731 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 70198 | 20240707 | 1153 | 20240707 | 1402 | 2508897 | 129 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1060 | 129058 | 37.9574 | -120.4389 | No | Clear-Heat Wave;Above 90 | Secondary | Broken | 24-0084855 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954739 | 0 | EPSS Ckt | Y | 2024 | B & GRD
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 23039 | 20240707 | 1325 | 20240707 | 1600 | 2509097 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 310 | 37.0803 | -120.4737 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084903 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954769 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 559635 | 20240707 | 1327 | 20240707 | 1435 | 2508945 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 363 | 37.0642 | -120.4374 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084881 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954757 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 22889 | 20240707 | 1421 | 20240707 | 1452 | 2509012 | 31 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 434 | 37.3533 | -120.7598 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084883 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954758 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | INTERRUPTER | 128246 | 20240707 | 1540 | 20240707 | 1645 | 2509066 | 65 | Distribution Circuit | Company Initiated | Coordination failure | 31 | 2015 | 37.8399 | -120.228 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Normal | 24-0084893 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1954762 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | TRANSFORMER | 320073527580 | 20240707 | 1542 | 20240707 | 1611 | 2509069 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 116 | 37.2581 | -120.4747 | No | Clear-Heat Wave;Above 90 | Fuse | Broken | 24-0084906 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954771 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 38882 | 20240707 | 1606 | 20240707 | 1806 | 2509093 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 313 | 37560 | 37.7169 | -120.3056 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084904 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954770 | 0 | EPSS Ckt | Y | 2024 | A C
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20240707 | 1802 | 20240707 | 2215 | 2509324 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 850 | 74780 | 37.8473 | -120.2023 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084924 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954783 | 0 | EPSS Ckt | Y | 2024 | C & GRD
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 23662 | 20240707 | 1847 | 20240707 | 1935 | 2509353 | 48 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 187 | 8964 | 36.9603 | -120.0885 | No | Overcast-Heat Wave;Above 90 |  |  | 24-0084951 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954808 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 6386 | 20240707 | 1913 | 20240707 | 2055 | 2509236 | 102 | Distribution Circuit | Equipment Failure/Involved | Underground | 109 | 2704 | 37.7253 | -120.9234 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Broken | 24-0084927 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954801 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | TRANSFORMER | T4298 | 20240707 | 2006 | 20240707 | 2114 | 2509445 | 68 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 1088 | 36.763 | -120.3793 | No | Clear;Above 90 |  |  | 24-0084997 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954856 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320519555606 | 20240707 | 2028 | 20240708 | 2 | 2509459 | 214 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 428 | 38.0272 | -120.321 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084981 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954839 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | T1817 | 20240707 | 2055 | 20240708 | 702 | 2509488 | 607 | Distribution Circuit | Equipment Failure/Involved | Underground | 4178 | 368608 | 37.3068 | -120.446 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084986 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954847 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | RECLOSER | 7100 | 20240707 | 2156 | 20240707 | 2348 | 2509567 | 112 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 574 | 64288 | 37.3251 | -120.4441 | No | Clear;32-90 F |  |  | 24-0085008 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | No | No | 1954867 | 0 | Non-EPSS | N | 2024 | A AND B- GROUND
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | RECLOSER | 90270 | 20240707 | 2156 | 20240708 | 155 | 2509569 | 239 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 406 | 88516 | 37.2846 | -120.4869 | No | Clear;32-90 F |  |  | 24-0085009 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954868 | 0 | Non-EPSS | N | 2024 | A
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | RECLOSER | 449613 | 20240707 | 2348 | 20240708 | 257 | 2509639 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 29253 | 37.2881 | -120.48 | No | Clear;32-90 F |  |  | 24-0085041 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1954888 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | T8236 | 20240708 | 104 | 20240708 | 934 | 2509634 | 510 | Distribution Circuit | Equipment Failure/Involved | Underground | 73 | 13650 | 37.2557 | -121.0143 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0085043 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954890 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319718827094 | 20240708 | 838 | 20240708 | 908 | 2509924 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 30 | 37.2441 | -120.5974 | No | Clear;32-90 F | Fuse | Broken | 24-0085131 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954996 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 6792 | 20240708 | 938 | 20240708 | 1457 | 2510035 | 319 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 879 | 37.0327 | -120.3923 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0085159 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955026 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | OCB | 1102/2 | 20240708 | 1014 | 20240708 | 1205 | 2510140 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 268 | 29748 | 36.72 | -120.6027 | No | Clear;32-90 F |  |  | 24-0085156 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955021 | 0 | EPSS Ckt | N | 2024 | B & GRD
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 20825 | 20240708 | 1044 | 20240708 | 1215 | 2510177 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 637 | 37.9262 | -120.4193 | No | Clear;Above 90 |  |  | 24-0085195 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955044 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | TRANSFORMER | 320013429375 | 20240708 | 1126 | 20240708 | 1606 | 2510235 | 280 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 4480 | 37.3077 | -120.4954 | No | Clear;Above 90 | Secondary | Burned/flashed | 24-0085210 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955052 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | TRANSFORMER | 318490121831 | 20240708 | 1230 | 20240708 | 1925 | 2510734 | 415 | Transformer only | 3rd Party | Customer Equipment | 23 | 9545 | 37.0982 | -121.0186 | No | Clear;Above 90 | Customer Equipment | Deteriorated | 24-0085353 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955102 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | T665540 | 20240708 | 1509 | 20240708 | 1528 | 2510530 | 19 | Transformer only | 3rd Party | Fire- house or bldg. | 1 | 19 | 36.9207 | -119.9609 | No | Partly Cloudy-Drizzle;Above 90 | Other | Burned/flashed | 24-0085293 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955081 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319681631134 | 20240708 | 1812 | 20240708 | 2024 | 2510718 | 132 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 396 | 37.3553 | -120.6105 | No | Clear;Above 90 | Connector or Splice (OH) | Burned Open | 24-0085360 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955104 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | OCB | 1101/2 | 20240708 | 1848 | 20240709 | 404 | 2510745 | 556 | Distribution Circuit | 3rd Party | Vehicle | 2682 | 96384 | 37.1208 | -120.2506 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0085358 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955103 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 23662 | 20240708 | 1853 | 20240708 | 1946 | 2510749 | 53 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 187 | 9898 | 36.9603 | -120.0885 | No | Overcast;Above 90 | Fuse | Failed/Faulted | 24-0085368 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955110 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | TRANSFORMER | 321229316747 | 20240708 | 1937 | 20240708 | 2010 | 2510811 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 264 | 36.9596 | -120.0808 | No | Overcast;Above 90 | Fuse | Burned Open | 24-0085378 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955116 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | FUSE | 6947 | 20240708 | 2042 | 20240709 | 823 | 2510896 | 701 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 2423 | 37.0542 | -120.4159 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0085411 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1955140 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 313549 | 20240709 | 653 | 20240709 | 818 | 2511162 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 283 | 36.8368 | -120.001 | No | Clear;32-90 F |  |  | 24-0085526 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955230 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | TRANSFORMER | 320661016440 | 20240709 | 709 | 20240709 | 932 | 2511167 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 143 | 36.9518 | -120.2736 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0085546 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955285 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | OTHER | J9799 TWD T47399 | 20240709 | 713 | 20240709 | 1624 | 2511384 | 551 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 551 | 36.9834 | -120.056 | No | Clear;Above 90 | Transformer (UG) | Deteriorated | 24-0085694 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955351 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | TRANSFORMER | 415248355651 | 20240709 | 745 | 20240709 | 1221 | 2511195 | 276 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 276 | 36.8509 | -120.6242 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0085557 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955290 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | S1267 | 20240709 | 851 | 20240709 | 1024 | 2511288 | 93 | Distribution Circuit | Vegetation | Other ground vegetation | 1 | 93 | 37.9789 | -120.3894 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0085533 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955246 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | SWITCH | 767 | 20240709 | 928 | 20240709 | 1008 | 2511330 | 40 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 400 | 37.7985 | -121.0412 | No | Clear;32-90 F | Switch (OH) | Broken | 24-0085516 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955276 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 70198 | 20240709 | 1057 | 20240709 | 1205 | 2511479 | 68 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 455 | 27778 | 37.9574 | -120.4389 | No | Clear;Above 90 | Secondary | Broken | 24-0085610 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955317 | 0 | EPSS Ckt | Y | 2024 | B & GRD
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 13344 | 20240709 | 1256 | 20240709 | 1418 | 2511656 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 82 | 37.4424 | -120.6304 | No | Clear;Above 90 | Transformer (OH) | Normal | 24-0085711 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955348 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318981629422 | 20240709 | 1534 | 20240709 | 1552 | 2511708 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 18 | 37.3058 | -120.8508 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0085751 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955358 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | OCB | 1109/2 | 20240709 | 1947 | 20240709 | 2105 | 2511910 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 289 | 22535 | 37.0551 | -120.3168 | No | Clear;32-90 F | Jumper | Burned Open | 24-0085832 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1955386 | 0 | Non-EPSS | N | 2024 | A/C INST OC
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 4679 | 20240709 | 1948 | 20240709 | 2043 | 2511902 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 94 | 5170 | 37.3587 | -120.6082 | No | Clear;Above 90 |  |  | 24-0085840 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955392 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | TRANSFORMER | 321238617630 | 20240709 | 2035 | 20240710 | 415 | 2511929 | 460 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1380 | 36.9839 | -120.0768 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 24-0085881 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955436 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | JUMPER | OJ 1 POLE SE/OF CGC 318846046280 | 20240709 | 2046 | 20240710 | 49 | 2511723 | 243 | Distribution Circuit | 3rd Party | Vehicle | 2 | 486 | 37.7702 | -120.9004 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0085825 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955380 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319699831288 | 20240709 | 2103 | 20240710 | 225 | 2511944 | 322 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1932 | 37.3595 | -120.6043 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0085851 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955405 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 196877 | 20240709 | 2126 | 20240709 | 2315 | 2511959 | 109 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 218 | 36.8498 | -120.0007 | No | Clear;32-90 F |  |  | 24-0085887 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955443 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20240710 | 100 | 20240710 | 233 | 2512023 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 971 | 61143 | 37.8306 | -120.2367 | No | Clear;32-90 F | Regulator | Malfunctioning | 24-0085351 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955448 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | OTHER | WIRE DOWN @CGC 319471530811 | 20240710 | 238 | 20240710 | 722 | 2512039 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 208 | 31443 | 37.3458 | -120.6847 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0085893 | OH | Sus | 46269420 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | Yes | 1955455 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 19277 | 20240710 | 701 | 20240710 | 800 | 2512102 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 197 | 37.3201 | -120.6144 | No | Clear;32-90 F |  |  | 24-0085945 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955497 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | TRANSFORMER | 416044051812 | 20240710 | 753 | 20240710 | 1023 | 2512125 | 150 | Transformer only | Animal | Other | 1 | 150 | 36.7489 | -120.3517 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0085938 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955489 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 415720457562 | 20240710 | 916 | 20240710 | 1047 | 2512293 | 91 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 91 | 36.9053 | -120.4649 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0086058 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955605 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321560536095 | 20240710 | 1030 | 20240710 | 1730 | 2512378 | 420 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 420 | 37.4892 | -119.963 | No | Clear;Above 90 | Secondary | Broken | 24-0086036 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955602 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | TRANSFORMER | 320133528746 | 20240710 | 1125 | 20240710 | 1159 | 2512370 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 68 | 37.29 | -120.4539 | No | Clear;Above 90 | Connector or Splice (OH) | Burned Open | 24-0086119 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955624 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320982612501 | 20240710 | 1432 | 20240710 | 1630 | 2512438 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 118 | 36.8426 | -120.1646 | No | Clear;Above 90 | Jumper | Broken | 24-0086278 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955648 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | TRANSFORMER | 416108849239 | 20240710 | 1815 | 20240711 | 1040 | 2512551 | 985 | Transformer only | Company Initiated | Coordination failure | 1 | 985 | 36.6781 | -120.3284 | No | Clear;Above 90 | Regulator | Broken | 24-0086397 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955683 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 731524 | 20240710 | 1942 | 20240710 | 2202 | 2512879 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 794 | 111160 | 37.155 | -119.7343 | No | Clear;Above 90 |  |  | 24-0086408 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955689 | 0 | EPSS Ckt | Y | 2024 | A- B- INST
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321437437340 | 20240710 | 1942 | 20240710 | 2035 | 2512884 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 53 | 37.5234 | -120.0049 | No | Clear;Above 90 | Transformer (OH) | Leaking | 24-0086401 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955686 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 10680 | 20240710 | 1948 | 20240710 | 2121 | 2512887 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 780 | 60205 | 37.3451 | -120.6327 | No | Clear;Above 90 |  |  | 24-0086404 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955688 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 5466 | 20240711 | 650 | 20240711 | 858 | 2513180 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1024 | 36.7916 | -120.241 | No | Clear;32-90 F |  |  | 24-0086589 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955869 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | FUSE | 2905 | 20240711 | 654 | 20240711 | 1321 | 2513187 | 387 | Distribution Circuit | Equipment Failure/Involved | Underground | 182 | 51653 | 36.9477 | -120.0559 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0086558 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955806 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 1735 | 20240711 | 654 | 20240711 | 827 | 2513188 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1395 | 37.7536 | -121.0421 | No | Clear;32-90 F |  |  | 24-0086563 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955823 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322087724430 | 20240711 | 714 | 20240711 | 1242 | 2513198 | 328 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 328 | 37.1691 | -119.7826 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0086600 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955892 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | TRANSFORMER | 318808046324 | 20240711 | 900 | 20240711 | 1400 | 2513489 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 600 | 37.7714 | -120.9135 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 24-0086687 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955950 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 319012052350 | 20240711 | 900 | 20240711 | 952 | 2513485 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 52 | 37.9371 | -120.8437 | No | Clear-Heat Wave;32-90 F | Secondary | Deteriorated | 24-0086581 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955848 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 8646 | 20240711 | 910 | 20240711 | 1006 | 2513512 | 56 | Distribution Circuit | 3rd Party | Vehicle | 40 | 2240 | 37.4183 | -120.614 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Broken | 24-0086634 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955921 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 278740 | 20240711 | 953 | 20240711 | 1510 | 2513589 | 317 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1893 | 399777 | 37.9881 | -120.2845 | No | Clear-Heat Wave;Above 90 |  |  | 24-0086617 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955908 | 0 | EPSS Ckt | Y | 2024 | DCD- SGF
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320466153798 | 20240711 | 1216 | 20240711 | 1847 | 2513762 | 391 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 4692 | 37.9775 | -120.3389 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0086883 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1955996 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 7746 | 20240711 | 1324 | 20240711 | 1433 | 2513827 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 552 | 37.1419 | -120.4644 | No | Clear-Heat Wave;Above 90 |  |  | 24-0086817 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1955975 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 100000101462 | 20240711 | 1412 | 20240711 | 1553 | 2513896 | 101 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 404 | 37.7384 | -120.9322 | No | Clear-Heat Wave;Above 90 |  |  | 24-0086863 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1955989 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 10590 | 20240711 | 1659 | 20240711 | 1943 | 2514124 | 164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 566 | 92824 | 37.9743 | -120.2383 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0086895 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956002 | 0 | EPSS Ckt | Y | 2024 | B- GRD
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320794354221 | 20240711 | 1659 | 20240712 | 25 | 2514412 | 446 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2230 | 37.989 | -120.2249 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 24-0086989 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956063 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320106329175 | 20240711 | 1850 | 20240711 | 2255 | 2514289 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1715 | 37.3018 | -120.4632 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0086946 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956033 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319404430542 | 20240711 | 2004 | 20240712 | 30 | 2514411 | 266 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1330 | 37.3384 | -120.7058 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0087000 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956072 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320146612927 | 20240711 | 2006 | 20240712 | 213 | 2514415 | 367 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3303 | 36.8548 | -120.4514 | No | Clear;32-90 F | Other | Malfunctioning | 24-0086996 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956068 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | TRANSFORMER | 320148512905 | 20240711 | 2009 | 20240712 | 356 | 2514421 | 467 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4203 | 36.8542 | -120.4507 | No | Clear;32-90 F | Other | Failed/Faulted | 24-0087027 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956096 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 6029 | 20240711 | 2051 | 20240711 | 2220 | 2514517 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 267 | 36.9026 | -119.7923 | No | Partly Cloudy;Above 90 |  |  | 24-0087029 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956097 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321838318025 | 20240711 | 2140 | 20240711 | 2304 | 2514478 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 336 | 36.9935 | -119.8719 | No | Clear;Above 90 | Fuse | Failed/Faulted | 24-0087034 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956104 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | T4086 | 20240711 | 2240 | 20240711 | 2332 | 2514520 | 52 | Transformer only | Unknown Cause | Patrol - found nothing | 12 | 624 | 37.9849 | -120.4025 | No | Clear;32-90 F |  |  | 24-0087042 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956111 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | L817 | 20240711 | 2248 | 20240712 | 104 | 2514524 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 680 | 37.9807 | -120.3921 | No | Clear;32-90 F |  |  | 24-0087050 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956118 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | RECLOSER | 9860 | 20240712 | 218 | 20240712 | 318 | 2514617 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 776 | 36000 | 37.7255 | -120.7831 | No | Clear;32-90 F | Recloser | Failed/Faulted | 24-0087055 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | No | No | 1956123 | 0 | EPSS Ckt | N | 2024 | A- B- GRD
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | JUMPER | FBS 2 SPANS SS OF CGC # 319836542180 | 20240712 | 839 | 20240712 | 958 | 2514831 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 79 | 37.6579 | -120.5589 | No | Clear-Heat Wave;32-90 F | Crossarm- Wood | Deteriorated | 24-0087111 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956192 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 9883 | 20240712 | 1022 | 20240712 | 1033 | 2514969 | 11 | Distribution Circuit | Company Initiated | Personnel- company | 26 | 286 | 36.7649 | -120.3817 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Normal | 24-0087175 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956247 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 2497 | 20240712 | 1045 | 20240712 | 1058 | 2515002 | 13 | Distribution Circuit | Company Initiated | Personnel- company | 24 | 312 | 36.7628 | -120.3829 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Normal | 24-0087175 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956256 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 3546 | 20240712 | 1109 | 20240712 | 1123 | 2515018 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 128 | 1792 | 36.7623 | -120.3831 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Normal | 24-0087175 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956261 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 3658 | 20240712 | 1134 | 20240712 | 1153 | 2515035 | 19 | Distribution Circuit | Company Initiated | Personnel- company | 21 | 399 | 36.7634 | -120.3825 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Normal | 24-0087175 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956267 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | TRANSFORMER | 321977513092 | 20240712 | 1153 | 20240712 | 1233 | 2515045 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 80 | 36.8568 | -119.8245 | No | Partly Cloudy-Heat Wave;Above 90 | Secondary | Broken | 24-0087243 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956274 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | FUSE | 9964 | 20240712 | 1219 | 20240712 | 1238 | 2515076 | 19 | Distribution Circuit | Company Initiated | Personnel- company | 48 | 912 | 36.7526 | -120.3869 | No | Partly Cloudy-Heat Wave;Above 90 | Conductor- Overhead | Normal | 24-0087175 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956279 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1112 | 252761112 | OCB | 1112/2 | 20240712 | 1300 | 20240712 | 1614 | 2515145 | 194 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 625 | 45974 | 36.9234 | -120.0551 | No | Partly Cloudy-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0087280 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1956287 | 0 | Non-EPSS | N | 2024 | C- GRD
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | JUMPER | OJ 1 E/OF CGC 319553117533 | 20240712 | 1319 | 20240712 | 1808 | 2515158 | 289 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 1445 | 36.982 | -120.6538 | No | Partly Cloudy-Heat Wave;Above 90 | Pole-Wood | Burned/flashed | 24-0087284 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956291 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | JUMPER | OJ 1 N/OF CGC 319752250533 | 20240712 | 1701 | 20240712 | 2022 | 2515371 | 201 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 41 | 8241 | 37.8885 | -120.5867 | No | Partly Cloudy-Heat Wave;Above 90 | Conductor- Overhead | Broken | 24-0087384 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956327 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | RECLOSER | 10680 | 20240712 | 1924 | 20240712 | 2023 | 2515580 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 780 | 46020 | 37.3451 | -120.6327 | No | Partly Cloudy-Heat Wave;Above 90 |  |  | 24-0087423 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956349 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7309 | 20240712 | 2154 | 20240712 | 2328 | 2515672 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1316 | 37.4913 | -120.629 | No | Partly Cloudy;32-90 F |  |  | 24-0087457 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956388 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 6452 | 20240713 | 427 | 20240713 | 1342 | 2515756 | 555 | Distribution Circuit | Animal | Bird found | 23 | 2491 | 37.0394 | -120.2566 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087469 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956410 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 68380 | 20240713 | 622 | 20240713 | 745 | 2515786 | 83 | Distribution Circuit | Animal | Squirrel | 552 | 45816 | 38.0151 | -120.2744 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0087470 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956414 | 0 | EPSS Ckt | Y | 2024 | A&C
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 6475 | 20240713 | 700 | 20240713 | 1128 | 2515794 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 6432 | 36.8953 | -119.811 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0087511 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1956452 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320474020930 | 20240713 | 820 | 20240713 | 1045 | 2515849 | 145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 290 | 37.0746 | -120.3379 | No | Overcast-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087522 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956462 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1101 | 162671101 | FUSE | 6791 | 20240713 | 1003 | 20240713 | 1152 | 2515908 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 436 | 37.5659 | -121.228 | No | Clear-Heat Wave;32-90 F |  |  | 24-0087538 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956470 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | RECLOSER | 9090 | 20240713 | 1219 | 20240713 | 2007 | 2516003 | 468 | Distribution Circuit | 3rd Party | Vehicle | 348 | 142968 | 37.096 | -120.9254 | No | Partly Cloudy-Heat Wave;Above 90 | Pole-Wood | Broken- wire on ground | 24-0087548 | OH | Sus | 35566116 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1956476 | 0 | EPSS Ckt | N | 2024 | A GRD
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 929360 | 20240713 | 1433 | 20240713 | 1737 | 2516105 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2894 | 323922 | 37.4926 | -119.9661 | No | Partly Cloudy-Heat Wave;Above 90 |  |  | 24-0087575 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956492 | 0 | EPSS Ckt | Y | 2024 | GRD
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | SWITCH | 3207 | 20240713 | 1603 | 20240714 | 20 | 2516157 | 497 | Distribution Circuit | 3rd Party | Vehicle | 16 | 7952 | 36.7333 | -120.3148 | No | Partly Cloudy-Heat Wave;Above 90 | Pole-Wood | Broken- wire on ground | 24-0087589 | OH | Sus | 35566173 | CENTRAL VALLEY | JUL | Force Out | 0 | No | Yes | No | 1956499 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 3792 | 20240713 | 1806 | 20240713 | 1839 | 2516215 | 33 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 638 | 37.0092 | -120.6447 | No | Partly Cloudy-Heat Wave;32-90 F |  |  | 24-0087603 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956511 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 1532 | 20240713 | 1812 | 20240714 | 20 | 2516219 | 368 | Distribution Circuit | 3rd Party | Vehicle | 210 | 27422 | 37.8674 | -120.8795 | No | Partly Cloudy-Heat Wave;Above 90 | Pole-Wood | Broken- wire on ground | 24-0087602 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | Yes | No | 1956510 | 0 | EPSS Ckt | N | 2024 | A- C- GRD
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 6003 | 20240713 | 2033 | 20240713 | 2215 | 2516285 | 102 | Distribution Circuit | Animal | Bird found | 21 | 2142 | 37.0981 | -120.4554 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0087644 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956556 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 20725 | 20240713 | 2351 | 20240714 | 331 | 2516342 | 220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 785 | 37.7895 | -120.745 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0087654 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956565 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | S1945 | 20240714 | 343 | 20240714 | 443 | 2516427 | 60 | Distribution Circuit | Animal | Bird found | 34 | 2040 | 37.749 | -120.8813 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0087664 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956575 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3504 | 20240714 | 419 | 20240714 | 623 | 2516431 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 827 | 36.9822 | -120.5271 | No | Partly Cloudy;32-90 F |  |  | 24-0087678 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956586 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 23266 | 20240714 | 522 | 20240714 | 1312 | 2516449 | 470 | Distribution Circuit | Animal | Other | 30 | 14100 | 37.2105 | -119.692 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Normal | 24-0087717 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956627 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 37282 | 20240714 | 527 | 20240715 | 52 | 2516461 | 1165 | Distribution Circuit | Environmental/External | Lightning | 2132 | 385897 | 37.462 | -119.9483 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087670 | OH | Sus | 35566321 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956580 | 0 | EPSS Ckt | Y | 2024 | A & GRD
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | RECLOSER | 661820 | 20240714 | 712 | 20240714 | 847 | 2516531 | 95 | Distribution Circuit | Animal | Bird found | 135 | 12825 | 37.1421 | -120.4949 | No | Partly Cloudy;32-90 F | Jumper | Normal | 24-0087686 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1956595 | 0 | Non-EPSS | N | 2024 | BC
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10330 | 20240714 | 725 | 20240714 | 1048 | 2516535 | 203 | Distribution Circuit | Environmental/External | Lightning | 1538 | 312214 | 37.2507 | -119.5619 | No | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Normal | 24-0087687 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956596 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 127906 | 20240714 | 738 | 20240714 | 2054 | 2516540 | 796 | Distribution Circuit | Environmental/External | Lightning | 7 | 3102 | 37.1556 | -119.4744 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087689 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956598 | 0 | EPSS Ckt | Y | 2024 | GRD
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | S209 | 20240715 | 358 | 20240715 | 1350 | 2516890 | 592 | Distribution Circuit | 3rd Party | Vehicle | 23 | 5408 | 37.311 | -121.0115 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0087809 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | Yes | No | 1956719 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 160233 | 20240715 | 436 | 20240715 | 1352 | 2516894 | 556 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 4448 | 37.7939 | -120.9911 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0087807 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956718 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | SWITCH | 295884 | 20240715 | 842 | 20240715 | 1514 | 2516968 | 392 | Distribution Circuit | 3rd Party | Vehicle | 7 | 2744 | 36.9819 | -120.275 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0087867 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956791 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | FUSE | 88021 | 20240715 | 846 | 20240715 | 2223 | 2517060 | 817 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 3268 | 36.815 | -120.1152 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0088039 | OH | Sus | 46279778 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | Yes | No | 1956910 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320158049685 | 20240715 | 1042 | 20240715 | 1305 | 2517327 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 429 | 37.8637 | -120.4481 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0087969 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956886 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318282229590 | 20240715 | 1046 | 20240715 | 1700 | 2517179 | 374 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1122 | 37.313 | -121.0932 | No | Clear;32-90 F | Service conductor | Broken | 24-0087951 | UG | Sus | 46280084 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956875 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | OTHER | J7662 TWD T78571 | 20240715 | 1048 | 20240715 | 1545 | 2517292 | 297 | Distribution Circuit | 3rd Party | Vehicle | 103 | 30591 | 36.9455 | -120.0224 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0087925 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956871 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320031528791 | 20240715 | 1440 | 20240715 | 1513 | 2517524 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 363 | 37.291 | -120.4892 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0088110 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1956931 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321542712891 | 20240715 | 1553 | 20240715 | 2106 | 2517596 | 313 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 313 | 36.8525 | -119.9741 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0088222 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956973 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321360619200 | 20240715 | 1555 | 20240716 | 148 | 2517598 | 593 | Transformer only | 3rd Party | Dig in- 3rd party | 1 | 593 | 37.0264 | -120.0352 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 24-0088203 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956955 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 27194 | 20240715 | 2136 | 20240716 | 40 | 2517760 | 184 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1 | 184 | 37.3156 | -121.0132 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088223 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1956976 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | OCB | 1708/2 | 20240716 | 611 | 20240716 | 1356 | 2517879 | 465 | Distribution Circuit | 3rd Party | Vehicle | 776 | 173283 | 37.7729 | -120.8258 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0088264 | OH | Sus | 35566535 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1957018 | 0 | EPSS Ckt | N | 2024 | A/B/C
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321360519200 | 20240716 | 1315 | 20240716 | 1330 | 2518307 | 15 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 2 | 30 | 37.0265 | -120.0352 | No | Clear;Above 90 | Secondary | Broken | 24-0088523 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957228 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 2147 | 20240716 | 1659 | 20240716 | 1937 | 2518489 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1264 | 37.3437 | -120.5792 | No | Clear;Above 90 |  |  | 24-0088655 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1957276 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20240717 | 123 | 20240717 | 200 | 2519011 | 37 | Distribution Circuit | 3rd Party | Vehicle | 480 | 17760 | 37.4305 | -120.0996 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0088688 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957308 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320078554460 | 20240717 | 502 | 20240717 | 1429 | 2519034 | 567 | Transformer only | 3rd Party | Fire- house or bldg. | 2 | 1134 | 37.9953 | -120.4744 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0088771 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957429 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | OCB | 1701/2 | 20240717 | 836 | 20240717 | 1141 | 2519146 | 185 | Distribution Circuit | Animal | Squirrel | 2642 | 488770 | 37.9742 | -120.3199 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0088757 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | Yes | No | No | 1957398 | 0 | EPSS Ckt | Y | 2024 | ABC
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 278740 | 20240717 | 836 | 20240717 | 1122 | 2519161 | 166 | Distribution Circuit | Company Initiated | Coordination failure | 1893 | 314238 | 37.9881 | -120.2845 | No | Clear;32-90 F | Recloser | Normal | 24-0088761 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957408 | 0 | EPSS Ckt | Y | 2024 | GRD
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 319972515530 | 20240717 | 851 | 20240717 | 1045 | 2519237 | 114 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 114 | 36.9269 | -120.512 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0088832 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957483 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320098654405 | 20240717 | 928 | 20240717 | 1013 | 2519294 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 90 | 37.9949 | -120.466 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0088780 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957447 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 320720040774 | 20240717 | 1221 | 20240717 | 1341 | 2519537 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 160 | 37.622 | -120.2451 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0088879 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957497 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | TRANSFORMER | T0326 | 20240717 | 1421 | 20240717 | 1439 | 2519641 | 18 | Transformer only | 3rd Party | Other | 17 | 306 | 37.3613 | -120.578 | No | Clear;Above 90 | Transformer (OH) | Normal | 24-0089003 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1957528 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 731524 | 20240717 | 1522 | 20240717 | 1732 | 2519691 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 788 | 46496 | 37.155 | -119.7343 | No | Clear;Above 90 |  |  | 24-0089010 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1957531 | 0 | EPSS Ckt | Y | 2024 | BC
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3518 | 20240717 | 2119 | 20240717 | 2255 | 2519925 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2400 | 36.96 | -120.6581 | No | Clear;32-90 F |  |  | 24-0089130 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1957600 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | S1945 | 20240718 | 130 | 20240718 | 728 | 2519965 | 358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 2338 | 37.749 | -120.8813 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0089137 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1957604 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1112 | 252421112 | FUSE | 6948 | 20240718 | 837 | 20240718 | 1157 | 2520127 | 200 | Distribution Circuit | Animal | Bird found | 9 | 1800 | 36.9809 | -120.4641 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0089283 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1957680 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | INTERRUPTER | 558890 | 20240718 | 914 | 20240718 | 1435 | s1957663 | 321 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 353 | 36.8516 | -119.9512 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0089152 | UG | Sus | 35567083 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957663 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319930534811 | 20240718 | 1154 | 20240718 | 1208 | 2520209 | 14 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 14 | 37.4568 | -120.525 | No | Clear;32-90 F |  |  | 24-0089303 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1957687 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322669525464 | 20240718 | 1351 | 20240718 | 1740 | 2520321 | 229 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 458 | 37.1964 | -119.584 | No | Clear;Above 90 | Transformer (OH) | Broken | 24-0089431 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957722 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 37282 | 20240718 | 1542 | 20240718 | 1814 | 2520376 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2134 | 267333 | 37.462 | -119.9483 | No | Clear;Above 90 |  |  | 24-0089447 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957725 | 0 | EPSS Ckt | Y | 2024 | C GRD
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 2473 | 20240719 | 947 | 20240719 | 1034 | 2521015 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 470 | 37.2821 | -121.031 | No | Clear;32-90 F |  |  | 24-0089695 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1957932 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | TRANSFORMER | 318355147311 | 20240719 | 1405 | 20240719 | 1530 | 2521198 | 85 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 170 | 37.798 | -121.0704 | No | Clear;Above 90 | Secondary | Normal | 24-0089814 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957980 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 731524 | 20240719 | 2132 | 20240719 | 2311 | 2521491 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 794 | 78606 | 37.155 | -119.7343 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0089932 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1958029 | 0 | EPSS Ckt | Y | 2024 | A & B
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 2611 | 20240719 | 2354 | 20240720 | 212 | 2521535 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1932 | 37.8385 | -120.9244 | No | Clear;32-90 F |  |  | 24-0089959 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1958047 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320618354744 | 20240720 | 815 | 20240720 | 906 | 2521633 | 51 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 102 | 38.003 | -120.287 | No | Clear;32-90 F |  |  | 24-0090001 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1958095 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320275421730 | 20240720 | 1012 | 20240720 | 1209 | 2521695 | 117 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 117 | 37.0969 | -120.4066 | No | Clear;32-90 F |  |  | 24-0090027 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1958116 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | TRANSFORMER | 321257216738 | 20240720 | 1248 | 20240720 | 1655 | 2521798 | 247 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 247 | 36.9592 | -120.0713 | No | Partly Cloudy-Drizzle;Above 90 | Transformer (OH) | Failed/Faulted | 24-0090041 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958123 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322087724430 | 20240720 | 1410 | 20240720 | 1938 | 2521837 | 328 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 328 | 37.1691 | -119.7826 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0090065 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958146 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | OTHER | WIRE DOWN 3 SPANS LD SIDE OF L473 | 20240721 | 725 | 20240721 | 1122 | 2522296 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 356 | 55351 | 37.939 | -120.4368 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0090136 | OH | Sus | 46282487 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | Yes | 1958211 | 1 | EPSS Ckt | Y | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322670325521 | 20240721 | 811 | 20240721 | 1010 | 2522306 | 119 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 119 | 37.1976 | -119.584 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0090140 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1958215 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 319096547485 | 20240721 | 1649 | 20240721 | 2058 | 2522594 | 249 | Transformer only | Animal | Bird found | 1 | 249 | 37.8041 | -120.8144 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 24-0090208 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958275 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320388637002 | 20240721 | 2333 | 20240722 | 613 | 2522715 | 400 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 800 | 37.5158 | -120.366 | No | Clear;32-90 F | Secondary | Broken | 24-0090241 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958301 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIGARDEN-2113 | 254552113 | FUSE | 6559 | 20240722 | 1125 | 20240722 | 1233 | 2523168 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 816 | 36.8588 | -119.9283 | No | Clear;32-90 F | Metering Equipment | Burned Open | 24-0090447 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1958500 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | FUSE | 7263 | 20240722 | 1229 | 20240722 | 1255 | 2523254 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 191 | 37.3289 | -120.5197 | No | Clear;Above 90 | Fuse | Broken | 24-0090467 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958505 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 20240722 | 1433 | 20240722 | 1721 | 2523408 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 306 | 50565 | 37.6769 | -119.7776 | No | Clear;Above 90 |  |  | 24-0090529 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958517 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | STANISLAUS | WESTLEY-1101 | 162671101 | TRANSFORMER | 317742338885 | 20240722 | 1442 | 20240722 | 1619 | 2523412 | 97 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 97 | 37.5656 | -121.2799 | No | Clear;Above 90 | Fuse | Failed/Faulted | 24-0090605 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958531 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | SWITCH | 23272 | 20240722 | 1452 | 20240722 | 2035 | 2523420 | 343 | Distribution Circuit | 3rd Party | Vehicle | 8 | 2744 | 36.9382 | -120.3049 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0090540 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958520 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 20240722 | 1902 | 20240722 | 2031 | 2523651 | 89 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 306 | 27234 | 37.6769 | -119.7776 | No | Clear;Above 90 |  |  | 24-0090647 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958543 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | FUSE | 3117 | 20240722 | 2052 | 20240722 | 2317 | 2523693 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3640 | 36.9533 | -120.5623 | No | Clear;32-90 F |  |  | 24-0090696 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1958585 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | TRANSFORMER | 319521233557 | 20240722 | 2337 | 20240723 | 819 | 2523705 | 522 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3132 | 37.4216 | -120.666 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0090702 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958590 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 9703 | 20240723 | 206 | 20240723 | 600 | 2523846 | 234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 5148 | 36.9152 | -120.7285 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0090710 | OH | Sus | 31701728 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958603 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320056628668 | 20240723 | 858 | 20240723 | 934 | 2524120 | 36 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 180 | 37.2881 | -120.4796 | No | Clear;32-90 F |  |  | 24-0090836 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1958765 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 4904 | 20240723 | 1308 | 20240724 | 401 | 2524403 | 663 | Distribution Circuit | Equipment Failure/Involved | Underground | 359 | 156328 | 37.3269 | -120.4693 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0090993 | UG | Sus | 35568179 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958834 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321959231258 | 20240723 | 1355 | 20240723 | 1800 | 2524458 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 245 | 37.3571 | -119.8305 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0091076 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958846 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5324 | 20240723 | 1407 | 20240724 | 125 | 2524457 | 678 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 120 | 34280 | 37.1952 | -119.5868 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Broken | 24-0091013 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958836 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | 20445 | 20240723 | 1933 | 20240723 | 2129 | 2524801 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 464 | 37.8396 | -121.0074 | No | Clear;Above 90 |  |  | 24-0091194 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958900 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | TRANSFORMER | T2147 | 20240723 | 1955 | 20240723 | 2129 | 2524917 | 94 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 846 | 36.9585 | -120.0962 | No | Overcast;Above 90 |  |  | 24-0091195 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1958901 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 8583 | 20240724 | 129 | 20240724 | 435 | s1958939 | 186 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 4056 | 37.3185 | -120.4554 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0091127 | UG | Sus | 35568252 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1958939 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 306717 | 20240724 | 612 | 20240724 | 823 | 2525207 | 131 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 1965 | 37.3713 | -120.6502 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0091339 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959057 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319516032745 | 20240724 | 657 | 20240724 | 853 | 2525221 | 116 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 116 | 37.3991 | -120.6667 | No | Clear;32-90 F |  |  | 24-0091335 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1959055 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320694928676 | 20240724 | 1305 | 20240724 | 1420 | 2525785 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 75 | 37.2874 | -120.2622 | No | Clear-Heat Wave;Above 90 | Fuse | Burned Open | 24-0091557 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959187 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 7026 | 20240724 | 1420 | 20240724 | 1556 | 2525863 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1056 | 37.3023 | -120.6448 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Deteriorated | 24-0091551 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1959186 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | OCB | 2101/2 | 20240724 | 1436 | 20240725 | 114 | 2525876 | 638 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1251 | 119710 | 37.5858 | -120.1258 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Burned/flashed | 24-0091571 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959190 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | TRANSFORMER | 321259218966 | 20240724 | 1707 | 20240724 | 1807 | 2526008 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 240 | 37.0203 | -120.0699 | No | Overcast-Heat Wave;Above 90 | Fuse | Failed/Faulted | 24-0091670 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959218 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | TRANSFORMER | 320022729587 | 20240724 | 1711 | 20240725 | 154 | 2526063 | 523 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 8801 | 37.3137 | -120.4922 | No | Clear-Heat Wave;Above 90 | Secondary | Broken | 24-0091674 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959221 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | TRANSFORMER | 321218517684 | 20240724 | 1837 | 20240724 | 2023 | 2525977 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 318 | 36.9854 | -120.0837 | No | Overcast-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0091703 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1959241 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | TRANSFORMER | 320061029197 | 20240724 | 1934 | 20240724 | 2119 | 2526094 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 64 | 6720 | 37.3026 | -120.4783 | No | Clear;Above 90 | Connector or Splice (OH) | Burned Open | 24-0091707 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959247 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | T3911 | 20240724 | 2044 | 20240724 | 2306 | 2526129 | 142 | Transformer only | Unknown Cause | Patrol - found nothing | 25 | 3550 | 37.2856 | -120.4899 | No | Clear;Above 90 |  |  | 24-0091749 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1959293 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 5442 | 20240725 | 509 | 20240725 | 630 | 2526295 | 81 | Distribution Circuit | Animal | Other | 10 | 810 | 37.151 | -120.0746 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0091775 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959318 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | TRANSFORMER | 322093519702 | 20240725 | 904 | 20240725 | 1645 | 2526472 | 461 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1383 | 37.0387 | -119.7826 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0091949 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959496 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 13152 | 20240725 | 924 | 20240725 | 1242 | 2526523 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 264 | 37.0747 | -120.0298 | No | Clear-Heat Wave;Above 90 |  |  | 24-0091977 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959508 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 76491 | 20240725 | 935 | 20240725 | 2053 | 2526541 | 678 | Distribution Circuit | Animal | Other | 2 | 1356 | 37.0393 | -119.9704 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Burned/flashed | 24-0091920 | OH | Sus | 46284243 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959483 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 20543 | 20240725 | 1524 | 20240725 | 1739 | 2526735 | 135 | Distribution Circuit | Equipment Failure/Involved | Underground | 63 | 4254 | 37.7619 | -120.8314 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Leaking | 24-0092077 | UG | Sus | 35568885 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959532 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322152522795 | 20240725 | 1705 | 20240725 | 1817 | 2526893 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 144 | 37.1219 | -119.7624 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Leaking | 24-0092155 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1959542 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 5841 | 20240725 | 2003 | 20240725 | 2146 | 2527005 | 103 | Distribution Circuit | Animal | Bird found | 9 | 927 | 37.7762 | -120.7898 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Normal | 24-0092197 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959582 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 67898 | 20240725 | 2131 | 20240726 | 1 | 2527040 | 150 | Distribution Circuit | Vegetation | Tree - fell into line | 1079 | 161850 | 37.9584 | -120.4387 | No | Clear;32-90 F | Anchor or Guy | Normal | 24-0092196 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | No | No | 1959580 | 0 | EPSS Ckt | Y | 2024 | AB- INST OC
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 322062116850 | 20240725 | 2343 | 20240726 | 58 | 2527024 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 300 | 36.9605 | -119.7963 | No | Clear;Above 90 | Other | Broken | 24-0092192 | OH | Sus | 31702076 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959576 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 26484 | 20240726 | 113 | 20240726 | 502 | 2527112 | 229 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 458 | 37.821 | -120.6991 | No | Clear;32-90 F |  |  | 24-0092233 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959624 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | T2324 | 20240726 | 337 | 20240726 | 1315 | 2527133 | 578 | Transformer only | Equipment Failure/Involved | Underground | 7 | 4046 | 37.3418 | -119.7102 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0092230 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959621 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 7346 | 20240726 | 611 | 20240726 | 733 | 2527165 | 82 | Distribution Circuit | Animal | Bird found | 111 | 9134 | 37.2897 | -120.4974 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092261 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959635 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322188525622 | 20240726 | 734 | 20240726 | 855 | 2527201 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 162 | 37.2018 | -119.7485 | No | Clear;32-90 F | Fuse | Broken | 24-0092321 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959713 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320187630932 | 20240726 | 1303 | 20240726 | 1810 | 2527622 | 307 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 307 | 37.3504 | -120.4359 | No | Clear;Above 90 | Transformer (OH) | Deteriorated | 24-0092544 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959819 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319647433549 | 20240726 | 1411 | 20240726 | 2212 | 2527750 | 481 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 481 | 37.4214 | -120.6218 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0092615 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1959836 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321789715555 | 20240726 | 1811 | 20240726 | 2024 | 2527876 | 133 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 532 | 36.9256 | -119.889 | No | Clear;Above 90 |  |  | 24-0092640 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1959862 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | RECLOSER | 466264 | 20240726 | 1954 | 20240726 | 2155 | 2527945 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 103 | 12463 | 37.3591 | -119.7304 | No | Clear;32-90 F |  |  | 24-0092637 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959859 | 0 | EPSS Ckt | Y | 2024 | BC
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | RECLOSER | 9600 | 20240727 | 48 | 20240727 | 1649 | 2528088 | 961 | Distribution Circuit | 3rd Party | Vehicle | 196 | 149482 | 37.1245 | -121.0153 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0092686 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | Yes | No | 1959903 | 0 | EPSS Ckt | N | 2024 | ABC
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9570 | 20240727 | 601 | 20240727 | 1004 | 2528116 | 243 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 513 | 53219 | 37.7155 | -120.2024 | No | Clear;32-90 F |  |  | 24-0092705 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959915 | 0 | EPSS Ckt | Y | 2024 | AB
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 6363 | 20240727 | 747 | 20240727 | 958 | 2528150 | 131 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 655 | 36.807 | -120.2606 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 24-0092740 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959959 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 23043 | 20240727 | 1149 | 20240727 | 1548 | 2528294 | 239 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 717 | 37.0729 | -120.4735 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0092791 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1960011 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S2685 | 20240727 | 1337 | 20240728 | 212 | 2528342 | 755 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 7396 | 37.8188 | -120.8688 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0092778 | UG | Sus | 31702564 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960001 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | OCB | 1704/2 | 20240728 | 158 | 20240728 | 601 | 2528506 | 243 | Distribution Circuit | Animal | Other | 3237 | 786591 | 37.9035 | -120.4971 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092837 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1960060 | 0 | EPSS Ckt | Y | 2024 | A & B
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 26884 | 20240728 | 1358 | 20240728 | 1407 | 2528716 | 9 | Distribution Circuit | Animal | Other | 14 | 126 | 37.3311 | -120.6238 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092895 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960103 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | RECLOSER | 11640 | 20240728 | 1746 | 20240728 | 1945 | 2528751 | 119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 2618 | 37.0618 | -120.8332 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0092912 | OH | Sus | 31702582 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960114 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319562519832 | 20240728 | 1834 | 20240728 | 2234 | 2528775 | 240 | Transformer only | 3rd Party | Vandalism | 2 | 480 | 37.0446 | -120.6502 | No | Clear;32-90 F | Customer Equipment | Broken | 24-0092932 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960131 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | S401 | 20240729 | 617 | 20240729 | 706 | 2528874 | 49 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 33 | 1601 | 37.829 | -120.9426 | No | Clear;32-90 F |  |  | 24-0092976 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960176 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 6064 | 20240729 | 635 | 20240729 | 853 | 2528881 | 138 | Distribution Circuit | Animal | Squirrel | 387 | 53406 | 37.9603 | -120.3771 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0092970 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960171 | 0 | EPSS Ckt | Y | 2024 | B PH & GRD INST OC
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10990 | 20240729 | 727 | 20240729 | 952 | 2528906 | 145 | Distribution Circuit | Animal | Other | 530 | 76850 | 37.4964 | -119.811 | No | Clear;32-90 F | Fuse | Normal | 24-0092990 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960189 | 0 | EPSS Ckt | Y | 2024 | A PH & GRD
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | FUSE | 6593 | 20240729 | 745 | 20240729 | 1125 | 2528911 | 220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2420 | 36.931 | -120.1835 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0092989 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960188 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320901656658 | 20240729 | 803 | 20240729 | 1715 | 2528959 | 552 | Transformer only | Vegetation | Tree - fell into line | 1 | 552 | 38.0557 | -120.1876 | No | Clear;32-90 F | Secondary | Normal | 24-0093020 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960226 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321958534042 | 20240729 | 1115 | 20240729 | 1155 | 2529233 | 40 | Transformer only | Animal | Other | 1 | 40 | 37.4333 | -119.8281 | No | Clear;32-90 F | Fuse | Normal | 24-0093206 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960351 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | TRANSFORMER | 100000001936 | 20240729 | 1121 | 20240729 | 1218 | 2529055 | 57 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 114 | 37.1877 | -121.0038 | No | Clear;32-90 F |  |  | 24-0093166 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1960343 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | OTHER | J778 TWD T9914 | 20240729 | 1342 | 20240729 | 1409 | 2529408 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 23 | 621 | 37.7632 | -120.832 | No | Clear;32-90 F | Elbow | Normal | 24-0093165 | UG | Sus | 35569275 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960384 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 20543 | 20240729 | 1440 | 20240729 | 1729 | 2529410 | 169 | Distribution Circuit | Equipment Failure/Involved | Underground | 63 | 2899 | 37.7619 | -120.8314 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0093165 | UG | Sus | 35569275 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960385 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 7903 | 20240729 | 1456 | 20240729 | 2019 | 2529427 | 323 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1292 | 37.5647 | -120.437 | No | Clear;32-90 F | Insulator | Broken | 24-0093389 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1960400 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 6017 | 20240729 | 1637 | 20240729 | 1825 | 2529671 | 108 | Distribution Circuit | 3rd Party | Vehicle | 16 | 1728 | 37.18 | -120.3246 | No | Clear;32-90 F | Anchor or Guy | Normal | 24-0093407 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1960407 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | JUMPER | 6160 SOURCE SIDE DISC JUMPER OPEN | 20240730 | 619 | 20240730 | 1045 | 2529952 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 25648 | 37.1416 | -120.2779 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0093498 | OH | Sus | 46286349 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1960475 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 11708 | 20240730 | 800 | 20240730 | 816 | 2530033 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 12 | 192 | 36.8905 | -120.7369 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0093542 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1960531 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321142018635 | 20240730 | 855 | 20240730 | 1203 | 2530128 | 188 | Transformer only | Animal | Bird found | 3 | 564 | 37.0111 | -120.1102 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0093700 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960694 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 25435 | 20240730 | 937 | 20240730 | 1156 | 2530206 | 139 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 185 | 37.3356 | -120.6145 | No | Clear;32-90 F |  |  | 24-0093705 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960699 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BIOLA-1102 | 252211102 | JUMPER | BURNT OPEN JUMPERS | 20240730 | 943 | 20240730 | 1645 | 2530210 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 422 | 36.8006 | -120.2178 | No | Clear;Above 90 | Jumper | Burned Open | 24-0093833 | OH | Sus | 46286685 | CENTRAL VALLEY | JUL | Open Circuit | 0 | No | No | No | 1960728 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | TRANSFORMER | 318341047655 | 20240730 | 1004 | 20240730 | 1540 | 2530226 | 336 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 336 | 37.8075 | -121.0753 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0093623 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960661 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321645713869 | 20240730 | 1018 | 20240730 | 1340 | 2530088 | 202 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 404 | 36.8793 | -119.9381 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0093633 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960666 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | SWITCH | 40258SW | 20240730 | 1210 | 20240730 | 1317 | 2530347 | 67 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 3484 | 37.7647 | -120.8285 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0093629 | UG | Sus | 35569549 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960697 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 916436 | 20240730 | 1331 | 20240731 | 1857 | 2530404 | 1766 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 453 | 176586 | 37.7217 | -120.2738 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0093760 | OH | Sus | 46287010 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960715 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 87222 | 20240730 | 1345 | 20240730 | 1609 | 2530412 | 144 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 207 | 7152 | 37.9608 | -120.4062 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093778 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960717 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 9470 | 20240730 | 1356 | 20240730 | 2311 | s1960745 | 555 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 667 | 322406 | 37.6459 | -120.3113 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093760 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960745 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 22769 | 20240730 | 1436 | 20240731 | 1131 | s1960805 | 1255 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 25 | 18113 | 37.6445 | -120.3093 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093760 | OH | Sus | 46287010 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960805 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 13304 | 20240730 | 1931 | 20240730 | 2300 | 2530642 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2090 | 36.9696 | -119.8936 | No | Clear;Above 90 |  |  | 24-0093978 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960800 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | RECLOSER | 5740 | 20240730 | 2104 | 20240730 | 2127 | 2530682 | 23 | Distribution Circuit | 3rd Party | Vehicle | 503 | 11569 | 36.9828 | -120.2023 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0093955 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1960780 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 10140 | 20240731 | 857 | 20240731 | 924 | 2531002 | 9 | Distribution Circuit | Company Initiated | Personnel- company | 921 | 13428 | 37.3665 | -119.6296 | No | Clear;32-90 F | Fuse | Normal | 24-0094065 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1960951 | 0 | EPSS Ckt | Y | 2024 | SGR/DCD
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | OCB | 1101/2 | 20240731 | 1305 | 20240731 | 2131 | 2531314 | 506 | Distribution Circuit | 3rd Party | Vehicle | 91 | 17948 | 36.7204 | -120.4588 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0094274 | OH | Sus | 35570060 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1961056 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | SWITCH | 2149 | 20240731 | 1437 | 20240731 | 2152 | 2531384 | 435 | Distribution Circuit | 3rd Party | Vehicle | 128 | 26144 | 37.3423 | -120.5766 | No | Clear;Above 90 | Switch (UG) | Broken | 24-0094326 | UG | Sus | 35569976 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1961071 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | TRANSFORMER | 319714131142 | 20240731 | 1915 | 20240731 | 1936 | 2531532 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 252 | 37.3556 | -120.5992 | No | Clear;Above 90 | Connector or Splice (OH) | Burned Open | 24-0094459 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1961111 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 8040 | 20240801 | 331 | 20240801 | 628 | 2531623 | 177 | Distribution Circuit | Equipment Failure/Involved | Underground | 131 | 22032 | 37.8999 | -120.5045 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0094494 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961139 | 0 | EPSS Ckt | Y | 2024 | A & GRD
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 320114544173 | 20240801 | 1028 | 20240801 | 1103 | 2531917 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 35 | 37.7133 | -120.4609 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0094635 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961282 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | JUMPER | 434329 | 20240801 | 1549 | 20240802 | 227 | 2532165 | 638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 638 | 37.0692 | -120.1718 | No | Overcast;Above 90 | Jumper | Broken | 24-0094922 | OH | Sus | 46287983 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1961393 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | FB 1.5 E/OF CGC 320516644289 | 20240801 | 1613 | 20240801 | 2006 | 2532188 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 6524 | 37.7186 | -120.3204 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0094622 | OH | Sus | 35392847 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961347 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | OTHER | J26155 TWD T14365 | 20240801 | 1641 | 20240801 | 1812 | 2532238 | 91 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 2184 | 36.8419 | -120.4419 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0094688 | UG | Sus | 35570126 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961354 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 798193 | 20240801 | 1826 | 20240801 | 1928 | 2532367 | 62 | Distribution Circuit | Animal | Other | 1 | 62 | 37.1203 | -120.4992 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0094890 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1961376 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | OTHER | T14354 TWD T14355 | 20240801 | 1839 | 20240801 | 1943 | 2532372 | 64 | Distribution Circuit | Equipment Failure/Involved | Underground | 84 | 5376 | 36.8407 | -120.4432 | No | Partly Cloudy;Above 90 | Transformer (UG) | Leaking | 24-0094727 | UG | Sus | 35570126 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961368 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | FUSE | 19095 | 20240801 | 1929 | 20240801 | 2026 | 2532410 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 152 | 37.3281 | -120.9149 | No | Clear;Above 90 |  |  | 24-0094909 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961386 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | OTHER | J26155 TWD T14367 | 20240801 | 2016 | 20240801 | 2107 | 2532426 | 51 | Distribution Circuit | Equipment Failure/Involved | Underground | 25 | 1275 | 36.8419 | -120.4419 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0094737 | UG | Sus | 35570126 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961383 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 8263 | 20240801 | 2107 | 20240801 | 2312 | 2532452 | 125 | Distribution Circuit | Equipment Failure/Involved | Underground | 125 | 13441 | 37.7309 | -120.9435 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 24-0094926 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961399 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321878735637 | 20240801 | 2120 | 20240802 | 115 | 2532456 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 235 | 37.4775 | -119.8544 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0094921 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961392 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319890048894 | 20240802 | 57 | 20240802 | 403 | 2532531 | 186 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 186 | 37.8429 | -120.5392 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0094952 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961433 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | SWITCH | 96969 | 20240802 | 759 | 20240802 | 1129 | 2532722 | 210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 2940 | 36.9824 | -120.0275 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0094951 | OH | Sus | 31703057 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961475 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | JUMPER | OJS @ FB E/OF CGC 322610029312 | 20240802 | 845 | 20240802 | 1045 | 2532797 | 120 | Distribution Circuit | Company Initiated | Other Circuits | 47 | 5640 | 37.3021 | -119.6033 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0095008 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961531 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319506448057 | 20240802 | 929 | 20240802 | 946 | 2532845 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 170 | 37.8195 | -120.6721 | No | Partly Cloudy;32-90 F | Secondary | Normal | 24-0095036 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961554 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | JUMPER | OJS 1 W/OF CGC 322621029348 | 20240802 | 1235 | 20240802 | 1301 | 2533065 | 26 | Distribution Circuit | Company Initiated | Other Circuits | 13 | 338 | 37.303 | -119.6008 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0095157 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961599 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321651413774 | 20240802 | 1354 | 20240802 | 1501 | 2533112 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 67 | 36.8768 | -119.9362 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0095248 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961631 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 21096 | 20240802 | 1428 | 20240802 | 1513 | 2533135 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 405 | 37.2742 | -120.5603 | No | Partly Cloudy;Above 90 |  |  | 24-0095253 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1961633 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 287264 | 20240802 | 1953 | 20240802 | 2040 | 2533291 | 47 | Distribution Circuit | Animal | Bird found | 10 | 470 | 37.7327 | -120.9444 | No | Overcast;Above 90 | Pothead(Riser Termination) | Normal | 24-0095326 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961664 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4674 | 20240802 | 2024 | 20240803 | 852 | 2533297 | 748 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 8482 | 37.1863 | -120.6348 | No | Partly Cloudy;32-90 F |  |  | 24-0095328 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961667 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | FUSE | 1995 | 20240802 | 2241 | 20240803 | 352 | 2533402 | 311 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1452 | 37.0034 | -120.3101 | No | Partly Cloudy;32-90 F |  |  | 24-0095349 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961692 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1101 | 254051101 | OCB | 1101/2 | 20240803 | 743 | 20240803 | 1104 | 2533477 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 232 | 46632 | 37.0856 | -121.0131 | No | Clear;32-90 F |  |  | 24-0095359 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1961701 | 0 | EPSS Ckt | Y | 2024 | C- GRD
YOSEMITE | YOSEMITE | ORTIGA-1105 | 254311105 | FUSE | 24058 | 20240803 | 1427 | 20240803 | 1511 | 2533717 | 44 | Distribution Circuit | Equipment Failure/Involved | Underground | 89 | 3916 | 37.0515 | -120.8616 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0095424 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961753 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | RECLOSER | 54922 | 20240803 | 1719 | 20240803 | 1733 | 2533828 | 14 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 14 | 37.3535 | -120.507 | No | Clear;Above 90 | Secondary | Burned/flashed | 24-0095447 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961766 | 0 | Non-EPSS | N | 2024 | NA
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | RECLOSER | 562202 | 20240803 | 1806 | 20240803 | 2005 | 2533859 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 664 | 79016 | 37.2435 | -121.0128 | No | Clear;Above 90 |  |  | 24-0095450 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1961767 | 0 | EPSS Ckt | Y | 2024 | A & B
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | RECLOSER | 56348 | 20240803 | 1851 | 20240804 | 325 | 2533876 | 514 | Distribution Circuit | 3rd Party | Vehicle | 291 | 19256 | 37.0546 | -120.2545 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0095456 | OH | Sus | 31703093 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961770 | 0 | Non-EPSS | N | 2024 | NA
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 66717 | 20240803 | 2000 | 20240804 | 155 | 2533930 | 355 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1420 | 36.9574 | -120.8376 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0095486 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1961809 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | RECLOSER | 5330 | 20240803 | 2227 | 20240803 | 2304 | 2533957 | 37 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 662 | 22883 | 36.9251 | -120.1285 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095490 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1961813 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6569 | 20240804 | 330 | 20240804 | 829 | 2534057 | 299 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 6578 | 36.8813 | -120.0743 | No | Clear;32-90 F |  |  | 24-0095522 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1961848 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | FUSE | 13245 | 20240804 | 1918 | 20240805 | 532 | 2534342 | 614 | Distribution Circuit | Equipment Failure/Involved | Underground | 3186 | 186700 | 36.9748 | -120.0466 | No | Partly Cloudy;Above 90 | Transformer (UG) | Burned/flashed | 24-0095586 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1961891 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | JUMPER | BURNT OJ @ 6705 | 20240805 | 55 | 20240805 | 807 | 2534474 | 432 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3456 | 36.88 | -120.2643 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0095634 | OH | Sus | 31703384 | CENTRAL VALLEY | AUG | Open Circuit | 0 | No | No | No | 1961927 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | FUSE | 6592 | 20240805 | 547 | 20240805 | 1417 | 2534594 | 510 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2040 | 36.9381 | -120.1823 | No | Clear;32-90 F |  |  | 24-0095999 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962131 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 23123 | 20240805 | 642 | 20240805 | 1100 | 2534775 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 258 | 36.8876 | -119.8574 | No | Clear;Above 90 |  |  | 24-0095818 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962076 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | JUMPER | 1 E & 5 S/OF OF 20001 | 20240805 | 936 | 20240805 | 1337 | 2534840 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 241 | 37.5005 | -121.3675 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0095765 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962061 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 67898 | 20240805 | 1149 | 20240805 | 1340 | 2534950 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1076 | 119436 | 37.9584 | -120.4387 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0095863 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962083 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320752954381 | 20240805 | 1439 | 20240805 | 1611 | 2534995 | 92 | Transformer only | 3rd Party | Dig in- 3rd party | 2 | 184 | 37.9937 | -120.2396 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0096018 | UG | Sus | 46289448 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962134 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321531837731 | 20240805 | 1616 | 20240805 | 1644 | 2535189 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 37.5348 | -119.972 | No | Clear;Above 90 | Cutout- fuse holder | Broken | 24-0096057 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962140 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | TRANSFORMER | 415173056706 | 20240805 | 1708 | 20240805 | 1756 | 2535229 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 48 | 36.8797 | -120.6521 | No | Clear;Above 90 | Secondary | Broken | 24-0096072 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962145 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | OTHER | 9576 | 20240805 | 2035 | 20240806 | 522 | 2535359 | 527 | Distribution Circuit | 3rd Party | Aircraft- crop dusting | 3 | 1581 | 36.9179 | -120.4413 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0096134 | OH | Sus | 46289672 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1962202 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 44143 | 20240805 | 2054 | 20240806 | 212 | 2535355 | 318 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6996 | 36.9704 | -120.0569 | No | Overcast-Drizzle;Above 90 | Secondary | Deteriorated | 24-0096102 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962168 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 47488 | 20240806 | 209 | 20240806 | 705 | 2535437 | 296 | Distribution Circuit | Animal | Bird found | 590 | 125753 | 37.9655 | -120.2508 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0096146 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962213 | 0 | EPSS Ckt | Y | 2024 | A & C
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | RECLOSER | 42444 | 20240806 | 838 | 20240806 | 854 | 2535631 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 35 | 560 | 37.3894 | -120.6014 | No | Clear;32-90 F | Anchor or Guy | Normal | 24-0096225 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962308 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | MADERA-1116 | 252761116 | TRANSFORMER | 321433113901 | 20240806 | 904 | 20240806 | 912 | 2535518 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 8 | 36.8803 | -120.0103 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0096255 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962342 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1777 | 20240806 | 906 | 20240806 | 1254 | 2535615 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 6156 | 37.822 | -120.6848 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0096223 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962296 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | FUSE | 6081 | 20240806 | 941 | 20240806 | 1620 | 2535717 | 118 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 30 | 3930 | 36.9786 | -120.0626 | No | Clear-Drizzle;32-90 F | Conductor- Underground | Broken | 24-0096289 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962387 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | RECLOSER | 9070 | 20240806 | 1120 | 20240807 | 301 | 2535810 | 941 | Distribution Circuit | 3rd Party | Vehicle | 388 | 40262 | 37.7931 | -120.8693 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0096306 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1962389 | 0 | Non-EPSS | N | 2024 | A- B- GRD
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | TRANSFORMER | 321337016684 | 20240806 | 1606 | 20240806 | 1706 | 2536058 | 60 | Transformer only | Equipment Failure/Involved | Fire- pole | 8 | 480 | 36.9574 | -120.0431 | No | Overcast;Above 90 | Cutout- fuse holder | Arcing | 24-0096530 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962477 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | TRANSFORMER | 318969345803 | 20240806 | 1612 | 20240806 | 1700 | 2536063 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 384 | 37.7573 | -120.8575 | No | Clear;Above 90 | Transformer (OH) | Broken | 24-0096508 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962472 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | S1949 | 20240806 | 1659 | 20240806 | 1846 | 2536087 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 749 | 37.7326 | -120.8895 | No | Clear;Above 90 |  |  | 24-0096545 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962491 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1102 | 254421102 | TRANSFORMER | 322504530158 | 20240806 | 1839 | 20240806 | 2100 | 2536174 | 141 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 564 | 37.3254 | -119.6392 | No | Clear;Above 90 | Service conductor | Broken | 24-0096569 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962511 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 318870145703 | 20240806 | 1919 | 20240806 | 2245 | 2535858 | 206 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 206 | 37.7567 | -120.8916 | No | Clear;Above 90 | Secondary | Broken | 24-0096558 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962504 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | FUSE | 6592 | 20240806 | 2156 | 20240807 | 653 | 2536260 | 537 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1110 | 36.9381 | -120.1823 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0096589 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962539 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | TRANSFORMER | 319659013897 | 20240806 | 2227 | 20240807 | 350 | 2536234 | 323 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 646 | 36.8817 | -120.6177 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0096577 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962522 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320825849114 | 20240807 | 325 | 20240807 | 340 | 2536136 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 135 | 37.8488 | -120.2151 | No | Clear;Above 90 | Secondary | Burned/flashed | 24-0096592 | OH | Sus | 31703415 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962542 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320785556540 | 20240807 | 914 | 20240807 | 1002 | 2536599 | 48 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 3 | 144 | 38.0525 | -120.2285 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0096718 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962706 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 318873945032 | 20240807 | 915 | 20240807 | 1400 | 2536587 | 285 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 285 | 37.736 | -120.8909 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0096711 | OH | Sus | 31703725 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962702 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 6868 | 20240807 | 1154 | 20240807 | 1258 | 2536736 | 64 | Distribution Circuit | Animal | Bird found | 27 | 1728 | 36.9614 | -120.0591 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0096818 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962744 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | FUSE | 4836 | 20240807 | 1847 | 20240807 | 2202 | 2537062 | 195 | Distribution Circuit | Company Initiated | Coordination failure | 197 | 38442 | 37.3222 | -120.4603 | No | Clear;Above 90 | Fuse | Normal | 24-0097018 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1962818 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 892403 | 20240807 | 2105 | 20240807 | 2318 | 2537158 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3325 | 37.2753 | -120.343 | No | Clear;Above 90 |  |  | 24-0097037 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1962830 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 20133 | 20240807 | 2307 | 20240808 | 1409 | 2537223 | 902 | Distribution Circuit | 3rd Party | Vehicle | 62 | 13544 | 37.7519 | -120.8399 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0097043 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1962836 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 7903 | 20240808 | 833 | 20240808 | 1059 | 2537445 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 584 | 37.5647 | -120.437 | No | Clear;32-90 F |  |  | 24-0097209 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1963014 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319312529500 | 20240808 | 943 | 20240808 | 1430 | 2537363 | 287 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 287 | 37.3095 | -120.7377 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0097189 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963006 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322821327066 | 20240808 | 1031 | 20240808 | 1059 | 2537619 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 84 | 37.2437 | -119.5333 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0097195 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963007 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 1103/2 | 20240808 | 1107 | 20240808 | 1135 | 2537671 | 28 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1113 | 31164 | 37.2537 | -119.5192 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0097224 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1963017 | 0 | EPSS Ckt | Y | 2024 | AC- ISNT OC
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10330 | 20240808 | 1438 | 20240808 | 1533 | 2538005 | 55 | Distribution Circuit | Company Initiated | Operating error | 1534 | 66722 | 37.2507 | -119.5619 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0097346 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963051 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 20240809 | 323 | 20240810 | 955 | 2538420 | 1832 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 37 | 67784 | 37.9718 | -120.2261 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0097490 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963138 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319176122360 | 20240809 | 829 | 20240809 | 842 | 2538446 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 13 | 37.1135 | -120.7833 | No | Clear;32-90 F | Fuse | Broken | 24-0097573 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963232 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 8818 | 20240809 | 1813 | 20240809 | 1930 | 2538999 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 360 | 37.1859 | -120.5533 | No | Clear;Above 90 |  |  | 24-0097899 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963359 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321189044483 | 20240810 | 140 | 20240810 | 1136 | 2539126 | 596 | Transformer only | Vegetation | Tree - fell into line | 3 | 1788 | 37.7226 | -120.09 | No | Clear;Above 90 | Transformer (OH) | Broken | 24-0097948 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963397 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319880330229 | 20240810 | 1805 | 20240810 | 1904 | 2539551 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 413 | 37.3308 | -120.5408 | No | Clear;Above 90 | Transformer (OH) | Leaking | 24-0098028 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963484 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 196877 | 20240810 | 1946 | 20240810 | 2047 | 2539596 | 61 | Distribution Circuit | Animal | Bird found | 2 | 122 | 36.8498 | -120.0007 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0098038 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963497 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | 9817 | 20240810 | 2132 | 20240811 | 40 | 2539619 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2632 | 37.9659 | -120.3136 | No | Clear;32-90 F |  |  | 24-0098042 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1963503 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1102 | 252091102 | TRANSFORMER | T1995 | 20240811 | 1232 | 20240812 | 117 | 2539787 | 765 | Distribution Circuit | Equipment Failure/Involved | Underground | 118 | 12930 | 37.0769 | -120.8409 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0098087 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963557 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | FUSE | 5303 | 20240811 | 1923 | 20240811 | 2024 | 2539888 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 183 | 36.9603 | -120.117 | No | Clear;Above 90 |  |  | 24-0098113 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1963575 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 7713 | 20240811 | 2031 | 20240811 | 2233 | 2539925 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1464 | 37.2287 | -120.2254 | No | Clear;32-90 F |  |  | 24-0098120 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1963577 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319539030942 | 20240812 | 1 | 20240812 | 11 | 2539943 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 10 | 37.3494 | -120.6594 | No | Clear;32-90 F | Fuse | Broken | 24-0098124 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963580 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 23167 | 20240812 | 724 | 20240812 | 826 | 2540086 | 62 | Distribution Circuit | Company Initiated | Improper Construction | 730 | 32156 | 36.8681 | -120.4632 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0091494 | UG | Sus | 35467346 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1963605 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 3132 | 20240812 | 751 | 20240812 | 1131 | 2540090 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2641 | 37.099 | -120.7776 | No | Clear;32-90 F |  |  | 24-0098275 | OH | Sus | 31704503 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963759 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | S1957 | 20240812 | 815 | 20240812 | 1437 | 2540136 | 293 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 6276 | 37.7994 | -120.9875 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0098179 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963653 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | SWITCH | 12116 | 20240812 | 939 | 20240812 | 947 | 2540295 | 8 | Distribution Circuit | Company Initiated | Improper Construction | 79 | 632 | 36.8674 | -120.4573 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0098220 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963731 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 13002 | 20240812 | 1209 | 20240812 | 1350 | 2540412 | 101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 606 | 37.0548 | -120.2658 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0098308 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963773 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 8941 | 20240812 | 1224 | 20240812 | 1508 | 2540440 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2788 | 37.5365 | -121.2431 | No | Clear;32-90 F |  |  | 24-0098467 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1963808 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10604 | 20240812 | 1500 | 20240812 | 2003 | 2540535 | 303 | Distribution Circuit | Equipment Failure/Involved | Underground | 37 | 11211 | 37.3141 | -119.634 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0098359 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963804 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 100000024852 | 20240812 | 1520 | 20240812 | 1542 | 2540528 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 22 | 37.7586 | -121.0327 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0098491 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1963813 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 28096 | 20240812 | 1845 | 20240812 | 2156 | 2540525 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 401 | 37.7848 | -120.8401 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0098543 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963826 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | JUMPER | FB S/OF CGC 320898521029 | 20240812 | 2110 | 20240812 | 2259 | 2540785 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 11881 | 37.0769 | -120.193 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0098514 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963845 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320239852926 | 20240813 | 701 | 20240813 | 843 | 2540893 | 102 | Transformer only | 3rd Party | Other | 5 | 510 | 37.9535 | -120.418 | No | Clear;32-90 F | Customer Equipment | Arcing | 24-0098692 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964034 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1645 | 20240813 | 744 | 20240813 | 1013 | 2540902 | 149 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 8940 | 37.8202 | -120.6777 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0098627 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963886 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11615 | 20240813 | 1050 | 20240813 | 1336 | 2541193 | 166 | Distribution Circuit | 3rd Party | Other | 7 | 1162 | 37.2328 | -120.3386 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0098813 | OH | Sus | 31704959 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1964068 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 6893 | 20240813 | 1051 | 20240813 | 1435 | 2541196 | 224 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2240 | 36.9133 | -119.867 | No | Clear;32-90 F |  |  | 24-0098960 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1964118 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | JUMPER | JPRS 3 W/OF CGC 320664020399 | 20240813 | 1144 | 20240813 | 1248 | 2541226 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 128 | 37.0601 | -120.2742 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0098819 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964070 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 4789 | 20240813 | 1338 | 20240813 | 2218 | 2541352 | 520 | Distribution Circuit | 3rd Party | Vehicle | 21 | 10920 | 37.5189 | -120.588 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0099022 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1964131 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | S1263 | 20240813 | 1349 | 20240813 | 1535 | 2541360 | 106 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 2968 | 37.7965 | -121.0052 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0098796 | UG | Sus | 35573606 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964107 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | TRANSFORMER | 320512324832 | 20240813 | 1520 | 20240814 | 105 | 2541563 | 585 | Transformer only | Environmental/External | Fire- Forest/Grass | 4 | 2340 | 37.1822 | -120.3255 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0099077 | OH | Sus | 31705089 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964145 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | SWITCH | 12288 | 20240813 | 1649 | 20240813 | 2131 | 2541496 | 282 | Distribution Circuit | 3rd Party | Other | 7 | 1974 | 36.913 | -120.0077 | No | Clear;Above 90 | Pole-Wood | Burned/flashed | 24-0099039 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964133 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | OTHER | WIRE DOWN | 20240813 | 2131 | 20240814 | 501 | 2541672 | 450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5419 | 36.7289 | -120.3149 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0099113 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1964171 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | SWITCH | 146563 | 20240814 | 747 | 20240814 | 755 | 2541740 | 8 | Distribution Circuit | Animal | Other | 45 | 360 | 37.3652 | -119.6975 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0099167 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964200 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1321 | 20240814 | 1121 | 20240814 | 1231 | 2541972 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 2170 | 37.7953 | -120.1228 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0099244 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964346 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 321068047882 | 20240814 | 1129 | 20240814 | 1505 | 2542090 | 216 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 432 | 37.8142 | -120.131 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0099288 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964378 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | JUMPER | OJ 4 POLES N/OF MTR#1005460879 | 20240814 | 1733 | 20240814 | 2202 | 2542342 | 269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 807 | 37.3253 | -120.619 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0099478 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964437 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1101 | 252531101 | TRANSFORMER | 322801629724 | 20240814 | 1824 | 20240814 | 1856 | 2542430 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 128 | 37.3133 | -119.5383 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0099497 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964443 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 9788 | 20240814 | 2021 | 20240814 | 2234 | 2542564 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 931 | 36.9766 | -120.8372 | No | Clear;32-90 F |  |  | 24-0099524 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1964465 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2104 | 255292104 | FUSE | 6734 | 20240814 | 2340 | 20240815 | 1226 | 2542647 | 766 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 25440 | 36.9559 | -119.7446 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0099536 | UG | Sus | 46299521 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964473 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320382555837 | 20240815 | 1000 | 20240815 | 1033 | 2542867 | 33 | Transformer only | 3rd Party | Customer Equipment | 2 | 66 | 38.0333 | -120.3681 | No | Clear;32-90 F | Other | Deteriorated | 24-0099617 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964540 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320773155703 | 20240815 | 1526 | 20240815 | 1551 | 2543095 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 75 | 38.0295 | -120.233 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0099780 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964579 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319778128556 | 20240816 | 641 | 20240816 | 856 | 2543403 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 675 | 37.2841 | -120.5765 | No | Clear;32-90 F | Fuse | Broken | 24-0099937 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964764 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | TRANSFORMER | 319048047210 | 20240816 | 827 | 20240816 | 1150 | 2543504 | 203 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 203 | 37.7961 | -120.8302 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0099926 | OH | Sus | 31705315 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964746 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 321093847255 | 20240816 | 1030 | 20240816 | 1058 | 2543637 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 37.7971 | -120.1223 | No | Clear;32-90 F | Secondary | Broken | 24-0099963 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964788 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319747328691 | 20240816 | 1154 | 20240816 | 1740 | 2543707 | 346 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 346 | 37.2877 | -120.588 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0100064 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964824 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L1413 | 20240816 | 1326 | 20240816 | 1730 | 2543780 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 1972 | 38.0595 | -120.3823 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0100112 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1964846 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 26367 | 20240816 | 1647 | 20240816 | 2051 | 2543970 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 732 | 38.0113 | -120.419 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0100172 | OH | Sus | 31705462 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1964868 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | TRANSFORMER | 321320216574 | 20240816 | 2058 | 20240817 | 431 | 2544054 | 453 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 8607 | 36.9546 | -120.0493 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 24-0100193 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1964883 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | RECLOSER | 90600 | 20240816 | 2241 | 20240817 | 10 | 2544082 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 105 | 9345 | 37.3618 | -121.0763 | No | Clear;32-90 F |  |  | 24-0100205 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1964896 | 0 | EPSS Ckt | N | 2024 | A- B
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20240817 | 42 | 20240817 | 627 | 2544096 | 345 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 480 | 68928 | 37.4305 | -120.0996 | No | Clear;32-90 F |  |  | 24-0100208 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1964900 | 0 | EPSS Ckt | Y | 2024 | A- C
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRANSFORMER | 322610529243 | 20240817 | 1341 | 20240817 | 1410 | 2544384 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 29 | 37.3001 | -119.6033 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0100279 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1964985 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | 27430 | 20240817 | 1727 | 20240817 | 1837 | 2544519 | 70 | Distribution Circuit | 3rd Party | Metallic Balloon | 58 | 4060 | 37.7355 | -120.9361 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100318 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965010 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319761430327 | 20240817 | 1910 | 20240817 | 2030 | 2544548 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 240 | 37.3331 | -120.582 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0100322 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965014 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 2177 | 20240817 | 2114 | 20240817 | 2236 | 2544614 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 547 | 37.0549 | -120.6718 | No | Clear;32-90 F |  |  | 24-0100338 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965030 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | TRANSFORMER | 319621219909 | 20240818 | 639 | 20240818 | 1139 | 2544672 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1800 | 37.0465 | -120.6303 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0100355 | OH | Sus | 31705521 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965049 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 88398 | 20240818 | 937 | 20240818 | 1130 | 2544736 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 3051 | 37.0183 | -120.1841 | No | Clear;32-90 F |  |  | 24-0100378 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965076 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320174153400 | 20240818 | 1140 | 20240818 | 1321 | 2544763 | 101 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 101 | 37.9673 | -120.4406 | No | Clear;32-90 F | Fuse | Broken | 24-0100397 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965088 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 6029 | 20240818 | 1820 | 20240819 | 335 | 2544893 | 555 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 1665 | 36.9026 | -119.7923 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0100420 | OH | Sus | 31705566 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965111 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 6225 | 20240818 | 1939 | 20240818 | 2100 | 2544914 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 324 | 36.8947 | -119.8108 | No | Clear;32-90 F |  |  | 24-0100435 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965125 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 6055 | 20240818 | 2144 | 20240818 | 2158 | 2544942 | 14 | Distribution Circuit | 3rd Party | Vehicle | 58 | 812 | 36.9522 | -120.0739 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0100410 | OH | Sus | 35575124 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965127 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | SWITCH | 2563 | 20240819 | 301 | 20240819 | 307 | -2544942 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 58 | 348 | 36.9527 | -120.079 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0100410 | OH | Sus | 35575124 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965135 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 6276 | 20240819 | 753 | 20240819 | 1355 | 2545060 | 362 | Distribution Circuit | Animal | Bird found | 2 | 724 | 36.8638 | -119.9561 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 24-0100512 | OH | Sus | 31705532 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965265 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318775531289 | 20240819 | 838 | 20240819 | 1359 | 2545168 | 321 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 321 | 37.3561 | -120.924 | No | Clear;32-90 F | Crossarm- Wood | Normal | 24-0100601 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965315 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321087015711 | 20240819 | 847 | 20240819 | 1530 | 2545198 | 403 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 403 | 36.9308 | -120.1284 | No | Clear;32-90 F | Service conductor | Broken | 24-0100516 | OH | Sus | 31705641 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965273 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | TRANSFORMER | 319883332024 | 20240819 | 939 | 20240819 | 1040 | 2545337 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 61 | 37.3795 | -120.5406 | No | Clear;32-90 F |  |  | 24-0100551 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1965294 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | TRANSFORMER | 318801130662 | 20240819 | 957 | 20240819 | 1430 | 2545412 | 273 | Transformer only | 3rd Party | Dig in- 3rd party | 1 | 273 | 37.3389 | -120.9147 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0100584 | UG | Sus | 46300858 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965306 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | SWITCH | 9129 | 20240819 | 1247 | 20240819 | 1326 | 2545539 | 39 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 272 | 10608 | 37.491 | -120.5612 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0100582 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965329 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 3132 | 20240819 | 1928 | 20240819 | 2145 | 2545910 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2466 | 37.099 | -120.7776 | No | Clear;32-90 F |  |  | 24-0100816 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965395 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321493220942 | 20240820 | 653 | 20240820 | 1104 | 2546160 | 251 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 251 | 37.0746 | -119.9894 | No | Clear;32-90 F | Secondary | Broken | 24-0100887 | OH | Sus | 46302199 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965500 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | OCB | 1108/2 | 20240820 | 907 | 20240820 | 1527 | 2546252 | 380 | Distribution Circuit | 3rd Party | Vehicle | 1765 | 99956 | 37.36 | -120.6145 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0100924 | OH | Sus | 35575601 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965561 | 0 | Non-EPSS | N | 2024 | B&C INSTANT OC
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 2381 | 20240820 | 1016 | 20240820 | 1103 | 2546347 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 627 | 37.8293 | -121.0249 | No | Clear;32-90 F |  |  | 24-0100983 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965605 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318848946293 | 20240820 | 1426 | 20240820 | 1648 | 2546597 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 426 | 37.7707 | -120.8993 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0101134 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965652 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9519 | 20240820 | 1752 | 20240820 | 2208 | 2546739 | 256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 11729 | 36.7518 | -120.3846 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0101231 | OH | Sus | 46303061 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1965686 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | JUMPER | OJ 1SP N/OF CGC #319739630336 | 20240820 | 1840 | 20240820 | 2258 | 2546684 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2580 | 37.334 | -120.589 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0101184 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1965666 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | TRANSFORMER | 319550516794 | 20240820 | 2320 | 20240821 | 159 | 2546717 | 159 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1590 | 36.9612 | -120.6553 | No | Clear;32-90 F | Secondary | Broken | 24-0101206 | OH | Sus | 31705651 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965673 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | RECLOSER | 562202 | 20240821 | 6 | 20240821 | 547 | 2546843 | 341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 665 | 102499 | 37.2435 | -121.0128 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0101247 | OH | Sus | 31705980 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1965710 | 0 | EPSS Ckt | N | 2024 | A- B
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | FUSE | 1527 | 20240821 | 329 | 20240821 | 1127 | 2546869 | 478 | Distribution Circuit | Equipment Failure/Involved | Underground | 66 | 31548 | 37.2794 | -120.4402 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0101253 | UG | Sus | 35575729 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965721 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 9648 | 20240821 | 448 | 20240821 | 1112 | 2546878 | 381 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2667 | 36.7753 | -120.2882 | No | Clear;32-90 F |  |  | 24-0101411 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965924 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | TRANSFORMER | T109229 | 20240821 | 520 | 20240821 | 723 | 2546877 | 123 | Transformer only | 3rd Party | Fire- house or bldg. | 21 | 2583 | 37.3636 | -120.5832 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0101258 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1965725 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 6225 | 20240821 | 605 | 20240821 | 744 | 2546900 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 396 | 36.8947 | -119.8108 | No | Partly Cloudy;32-90 F |  |  | 24-0101288 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965755 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | RECLOSER | 999258 | 20240821 | 635 | 20240821 | 1000 | 2546916 | 205 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 5125 | 37.1542 | -121.0608 | No | Clear;32-90 F |  |  | 24-0101270 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965739 | 0 | EPSS Ckt | Y | 2024 | B- C- INST
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 6704 | 20240821 | 642 | 20240821 | 1137 | 2546917 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1530 | 36.8811 | -120.2732 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0101324 | OH | Sus | 31705653 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965835 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 6060 | 20240821 | 1245 | 20240821 | 1501 | 2547321 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2631 | 183376 | 37.9892 | -120.3332 | No | Clear;32-90 F |  |  | 24-0101479 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965939 | 0 | EPSS Ckt | Y | 2024 | A- B- DCD
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | OTHER | T8737 TWD T8738 | 20240821 | 1509 | 20240821 | 1603 | 2547429 | 54 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 1512 | 37.3216 | -121.0074 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0101491 | UG | Sus | 35575796 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1965962 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 28139 | 20240821 | 1644 | 20240821 | 1743 | 2547562 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 177 | 37.7917 | -120.8641 | No | Clear;32-90 F |  |  | 24-0101651 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965977 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 13005 | 20240821 | 1828 | 20240821 | 2308 | 2547582 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2216 | 37.0474 | -120.2566 | No | Clear;32-90 F | PGs- Kearneys | Arcing | 24-0101682 | OH | Sus | 46303351 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1965986 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | FUSE | S2233 | 20240822 | 52 | 20240822 | 319 | 2547714 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 735 | 37.7692 | -120.9133 | No | Clear;32-90 F |  |  | 24-0101718 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1966022 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320266654259 | 20240822 | 315 | 20240822 | 436 | 2547744 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 243 | 37.9903 | -120.4085 | No | Clear;32-90 F | Fuse | Broken | 24-0101725 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966030 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | INTERRUPTER | 14340 | 20240822 | 449 | 20240822 | 922 | 2547751 | 189 | Distribution Circuit | Equipment Failure/Involved | Underground | 465 | 60122 | 37.3194 | -120.4916 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0101723 | UG | Sus | 46303622 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1966028 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 4832 | 20240822 | 806 | 20240822 | 1332 | 2548021 | 326 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 652 | 37.2806 | -120.4403 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0101853 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1966176 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | OCB | 1109/2 | 20240822 | 1017 | 20240822 | 1028 | 2548043 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 289 | 3179 | 37.0551 | -120.3168 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 24-0101870 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966187 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | FUSE | 23173 | 20240822 | 1210 | 20240822 | 1426 | 2548150 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1192 | 36.8828 | -120.4916 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0101883 | OH | Sus | 31705725 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966217 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | OCB | 1103/2 | 20240822 | 1237 | 20240822 | 1358 | 2548198 | 81 | Distribution Circuit | 3rd Party | Vehicle | 1033 | 83673 | 37.5792 | -121.2057 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0101962 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966224 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | SWITCH | 1919 | 20240822 | 1407 | 20240822 | 1523 | 2548372 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 1907 | 87049 | 37.3198 | -120.497 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0101723 | UG | Sus | 46303622 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966254 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | RECLOSER | 7080 | 20240822 | 1610 | 20240822 | 2011 | 2548469 | 241 | Distribution Circuit | 3rd Party | Vehicle | 431 | 87582 | 37.3272 | -120.6145 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0102110 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1966266 | 0 | Non-EPSS | N | 2024 | BC
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRIP-SAVER | 22774 | 20240822 | 2008 | 20240822 | 2026 | 2548631 | 18 | Distribution Circuit | Animal | Other | 85 | 1530 | 37.5883 | -120.2764 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102185 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966298 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 26769 | 20240822 | 2057 | 20240822 | 2200 | 2548650 | 63 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 189 | 37.7836 | -120.8657 | No | Clear;32-90 F | Insulator | Broken | 24-0102192 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966305 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 2001 | 20240822 | 2125 | 20240822 | 2330 | 2548690 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 875 | 37.5827 | -121.2098 | No | Clear;32-90 F |  |  | 24-0102215 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966332 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320422554207 | 20240822 | 2332 | 20240823 | 728 | 2548743 | 476 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 952 | 37.9892 | -120.3548 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0102216 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966335 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | FUSE | 3749 | 20240823 | 339 | 20240823 | 816 | 2548823 | 277 | Distribution Circuit | 3rd Party | Vehicle | 712 | 31696 | 37.0759 | -120.7464 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0102220 | OH | Sus | 31706148 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | Yes | No | 1966344 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | 20013 | 20240823 | 635 | 20240823 | 1002 | 2548839 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2070 | 37.8323 | -120.4867 | No | Partly Cloudy;32-90 F |  |  | 24-0102261 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1966364 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 90090 | 20240823 | 730 | 20240823 | 1159 | 2548864 | 269 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2694 | 724686 | 37.9028 | -120.4538 | No | Partly Cloudy;32-90 F |  |  | 24-0102252 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966357 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | TRANSFORMER | 321253918889 | 20240823 | 1133 | 20240823 | 1445 | 2549306 | 192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 192 | 37.0181 | -120.0717 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0102571 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966572 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 320062348100 | 20240823 | 1400 | 20240823 | 1500 | 2549328 | 60 | Transformer only | Animal | Bird found | 1 | 60 | 37.8179 | -120.4762 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0102580 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966576 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | OCB | 1119/2 | 20240824 | 46 | 20240824 | 1351 | 2549586 | 785 | Distribution Circuit | 3rd Party | Vehicle | 1527 | 525471 | 36.9232 | -120.0551 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0102675 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966608 | 0 | Non-EPSS | N | 2024 | C GRD
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320269854810 | 20240824 | 1057 | 20240824 | 1137 | 2550120 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 40 | 38.0049 | -120.4074 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0102765 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966707 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 26855 | 20240824 | 1644 | 20240824 | 1915 | 2550342 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 151 | 37.0573 | -120.5287 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0102816 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966747 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318260830819 | 20240825 | 843 | 20240825 | 948 | 2550783 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 65 | 37.3444 | -121.0988 | No | Clear;32-90 F | Fuse | Burned Open | 24-0102899 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1966854 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 13239 | 20240825 | 1447 | 20240825 | 1631 | 2550883 | 104 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 104 | 36.9744 | -120.0386 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0102915 | UG | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1966872 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 19299 | 20240826 | 247 | 20240826 | 521 | 2551076 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 8624 | 37.013 | -119.9651 | No | Clear;32-90 F |  |  | 24-0102966 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1966919 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 24349 | 20240826 | 452 | 20240826 | 624 | 2551086 | 92 | Distribution Circuit | 3rd Party | Vehicle | 19 | 1748 | 37.2312 | -121.0308 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102975 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1966925 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | FUSE | 3927 | 20240826 | 752 | 20240826 | 952 | 2551142 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2001 | 37.1587 | -121.0096 | No | Clear;32-90 F |  |  | 24-0103086 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967114 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321779715463 | 20240826 | 814 | 20240826 | 1040 | 2551201 | 146 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 584 | 36.9225 | -119.8925 | No | Clear;32-90 F | Secondary | Broken | 24-0103062 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967088 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | RECLOSER | 4350 | 20240826 | 824 | 20240826 | 1347 | 2551232 | 323 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 252 | 34904 | 37.4183 | -120.5938 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0103035 | OH | Sus | 31706457 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1967053 | 0 | Non-EPSS | N | 2024 | A- B- C
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | JUMPER | OJ'S 2 S/OF CGC# 320265254935 | 20240826 | 914 | 20240826 | 952 | 2551310 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 114 | 38.0075 | -120.4094 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0103044 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967070 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | TRANSFORMER | 320941116443 | 20240826 | 1258 | 20240826 | 1412 | 2551619 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 222 | 36.9518 | -120.1789 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0103183 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967161 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | RECLOSER | 36934 | 20240826 | 1442 | 20240827 | 149 | 2551740 | 667 | Distribution Circuit | Equipment Failure/Involved | Overhead | 632 | 63612 | 36.8579 | -120.4545 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0103244 | OH | Sus | 46305409 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1967185 | 0 | Non-EPSS | N | 2024 | B- C
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 10030 | 20240826 | 1524 | 20240826 | 1814 | 2551788 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 453 | 77010 | 37.2234 | -119.7689 | No | Clear;32-90 F |  |  | 24-0103279 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967193 | 0 | EPSS Ckt | Y | 2024 | GRD
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321947136577 | 20240826 | 1633 | 20240826 | 1720 | 2551847 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 47 | 37.5028 | -119.83 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0103306 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967200 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320583955381 | 20240826 | 1654 | 20240826 | 2236 | 2551867 | 342 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1026 | 38.0205 | -120.2982 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0103333 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967213 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | FUSE | 9666 | 20240826 | 2313 | 20240826 | 2331 | 2552088 | 18 | Distribution Circuit | 3rd Party | Kite | 81 | 1458 | 36.8723 | -120.4742 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103382 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967242 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 9802 | 20240827 | 232 | 20240827 | 506 | 2552128 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 383 | 58982 | 36.8629 | -120.4583 | No | Clear;32-90 F |  |  | 24-0103400 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1967256 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | RECLOSER | 48236 | 20240827 | 731 | 20240827 | 1201 | 2552186 | 270 | Distribution Circuit | 3rd Party | Vehicle | 398 | 24555 | 37.3099 | -120.3741 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0103431 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967277 | 0 | EPSS Ckt | N | 2024 | NA
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 905960 | 20240827 | 814 | 20240827 | 1057 | 2552293 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2629 | 426352 | 37.2274 | -119.7103 | No | Clear;32-90 F |  |  | 24-0103455 | OH | Sus | 46305776 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967345 | 0 | EPSS Ckt | Y | 2024 | GRD
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | T4098 | 20240827 | 1343 | 20240827 | 1940 | 2552753 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 357 | 36.9853 | -120.6216 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0103690 | OH | Sus | 31706597 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967548 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | SWITCH | 22962 | 20240827 | 1752 | 20240827 | 1847 | s1981785 | 55 | Distribution Circuit | Company Initiated | Return Circuit Normal | 198 | 7004 | 37.3265 | -120.4637 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Normal | 24-0090993 | UG | Sus | 35568179 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1981785 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9280 | 20240827 | 2220 | 20240828 | 30 | 2553225 | 130 | Distribution Circuit | Animal | Squirrel | 1536 | 127606 | 38.1994 | -120.0195 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0103812 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1967604 | 0 | EPSS Ckt | Y | 2024 | AB
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | TRANSFORMER | 318920121663 | 20240827 | 2244 | 20240827 | 2316 | 2553131 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 32 | 37.0939 | -120.8713 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0103828 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967616 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 25042 | 20240828 | 1034 | 20240828 | 1159 | 2553738 | 85 | Distribution Circuit | Animal | Bird found | 14 | 1190 | 37.7857 | -120.9964 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0104084 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1967862 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRANSFORMER | 322589629047 | 20240828 | 1157 | 20240828 | 1304 | 2553814 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 201 | 37.2946 | -119.6123 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0104101 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967868 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | JUMPER | OJ 3 E/OF 9602 TWD SOUTH | 20240828 | 1552 | 20240828 | 1715 | 2554032 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 498 | 37.0057 | -120.8856 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0104305 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1967921 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | SWITCH | 19986 | 20240828 | 1749 | 20240828 | 1910 | 2554236 | 81 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 81 | 36.8485 | -120.7578 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 24-0104411 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967951 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 196877 | 20240828 | 1850 | 20240828 | 2055 | 2554273 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 250 | 36.8498 | -120.0007 | No | Clear;32-90 F |  |  | 24-0104441 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1967973 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | FUSE | 3594 | 20240829 | 438 | 20240829 | 508 | 2554431 | 30 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 16 | 480 | 37.0547 | -120.867 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0104465 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1967989 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318622847117 | 20240829 | 707 | 20240829 | 845 | 2554482 | 98 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 196 | 37.7928 | -120.9773 | No | Clear;32-90 F | Other | Failed/Faulted | 24-0104575 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968121 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | T4098 | 20240829 | 910 | 20240829 | 1045 | 2554467 | 95 | Transformer only | Equipment Failure/Involved | Underground | 1 | 95 | 36.9853 | -120.6216 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0104585 | UG | Sus | 46306276 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968169 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 21039 | 20240829 | 919 | 20240829 | 1100 | 2554719 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2287 | 36.9228 | -119.8719 | No | Clear;32-90 F |  |  | 24-0104689 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968224 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320436037205 | 20240829 | 1229 | 20240829 | 1719 | 2555031 | 290 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 870 | 37.5224 | -120.3495 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0104822 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1968265 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 731524 | 20240829 | 1326 | 20240829 | 1525 | 2555073 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 792 | 40059 | 37.155 | -119.7343 | No | Clear;Above 90 |  |  | 24-0104790 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968259 | 0 | EPSS Ckt | Y | 2024 | B
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 550083 | 20240829 | 1741 | 20240829 | 2209 | 2555330 | 268 | Distribution Circuit | 3rd Party | Vehicle | 8 | 2144 | 37.3692 | -120.6774 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0105020 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1968292 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9570 | 20240829 | 1923 | 20240829 | 2210 | 2555378 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 513 | 78651 | 37.7155 | -120.2024 | No | Clear;32-90 F |  |  | 24-0105032 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1968299 | 0 | EPSS Ckt | Y | 2024 | A&B INSTANT
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | RECLOSER | 9020 | 20240829 | 2003 | 20240830 | 529 | 2555403 | 566 | Distribution Circuit | 3rd Party | Vehicle | 1143 | 121872 | 37.7627 | -120.9789 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105039 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1968307 | 0 | Non-EPSS | N | 2024 | B&C
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | OCB | 1103/2 | 20240830 | 513 | 20240830 | 1210 | 2555579 | 417 | Distribution Circuit | 3rd Party | Vehicle | 674 | 82818 | 36.9221 | -119.9845 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0105081 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1968356 | 0 | Non-EPSS | N | 2024 | A&B
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 4714 | 20240830 | 606 | 20240830 | 846 | 2555594 | 160 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 1280 | 37.3332 | -120.3785 | No | Clear;32-90 F |  |  | 24-0105176 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1968449 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | 4151 | 20240830 | 755 | 20240830 | 1607 | 2555641 | 492 | Distribution Circuit | 3rd Party | Vehicle | 35 | 10488 | 37.7327 | -120.894 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105150 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | Yes | No | 1968420 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | OTHER | T8232 TWD T8233 | 20240830 | 1128 | 20240830 | 1200 | 2555916 | 32 | Distribution Circuit | Equipment Failure/Involved | Underground | 32 | 1024 | 37.3049 | -121.0319 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0105227 | UG | Sus | 35577943 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1968517 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | JUMPER | OJ @ CGC 320302130298 | 20240830 | 1131 | 20240830 | 1205 | 2555918 | 34 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 68 | 37.3321 | -120.396 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0105274 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1968518 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 2381 | 20240830 | 1257 | 20240830 | 1350 | 2555988 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 707 | 37.8293 | -121.0249 | No | Clear;32-90 F | Insulator | Arcing | 24-0105397 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968549 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319939229086 | 20240830 | 1607 | 20240830 | 1941 | 2556109 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 642 | 37.2992 | -120.5208 | No | Clear;Above 90 | Transformer (OH) | Burned/flashed | 24-0105468 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968569 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | SWITCH | 3405 | 20240830 | 2217 | 20240830 | 2315 | 2556289 | 58 | Distribution Circuit | 3rd Party | Vehicle | 47 | 2726 | 37.8288 | -120.9609 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0105518 | OH | Sus | 0 | CENTRAL VALLEY | AUG | None | 0 | No | No | No | 1968593 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 350427 | 20240831 | 610 | 20240831 | 811 | 2556347 | 121 | Distribution Circuit | Animal | Bird found | 15 | 1815 | 38.0008 | -120.3126 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105540 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1968613 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 7873 | 20240831 | 839 | 20240831 | 946 | 2556393 | 67 | Distribution Circuit | Animal | Bird found | 31 | 2100 | 37.3336 | -120.5994 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105558 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1968635 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 2381 | 20240831 | 1016 | 20240831 | 1130 | 2556428 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 1480 | 37.8293 | -121.0249 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0105565 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1968638 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 20617 | 20240831 | 1436 | 20240831 | 1618 | 2556567 | 102 | Distribution Circuit | Animal | Bird found | 17 | 1734 | 37.9983 | -120.3154 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0105609 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1968665 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 9502 | 20240901 | 541 | 20240901 | 725 | 2557002 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1352 | 36.9973 | -120.6177 | No | Clear;32-90 F |  |  | 24-0105662 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1968705 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 25042 | 20240901 | 852 | 20240901 | 903 | 2557085 | 11 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 104 | 1144 | 37.7857 | -120.9964 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105686 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968726 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1111 | 252421111 | TRANSFORMER | 320445122050 | 20240901 | 928 | 20240901 | 1210 | 2557100 | 162 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 324 | 37.1053 | -120.3476 | No | Clear;32-90 F |  |  | 24-0105704 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1968740 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | FUSE | 6229 | 20240901 | 946 | 20240901 | 1125 | 2557103 | 99 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 53 | 5247 | 37.1245 | -120.2711 | No | Clear;32-90 F |  |  | 24-0105697 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1968733 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 23266 | 20240901 | 1123 | 20240901 | 1825 | 2557138 | 422 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 30 | 12660 | 37.2105 | -119.692 | No | Clear;32-90 F | Insulator | Failed/Faulted | 24-0105702 | OH | Sus | 31707161 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1968738 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10040 | 20240901 | 1524 | 20240901 | 1825 | 2557203 | 180 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 939 | 45582 | 37.3104 | -119.5846 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0105717 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1968750 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 25042 | 20240901 | 1811 | 20240901 | 1838 | 2557255 | 27 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 69 | 1873 | 37.7857 | -120.9964 | No | Clear;32-90 F |  |  | 24-0105735 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968765 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1116 | 252761116 | FUSE | 6554 | 20240901 | 1821 | 20240901 | 1925 | 2557274 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 213 | 36.8803 | -120.0197 | No | Clear;Above 90 |  |  | 24-0105738 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968768 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | RECLOSER | 10800 | 20240902 | 405 | 20240902 | 2311 | 2557429 | 1146 | Distribution Circuit | 3rd Party | Vehicle | 239 | 159962 | 37.2974 | -121.0128 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105763 | OH | Sus | 31707147 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | Yes | No | 1968789 | 0 | Non-EPSS | N | 2024 | A-B-C & GRD
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319609034623 | 20240902 | 826 | 20240902 | 1020 | 2557480 | 114 | Transformer only | Animal | Bird found | 3 | 342 | 37.4506 | -120.635 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0105807 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968821 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20240902 | 1408 | 20240902 | 1740 | 2557651 | 212 | Distribution Circuit | Company Initiated | Coordination failure | 581 | 57043 | 38.0085 | -120.3034 | No | Clear;32-90 F | Recloser | Normal | 24-0105845 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968840 | 0 | EPSS Ckt | Y | 2024 | GROUND- INST OC
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L661 | 20240902 | 1410 | 20240903 | 636 | 2557652 | 986 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 9207 | 37.9862 | -120.2871 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0105858 | UG | Sus | 46307599 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968851 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1105 | 254611105 | TRANSFORMER | 321290417782 | 20240903 | 220 | 20240903 | 445 | 2557814 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 580 | 36.9878 | -120.0596 | No | Clear;32-90 F | Secondary | Broken | 24-0105875 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1968870 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 321502513902 | 20240903 | 528 | 20240903 | 737 | 2557825 | 129 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 258 | 36.8803 | -119.9881 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0105887 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1968884 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | S1331 | 20240903 | 1513 | 20240903 | 1806 | 2558575 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 123 | 21232 | 37.7941 | -120.986 | No | Clear;Above 90 |  |  | 24-0106328 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969154 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1102 | 254421102 | FUSE | 6492 | 20240903 | 1940 | 20240903 | 2011 | 2558746 | 31 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 155 | 37.3336 | -119.6634 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0106421 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1969176 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | L2097 | 20240903 | 2007 | 20240903 | 2032 | 2558709 | 25 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 92 | 2300 | 37.9672 | -120.2841 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106422 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1969177 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | OTHER | 6187 | 20240903 | 2341 | 20240904 | 1239 | 2558941 | 778 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 24043 | 37.1014 | -120.1929 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0106492 | OH | Sus | 46308466 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | Yes | 1969231 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 6742 | 20240904 | 414 | 20240904 | 1728 | 2558874 | 794 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4148 | 37.1561 | -120.1695 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0106582 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969376 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20240904 | 508 | 20240904 | 1206 | 2558879 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 1311 | 292492 | 38.0063 | -120.3474 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0106452 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1969209 | 0 | EPSS Ckt | Y | 2024 | A PH GRD
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320379038525 | 20240904 | 853 | 20240904 | 1056 | 2559107 | 123 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 123 | 37.5573 | -120.3703 | No | Clear;Above 90 | Lightning Arrestor | Failed/Faulted | 24-0106650 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969416 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 19398 | 20240904 | 1627 | 20240904 | 2020 | 2559585 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3961 | 37.3535 | -120.6163 | No | Clear;Above 90 | Secondary | Broken- wire on ground | 24-0106969 | OH | Sus | 46308771 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969510 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | TRANSFORMER | 323122524378 | 20240904 | 1643 | 20240904 | 1858 | 2559599 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 135 | 37.1654 | -119.4349 | No | Clear;Above 90 | Fuse | Burned Open | 24-0106987 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969520 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | RECLOSER | 8500 | 20240904 | 1648 | 20240905 | 140 | 2559605 | 532 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1235 | 245014 | 37.3185 | -120.4639 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0106937 | OH | Sus | 46308757 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1969498 | 0 | Non-EPSS | N | 2024 | A & B
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 21072 | 20240904 | 1717 | 20240904 | 2106 | 2559618 | 229 | Distribution Circuit | 3rd Party | Vehicle | 88 | 19807 | 37.3603 | -120.6867 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0106945 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1969500 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | FUSE | 8643 | 20240904 | 1720 | 20240904 | 2002 | 2559627 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 128 | 20736 | 37.3966 | -120.6145 | No | Clear;Above 90 |  |  | 24-0106980 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1969517 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 13122 | 20240904 | 1920 | 20240904 | 2025 | 2559721 | 65 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 37 | 2405 | 37.0093 | -119.8844 | No | Clear;Above 90 | Fuse | Failed/Faulted | 24-0107003 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969529 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 454432 | 20240905 | 625 | 20240905 | 930 | 2559825 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 137 | 25345 | 37.7487 | -120.1257 | No | Clear;32-90 F |  |  | 24-0107037 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1969557 | 0 | EPSS Ckt | Y | 2024 | B & C
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6852 | 20240905 | 714 | 20240905 | 911 | 2559854 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1015 | 37.04 | -120.0747 | No | Clear;32-90 F |  |  | 24-0107134 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969703 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 21449 | 20240905 | 733 | 20240905 | 1024 | 2559869 | 171 | Distribution Circuit | Animal | Bird found | 8 | 1368 | 37.9546 | -120.436 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0107182 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1969729 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320355919923 | 20240905 | 1132 | 20240905 | 1200 | 2560259 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 56 | 37.0469 | -120.3783 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0107223 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1969744 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 320072011727 | 20240905 | 1518 | 20240905 | 1940 | 2560517 | 262 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 524 | 36.8214 | -120.4762 | No | Clear;Above 90 | Secondary | Broken- wire on ground | 24-0107525 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1969803 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | OTHER | T8144 TWD T8142 | 20240905 | 1540 | 20240905 | 1832 | 2560459 | 172 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 5332 | 36.9844 | -120.0439 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0107320 | UG | Sus | 35579214 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1969792 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 3186 | 20240906 | 26 | 20240906 | 328 | 2560720 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1423 | 258986 | 37.8624 | -120.2266 | No | Clear;32-90 F |  |  | 24-0107634 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1969856 | 0 | EPSS Ckt | Y | 2024 | A & B
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3377 | 20240906 | 743 | 20240906 | 935 | 2560984 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 112 | 36.9855 | -120.6254 | No | Clear;32-90 F |  |  | 24-0107777 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970013 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318364046445 | 20240906 | 827 | 20240906 | 956 | 2560881 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 89 | 37.7741 | -121.0667 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0107870 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970051 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | RECLOSER | 187702 | 20240906 | 1159 | 20240906 | 1951 | 2561134 | 472 | Distribution Circuit | 3rd Party | Vehicle | 196 | 59576 | 37.3599 | -120.8525 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0107906 | OH | Sus | 31707869 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970064 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319227032171 | 20240906 | 1400 | 20240906 | 2200 | 2561267 | 480 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 480 | 37.3825 | -120.7671 | No | Clear;Above 90 | Transformer (OH) | Leaking | 24-0107964 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970082 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319790728381 | 20240906 | 1859 | 20240906 | 2330 | 2561530 | 271 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 542 | 37.2785 | -120.5858 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0108126 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970146 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | OCB | 1102/2 | 20240907 | 124 | 20240907 | 2118 | 2561736 | 1159 | Distribution Circuit | 3rd Party | Vehicle | 607 | 72345 | 37.055 | -120.6342 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0108156 | OH | Sus | 35579569 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1970177 | 0 | Non-EPSS | N | 2024 | A-B- OC TGTS
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | SWITCH | 2161 | 20240907 | 300 | 20240907 | 2137 | 2561747 | 1117 | Distribution Circuit | 3rd Party | Vehicle | 93 | 103881 | 37.0118 | -120.6355 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0108156 | OH | Sus | 35579569 | CENTRAL VALLEY | SEP | Force Out | 0 | No | Yes | Yes | 1970183 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5503 | 20240907 | 548 | 20240907 | 919 | 2561772 | 211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 872 | 123386 | 37.2077 | -119.5419 | No | Clear;32-90 F |  |  | 24-0108164 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970188 | 1 | EPSS Ckt | Y | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320920756800 | 20240907 | 1305 | 20240907 | 1420 | 2562041 | 75 | Transformer only | Animal | Bird found | 4 | 300 | 38.0598 | -120.1811 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0108269 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970297 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 11547 | 20240907 | 1348 | 20240907 | 1940 | 2562059 | 352 | Distribution Circuit | 3rd Party | Vehicle | 22 | 5094 | 37.171 | -120.3832 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0108274 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970300 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | FUSE | 3742 | 20240907 | 1544 | 20240907 | 1734 | 2562114 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 550 | 36.8148 | -120.7669 | No | Clear;Above 90 |  |  | 24-0108290 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970305 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320819249468 | 20240907 | 1738 | 20240907 | 1932 | 2562162 | 114 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 456 | 37.8586 | -120.2173 | No | Clear;32-90 F |  |  | 24-0108308 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970319 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | OCB | 1702/2 | 20240907 | 2133 | 20240908 | 938 | 2562228 | 725 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1705 | 1236125 | 38.1865 | -120.1114 | No | Clear;32-90 F |  |  | 24-0108313 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970323 | 0 | EPSS Ckt | Y | 2024 | B-C- INST OC
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 68380 | 20240907 | 2229 | 20240908 | 935 | 2562246 | 666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 552 | 203182 | 38.0151 | -120.2744 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0108317 | OH | Sus | 35579762 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970328 | 0 | EPSS Ckt | Y | 2024 | A- C
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | OCB | 1103/2 | 20240907 | 2242 | 20240908 | 742 | 2562248 | 540 | Distribution Circuit | 3rd Party | Vehicle | 717 | 47503 | 37.3359 | -120.5053 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0108318 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970329 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320660355216 | 20240908 | 552 | 20240908 | 854 | 2562353 | 182 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 546 | 38.0161 | -120.2716 | No | Clear;32-90 F |  |  | 24-0108342 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970359 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 8170 | 20240908 | 612 | 20240908 | 748 | 2562357 | 96 | Distribution Circuit | Animal | Bird found | 502 | 48192 | 37.9873 | -120.2605 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108330 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970344 | 0 | EPSS Ckt | Y | 2024 | AC
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 786213 | 20240908 | 1515 | 20240908 | 1637 | 2562685 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1148 | 37.0907 | -120.2971 | No | Clear;Above 90 |  |  | 24-0108414 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970413 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 7524 | 20240908 | 1845 | 20240908 | 1945 | 2562813 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 2160 | 37.2969 | -120.4726 | No | Clear;Above 90 | Secondary | Broken- wire on ground | 24-0108426 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970429 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | FUSE | 9633 | 20240908 | 1857 | 20240909 | 503 | 2562820 | 606 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 10908 | 37.1805 | -121.0309 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0108434 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | Yes | No | 1970437 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 310011 | 20240909 | 636 | 20240909 | 1003 | 2563114 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1449 | 36.8063 | -120.3497 | No | Clear;32-90 F |  |  | 24-0108500 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970543 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 9576 | 20240909 | 745 | 20240909 | 1703 | 2563202 | 558 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1674 | 36.9179 | -120.4413 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0108635 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1970643 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 7919 | 20240909 | 933 | 20240909 | 1056 | 2563218 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 388 | 37.1003 | -120.5583 | No | Clear;32-90 F |  |  | 24-0108613 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1970637 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1105 | 253611105 | TRANSFORMER | T0965 | 20240909 | 1557 | 20240909 | 1650 | 2563664 | 53 | Transformer only | Unknown Cause | Patrol - found nothing | 29 | 1537 | 37.3626 | -120.5821 | No | Clear;Above 90 |  |  | 24-0108897 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1970708 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | TRANSFORMER | 318988346164 | 20240909 | 2020 | 20240910 | 3 | 2563935 | 223 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2899 | 37.7674 | -120.851 | No | Clear;32-90 F | Secondary | Broken | 24-0108946 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970734 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 9703 | 20240909 | 2031 | 20240909 | 2303 | 2563913 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3344 | 36.9152 | -120.7285 | No | Clear;32-90 F |  |  | 24-0108958 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970746 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | FUSE | 21046 | 20240910 | 536 | 20240910 | 700 | 2564034 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 3528 | 37.4038 | -120.6148 | No | Clear;32-90 F |  |  | 24-0108994 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970771 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 39256 | 20240910 | 803 | 20240910 | 934 | 2564141 | 91 | Distribution Circuit | Animal | Bird found | 525 | 42143 | 37.9571 | -120.3087 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0109023 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970841 | 0 | EPSS Ckt | Y | 2024 | A C INST
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7546 | 20240911 | 934 | 20240911 | 1810 | 2565310 | 516 | Distribution Circuit | 3rd Party | Vehicle | 41 | 4321 | 37.3132 | -120.841 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0109629 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1971307 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | TRANSFORMER | 100000028129 | 20240911 | 1311 | 20240913 | 2132 | 2565568 | 3381 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3381 | 37.9359 | -120.8771 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0109906 | OH | Sus | 35580650 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971395 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | TRANSFORMER | 319603817547 | 20240911 | 1428 | 20240911 | 1525 | 2565643 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 285 | 36.982 | -120.6369 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0109820 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971370 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | FUSE | S1471 | 20240911 | 1905 | 20240911 | 2055 | 2565939 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 293 | 37.7681 | -120.8411 | No | Clear;32-90 F |  |  | 24-0109968 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971433 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 24188 | 20240911 | 2015 | 20240911 | 2210 | 2566017 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 575 | 37.1294 | -120.4921 | No | Clear;32-90 F |  |  | 24-0109980 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971446 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | 4063 | 20240912 | 554 | 20240912 | 725 | 2566148 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 486 | 37.74 | -120.7542 | No | Fog;32-90 F |  |  | 24-0110078 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971502 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | TRANSFORMER | T3071 | 20240912 | 711 | 20240912 | 725 | 2566200 | 14 | Transformer only | Animal | Other | 2 | 28 | 36.9458 | -119.7498 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0110070 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971497 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | RECLOSER | 3400 | 20240912 | 802 | 20240912 | 931 | 2566247 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 287 | 25543 | 36.9816 | -120.5941 | No | Partly Cloudy;32-90 F |  |  | 24-0110145 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971624 | 0 | Non-EPSS | N | 2024 | GRD TARGET
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | SWITCH | 5455 | 20240912 | 822 | 20240912 | 955 | 2566462 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 558 | 37.2561 | -120.4345 | No | Clear;32-90 F | Jumper | Broken | 24-0105313 | OH | Sus | 35429682 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1971644 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 320870820107 | 20240912 | 1005 | 20240912 | 1207 | 2566471 | 122 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 122 | 37.0518 | -120.2025 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0110166 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971649 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 434305 | 20240912 | 1118 | 20240912 | 1456 | 2566564 | 218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 492 | 31642 | 37.5603 | -121.1786 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0110258 | OH | Sus | 31708653 | CENTRAL VALLEY | SEP | Force Out | 0 | No | Yes | No | 1971686 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | TRANSFORMER | 320272237229 | 20240912 | 1309 | 20240912 | 2003 | 2566662 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 584 | 37.5223 | -120.407 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0110306 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971697 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 20969 | 20240912 | 1449 | 20240912 | 1700 | 2566741 | 131 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 2392 | 37.7325 | -120.9645 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0110091 | UG | Sus | 35580820 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971706 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | JUMPER | 26544 | 20240912 | 1549 | 20240912 | 1650 | 2566796 | 61 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 37 | 2257 | 37.3325 | -120.992 | No | Clear;32-90 F | Fuse | Normal | 24-0110476 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971717 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 2273 | 20240913 | 124 | 20240913 | 238 | 2567042 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 280 | 20720 | 37.3108 | -121.0221 | No | Clear;32-90 F |  |  | 24-0110547 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1971774 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | FUSE | 4714 | 20240913 | 227 | 20240913 | 345 | 2567050 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 624 | 37.3332 | -120.3785 | No | Clear;32-90 F |  |  | 24-0110551 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1971779 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1821 | 20240913 | 438 | 20240913 | 650 | 2567063 | 132 | Distribution Circuit | Animal | Bird found | 13 | 1673 | 37.7812 | -120.775 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0110555 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971787 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318471729238 | 20240913 | 602 | 20240913 | 1104 | 2567076 | 302 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 302 | 37.3019 | -121.0258 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0110634 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971867 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 5133 | 20240913 | 638 | 20240913 | 1530 | 2567092 | 532 | Distribution Circuit | 3rd Party | Vehicle | 49 | 26068 | 37.0202 | -119.9655 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0110612 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1971820 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322589025379 | 20240913 | 811 | 20240913 | 1034 | 2567181 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 286 | 37.1938 | -119.6114 | No | Clear;32-90 F | Jumper | Broken | 24-0110675 | OH | Sus | 46321370 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1971922 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | JUMPER | BURNT OPEN JUMPER SS OF 325829 | 20240913 | 1009 | 20240913 | 1131 | 2567386 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 2952 | 37.0542 | -120.4924 | No | Clear;32-90 F | Jumper | Burned Open | 24-0110770 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1971950 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | RECLOSER | 560074 | 20240913 | 1109 | 20240913 | 1134 | 2567198 | 25 | Distribution Circuit | Equipment Failure/Involved | Underground | 125 | 3125 | 37.1741 | -120.2021 | No | Clear;32-90 F | Customer Equipment | Arcing | 24-0110761 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1971949 | 0 | EPSS Ckt | N | 2024 | NO TARGETS
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 3337 | 20240913 | 1300 | 20240913 | 1520 | 2567533 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1680 | 37.8577 | -120.9055 | No | Clear;32-90 F |  |  | 24-0110900 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972003 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322056936279 | 20240913 | 1527 | 20240913 | 1623 | 2567664 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 56 | 37.4944 | -119.7926 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0110897 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1972002 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10890 | 20240913 | 1746 | 20240913 | 1944 | 2567749 | 118 | Distribution Circuit | Animal | Squirrel | 1373 | 82996 | 37.31 | -119.5845 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0110931 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972011 | 0 | EPSS Ckt | Y | 2024 | B & GRD
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | SWITCH | 332693 | 20240913 | 1829 | 20240913 | 1854 | 2567783 | 25 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 50 | 37.3104 | -120.4237 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0110933 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972013 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | SWITCH | L1423 | 20240913 | 1911 | 20240913 | 2008 | 2567833 | 57 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 57 | 38.0433 | -120.3887 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0110894 | UG | Sus | 35581363 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972018 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 6225 | 20240913 | 1933 | 20240914 | 134 | 2567840 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1444 | 36.8947 | -119.8108 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0110949 | OH | Sus | 46321807 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1972026 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | RECLOSER | 9630 | 20240914 | 48 | 20240914 | 732 | 2567921 | 404 | Distribution Circuit | 3rd Party | Vehicle | 452 | 51090 | 37.2274 | -120.2709 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0110961 | OH | Sus | 35581257 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1972042 | 0 | EPSS Ckt | N | 2024 | A PH & GRD
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 100000006381 | 20240914 | 846 | 20240914 | 1022 | 2568069 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 96 | 37.2981 | -120.9684 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0111022 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972131 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6748 | 20240914 | 1038 | 20240914 | 1114 | 2568141 | 36 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 936 | 36.9084 | -120.1375 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0111020 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972130 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 310011 | 20240914 | 1119 | 20240914 | 1347 | 2568274 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1628 | 36.8063 | -120.3496 | No | Clear;32-90 F |  |  | 24-0111074 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972165 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | RECLOSER | 11870 | 20240914 | 1451 | 20240914 | 1504 | 2568350 | 13 | Distribution Circuit | Equipment Failure/Involved | Overhead | 771 | 10023 | 36.9658 | -120.1284 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0111083 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972174 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 3982 | 20240914 | 1755 | 20240915 | 205 | 2568405 | 490 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2870 | 37.0261 | -120.9089 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0111100 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1972189 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 1592 | 20240915 | 557 | 20240915 | 740 | 2568501 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 206 | 37.3377 | -120.2772 | No | Clear;32-90 F |  |  | 24-0111142 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972221 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1101 | 162671101 | FUSE | S217 | 20240915 | 825 | 20240915 | 1738 | 2568587 | 553 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 7742 | 37.5659 | -121.2691 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0111154 | OH | Sus | 46322003 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972238 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | SECTIONALIZER | 11180 | 20240915 | 1002 | 20240915 | 1405 | 2568671 | 243 | Distribution Circuit | 3rd Party | Metallic Balloon | 267 | 64881 | 37.0546 | -120.8701 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0111179 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972260 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | OCB | 1110/2 | 20240915 | 1630 | 20240915 | 2024 | 2568944 | 234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 718 | 168012 | 37.0139 | -120.9447 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0111203 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972280 | 0 | EPSS Ckt | Y | 2024 | A & B
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 462685 | 20240915 | 1724 | 20240915 | 2225 | 2569057 | 301 | Distribution Circuit | Animal | Bird found | 8 | 2408 | 36.8658 | -120.0556 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0111250 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972325 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 9599 | 20240915 | 2035 | 20240916 | 225 | 2569086 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 8864 | 37.0364 | -120.8924 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0111266 | OH | Sus | 46321945 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972339 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | RECLOSER | 11942 | 20240915 | 2045 | 20240915 | 2205 | 2569070 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 174 | 13920 | 37.1 | -120.9306 | No | Overcast;32-90 F |  |  | 24-0111237 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972315 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 550643 | 20240916 | 215 | 20240916 | 333 | 2569195 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 14271 | 37.2198 | -119.9047 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 24-0111274 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1972347 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 44893 | 20240916 | 806 | 20240916 | 834 | 2569304 | 28 | Distribution Circuit | Animal | Bird found | 1 | 28 | 37.4893 | -119.9629 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0111351 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972436 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 310011 | 20240916 | 944 | 20240916 | 1452 | 2569531 | 308 | Distribution Circuit | 3rd Party | Customer Equipment | 11 | 3388 | 36.8062 | -120.3497 | No | Clear;32-90 F | Metering Equipment | Normal | 24-0111648 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972623 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | RECLOSER | 11060 | 20240916 | 1016 | 20240916 | 1243 | 2569579 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1437 | 18594 | 37.0699 | -120.8656 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0111436 | OH | Sus | 31708888 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972538 | 0 | Non-EPSS | N | 2024 | NA
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320669555330 | 20240916 | 1213 | 20240916 | 1338 | 2569728 | 85 | Transformer only | Vegetation | Tree - fell into line | 3 | 255 | 38.0193 | -120.2685 | No | Partly Cloudy;32-90 F | Service conductor | Broken- wire on ground | 24-0111633 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972618 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | RECLOSER | 149636 | 20240916 | 1255 | 20240916 | 1405 | 2569782 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 246 | 17220 | 37.2733 | -120.5259 | No | Partly Cloudy;32-90 F |  |  | 24-0111570 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1972594 | 0 | Non-EPSS | N | 2024 | A- B- C- TIME- INST
YOSEMITE | YOSEMITE | BONITA-1103 | 255391103 | TRANSFORMER | 320734018655 | 20240916 | 1555 | 20240916 | 2101 | 2569931 | 306 | Transformer only | 3rd Party | Contact with High Voltage- 3rd party | 1 | 306 | 37.0117 | -120.2493 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0111731 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972644 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 573945 | 20240916 | 1637 | 20240916 | 1755 | 2569962 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 156 | 37.7784 | -120.6965 | No | Clear;32-90 F |  |  | 24-0111746 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972652 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 7705 | 20240916 | 1833 | 20240916 | 2309 | 2570049 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4140 | 37.2521 | -120.3614 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0111772 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1972666 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | SWITCH | 55891 | 20240916 | 1954 | 20240917 | 121 | 2570080 | 327 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 8175 | 37.9736 | -120.428 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0111716 | OH | Sus | 31709087 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972663 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321278860281 | 20240917 | 120 | 20240917 | 305 | 2570213 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1365 | 38.1541 | -120.056 | No | Clear;32-90 F | Fuse | Broken | 24-0111800 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972698 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BONITA-1103 | 255391103 | JUMPER | 1103/2 | 20240917 | 715 | 20240917 | 1058 | 2570269 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 257 | 19763 | 36.9678 | -120.2032 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0111855 | OH | Sus | 46322560 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1972762 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 169700 | 20240917 | 822 | 20240917 | 943 | s1972807 | 81 | Distribution Circuit | Company Initiated | Personnel- company | 2873 | 192729 | 37.8364 | -120.2605 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105710 | OH | Sus | 35465587 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972807 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 499879 | 20240917 | 900 | 20240917 | 935 | 2570518 | 35 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 245 | 37.3894 | -120.6402 | No | Clear;32-90 F | Insulator | Broken | 24-0111889 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972827 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 121108 | 20240917 | 1015 | 20240917 | 1032 | 2570646 | 17 | Distribution Circuit | Company Initiated | Personnel- company | 123 | 2091 | 37.4044 | -119.6251 | No | Clear;32-90 F |  |  | 24-0111939 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1972900 | 0 | EPSS Ckt | Y | 2024 | AC
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | FUSE | 7404 | 20240917 | 1253 | 20240917 | 1400 | 2570773 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 134 | 37.0971 | -120.5195 | No | Clear;32-90 F |  |  | 24-0112073 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972957 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | JUMPER | DDE JUMPERS @ CGC# 320280654383 | 20240917 | 1601 | 20240917 | 1746 | 2570870 | 105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 12600 | 37.994 | -120.4035 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0112119 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1972966 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | T9490 | 20240918 | 305 | 20240918 | 415 | 2571158 | 70 | Transformer only | Equipment Failure/Involved | Underground | 13 | 910 | 37.7231 | -120.924 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0112220 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1973027 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 20735 | 20240918 | 718 | 20240918 | 940 | 2571191 | 142 | Distribution Circuit | 3rd Party | Vehicle | 2 | 284 | 37.7893 | -120.7516 | No | Overcast;32-90 F | Conductor- Underground | Normal | 24-0112291 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973090 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | OTHER | WIRE DOWN NE OF CGC 100000019375 | 20240918 | 1301 | 20240918 | 1421 | 2571723 | 80 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 76 | 5880 | 37.6024 | -120.1926 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0112553 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1973314 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | JUMPER | OJ 1 NW/OF CGC 320670954570 | 20240918 | 1334 | 20240918 | 1609 | 2571747 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 155 | 37.9991 | -120.2687 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0112552 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1973311 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320150054515 | 20240918 | 1611 | 20240919 | 106 | 2571895 | 535 | Transformer only | 3rd Party | Vehicle | 2 | 1070 | 37.9975 | -120.4484 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0112753 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973367 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 320884740191 | 20240918 | 1748 | 20240918 | 1917 | 2571965 | 89 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 89 | 37.6032 | -120.1914 | No | Clear;32-90 F |  |  | 24-0112758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1973372 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 9844 | 20240919 | 110 | 20240919 | 401 | 2572143 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2053 | 37.3275 | -120.8408 | No | Clear;32-90 F |  |  | 24-0112807 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973398 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | FUSE 310011 | 20240919 | 814 | 20240919 | 1150 | s1973539 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2376 | 36.8061 | -120.3497 | No | Clear;32-90 F | Fuse | Normal | 24-0113007 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973539 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 36862 | 20240919 | 819 | 20240919 | 926 | 2572291 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 335 | 37.2938 | -120.777 | No | Partly Cloudy;32-90 F |  |  | 24-0112907 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973507 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | 67161 | 20240919 | 1119 | 20240919 | 1317 | 2572520 | 118 | Distribution Circuit | Animal | Bird found | 5 | 590 | 37.9904 | -120.4418 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0113092 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973572 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 1588 | 20240919 | 1246 | 20240919 | 1336 | 2572572 | 50 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 56 | 2814 | 36.9232 | -119.8852 | No | Partly Cloudy;32-90 F |  |  | 24-0113109 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973578 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRIP-SAVER | 5525 | 20240919 | 1438 | 20240919 | 1655 | 2572721 | 137 | Distribution Circuit | Animal | Bird found | 1491 | 115955 | 37.1932 | -119.7709 | No | Partly Cloudy-Drizzle;32-90 F | Fuse | Burned Open | 24-0113195 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973602 | 1 | EPSS Ckt | N | 2024 | A
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322178025582 | 20240919 | 1717 | 20240919 | 2032 | 2572818 | 195 | Transformer only | Animal | Bird found | 2 | 390 | 37.2007 | -119.7521 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0113286 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973624 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 41506 | 20240919 | 1800 | 20240919 | 1839 | 2572844 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 351 | 37.8495 | -120.8806 | No | Partly Cloudy;32-90 F |  |  | 24-0113298 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973629 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1106 | 254101106 | FUSE | 536777 | 20240920 | 429 | 20240920 | 625 | 2573026 | 116 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 116 | 37.1269 | -120.0927 | No | Clear;32-90 F |  |  | 24-0113423 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973687 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20240920 | 648 | 20240920 | 834 | 2573069 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 368 | 24169 | 37.9754 | -120.4464 | No | Clear;32-90 F |  |  | 24-0113439 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973694 | 0 | EPSS Ckt | Y | 2024 | A- B
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | JUMPER | OJ @ CGC 320297027741 | 20240920 | 1106 | 20240920 | 1120 | 2573412 | 14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 14 | 37.2626 | -120.3977 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0113599 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1973880 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318884545551 | 20240920 | 1144 | 20240920 | 1230 | 2573478 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 46 | 37.7504 | -120.8868 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0113630 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1973890 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | RECLOSER | 606810 | 20240920 | 1244 | 20240920 | 1656 | 2573533 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 4536 | 37.2286 | -120.2162 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0113683 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1973910 | 0 | EPSS Ckt | Y | 2024 | NA
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | JUMPER | BROKEN VERT JMPR | 20240920 | 1459 | 20240920 | 2032 | 2573627 | 333 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 15609 | 37.3132 | -120.8421 | No | Clear;32-90 F | Jumper | Broken | 24-0113830 | OH | Sus | 46324823 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1973936 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 90090 | 20240920 | 1946 | 20240920 | 2138 | 2573766 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2696 | 251032 | 37.9028 | -120.4538 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0113888 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973955 | 0 | EPSS Ckt | Y | 2024 | A GRD
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318661747502 | 20240921 | 713 | 20240921 | 730 | 2573840 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 17 | 37.8037 | -120.9639 | No | Fog;32-90 F | Fuse | Broken | 24-0113905 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973976 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | JUMPER | OJ 1 P E/OF CGC# 320148553680 | 20240921 | 900 | 20240921 | 1226 | 2573906 | 206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 618 | 37.9738 | -120.4489 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0113915 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1974021 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 4563 | 20240921 | 1502 | 20240921 | 1605 | 2574167 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 294 | 37.2223 | -120.5823 | No | Clear;32-90 F |  |  | 24-0114052 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974119 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1811 | 20240921 | 1614 | 20240921 | 1810 | 2574174 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 3480 | 37.8052 | -120.7245 | No | Clear;32-90 F |  |  | 24-0114064 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974126 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 3714 | 20240922 | 534 | 20240922 | 746 | 2574356 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 7788 | 37.0459 | -120.5951 | No | Clear;32-90 F |  |  | 24-0114101 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974181 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320290854733 | 20240922 | 721 | 20240922 | 928 | 2574390 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 127 | 38.0028 | -120.4001 | No | Clear;32-90 F | Fuse | Broken | 24-0114114 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974210 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 9547 | 20240922 | 1150 | 20240922 | 1318 | 2574531 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 176 | 37.7708 | -120.9967 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0114129 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1974228 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 11825 | 20240922 | 1809 | 20240922 | 1953 | 2574665 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 2184 | 37.4604 | -120.0717 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0114154 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1974266 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 321826916514 | 20240922 | 1812 | 20240922 | 2008 | 2574685 | 116 | Transformer only | Animal | Bird found | 3 | 348 | 36.9517 | -119.8757 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0114161 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974274 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 6855 | 20240923 | 22 | 20240923 | 334 | 2574837 | 192 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 3648 | 36.9894 | -120.0128 | No | Clear;32-90 F |  |  | 24-0114181 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974292 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 7839 | 20240923 | 419 | 20240923 | 536 | 2574861 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 385 | 37.3097 | -120.4547 | No | Clear;32-90 F |  |  | 24-0114182 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974293 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 94866 | 20240923 | 811 | 20240923 | 1037 | 2575008 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 7304 | 37.7156 | -120.457 | No | Clear;32-90 F |  |  | 24-0114302 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974505 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | FUSE | 9613 | 20240923 | 850 | 20240923 | 1038 | 2575096 | 108 | Distribution Circuit | Animal | Other | 2 | 216 | 36.7493 | -120.4595 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0114304 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974507 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318617845188 | 20240923 | 1035 | 20240923 | 1137 | 2575272 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 62 | 37.7398 | -120.9781 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0114362 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974524 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | S2677 | 20240923 | 2020 | 20240924 | 148 | 2575767 | 328 | Distribution Circuit | 3rd Party | Gun Shot | 5 | 1640 | 37.3237 | -120.9803 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0114596 | OH | Sus | 46325692 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1974609 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 9806 | 20240924 | 253 | 20240924 | 503 | 2575875 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1820 | 36.8558 | -120.4177 | No | Clear;32-90 F |  |  | 24-0114646 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974648 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRANSFORMER | T7670 | 20240924 | 557 | 20240924 | 1209 | 2575908 | 372 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1116 | 37.3269 | -119.6315 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0114688 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974672 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | FUSE | 153021 | 20240924 | 1024 | 20240924 | 1520 | 2576456 | 296 | Distribution Circuit | 3rd Party | Vehicle | 1 | 296 | 37.8276 | -121.006 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0114918 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1974912 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6875 | 20240924 | 1025 | 20240924 | 1256 | 2576307 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 906 | 36.9094 | -120.0718 | No | Clear;32-90 F |  |  | 24-0114899 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974906 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 93062 | 20240924 | 1048 | 20240924 | 1310 | 2576328 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 166 | 23572 | 38.0205 | -120.2221 | No | Clear;32-90 F |  |  | 24-0114850 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974869 | 0 | EPSS Ckt | Y | 2024 | B & C
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | OTHER | 9650 | 20240924 | 1053 | 20240924 | 1123 | 2576332 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 1794 | 37.3021 | -120.6354 | No | Clear;32-90 F | Other | Burned Open | 24-0114865 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1974877 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 343 | 20240924 | 1204 | 20240924 | 1243 | 2576421 | 39 | Distribution Circuit | 3rd Party | Other | 73 | 2847 | 37.3335 | -121.0041 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0114924 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974916 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319397123342 | 20240924 | 1337 | 20240924 | 1443 | 2576501 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 66 | 37.1405 | -120.7071 | No | Clear;Above 90 |  | Failed/Faulted | 24-0115045 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974950 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320238124848 | 20240924 | 1535 | 20240924 | 1622 | 2576603 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 47 | 37.1835 | -120.4195 | No | Clear;Above 90 | Fuse | Broken | 24-0115094 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1974965 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20240924 | 1745 | 20240925 | 214 | 2576756 | 509 | Distribution Circuit | 3rd Party | Vehicle | 1311 | 299051 | 38.0063 | -120.3474 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0115126 | OH | Sus | 31710024 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1974980 | 0 | EPSS Ckt | Y | 2024 | B & C
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | OTHER | T6995 TWD T7061 | 20240925 | 1409 | 20240925 | 1539 | 2577574 | 90 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 2700 | 37.0691 | -120.8217 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0115366 | UG | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1975318 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | FUSE | 6008 | 20240925 | 1410 | 20240925 | 1510 | 2577491 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 480 | 37.0529 | -120.4451 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0115477 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975296 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 667249 | 20240925 | 1445 | 20240925 | 1624 | 2577617 | 99 | Distribution Circuit | Animal | Bird found | 12 | 1188 | 36.8508 | -119.9832 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115666 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1975346 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | SWITCH | L1681 | 20240925 | 1449 | 20240925 | 1745 | 2577614 | 176 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 3520 | 38.0102 | -120.3339 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0115590 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975326 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | OTHER | J23142 TWD T7395 | 20240925 | 1631 | 20240925 | 1706 | 2577696 | 35 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 1085 | 37.0692 | -120.8261 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0115359 | UG | Sus | 35583702 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975343 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | OTHER | J22407 TWD T6991 | 20240925 | 1729 | 20240925 | 1845 | 2577739 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 1292 | 37.0676 | -120.8208 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0115372 | UG | Sus | 35583704 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975355 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1101 | 252311101 | RECLOSER | 96158 | 20240925 | 2057 | 20240926 | 236 | 2577836 | 339 | Distribution Circuit | 3rd Party | Vehicle | 47 | 12759 | 36.7633 | -120.494 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0115712 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Multi-Fault | 0 | No | Yes | No | 1975376 | 0 | Non-EPSS | N | 2024 | A- B- C- SGF
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 21115 | 20240926 | 928 | 20240926 | 1701 | 2578194 | 453 | Distribution Circuit | 3rd Party | Vehicle | 19 | 3263 | 37.0275 | -120.8569 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0115909 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Three Phase Fault | 0 | No | No | No | 1975576 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | SWITCH | 9111 | 20240926 | 1109 | 20240926 | 1236 | 2578351 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 275 | 23925 | 37.5212 | -120.4365 | No | Clear;32-90 F | Switch (OH) | Failed/Faulted | 24-0115968 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1975600 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 264976 | 20240926 | 1115 | 20240926 | 2208 | 2578310 | 653 | Distribution Circuit | 3rd Party | Vehicle | 61 | 38573 | 37.0732 | -120.0297 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0115941 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975589 | 0 | EPSS Ckt | N | 2024 | C
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | TRANSFORMER | 319633014272 | 20240926 | 1406 | 20240926 | 1422 | 2578304 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 16 | 36.909 | -120.6264 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0116097 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1975642 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 2611 | 20240927 | 646 | 20240927 | 828 | 2579072 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1428 | 37.8385 | -120.9244 | No | Clear;32-90 F |  |  | 24-0116385 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1975825 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | JUMPER | JUMPERS 1 SPAN S/OF 319656830296 | 20240927 | 845 | 20240927 | 1250 | 2579176 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 490 | 37.3312 | -120.6191 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0116387 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975826 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | JUMPER | JUMPERS 2 POLES S/OF CGC#319777019149 | 20240927 | 923 | 20240927 | 1040 | 2579282 | 77 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 154 | 37.0246 | -120.5766 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0116438 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975900 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 321021057517 | 20240927 | 1018 | 20240927 | 1320 | 2579292 | 182 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1092 | 38.0791 | -120.1466 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0116691 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975972 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | JUMPER | 7221 | 20240927 | 1304 | 20240927 | 1329 | 2579472 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 50 | 36.9054 | -120.7467 | No | Clear;32-90 F | Jumper | Burned Open | 24-0116660 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1975963 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 90927 | 20240927 | 1458 | 20240927 | 1857 | 2579569 | 239 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2 | 478 | 37.411 | -120.6379 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0116749 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1975992 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | FUSE | 6815 | 20240927 | 1507 | 20240927 | 1657 | 2579574 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 440 | 36.9382 | -120.2301 | No | Partly Cloudy;Above 90 | Anchor or Guy | Broken | 24-0116804 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1976013 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | FUSE | 10135 | 20240927 | 1732 | 20240928 | 744 | 2579660 | 852 | Distribution Circuit | Equipment Failure/Involved | Underground | 136 | 55610 | 37.069 | -120.853 | No | Clear;Above 90 | Transformer (UG) | Broken | 24-0116835 | UG | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1976036 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | FUSE | 26905 | 20240927 | 1819 | 20240927 | 2005 | 2579667 | 106 | Distribution Circuit | 3rd Party | Metallic Balloon | 31 | 3318 | 37.2979 | -120.4929 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0116829 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976029 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 19299 | 20240927 | 2217 | 20240928 | 18 | 2579748 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 6776 | 37.013 | -119.9651 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0116839 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1976049 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1712 | 163191712 | JUMPER | 318806048125 | 20240928 | 815 | 20240928 | 1115 | 2579864 | 180 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 540 | 37.8208 | -120.9147 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0116860 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1976089 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 68555 | 20240928 | 848 | 20240928 | 1515 | 2579985 | 387 | Distribution Circuit | 3rd Party | Vehicle | 1 | 387 | 37.8167 | -120.8979 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0116876 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1976153 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | FUSE | 23875 | 20240928 | 935 | 20240928 | 2250 | 2579977 | 795 | Distribution Circuit | Equipment Failure/Involved | Underground | 155 | 58889 | 37.7744 | -120.8459 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0116879 | UG | Sus | 31710324 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976159 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | SWITCH | 6449 | 20240928 | 1500 | 20240929 | 118 | 2580196 | 618 | Distribution Circuit | 3rd Party | Vehicle | 23 | 14214 | 37.0976 | -120.0682 | No | Overcast;Above 90 | Pole-Wood | Broken | 24-0116930 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1976215 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | TRANSFORMER | 320728626516 | 20240928 | 1610 | 20240928 | 1625 | 2580118 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 60 | 37.2286 | -120.2494 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0116908 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1976199 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | RECLOSER | 9610 | 20240928 | 1827 | 20240929 | 537 | 2580292 | 670 | Distribution Circuit | 3rd Party | Vehicle | 1003 | 89408 | 37.3406 | -120.5224 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0116955 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1976240 | 0 | Non-EPSS | N | 2024 | A & C
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 24472 | 20240929 | 214 | 20240929 | 332 | 2580450 | 78 | Distribution Circuit | Animal | Bird found | 30 | 2340 | 36.9667 | -120.0548 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0116993 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1976265 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 8040 | 20240929 | 904 | 20240929 | 1330 | 2580583 | 266 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 130 | 31376 | 37.8999 | -120.5045 | No | Clear;32-90 F |  |  | 24-0117021 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976305 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3757 | 20240930 | 558 | 20240930 | 854 | 2580942 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 587 | 36.9241 | -120.6889 | No | Clear;32-90 F |  |  | 24-0117228 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976543 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | S1319 | 20240930 | 709 | 20240930 | 916 | 2581011 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 19939 | 37.2457 | -121.0058 | No | Clear;32-90 F |  |  | 24-0117233 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1976554 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | 319291632412 | 20240930 | 1014 | 20240930 | 1046 | 2581301 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 32 | 37.3896 | -120.7434 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0117267 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1976581 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 22993 | 20240930 | 1435 | 20240930 | 1720 | 2581569 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 440 | 37.1711 | -120.4919 | No | Clear;Above 90 |  |  | 24-0117495 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976654 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | RECLOSER | 877670 | 20240930 | 1438 | 20240930 | 1450 | 2581571 | 12 | Distribution Circuit | Company Initiated | Personnel- company | 16 | 192 | 37.9044 | -120.5093 | No | Clear;32-90 F | Fuse | Normal | 24-0117425 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1976630 | 0 | EPSS Ckt | Y | 2024 | C GRD
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | OCB | 1101/2 | 20241001 | 807 | 20241001 | 1314 | 2582011 | 307 | Distribution Circuit | 3rd Party | Other | 2 | 614 | 37.1589 | -119.4057 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976818 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 127906 | 20241001 | 807 | 20241001 | 1314 | 2582084 | 307 | Distribution Circuit | 3rd Party | Other | 7 | 2149 | 37.1556 | -119.4744 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976826 | 0 | EPSS Ckt | Y | 2024 | N/A
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 29336 | 20241001 | 807 | 20241001 | 1314 | 2582086 | 307 | Distribution Circuit | 3rd Party | Other | 3 | 921 | 37.1549 | -119.4844 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976828 | 0 | EPSS Ckt | Y | 2024 | N/A
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 222874 | 20241001 | 807 | 20241001 | 1314 | 2582090 | 307 | Distribution Circuit | 3rd Party | Other | 3 | 921 | 37.1539 | -119.4886 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976832 | 0 | EPSS Ckt | Y | 2024 | NA
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 43806 | 20241001 | 807 | 20241001 | 1314 | 2582094 | 307 | Distribution Circuit | 3rd Party | Other | 3 | 921 | 37.1649 | -119.4385 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976835 | 0 | EPSS Ckt | Y | 2024 | N/A
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | FUSE | BF50039 | 20241001 | 807 | 20241001 | 1314 | 2582254 | 307 | Distribution Circuit | 3rd Party | Other | 4 | 1228 | 37.1679 | -119.4293 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976928 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 32428 | 20241001 | 1009 | 20241001 | 1149 | 2582360 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 400 | 37.0612 | -120.0748 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0117821 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1976951 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | TRANSFORMER | 318999320167 | 20241001 | 1143 | 20241001 | 2059 | 2582115 | 556 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2780 | 37.0532 | -120.8436 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0117801 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1976945 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 49167 | 20241001 | 1210 | 20241001 | 1321 | 2582362 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 142 | 37.5544 | -120.5064 | No | Clear;Above 90 |  |  | 24-0117882 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1976993 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321892036649 | 20241001 | 1233 | 20241001 | 1300 | 2582377 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 27 | 37.507 | -119.849 | No | Clear;Above 90 | Transformer (OH) | Broken | 24-0117835 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976960 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 100000070973 | 20241001 | 1234 | 20241001 | 1300 | 2582384 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 130 | 38.0821 | -120.1481 | No | Clear;Above 90 | Crossarm- Wood | Burned/flashed | 24-0117849 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976967 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319209047295 | 20241001 | 1241 | 20241001 | 1820 | 2582391 | 339 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 339 | 37.7986 | -120.7746 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0117951 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977017 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 321816526257 | 20241001 | 1310 | 20241001 | 1424 | 2582434 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 74 | 37.219 | -119.8753 | No | Clear;Above 90 | Fuse | Broken | 24-0117930 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977013 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 378703 | 20241001 | 1351 | 20241001 | 1400 | 2582479 | 9 | Distribution Circuit | Animal | Other | 3 | 27 | 37.4613 | -120.5151 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0117906 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977001 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321467861379 | 20241001 | 1400 | 20241001 | 1447 | 2582486 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 94 | 38.1849 | -119.9905 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0117912 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977003 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | OTHER | T8338 TWD T14060 | 20241001 | 1416 | 20241001 | 1515 | 2582501 | 59 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 649 | 37.0507 | -120.8784 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0117741 | UG | Sus | 35584725 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977008 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4669 | 20241001 | 1648 | 20241001 | 1753 | 2582719 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 303 | 37.1857 | -120.6006 | No | Clear;Above 90 |  |  | 24-0118035 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977038 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | OTHER | J26182 TWD T14329 | 20241001 | 1715 | 20241001 | 1802 | 2582738 | 47 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 517 | 37.0486 | -120.8767 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0117728 | UG | Sus | 35584656 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977036 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | RECLOSER | 187702 | 20241001 | 2353 | 20241002 | 1703 | 2582915 | 770 | Distribution Circuit | Equipment Failure/Involved | Overhead | 196 | 165644 | 37.3599 | -120.8525 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0118093 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977083 | 0 | Non-EPSS | N | 2024 | C & GRD
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321235317937 | 20241001 | 2355 | 20241002 | 18 | 2582886 | 23 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 92 | 36.9923 | -120.0782 | No | Clear;32-90 F | Secondary | Normal | 24-0118090 | OH | Sus | 46330028 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977082 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 5020 | 20241002 | 420 | 20241002 | 813 | 2582954 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1205 | 209773 | 37.2065 | -119.7142 | No | Clear;32-90 F |  |  | 24-0118101 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977093 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322251525130 | 20241002 | 529 | 20241002 | 1232 | 2582970 | 423 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 423 | 37.1878 | -119.7274 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0118231 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977263 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | 20679 | 20241002 | 815 | 20241002 | 928 | 2583096 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 146 | 37.7546 | -120.765 | No | Clear;32-90 F |  |  | 24-0118213 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1977246 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | SWITCH | 5216 | 20241002 | 1013 | 20241002 | 1110 | 2583316 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 513 | 37.0837 | -120.4386 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0118226 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1977261 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 3705 | 20241002 | 1129 | 20241002 | 1540 | 2583491 | 251 | Distribution Circuit | 3rd Party | Vehicle | 27 | 3865 | 37.0002 | -120.8551 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 24-0118339 | OH | Sus | 35585077 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1977316 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | TRANSFORMER | 319868124039 | 20241002 | 1320 | 20241002 | 1443 | 2583597 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 83 | 37.1607 | -120.5464 | No | Clear;Above 90 | Connector or Splice (OH) | Burned Open | 24-0118490 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977357 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 20241002 | 1406 | 20241002 | 1649 | 2583644 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 901 | 65309 | 37.6313 | -120.1536 | No | Clear;Above 90 |  |  | 24-0118449 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977351 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 3778 | 20241002 | 1426 | 20241002 | 1616 | 2583785 | 110 | Distribution Circuit | Animal | Other | 1 | 110 | 36.6777 | -120.6406 | No | Clear;Above 90 | Fuse | Failed/Faulted | 24-0118564 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977371 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 319744628142 | 20241002 | 1625 | 20241002 | 2028 | 2583791 | 243 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 486 | 37.2724 | -120.5888 | No | Clear;Above 90 | Jumper | Burned Open | 24-0118597 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977380 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | 950145 | 20241002 | 1625 | 20241002 | 1758 | 2583790 | 93 | Distribution Circuit | Animal | Bird found | 3 | 279 | 37.7478 | -120.8882 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0118608 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1977387 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | JUMPER | OJ'S 3 E/OF CGC# 319737428029 | 20241002 | 2003 | 20241002 | 2028 | 2584131 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 50 | 37.27 | -120.589 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0118635 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977406 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | OCB | 1108/2 | 20241002 | 2203 | 20241003 | 628 | 2584192 | 505 | Distribution Circuit | 3rd Party | Vehicle | 2344 | 168972 | 37.2732 | -120.4872 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0118664 | OH | Sus | 35585159 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1977425 | 0 | Non-EPSS | N | 2024 | A & C
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320043528683 | 20241002 | 2253 | 20241003 | 244 | 2584207 | 231 | Transformer only | 3rd Party | Vehicle | 1 | 231 | 37.2885 | -120.4847 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0118673 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977431 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | JUMPER | BROKEN WIRE AT CGC #320241422570 | 20241003 | 730 | 20241003 | 1044 | 2584447 | 194 | Distribution Circuit | 3rd Party | Vehicle | 18 | 660 | 37.1201 | -120.4192 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0118774 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977504 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322354527385 | 20241003 | 1029 | 20241003 | 1144 | 2584713 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 75 | 37.2509 | -119.6926 | No | Clear;32-90 F | Fuse | Broken | 24-0118942 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977614 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1116 | 255371116 | FUSE | 9809 | 20241003 | 1106 | 20241003 | 1322 | 2584750 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 680 | 36.8798 | -120.6243 | No | Clear;Above 90 |  |  | 24-0119004 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1977627 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1105 | 254101105 | FUSE | 5758 | 20241003 | 1115 | 20241003 | 1214 | 2584754 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 59 | 37.1076 | -120.2478 | No | Clear;Above 90 | Fuse | Broken | 24-0118959 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977618 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 9926 | 20241003 | 1256 | 20241003 | 1655 | 2584844 | 239 | Distribution Circuit | 3rd Party | Vehicle | 3 | 717 | 37.1001 | -120.8894 | No | Clear;Above 90 | Pole-Wood | Normal | 24-0119034 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1977631 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 5861 | 20241003 | 1315 | 20241003 | 1430 | 2584850 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 75 | 36.849 | -119.9741 | No | Clear;32-90 F |  |  | 24-0119055 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977634 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | SWITCH | 6455 | 20241003 | 1330 | 20241003 | 1434 | 2584826 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 1728 | 37.0764 | -120.1823 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0118973 | OH | Sus | 31710542 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1977622 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | JUMPER | 22587 POS 3 BURNED OJ | 20241003 | 1353 | 20241003 | 1747 | 2584885 | 234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 234 | 37.2948 | -120.5041 | No | Clear;Above 90 | Connector or Splice (OH) | Broken | 24-0119107 | OH | Sus | 46331090 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977647 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 11726 | 20241003 | 1607 | 20241003 | 2232 | 2585083 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 770 | 37.5224 | -120.4325 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0119171 | OH | Sus | 46331182 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1977666 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 4535 | 20241004 | 644 | 20241004 | 812 | 2585412 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1115 | 37.2295 | -120.547 | No | Clear;32-90 F |  |  | 24-0119342 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977798 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 322218532210 | 20241004 | 742 | 20241004 | 822 | 2585440 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 80 | 37.3824 | -119.7397 | No | Clear;32-90 F | Service conductor | Deteriorated | 24-0119305 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1977758 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6595 | 20241004 | 846 | 20241004 | 1027 | 2585547 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1213 | 36.9457 | -120.1294 | No | Clear;32-90 F |  |  | 24-0119399 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977868 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321519222637 | 20241004 | 850 | 20241004 | 1018 | 2585551 | 88 | Transformer only | Animal | Bird found | 1 | 88 | 37.1204 | -119.9821 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0119438 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977889 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | TRANSFORMER | 417068854573 | 20241004 | 851 | 20241004 | 1111 | 2585552 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 140 | 36.8288 | -120.0019 | No | Clear;32-90 F | Fuse | Broken | 24-0119485 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977908 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 6773 | 20241004 | 1128 | 20241004 | 1800 | 2585765 | 392 | Distribution Circuit | 3rd Party | Vehicle | 19 | 7448 | 36.8925 | -119.9651 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0119606 | OH | Sus | 35585656 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1977933 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321057215969 | 20241004 | 1337 | 20241004 | 1552 | 2585914 | 135 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 135 | 36.9383 | -120.1385 | No | Clear;Above 90 |  |  | 24-0119668 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1977942 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7392 | 20241004 | 1624 | 20241004 | 1745 | 2586013 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1620 | 37.411 | -120.5961 | No | Clear;Above 90 |  |  | 24-0119688 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1977946 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 6738 | 20241005 | 1458 | 20241005 | 1636 | 2586859 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 196 | 36.9246 | -119.7684 | No | Clear;Above 90 |  |  | 24-0119846 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978099 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | 20013 | 20241006 | 923 | 20241006 | 1211 | 2587329 | 168 | Distribution Circuit | Animal | Bird found | 10 | 1680 | 37.8323 | -120.4867 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0119943 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1978195 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 20123 | 20241006 | 2231 | 20241007 | 1510 | 2587821 | 999 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 22039 | 37.7366 | -120.9585 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0120033 | UG | Sus | 31711283 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978284 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | TRANSFORMER | 319675632426 | 20241007 | 52 | 20241007 | 154 | 2587871 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 1116 | 37.3906 | -120.6123 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0120042 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1978294 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319347447622 | 20241007 | 830 | 20241007 | 1130 | 2588069 | 180 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 180 | 37.8079 | -120.7267 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0120102 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1978386 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | TRANSFORMER | 318880245581 | 20241007 | 906 | 20241007 | 1226 | 2588104 | 200 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 600 | 37.7512 | -120.8883 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0120110 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1978415 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | TRANSFORMER | 320606519418 | 20241007 | 928 | 20241007 | 1028 | 2588203 | 60 | Transformer only | Animal | Bird found | 1 | 60 | 37.0328 | -120.2915 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0120185 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978492 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318289230620 | 20241007 | 1054 | 20241007 | 1506 | 2588281 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 252 | 37.3392 | -121.0903 | No | Clear;Above 90 | Jumper | Broken | 24-0120240 | OH | Sus | 31711367 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978530 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | OTHER | J604 TWD T5857 | 20241007 | 1542 | 20241007 | 1821 | 2588557 | 159 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 2789 | 38.0517 | -120.4134 | No | Clear;Above 90 | Transformer (UG) | Broken | 24-0120262 | UG | Sus | 35586119 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1978592 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 20277 | 20241007 | 1550 | 20241007 | 2048 | 2588605 | 298 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1490 | 37.8575 | -120.2035 | No | Clear;Above 90 |  |  | 24-0120443 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1978642 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | RECLOSER | 11260 | 20241007 | 1637 | 20241008 | 126 | 2588649 | 529 | Distribution Circuit | 3rd Party | Vehicle | 209 | 16429 | 37.3567 | -120.7238 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0120396 | OH | Sus | 31711398 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1978607 | 0 | Non-EPSS | N | 2024 | A B C
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | JUMPER | FB E/OF CGC 319354547825 | 20241008 | 1131 | 20241008 | 1341 | 2589537 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 520 | 37.8135 | -120.7243 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0120678 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1978891 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320273854164 | 20241008 | 1316 | 20241008 | 1541 | 2589607 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 145 | 37.9873 | -120.4059 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0120721 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1978907 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | 319721030725 | 20241008 | 1815 | 20241008 | 1840 | 2589848 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 225 | 37.3441 | -120.5968 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0120910 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1978964 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 6008 | 20241008 | 1934 | 20241008 | 2018 | s1979471 | 44 | Distribution Circuit | Company Initiated | Coordination failure | 581 | 25564 | 38.0085 | -120.3034 | No | Clear;32-90 F | Recloser | Normal | 24-0120930 | OH | Sus | 31711215 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979471 | 0 | EPSS Ckt | Y | 2024 | GRD INST
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 11300 | 20241008 | 1940 | 20241009 | 126 | 2589966 | 346 | Distribution Circuit | Equipment Failure/Involved | Underground | 914 | 277603 | 38.0058 | -120.3473 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0120930 | UG | Sus | 31711215 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978975 | 0 | EPSS Ckt | Y | 2024 | A GRD
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 32876 | 20241008 | 2032 | 20241008 | 2210 | 2589996 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 882 | 36.9094 | -120.0256 | No | Clear;32-90 F |  |  | 24-0120946 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1978985 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | OCB | 1101/2 | 20241009 | 733 | 20241009 | 1650 | 2590392 | 557 | Distribution Circuit | 3rd Party | Other | 22 | 12254 | 37.1589 | -119.4057 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0121508 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1979307 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 19138 | 20241009 | 929 | 20241009 | 1835 | 2590474 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 546 | 37.2938 | -120.6333 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0121140 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979194 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322199327596 | 20241009 | 1712 | 20241009 | 1746 | 2590943 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 34 | 37.2558 | -119.745 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0121488 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979302 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | RECLOSER | 3520 | 20241010 | 1011 | 20241010 | 1500 | 2591467 | 289 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 24 | 6936 | 37.0547 | -120.5489 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0121728 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979501 | 0 | Non-EPSS | N | 2024 | C- GRD
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 11900 | 20241010 | 1247 | 20241010 | 1310 | 2591614 | 23 | Distribution Circuit | Animal | Squirrel | 222 | 5106 | 37.334 | -119.6447 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0121825 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979544 | 0 | EPSS Ckt | Y | 2024 | B- GRD- INST OC
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | TRANSFORMER | 319042344154 | 20241010 | 1322 | 20241010 | 1339 | 2591646 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 17 | 37.7126 | -120.8321 | No | Partly Cloudy;32-90 F | Secondary | Normal | 24-0121843 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979550 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | TRANSFORMER | 318997822403 | 20241010 | 1435 | 20241010 | 1658 | 2591685 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 143 | 37.1142 | -120.8446 | No | Overcast;32-90 F | Fuse | Broken | 24-0121975 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979578 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | JUMPER | OJ 1/E/OF CGC# 319626919838 | 20241010 | 1602 | 20241010 | 1818 | 2591747 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 272 | 37.0449 | -120.6277 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0121944 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979572 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 9991 | 20241010 | 1741 | 20241010 | 2058 | 2591812 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 394 | 36.9888 | -120.8735 | No | Overcast;32-90 F |  |  | 24-0122011 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1979595 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 322046616629 | 20241011 | 744 | 20241011 | 1521 | 2592029 | 457 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 1828 | 36.9544 | -119.8015 | No | Partly Cloudy;32-90 F |  |  | 24-0122333 | OH | Sus | 46338250 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979835 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320922849079 | 20241011 | 747 | 20241011 | 810 | 2592028 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 92 | 37.8474 | -120.1814 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0122088 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979658 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | OCB | 1703/2 | 20241011 | 849 | 20241011 | 955 | 2592140 | 66 | Distribution Circuit | Animal | Squirrel | 3116 | 205656 | 37.9799 | -120.4136 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0122127 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1979724 | 0 | EPSS Ckt | Y | 2024 | B- GRD- INST OC
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 7407 | 20241011 | 903 | 20241011 | 1025 | 2592169 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 82 | 37.4441 | -119.7994 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0122135 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979743 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | JUMPER | OJ'S 1 N/OF CGC# 320117613335 | 20241011 | 912 | 20241011 | 1320 | 2592150 | 248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 10416 | 36.867 | -120.4608 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0122129 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979730 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6875 | 20241011 | 1300 | 20241011 | 1547 | 2592408 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1002 | 36.9094 | -120.0718 | No | Clear;32-90 F |  |  | 24-0122414 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1979862 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | SWITCH | 26663 | 20241012 | 143 | 20241012 | 654 | 2592637 | 311 | Distribution Circuit | 3rd Party | Vehicle | 59 | 18349 | 37.9657 | -120.2802 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0122475 | OH | Sus | 35587380 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979901 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 7034 | 20241012 | 1108 | 20241012 | 1257 | 2592954 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 727 | 37.2673 | -120.5973 | No | Clear;32-90 F |  |  | 24-0122582 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980008 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | T6908 | 20241012 | 1945 | 20241012 | 2225 | 2593239 | 160 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 3120 | 37.2594 | -121.016 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0122630 | UG | Sus | 35587294 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980063 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | 191939 | 20241013 | 2106 | 20241013 | 2305 | 2593774 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 8925 | 37.351 | -120.9809 | No | Clear;32-90 F |  |  | 24-0122735 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1980165 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 361367 | 20241014 | 46 | 20241014 | 215 | 2593790 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 445 | 37.3112 | -120.3608 | No | Clear;32-90 F |  |  | 24-0122744 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1980174 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7887 | 20241014 | 414 | 20241014 | 725 | 2593828 | 191 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1910 | 37.3267 | -120.2518 | No | Clear;32-90 F |  |  | 24-0122774 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1980199 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 9559 | 20241014 | 732 | 20241014 | 845 | 2593901 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 536 | 37.1894 | -120.7084 | No | Fog;32-90 F |  |  | 24-0122838 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980362 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | TRANSFORMER | 322058014958 | 20241014 | 819 | 20241014 | 905 | 2593895 | 46 | Transformer only | Vegetation | Tree - fell into line | 3 | 138 | 36.9086 | -119.798 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0122787 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980226 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321706415590 | 20241014 | 1152 | 20241014 | 1333 | 2594349 | 101 | Transformer only | Animal | Squirrel | 1 | 101 | 36.9265 | -119.9172 | No | Clear;32-90 F | Service conductor | Broken | 24-0122981 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980450 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1103 | 252311103 | OCB | 1103/2 | 20241014 | 1206 | 20241014 | 1522 | 2594268 | 196 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 5616 | 36.7203 | -120.4588 | No | Clear;32-90 F | Transformer (UG) | Arcing | 24-0122925 | UG | Sus | 35587577 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980426 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319591830782 | 20241015 | 728 | 20241015 | 1033 | 2594859 | 185 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 370 | 37.3452 | -120.6416 | No | Fog;32-90 F | Conductor- Overhead | Deteriorated | 24-0123258 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980652 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 24826 | 20241015 | 817 | 20241015 | 905 | 2594952 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 384 | 37.1201 | -120.4009 | No | Fog;32-90 F |  |  | 24-0123275 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980690 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322099925207 | 20241015 | 845 | 20241015 | 910 | 2595000 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 50 | 37.1902 | -119.7787 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0123245 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980628 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 5691 | 20241015 | 852 | 20241015 | 1204 | 2595031 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1330 | 37.6566 | -120.5642 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0123253 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980640 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1716 | 163191716 | TRANSFORMER | 318750444976 | 20241015 | 952 | 20241015 | 1531 | 2595140 | 339 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2712 | 37.7345 | -120.9329 | No | Clear;32-90 F | Secondary | Broken | 24-0123412 | OH | Sus | 31712863 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980783 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 13099 | 20241015 | 1335 | 20241015 | 2051 | 2595390 | 436 | Distribution Circuit | 3rd Party | Vehicle | 22 | 9592 | 37.0908 | -120.2937 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0123558 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | No | No | 1980824 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 820503 | 20241015 | 1508 | 20241015 | 1738 | 2595451 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 450 | 37.2563 | -120.9989 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0123478 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980805 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322127524440 | 20241015 | 1548 | 20241015 | 1647 | 2595515 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 295 | 37.1692 | -119.7692 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0123515 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1980811 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | TRANSFORMER | 414944054549 | 20241015 | 1602 | 20241016 | 358 | 2595537 | 716 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2212 | 36.8196 | -120.7286 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0123599 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980847 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | TRANSFORMER | 318503046920 | 20241015 | 1707 | 20241015 | 1834 | 2595598 | 87 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 87 | 37.7876 | -121.0195 | No | Clear;32-90 F |  |  | 24-0123582 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1980837 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | OCB | 1102/2 | 20241016 | 301 | 20241016 | 1056 | 2595742 | 475 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1579 | 196887 | 37.5231 | -120.3304 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0123637 | OH | Sus | 46339811 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1980878 | 0 | EPSS Ckt | N | 2024 | A- GRD- SGF- INST OC
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | TRANSFORMER | 319846930098 | 20241016 | 829 | 20241016 | 1644 | 2596077 | 495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 3458 | 37.3267 | -120.5528 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0123890 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981055 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1101 | 252091101 | TRANSFORMER | 319531720295 | 20241016 | 856 | 20241016 | 959 | 2595927 | 63 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 63 | 37.0572 | -120.6616 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0123867 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981050 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 18361 | 20241016 | 1239 | 20241017 | 210 | 2596291 | 811 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 811 | 37.6125 | -121.2206 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0124040 | UG | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1981110 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322535131768 | 20241016 | 1319 | 20241016 | 1344 | 2596315 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 225 | 37.3697 | -119.628 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 24-0124046 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981122 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 6003 | 20241016 | 1342 | 20241017 | 331 | 2596344 | 829 | Distribution Circuit | 3rd Party | Vehicle | 21 | 16625 | 37.0981 | -120.4554 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0124104 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1981146 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | OCB | 1701/2 | 20241016 | 1409 | 20241016 | 1504 | 2596363 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3740 | 205700 | 38.0529 | -120.2172 | No | Overcast-Drizzle;32-90 F | Lightning Arrestor | Broken | 24-0124085 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981137 | 0 | EPSS Ckt | Y | 2024 | SGF
YOSEMITE | STANISLAUS | TAR FLAT-0401 | 163240401 | TRANSFORMER | 320347954135 | 20241016 | 2037 | 20241016 | 2230 | 2596645 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1469 | 37.9868 | -120.3804 | No | Clear;32-90 F | Fuse | Broken | 24-0124276 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981194 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1102 | 252091102 | OTHER | J27387 TWD T14883 | 20241016 | 2344 | 20241017 | 25 | 2596626 | 41 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 164 | 37.0556 | -120.8759 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0124249 | UG | Sus | 35589693 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981181 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1109 | 252421109 | OCB | 1109/2 | 20241017 | 623 | 20241017 | 1130 | 2596798 | 307 | Distribution Circuit | 3rd Party | Vehicle | 289 | 9591 | 37.0551 | -120.3168 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0124311 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981209 | 0 | Non-EPSS | N | 2024 | NA
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | SWITCH | 91063 | 20241017 | 640 | 20241017 | 943 | 2596812 | 183 | Distribution Circuit | 3rd Party | Vehicle | 9 | 1647 | 37.7939 | -120.9583 | Yes | Fog;32-90 F | Pole-Wood | Broken | 24-0124289 | OH | Sus | 35590388 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981210 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241017 | 659 | 20241017 | 823 | 2596816 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 368 | 22299 | 37.9754 | -120.4464 | Yes | Partly Cloudy;32-90 F |  |  | 24-0124325 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981215 | 0 | EPSS Ckt | Y | 2024 | A- B- INST OC
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | RECLOSER | 968888 | 20241017 | 1039 | 20241017 | 1532 | 2597034 | 293 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 228 | 66804 | 37.7108 | -120.6742 | Yes | Clear;32-90 F |  |  | 24-0124472 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981295 | 0 | EPSS Ckt | Y | 2024 | A- C- INST OC
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | TRANSFORMER | 100000044549 | 20241017 | 1045 | 20241017 | 1227 | 2597038 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 102 | 36.8509 | -120.5138 | Yes | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0124544 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981317 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | S2685 | 20241017 | 1253 | 20241018 | 440 | 2597160 | 947 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 71972 | 37.8188 | -120.8688 | Yes | Clear;32-90 F | Conductor- Underground | Broken | 24-0124638 | UG | Sus | 46340722 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981384 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318497229650 | 20241017 | 1420 | 20241017 | 1809 | 2597355 | 229 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 229 | 37.3131 | -121.0177 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0124644 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981390 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 237522 | 20241017 | 2117 | 20241019 | 1155 | 2598006 | 2318 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 37 | 85766 | 37.536 | -121.2758 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124309 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981571 | 0 | EPSS Ckt | N | 2024 | NA
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 318882018363 | 20241018 | 122 | 20241018 | 853 | 2598110 | 451 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2706 | 37.0038 | -120.8837 | No | Clear;32-90 F | Jumper | Burned Open | 24-0124833 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981610 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241018 | 701 | 20241018 | 902 | 2598195 | 121 | Distribution Circuit | Animal | Other | 368 | 23837 | 37.9754 | -120.4464 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0124875 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981643 | 0 | EPSS Ckt | Y | 2024 | A- C- INST OC
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3834 | 20241018 | 723 | 20241018 | 1047 | 2598238 | 204 | Distribution Circuit | Animal | Other | 9 | 1769 | 36.9238 | -120.6549 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125017 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981775 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 1558 | 20241018 | 754 | 20241018 | 1418 | 2598282 | 384 | Distribution Circuit | Company Initiated | Improper Construction | 181 | 22121 | 37.9 | -120.9447 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0124912 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981657 | 0 | EPSS Ckt | Y | 2024 | A- C
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318450429779 | 20241018 | 1123 | 20241018 | 1614 | 2598596 | 291 | Transformer only | Vegetation | Tree - grew into line | 6 | 1746 | 37.3165 | -121.0337 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 24-0125110 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981805 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 439030 | 20241018 | 1159 | 20241018 | 1339 | 2598629 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 405 | 40500 | 37.466 | -119.7557 | No | Clear;32-90 F |  |  | 24-0125085 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981798 | 0 | EPSS Ckt | Y | 2024 | A- C
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 11814 | 20241018 | 1243 | 20241018 | 1333 | 2598662 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 150 | 37.0705 | -120.3031 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0125103 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981803 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1104 | 252091104 | TRANSFORMER | 318997920279 | 20241018 | 1254 | 20241018 | 1524 | 2598676 | 150 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1650 | 37.0563 | -120.8441 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0125197 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981832 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | RECLOSER | 5890 | 20241019 | 752 | 20241019 | 1410 | 2599137 | 378 | Distribution Circuit | 3rd Party | Vehicle | 267 | 14672 | 37.1198 | -120.4371 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0125308 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1981925 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 26922 | 20241019 | 1210 | 20241019 | 1418 | 2599353 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2688 | 37.3473 | -121.0359 | No | Clear;32-90 F |  |  | 24-0125426 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1982013 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | FUSE | 5519 | 20241019 | 1221 | 20241019 | 1230 | 2599346 | 9 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 120 | 1080 | 37.1415 | -119.6791 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123841 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1981996 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | OTHER | J94741 TWD T0966 | 20241019 | 1430 | 20241019 | 1449 | 2599374 | 19 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 95 | 37.3214 | -120.4798 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0125424 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1982011 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1103 | 252451103 | FUSE | 621001 | 20241020 | 953 | 20241020 | 1117 | 2599744 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 336 | 37.1568 | -120.5283 | No | Clear;32-90 F |  |  | 24-0125535 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1982108 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10990 | 20241020 | 1804 | 20241020 | 2038 | 2599903 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 530 | 81620 | 37.4964 | -119.811 | No | Clear;32-90 F | Transformer (OH) | Arcing | 24-0125565 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1982129 | 0 | EPSS Ckt | Y | 2024 | A GRD
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 5288 | 20241020 | 2132 | 20241021 | 948 | 2599947 | 736 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3436 | 37.258 | -120.421 | No | Clear;32-90 F | Jumper | Burned Open | 24-0125584 | OH | Sus | 46342324 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1982147 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321961735104 | 20241021 | 855 | 20241021 | 947 | 2600159 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 52 | 37.4613 | -119.8261 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0125659 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1982255 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322132525430 | 20241021 | 1342 | 20241021 | 1410 | 2600528 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 56 | 37.1963 | -119.7677 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0125871 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1982380 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 759144 | 20241021 | 1529 | 20241022 | 328 | 2600612 | 719 | Distribution Circuit | 3rd Party | Vehicle | 389 | 68425 | 38.005 | -120.4056 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0125967 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1982395 | 0 | EPSS Ckt | Y | 2024 | A-B- INST OC
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 320992518626 | 20241021 | 1742 | 20241021 | 1921 | 2600706 | 99 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 1 | 99 | 37.011 | -120.1606 | No | Clear;32-90 F | Service conductor | Broken | 24-0126030 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1982417 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | TRANSFORMER | 321288817414 | 20241021 | 2035 | 20241021 | 2046 | 2600756 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 66 | 36.9776 | -120.0603 | No | Clear;32-90 F | PGs- Kearneys | Arcing | 24-0126037 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1982419 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | OTHER | J27153 TWD T14822 | 20241021 | 2222 | 20241021 | 2321 | s1982438 | 59 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 59 | 37.3089 | -121.0248 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0125854 | UG | Sus | 35591838 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1982438 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | SECTIONALIZER | 10810 | 20241022 | 837 | 20241022 | 1032 | 2601016 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 5175 | 37.5363 | -120.5166 | No | Clear;32-90 F |  |  | 24-0126160 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1982611 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | RECLOSER | 5550 | 20241022 | 1103 | 20241022 | 1515 | 2601238 | 252 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 274 | 39298 | 37.0838 | -120.2866 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0126251 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1982655 | 0 | Non-EPSS | N | 2024 | B&C
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | TRANSFORMER | 318478729897 | 20241022 | 1156 | 20241022 | 1217 | 2601304 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 63 | 37.3199 | -121.0241 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0126284 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1982665 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1103 | 255121103 | FUSE | 5856 | 20241022 | 1703 | 20241022 | 2356 | 2601590 | 413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 8673 | 36.85 | -119.9481 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0126572 | OH | Sus | 46343410 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1982733 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | TRANSFORMER | 320843522067 | 20241022 | 1830 | 20241023 | 145 | 2601614 | 435 | Transformer only | 3rd Party | Vehicle | 3 | 1305 | 37.1054 | -120.211 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0126505 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1982730 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320567452987 | 20241022 | 2108 | 20241022 | 2207 | 2601668 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 118 | 37.9551 | -120.3044 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0126601 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1982745 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | TRANSFORMER | 319035543585 | 20241023 | 908 | 20241023 | 1034 | 2601950 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 86 | 37.6965 | -120.8343 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0126722 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1982890 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 3705 | 20241023 | 949 | 20241023 | 1420 | 2602075 | 271 | Distribution Circuit | 3rd Party | Vehicle | 27 | 5627 | 37.0002 | -120.8551 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0126806 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1982985 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 482838 | 20241023 | 1804 | 20241023 | 1944 | 2602478 | 100 | Distribution Circuit | 3rd Party | Metallic Balloon | 1429 | 142900 | 37.5247 | -120.3293 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127074 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983060 | 0 | EPSS Ckt | Y | 2024 | A- B
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | TRANSFORMER | 320321813008 | 20241023 | 2003 | 20241023 | 2033 | 2602477 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 30 | 36.8571 | -120.3909 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0127098 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983075 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | 20903 | 20241023 | 2054 | 20241023 | 2147 | 2602576 | 53 | Distribution Circuit | 3rd Party | Metallic Balloon | 76 | 4028 | 37.7324 | -120.9131 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127103 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983079 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | S957 | 20241024 | 841 | 20241024 | 1019 | 2602805 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1666 | 37.7111 | -120.7919 | No | Clear;32-90 F |  |  | 24-0127222 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983235 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | FUSE | 6454 | 20241024 | 845 | 20241024 | 1810 | 2602817 | 565 | Distribution Circuit | 3rd Party | Vehicle | 39 | 5543 | 37.0692 | -120.1933 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0127255 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1983259 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 759144 | 20241024 | 955 | 20241024 | 1127 | 2602950 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 389 | 35788 | 38.005 | -120.4056 | No | Clear;32-90 F |  |  | 24-0127243 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983246 | 0 | EPSS Ckt | Y | 2024 | GRD INST OC
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | JUMPER | OJS 1SP LD SIDE OF CGC 320170854157 | 20241024 | 1111 | 20241024 | 1249 | 2603034 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 294 | 37.9875 | -120.4417 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0127303 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983279 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | AVENA-1701 | 163571701 | FUSE | 5323 | 20241024 | 1503 | 20241024 | 1608 | 2603196 | 65 | Distribution Circuit | 3rd Party | Vehicle | 6 | 390 | 37.8021 | -121.0525 | No | Clear;32-90 F | Anchor or Guy | Normal | 24-0127567 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983346 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20241024 | 1805 | 20241024 | 1954 | 2603314 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 3270 | 37.9913 | -120.4128 | No | Clear;32-90 F |  |  | 24-0127634 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983368 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 90090 | 20241025 | 614 | 20241025 | 958 | 2603542 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2696 | 523120 | 37.9028 | -120.4538 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0127670 | OH | Sus | 46344722 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | Yes | No | 1983402 | 0 | EPSS Ckt | Y | 2024 | DCD SGF
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20241025 | 712 | 20241025 | 1015 | 2603563 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1311 | 161853 | 38.0063 | -120.3474 | No | Clear;32-90 F |  |  | 24-0127686 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983408 | 0 | EPSS Ckt | Y | 2024 | A C
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | JUMPER | 439623 1/3 #1 | 20241025 | 820 | 20241025 | 851 | 2603684 | 31 | Distribution Circuit | Company Initiated | Personnel- company | 29 | 899 | 37.3778 | -120.6233 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0121761 | OH | Sus | 35560126 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983480 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | TRANSFORMER | 318473129951 | 20241025 | 853 | 20241025 | 1035 | 2603697 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 714 | 37.3214 | -121.026 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0127749 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983489 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321964836784 | 20241025 | 944 | 20241025 | 1147 | 2603801 | 123 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 246 | 37.5082 | -119.8237 | No | Clear;32-90 F |  |  | 24-0127861 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983562 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1102 | 254421102 | RECLOSER | 333062 | 20241025 | 1449 | 20241025 | 1650 | 2603990 | 121 | Distribution Circuit | Animal | Bird found | 805 | 83125 | 37.3272 | -119.6492 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0128013 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983599 | 0 | EPSS Ckt | Y | 2024 | A GRD INST OC
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | S731 | 20241025 | 2004 | 20241025 | 2239 | 2604345 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 4495 | 37.8351 | -120.8428 | No | Clear;32-90 F |  |  | 24-0128090 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983639 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | RECLOSER | 905960 | 20241026 | 1416 | 20241026 | 1449 | 2604922 | 33 | Distribution Circuit | Company Initiated | Personnel- company | 2452 | 80916 | 37.2274 | -119.7103 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0128199 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1983806 | 0 | EPSS Ckt | Y | 2024 | DCD
YOSEMITE | YOSEMITE | MADERA-1106 | 252761106 | FUSE | 2658 | 20241026 | 1446 | 20241026 | 1718 | 2604941 | 152 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 5617 | 36.9386 | -120.0512 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0128193 | UG | Sus | 35592901 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1983810 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 80729 | 20241026 | 1653 | 20241026 | 1801 | 2605006 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 1860 | 36.9836 | -120.6273 | No | Overcast;32-90 F |  |  | 24-0128223 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983831 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | RECLOSER | 10890 | 20241027 | 730 | 20241027 | 932 | 2605264 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1373 | 55090 | 37.31 | -119.5845 | No | Overcast;32-90 F |  |  | 24-0128258 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983875 | 0 | EPSS Ckt | Y | 2024 | B- GRD
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 6676 | 20241027 | 1746 | 20241027 | 1940 | 2605511 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 912 | 36.9091 | -119.8209 | No | Overcast;32-90 F |  |  | 24-0128333 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983954 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 98485 | 20241027 | 2215 | 20241028 | 24 | 2605617 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 387 | 37.5076 | -119.8245 | No | Partly Cloudy;32-90 F |  |  | 24-0128345 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1983967 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | S1821 | 20241028 | 950 | 20241028 | 1246 | 2606047 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 3344 | 37.7812 | -120.775 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0128458 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984132 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | TRANSFORMER | T0884 | 20241028 | 1447 | 20241028 | 1754 | 2606425 | 187 | Transformer only | Equipment Failure/Involved | Underground | 10 | 1870 | 37.3543 | -120.5932 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0128648 | UG | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984225 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | RECLOSER | 6010 | 20241028 | 1625 | 20241029 | 114 | 2606514 | 529 | Distribution Circuit | 3rd Party | Vehicle | 1237 | 9181 | 36.967 | -120.0081 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0128738 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1984244 | 0 | Non-EPSS | N | 2024 | B/C
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | RECLOSER | 90120 | 20241029 | 928 | 20241029 | 1333 | 2607115 | 245 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3628 | 251745 | 37.9737 | -120.3748 | No | Clear;32-90 F |  |  | 24-0128900 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984467 | 0 | EPSS Ckt | Y | 2024 | INST OC TGT
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320043029064 | 20241029 | 1147 | 20241029 | 1532 | 2607272 | 225 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 450 | 37.2991 | -120.4846 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0128992 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984540 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | 4387 | 20241029 | 1626 | 20241030 | 258 | 2607698 | 632 | Distribution Circuit | 3rd Party | Vehicle | 35 | 22120 | 37.7103 | -120.8666 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0129230 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Three Phase Fault | 0 | No | Yes | No | 1984612 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 7875 | 20241029 | 1847 | 20241030 | 145 | 2607766 | 418 | Distribution Circuit | 3rd Party | Vehicle | 56 | 23408 | 37.3529 | -120.6583 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0129257 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | Yes | No | 1984622 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1704 | 163711704 | JUMPER | FB 1 S/OF CGC 318946846162 | 20241029 | 2314 | 20241030 | 456 | 2607852 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 684 | 37.7665 | -120.8653 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0129300 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984641 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 5133 | 20241030 | 718 | 20241030 | 1005 | 2607911 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 8183 | 37.0202 | -119.9655 | No | Clear;32-90 F |  |  | 24-0129442 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1984758 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | TRANSFORMER | 100000033388 | 20241030 | 850 | 20241030 | 1036 | 2608069 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 318 | 37.2803 | -120.5631 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0129521 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984863 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | 20679 | 20241030 | 1139 | 20241030 | 1248 | 2608351 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 138 | 37.7546 | -120.765 | No | Clear;32-90 F |  |  | 24-0129600 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984903 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 320030543571 | 20241030 | 1150 | 20241030 | 1246 | 2608350 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 56 | 37.6966 | -120.4905 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0129556 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984875 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | TRANSFORMER | 100000134073 | 20241030 | 1200 | 20241030 | 1437 | 2608360 | 157 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 157 | 37.0899 | -120.5662 | No | Clear;32-90 F |  |  | 24-0129676 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1984939 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | JUMPER | OJ'S 1 E/OF CGC# 322229726231 | 20241030 | 1547 | 20241030 | 1737 | 2608598 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1320 | 37.2171 | -119.7336 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0129711 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984957 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 7007 | 20241030 | 1847 | 20241030 | 2030 | 2608742 | 103 | Distribution Circuit | 3rd Party | Vehicle | 4 | 412 | 37.0928 | -120.5543 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0129766 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984975 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | TRANSFORMER | 319239145669 | 20241030 | 2145 | 20241030 | 2350 | 2608800 | 125 | Transformer only | Company Initiated | Improper Construction | 1 | 125 | 37.7536 | -120.7643 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0129792 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984992 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | RECLOSER | 39256 | 20241031 | 34 | 20241031 | 216 | 2608868 | 102 | Distribution Circuit | Animal | Bird found | 525 | 53550 | 37.9571 | -120.3087 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0129817 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1985015 | 0 | EPSS Ckt | Y | 2024 | AB
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 278740 | 20241031 | 521 | 20241031 | 1059 | 2609040 | 338 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1884 | 188662 | 37.9881 | -120.2845 | No | Overcast;32-90 F |  |  | 24-0129863 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1985053 | 0 | EPSS Ckt | Y | 2024 | BC
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | FUSE | 4914 | 20241031 | 631 | 20241031 | 748 | 2609097 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 3234 | 37.3749 | -120.7606 | No | Overcast;32-90 F |  |  | 24-0129911 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1985078 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 13344 | 20241031 | 653 | 20241031 | 813 | 2609105 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 240 | 37.4424 | -120.6304 | No | Overcast-Fog;32-90 F |  |  | 24-0129939 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1985122 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | RECLOSER | 407366 | 20241031 | 804 | 20241031 | 935 | 2609168 | 91 | Distribution Circuit | Animal | Squirrel | 1156 | 98724 | 37.9788 | -120.3729 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0129916 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1985090 | 0 | EPSS Ckt | Y | 2024 | A & B
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | TRANSFORMER | 320355154076 | 20241031 | 1012 | 20241031 | 1622 | 2609428 | 370 | Transformer only | Animal | Squirrel | 1 | 370 | 37.9852 | -120.3778 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0130016 | OH | Sus | 31714700 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1985225 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | TRANSFORMER | T14867 | 20241031 | 1015 | 20241031 | 1310 | 2609434 | 175 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 175 | 37.3361 | -120.903 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0130088 | OH | Sus | 46354371 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1985250 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | OCB | 1108/2 | 20241031 | 1412 | 20241101 | 325 | s1985363 | 741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1807 | 208840 | 37.36 | -120.6145 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0130244 | OH | Sus | 31714733 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1985363 | 0 | Non-EPSS | N | 2024 | A & GRD
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | TRANSFORMER | 319664231439 | 20241031 | 1625 | 20241101 | 329 | 2609825 | 664 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1328 | 37.3635 | -120.6166 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0130310 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1985327 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 8673 | 20241031 | 1643 | 20241031 | 1929 | 2609842 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2547 | 37.3821 | -120.6491 | No | Clear;32-90 F |  |  | 24-0130327 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1985338 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 630815 | 20241031 | 1649 | 20241031 | 1949 | 2609846 | 180 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 2521 | 37.3781 | -120.6956 | No | Clear;32-90 F |  |  | 24-0130329 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1985340 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 7963 | 20241031 | 1752 | 20241031 | 2127 | 2609850 | 215 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 18490 | 37.3674 | -120.6262 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0130244 | OH | Sus | 31714637 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1985329 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 100000012940 | 20241101 | 811 | 20241101 | 1212 | 2610070 | 241 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 241 | 37.0563 | -120.3702 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0130555 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985550 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | 25187 | 20241101 | 836 | 20241101 | 908 | 2610105 | 32 | Distribution Circuit | Company Initiated | Improper Construction | 1 | 32 | 37.7683 | -121.0511 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0130409 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1985428 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | JUMPER | OJ'S @ CGC# 319138346937 | 20241101 | 927 | 20241101 | 1327 | 2610150 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 720 | 37.7885 | -120.7994 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0130427 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985460 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321820417843 | 20241101 | 1027 | 20241101 | 1236 | 2610249 | 129 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 129 | 36.9886 | -119.8772 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0130484 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985509 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BIOLA-1101 | 252211101 | FUSE | 6959 | 20241101 | 1058 | 20241101 | 1239 | 2610303 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 606 | 36.8294 | -120.0832 | No | Clear;32-90 F |  |  | 24-0130561 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985554 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | TRANSFORMER | 319086846620 | 20241101 | 1245 | 20241101 | 2056 | 2610470 | 491 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 491 | 37.7798 | -120.8168 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0130583 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985563 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 5378 | 20241101 | 1436 | 20241101 | 1546 | 2610569 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 280 | 36.9385 | -120.1117 | No | Clear;32-90 F |  |  | 24-0130686 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985596 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322758926569 | 20241101 | 1505 | 20241101 | 1531 | 2610630 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 52 | 37.2274 | -119.5537 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0130669 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985590 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 4239 | 20241101 | 1610 | 20241101 | 2303 | 2610672 | 413 | Distribution Circuit | 3rd Party | Vehicle | 14 | 5737 | 37.2855 | -120.4697 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0130619 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985599 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | FUSE | 9645 | 20241101 | 1748 | 20241101 | 2124 | 2610734 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2376 | 36.7294 | -120.3146 | No | Partly Cloudy;32-90 F |  |  | 24-0130762 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985636 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | OCB | 1102/2 | 20241102 | 204 | 20241102 | 630 | 2611095 | 266 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1579 | 259518 | 37.5231 | -120.3304 | No | Overcast;32-90 F |  |  | 24-0130813 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985676 | 0 | EPSS Ckt | N | 2024 | AC
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | FUSE | 9508 | 20241102 | 325 | 20241102 | 904 | 2611158 | 339 | Distribution Circuit | Animal | Other | 5 | 1695 | 36.8068 | -120.7142 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Normal | 24-0130889 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985798 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 4496 | 20241102 | 356 | 20241102 | 1340 | 2611165 | 584 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 7008 | 37.1999 | -120.3163 | No | Clear;32-90 F |  |  | 24-0130971 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985870 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1103 | 255391103 | FUSE | 6585 | 20241102 | 418 | 20241102 | 1158 | 2611171 | 460 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 19 | 8740 | 36.9692 | -120.2203 | No | Overcast-Rain;32-90 F |  |  | 24-0130946 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985842 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | FUSE | 1589 | 20241102 | 427 | 20241102 | 804 | 2611177 | 217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 12718 | 36.9233 | -119.8762 | No | Overcast-Drizzle;32-90 F |  |  | 24-0130859 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985732 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 9576 | 20241102 | 450 | 20241102 | 1016 | 2611194 | 326 | Distribution Circuit | Animal | Other | 3 | 978 | 36.9179 | -120.4413 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 24-0130928 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985827 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 6887 | 20241102 | 456 | 20241102 | 1802 | 2611198 | 786 | Distribution Circuit | Animal | Other | 40 | 11512 | 36.9592 | -119.9121 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 24-0130879 | OH | Sus | 46370263 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1985782 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 2296 | 20241102 | 611 | 20241102 | 718 | 2611267 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 268 | 37.4537 | -120.5578 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0130851 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985721 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | TRANSFORMER | 319353030007 | 20241102 | 622 | 20241102 | 823 | 2611274 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 363 | 37.3235 | -120.724 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Broken | 24-0130864 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985757 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 21066 | 20241102 | 754 | 20241102 | 1851 | 2611393 | 657 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3177 | 37.5067 | -120.4212 | No | Overcast-Drizzle;32-90 F | Insulator | Burned/flashed | 24-0130932 | OH | Sus | 46371760 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985833 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | RECLOSER | 6460 | 20241102 | 926 | 20241102 | 1744 | 2611534 | 498 | Distribution Circuit | Equipment Failure/Involved | Overhead | 591 | 18077 | 36.9667 | -119.8928 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 24-0130902 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | No | No | 1985810 | 0 | Non-EPSS | N | 2024 | B-C-GRD
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | FUSE | 775859 | 20241102 | 1012 | 20241103 | 635 | 2611642 | 1223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 6115 | 36.9309 | -120.3825 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0130943 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985839 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 321819815686 | 20241102 | 1015 | 20241102 | 1425 | 2611584 | 250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 176 | 3918 | 36.9293 | -119.8785 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0130948 | OH | Sus | 31715315 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985843 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1112 | 252761112 | TRANSFORMER | 321153115986 | 20241102 | 1216 | 20241102 | 1256 | 2611705 | 40 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 160 | 36.9385 | -120.107 | No | Partly Cloudy;32-90 F |  |  | 24-0130962 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1985861 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | RECLOSER | 731524 | 20241102 | 1241 | 20241102 | 1429 | 2611726 | 108 | Distribution Circuit | 3rd Party | Vehicle | 96 | 10368 | 37.155 | -119.7343 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0130925 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985857 | 0 | EPSS Ckt | N | 2024 | NA
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319535132916 | 20241102 | 1242 | 20241102 | 1429 | 2611728 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 107 | 37.4039 | -120.6602 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0130980 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985877 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | FUSE | 13224 | 20241102 | 1329 | 20241103 | 110 | 2611759 | 701 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3015 | 37.0042 | -119.8719 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0131012 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1985891 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 310816 | 20241102 | 1407 | 20241102 | 1537 | 2611769 | 90 | Distribution Circuit | Company Initiated | Personnel- company | 195 | 17550 | 37.5335 | -119.8351 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0130977 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985872 | 0 | EPSS Ckt | N | 2024 | B-C
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 7744 | 20241102 | 1820 | 20241102 | 1945 | 2611853 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 340 | 37.1417 | -120.4333 | No | Clear;32-90 F |  |  | 24-0131044 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985910 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | RECLOSER | 7190 | 20241103 | 22 | 20241103 | 1109 | 2612100 | 647 | Distribution Circuit | 3rd Party | Vehicle | 950 | 61018 | 37.3624 | -120.6412 | No | Fog;32-90 F | Pole-Wood | Broken | 24-0131070 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985927 | 0 | Non-EPSS | N | 2024 | SGF
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20241103 | 353 | 20241103 | 542 | 2612131 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 196 | 12828 | 37.8998 | -120.4541 | No | Clear;32-90 F |  |  | 24-0131076 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985934 | 0 | EPSS Ckt | Y | 2024 | AB
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6875 | 20241103 | 454 | 20241103 | 626 | 2612151 | 92 | Distribution Circuit | Animal | Bird found | 4 | 368 | 36.9094 | -120.0718 | No | Fog;32-90 F | Conductor- Overhead | Normal | 24-0131078 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985938 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1102 | 253981102 | FUSE | 6599 | 20241103 | 515 | 20241103 | 716 | 2612152 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 363 | 36.8948 | -120.1689 | No | Partly Cloudy;32-90 F |  |  | 24-0131084 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985948 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241103 | 605 | 20241103 | 659 | 2612159 | 54 | Distribution Circuit | Animal | Bird found | 368 | 19872 | 37.9754 | -120.4464 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131080 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985940 | 0 | EPSS Ckt | Y | 2024 | A- B- INST OC
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 6755 | 20241103 | 758 | 20241103 | 1154 | 2612417 | 236 | Distribution Circuit | Animal | Bird found | 3 | 708 | 36.9817 | -120.1379 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131126 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985997 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | SWITCH | 1119/2 | 20241103 | 807 | 20241103 | 1650 | 2612194 | 517 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1527 | 19098 | 36.9232 | -120.0551 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0131087 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985950 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 875697 | 20241103 | 807 | 20241103 | 1017 | 2612321 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 130 | 36.8512 | -120.0328 | No | Clear;32-90 F |  |  | 24-0131111 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985981 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | SWITCH | S1193 | 20241103 | 930 | 20241103 | 1553 | 2612284 | 383 | Distribution Circuit | 3rd Party | Vehicle | 1093 | 333407 | 37.7766 | -120.788 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0131103 | OH | Sus | 35595662 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1985972 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 376707 | 20241103 | 945 | 20241103 | 1107 | 2612308 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 246 | 36.9035 | -120.056 | No | Partly Cloudy;32-90 F |  |  | 24-0131118 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1985989 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1102 | 254301102 | RECLOSER | 90190 | 20241103 | 1055 | 20241103 | 1131 | 2612395 | 36 | Distribution Circuit | Vegetation | Tree - branch fell on line | 54 | 1944 | 37.3321 | -120.4172 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131115 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985986 | 0 | Non-EPSS | N | 2024 | B AND C
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23223 | 20241103 | 1101 | 20241103 | 1424 | 2612408 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 10799 | 37.9785 | -120.3151 | No | Clear;32-90 F | Other | Broken | 24-0131125 | OH | Sus | 46379945 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985996 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | RECLOSER | 30980 | 20241103 | 1215 | 20241103 | 1930 | 2612440 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 2993 | 182555 | 37.3044 | -120.4833 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131132 | OH | Sus | 46378724 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1986001 | 0 | Non-EPSS | N | 2024 | B- GRD
YOSEMITE | YOSEMITE | MENDOTA-1104 | 252311104 | RECLOSER | 3630 | 20241103 | 1239 | 20241104 | 255 | 2612499 | 856 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 19184 | 36.6912 | -120.4598 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0131133 | OH | Sus | 31716384 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1986003 | 0 | Non-EPSS | N | 2024 | A-B-C
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 482838 | 20241103 | 1403 | 20241103 | 1814 | 2612550 | 251 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1429 | 358679 | 37.5247 | -120.3293 | No | Clear;32-90 F |  |  | 24-0131147 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1986014 | 0 | EPSS Ckt | Y | 2024 | A-B- INST OC
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | 318521427575 | 20241103 | 1708 | 20241103 | 2058 | 2612675 | 230 | Transformer only | Vegetation | Tree - fell into line | 5 | 1150 | 37.2562 | -121.0089 | No | Clear;32-90 F | Transformer | Normal | 24-0131206 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986039 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | TRANSFORMER | 319487032332 | 20241103 | 1722 | 20241104 | 1526 | 2612677 | 1324 | Transformer only | Vegetation | Other ground vegetation | 2 | 2648 | 37.3878 | -120.6771 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0131207 | OH | Sus | 31716464 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986041 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6527 | 20241104 | 707 | 20241104 | 836 | 2612929 | 89 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 89 | 36.9325 | -120.0739 | No | Clear;32-90 F |  |  | 24-0131286 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986141 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1112 | 252761112 | FUSE | 5981 | 20241104 | 734 | 20241104 | 949 | 2612955 | 135 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 135 | 36.9359 | -120.0987 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0131257 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986091 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 3509 | 20241104 | 743 | 20241104 | 1046 | 2612962 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 183 | 36.7258 | -120.764 | No | Clear;32-90 F |  |  | 24-0131363 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1986264 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6071 | 20241104 | 754 | 20241104 | 900 | 2612972 | 66 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 66 | 36.8359 | -120.0545 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0131319 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986196 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 319987535275 | 20241104 | 829 | 20241104 | 1035 | 2613034 | 126 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 126 | 37.4701 | -120.5054 | No | Clear;32-90 F |  |  | 24-0131377 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1986274 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1703 | 163711703 | FUSE | 4183 | 20241104 | 858 | 20241104 | 1630 | 2613084 | 452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1088 | 37.7623 | -120.7749 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0131416 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1986289 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PINECREST-0401 | 163160401 | FUSE | 1863 | 20241104 | 915 | 20241104 | 1018 | 2613116 | 63 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 4725 | 38.1899 | -119.987 | No | Clear;32-90 F | Other | Deteriorated | 24-0131317 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986179 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319407044510 | 20241104 | 945 | 20241104 | 1835 | 2613503 | 530 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 530 | 37.7221 | -120.7065 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0131546 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986332 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1102 | 253671102 | FUSE | UN# FUSES E OF CGC# 415584047656 | 20241104 | 1121 | 20241104 | 1525 | 2613569 | 244 | Distribution Circuit | Animal | Other | 4 | 976 | 36.6326 | -120.5051 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0131595 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1986362 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | TRANSFORMER | 318438127861 | 20241104 | 1137 | 20241104 | 1541 | 2613335 | 244 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 244 | 37.2638 | -121.0371 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0131469 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986314 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 376707 | 20241104 | 1204 | 20241104 | 1317 | 2613357 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 219 | 36.9035 | -120.056 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0131483 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986318 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322189025745 | 20241104 | 1439 | 20241104 | 2215 | 2613523 | 456 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 912 | 37.2054 | -119.7485 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0131645 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986372 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | FUSE | 9655 | 20241105 | 417 | 20241105 | 657 | 2613894 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 427 | 36.7901 | -120.3625 | Yes | Clear;32-90 F |  |  | 24-0131829 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986431 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | TRANSFORMER | 322249018331 | 20241105 | 1038 | 20241105 | 1228 | 2614243 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 220 | 37.001 | -119.7307 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0132083 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986642 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | OTHER | 1 PHASE OF WIRE DOWN | 20241105 | 1256 | 20241105 | 1536 | 2614460 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1920 | 37.0813 | -120.6555 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132146 | OH | Sus | 46381926 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | Yes | No | 1986666 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 63502 | 20241105 | 1419 | 20241105 | 1634 | 2614454 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1311 | 90262 | 38.0456 | -120.3921 | Yes | Clear;32-90 F |  |  | 24-0132141 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986663 | 0 | EPSS Ckt | Y | 2024 | B
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322215035612 | 20241105 | 1618 | 20241105 | 2237 | 2614566 | 379 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 379 | 37.4744 | -119.7384 | Yes | Clear;32-90 F |  |  | 24-0132272 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986687 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 237522 | 20241105 | 2124 | 20241106 | 1617 | 2614988 | 1133 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 37 | 41921 | 37.536 | -121.2758 | Yes | Partly Cloudy;32-90 F | Recloser | Normal | 24-0131158 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986803 | 0 | EPSS Ckt | N | 2024 | n/a
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20241105 | 2137 | 20241105 | 2303 | 2615002 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1312 | 109016 | 38.0063 | -120.3474 | Yes | Partly Cloudy;32-90 F | Capacitor | Failed/Faulted | 24-0132293 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986809 | 0 | EPSS Ckt | Y | 2024 | B
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20241106 | 2 | 20241106 | 146 | 2615225 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 3120 | 37.9913 | -120.4128 | No | Partly Cloudy;32-90 F |  |  | 24-0132325 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1986897 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | SWITCH | 959 | 20241106 | 509 | 20241106 | 1024 | 2615545 | 301 | Distribution Circuit | 3rd Party | Vehicle | 94 | 18842 | 37.8973 | -120.8438 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0132364 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986932 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | FUSE | 2081 | 20241106 | 613 | 20241106 | 740 | 2615633 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 261 | 37.7762 | -120.8073 | No | Clear;32-90 F |  |  | 24-0132408 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1986990 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | TRANSFORMER | 319231114878 | 20241106 | 1004 | 20241106 | 1020 | 2616485 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 16 | 36.9078 | -120.7639 | No | Clear;32-90 F | Insulator | Broken | 24-0132546 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987189 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322119524372 | 20241106 | 1120 | 20241106 | 1133 | 2616051 | 13 | Transformer only | Equipment Failure/Involved | Underground | 1 | 13 | 37.1672 | -119.772 | No | Clear;32-90 F | Service conductor | Deteriorated | 24-0132606 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987225 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 11547 | 20241106 | 1510 | 20241106 | 1603 | 2617014 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 1166 | 37.171 | -120.3832 | No | Clear;32-90 F |  |  | 24-0132837 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1987308 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320554623535 | 20241106 | 1950 | 20241106 | 2033 | 2617275 | 43 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 43 | 37.146 | -120.311 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0132896 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987333 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241107 | 612 | 20241107 | 847 | 2617386 | 155 | Distribution Circuit | Animal | Bird found | 368 | 36184 | 37.9754 | -120.4464 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132956 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1987372 | 0 | EPSS Ckt | Y | 2024 | B- C- INST OC
YOSEMITE | YOSEMITE | DAIRYLAND-1110 | 252421110 | TRANSFORMER | 320558516835 | 20241107 | 821 | 20241107 | 1153 | 2617569 | 212 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 212 | 36.9626 | -120.3097 | No | Clear;32-90 F | Jumper | Broken | 24-0133121 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987560 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1701 | 163711701 | SWITCH | S1193 | 20241107 | 1244 | 20241107 | 1554 | 2617972 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 554 | 14732 | 37.7766 | -120.788 | No | Clear;32-90 F | Insulator | Broken | 24-0123721 | OH | Sus | 31675111 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1987575 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | TRANSFORMER | 320109729736 | 20241107 | 1910 | 20241107 | 2005 | 2618240 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 440 | 37.3175 | -120.462 | No | Clear;32-90 F | Secondary | Broken | 24-0133313 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987627 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7028 | 20241107 | 2026 | 20241107 | 2142 | 2618260 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 988 | 37.2994 | -120.6948 | No | Clear;32-90 F |  |  | 24-0133335 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1987644 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2104 | 254702104 | FUSE | 7312 | 20241108 | 712 | 20241108 | 855 | 2618448 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 412 | 37.4911 | -120.6306 | No | Clear;32-90 F |  |  | 24-0133457 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987782 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 258550 | 20241108 | 951 | 20241108 | 1319 | 2618940 | 208 | Distribution Circuit | Animal | Squirrel | 2575 | 525926 | 37.8844 | -120.3058 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133532 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987872 | 0 | EPSS Ckt | Y | 2024 | GRD
YOSEMITE | YOSEMITE | STOREY-1106 | 254611106 | TRANSFORMER | 321260317283 | 20241108 | 1514 | 20241108 | 1605 | 2619199 | 51 | Transformer only | Unknown Cause | Patrol - not conducted | 30 | 1530 | 36.974 | -120.07 | No | Clear;32-90 F |  |  | 24-0133701 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1987934 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 5378 | 20241108 | 1808 | 20241108 | 1943 | 2619340 | 95 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 253 | 36.9385 | -120.1117 | No | Clear;32-90 F |  |  | 24-0133736 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987952 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319670230370 | 20241109 | 253 | 20241109 | 921 | 2619400 | 388 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1164 | 37.3341 | -120.6145 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0133755 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987974 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | RECLOSER | 5740 | 20241109 | 826 | 20241109 | 1823 | 2619576 | 597 | Distribution Circuit | 3rd Party | Vehicle | 503 | 75819 | 36.9828 | -120.2023 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0133776 | OH | Sus | 35596919 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1988023 | 0 | Non-EPSS | N | 2024 | A & C
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 123431 | 20241109 | 927 | 20241109 | 1724 | 2619936 | 477 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 954 | 36.9665 | -120.6265 | No | Partly Cloudy;32-90 F |  |  | 24-0133855 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988118 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 21068 | 20241109 | 1613 | 20241109 | 1709 | 2619903 | 56 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 560 | 37.3604 | -120.6935 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0133854 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988117 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 57879 | 20241109 | 1616 | 20241109 | 1752 | 2619906 | 96 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 96 | 37.2287 | -120.4518 | No | Clear;32-90 F |  |  | 24-0133860 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988123 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2107 | 254272107 | TRANSFORMER | 322046616629 | 20241110 | 315 | 20241110 | 453 | 2620015 | 98 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 392 | 36.9544 | -119.8015 | No | Partly Cloudy;32-90 F |  |  | 24-0133884 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1988155 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | OTHER | CENTER PHASE WIRE DOWN | 20241110 | 707 | 20241110 | 1200 | 2620124 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 1854 | 37.2153 | -120.5154 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0133897 | OH | Sus | 31717200 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | Yes | 1988179 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 90090 | 20241110 | 937 | 20241110 | 1121 | 2620148 | 104 | Distribution Circuit | Animal | Squirrel | 2696 | 127741 | 37.9028 | -120.4538 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133907 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988186 | 0 | EPSS Ckt | Y | 2024 | GROUND- INST OC
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 3382 | 20241110 | 1112 | 20241110 | 1425 | 2620182 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1930 | 37.1008 | -120.8213 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0133945 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988215 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | FUSE | 1769 | 20241110 | 1311 | 20241110 | 1322 | 2620190 | 11 | Distribution Circuit | 3rd Party | Metallic Balloon | 56 | 616 | 37.7878 | -120.8601 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133938 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988207 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 6166 | 20241110 | 1700 | 20241111 | 4 | 2620303 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2968 | 36.9963 | -120.1781 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0133984 | OH | Sus | 46387026 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988247 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | FUSE | S1819 | 20241111 | 543 | 20241111 | 715 | 2620438 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2392 | 37.8036 | -120.9603 | No | Clear;32-90 F |  |  | 24-0134019 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988299 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7734 | 20241111 | 629 | 20241111 | 814 | 2620452 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 315 | 37.2639 | -120.7428 | No | Clear;32-90 F |  |  | 24-0134039 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988328 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 7995 | 20241111 | 727 | 20241111 | 944 | 2620501 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2740 | 37.3117 | -120.4448 | No | Clear;32-90 F |  |  | 24-0134066 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988367 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 24605 | 20241111 | 742 | 20241111 | 846 | 2620513 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 192 | 37.3037 | -120.7673 | No | Clear;32-90 F |  |  | 24-0134045 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988338 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | FUSE | 324471 | 20241111 | 911 | 20241111 | 1037 | 2620619 | 86 | Distribution Circuit | 3rd Party | Vehicle | 1 | 86 | 37.8567 | -120.9367 | No | Partly Cloudy;32-90 F | Other | Broken | 24-0134058 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988355 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | JUMPER | FB S/OF CGC 321327217136 | 20241111 | 913 | 20241111 | 1226 | 2620610 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3281 | 36.9693 | -120.0461 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0134053 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988349 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319144044770 | 20241111 | 1019 | 20241111 | 1055 | 2620812 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 72 | 37.7291 | -120.7971 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0134081 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988388 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 26587 | 20241111 | 1156 | 20241112 | 515 | 2621001 | 1039 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3117 | 37.2877 | -120.799 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0134316 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1988617 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7329 | 20241111 | 1200 | 20241111 | 1635 | 2621010 | 275 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 8250 | 37.4622 | -120.6214 | No | Overcast-Drizzle;32-90 F |  |  | 24-0134282 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988583 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRANSFORMER | 319130045170 | 20241111 | 1205 | 20241111 | 1700 | 2621043 | 295 | Transformer only | Vegetation | Tree - grew into line | 3 | 885 | 37.7401 | -120.8012 | No | Overcast;32-90 F | Service conductor | Broken- wire on ground | 24-0134134 | OH | Sus | 31717266 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988443 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | TRANSFORMER | 319700730273 | 20241111 | 1217 | 20241111 | 1606 | 2621089 | 229 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 229 | 37.3315 | -120.6039 | No | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0134137 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1988448 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 10982 | 20241111 | 1222 | 20241111 | 1459 | 2621093 | 157 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 1413 | 37.2884 | -120.4697 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0134144 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1988454 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 11509 | 20241111 | 1226 | 20241111 | 1638 | 2621090 | 252 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 7560 | 37.3103 | -120.4445 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0134249 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988553 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 482838 | 20241111 | 1235 | 20241111 | 1605 | 2621101 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1429 | 300090 | 37.5247 | -120.3293 | No | Overcast;32-90 F |  |  | 24-0134131 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988440 | 0 | EPSS Ckt | Y | 2024 | A B INSTA OC
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20241111 | 1236 | 20241111 | 1511 | 2621115 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 4680 | 37.9913 | -120.4128 | No | Overcast-Rain;32-90 F |  |  | 24-0134204 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988518 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7677 | 20241111 | 1241 | 20241111 | 1551 | 2621131 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 28768 | 37.3222 | -120.3247 | No | Clear;32-90 F |  |  | 24-0134237 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988547 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | TRANSFORMER | 319601819990 | 20241111 | 1243 | 20241111 | 2022 | 2621132 | 459 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2754 | 37.049 | -120.6371 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 24-0134341 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988645 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | FUSE | 8609 | 20241111 | 1246 | 20241111 | 1647 | 2621139 | 241 | Distribution Circuit | Vegetation | Tree - branch fell on line | 159 | 38319 | 37.2211 | -120.2441 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0134274 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988575 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20241111 | 1259 | 20241111 | 1723 | 2621152 | 264 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 480 | 30770 | 37.4305 | -120.0996 | No | Overcast-Drizzle;32-90 F |  |  | 24-0134135 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988445 | 0 | EPSS Ckt | Y | 2024 | A B INSTA OC
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | RECLOSER | 3830 | 20241111 | 1307 | 20241111 | 2041 | 2621167 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 454 | 150600 | 36.8655 | -120.4719 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0134290 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1988591 | 0 | Non-EPSS | N | 2024 | B & GROUND
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | RECLOSER | 65734 | 20241111 | 1316 | 20241112 | 224 | 2621171 | 788 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 61313 | 37.0108 | -120.3468 | No | Overcast-Drizzle;32-90 F | Insulator | Broken | 24-0134143 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1988453 | 0 | Non-EPSS | N | 2024 | A B C
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | RECLOSER | 9540 | 20241111 | 1335 | 20241111 | 1536 | 2621188 | 121 | Distribution Circuit | Vegetation | Tree - branch fell on line | 411 | 49731 | 36.9042 | -120.0559 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Normal | 24-0134152 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988463 | 0 | Non-EPSS | N | 2024 | A C
YOSEMITE | YOSEMITE | STOREY-1111 | 254611111 | FUSE | 836491 | 20241111 | 1339 | 20241112 | 26 | 2621210 | 647 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 198 | 96484 | 37.011 | -120.0746 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0134239 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988548 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | FUSE | 6545 | 20241111 | 1341 | 20241111 | 1802 | 2621199 | 261 | Distribution Circuit | Vegetation | Tree - branch fell on line | 101 | 26361 | 36.9229 | -119.8821 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0134164 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1988472 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1103 | 253881103 | FUSE | 11946 | 20241111 | 1402 | 20241111 | 1856 | 2621279 | 294 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 19 | 4718 | 37.5044 | -120.3533 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0134292 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988593 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1118 | 255371118 | FUSE | 9508 | 20241111 | 1402 | 20241111 | 1946 | 2621278 | 344 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1147 | 36.8068 | -120.7142 | No | Partly Cloudy;32-90 F |  |  | 24-0134322 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988622 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | RECLOSER | 11480 | 20241111 | 1408 | 20241111 | 1825 | 2621298 | 257 | Distribution Circuit | Equipment Failure/Involved | Overhead | 531 | 42290 | 37.3158 | -120.4865 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0134194 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988508 | 0 | Non-EPSS | N | 2024 | C AND GROUND
YOSEMITE | YOSEMITE | WOODWARD-2108 | 255292108 | RECLOSER | 935396 | 20241111 | 1412 | 20241111 | 1701 | 2621351 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 21448 | 37.0158 | -119.7296 | No | Overcast-Drizzle;32-90 F |  |  | 24-0134172 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988482 | 0 | EPSS Ckt | Y | 2024 | A & C
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 768534 | 20241111 | 1422 | 20241111 | 1742 | 2621377 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 600 | 37.8867 | -120.925 | No | Overcast-Fog;32-90 F |  |  | 24-0134173 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1988488 | 0 | EPSS Ckt | N | 2024 | A B C
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 94866 | 20241111 | 1430 | 20241112 | 1327 | 2621411 | 1377 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 75 | 18960 | 37.7156 | -120.457 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0134300 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988601 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7667 | 20241111 | 1434 | 20241111 | 1749 | 2621445 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2535 | 37.3102 | -120.3813 | No | Overcast-Rain;32-90 F |  |  | 24-0134286 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988587 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 24429 | 20241111 | 1529 | 20241112 | 232 | 2621625 | 663 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 22 | 14586 | 36.7481 | -120.5674 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0134365 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1988669 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321938436197 | 20241111 | 1602 | 20241111 | 1841 | 2621720 | 159 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 636 | 37.4923 | -119.8328 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Broken | 24-0134266 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988567 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | FUSE | 13263 | 20241111 | 1617 | 20241111 | 1658 | 2621752 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 2132 | 36.9679 | -120.0586 | No | Overcast-Rain;32-90 F |  |  | 24-0134267 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988568 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | FUSE | 13267 | 20241111 | 1621 | 20241112 | 630 | 2621728 | 849 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 37 | 31413 | 36.9602 | -120.0713 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0134257 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1988559 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | OCB | 9440 | 20241111 | 1730 | 20241112 | 414 | 2621923 | 644 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1788 | 271236 | 37.4477 | -120.646 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0134295 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1988596 | 0 | Non-EPSS | N | 2024 | A B C TIME OC
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | FUSE | 4199 | 20241111 | 2139 | 20241111 | 2250 | 2622191 | 71 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 41 | 2911 | 37.3913 | -120.6287 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0134370 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1988674 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | FUSE | 477665 | 20241112 | 616 | 20241112 | 1714 | 2622374 | 658 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 1974 | 37.1125 | -120.8702 | No | Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0134492 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1988848 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1112 | 255361112 | FUSE | 11622 | 20241112 | 1312 | 20241112 | 2321 | 2623045 | 609 | Distribution Circuit | 3rd Party | Vehicle | 13 | 1905 | 37.2074 | -120.3357 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0134736 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1989060 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1102 | 252451102 | SECTIONALIZER | 325829 | 20241112 | 1328 | 20241113 | 146 | 2623060 | 738 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 36 | 16783 | 37.0541 | -120.4924 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0134681 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989079 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | TRANSFORMER | 320519220262 | 20241112 | 1335 | 20241112 | 1755 | 2623073 | 260 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 260 | 37.0561 | -120.3217 | No | Clear;32-90 F |  |  | 24-0134839 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1989102 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320248552680 | 20241112 | 1634 | 20241112 | 1752 | 2623310 | 78 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 312 | 37.9468 | -120.4148 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0134804 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989080 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320735754550 | 20241112 | 1803 | 20241112 | 1859 | 2623391 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 168 | 37.9977 | -120.2456 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0134845 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989105 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320579753672 | 20241112 | 1809 | 20241112 | 1908 | 2623390 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 118 | 37.9744 | -120.3005 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0134844 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1989104 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | FUSE | 26159 | 20241112 | 1948 | 20241113 | 37 | 2623428 | 289 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 8670 | 36.8396 | -120.4415 | No | Partly Cloudy;32-90 F |  |  | 24-0134860 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989114 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | RECLOSER | 910120 | 20241113 | 747 | 20241113 | 909 | 2623687 | 82 | Distribution Circuit | Animal | Squirrel | 142 | 11644 | 37.3342 | -119.6514 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0134949 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989227 | 0 | EPSS Ckt | Y | 2024 | NONE
YOSEMITE | YOSEMITE | PANOCHE-1102 | 253671102 | OTHER | WIRE DOWN @ CGC 415454149030 TWD W | 20241113 | 1120 | 20241113 | 1606 | 2623975 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 572 | 36.6696 | -120.5501 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0135117 | OH | Sus | 31717385 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | Yes | 1989394 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | TRANSFORMER | 320078737785 | 20241113 | 1432 | 20241113 | 2140 | 2624186 | 428 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 428 | 37.5375 | -120.4736 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0135264 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1989445 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320890648965 | 20241113 | 1433 | 20241113 | 1449 | 2624176 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 32 | 37.8445 | -120.1929 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0135187 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989425 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1103 | 253471103 | OCB | 1103/2 | 20241113 | 1516 | 20241113 | 2145 | 2624222 | 389 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 624 | 60694 | 36.8508 | -120.4658 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0135230 | OH | Sus | 31717392 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1989438 | 0 | Non-EPSS | N | 2024 | A- GRD
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | 77073 | 20241113 | 1611 | 20241113 | 1710 | 2624255 | 59 | Distribution Circuit | Animal | Bird found | 11 | 649 | 37.9736 | -120.359 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 24-0135278 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989458 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | OCB | 1117/2 | 20241113 | 1945 | 20241113 | 2212 | 2624490 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 203 | 29841 | 36.8859 | -120.6559 | No | Overcast;32-90 F | Capacitor | Broken | 24-0135306 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1989479 | 0 | EPSS Ckt | N | 2024 | A-B-C- TIME OC
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322201628480 | 20241113 | 2000 | 20241113 | 2044 | 2624492 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 44 | 37.2797 | -119.7443 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0135307 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1989480 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | WILSON-1101 | 254301101 | TRANSFORMER | 320231128944 | 20241114 | 757 | 20241114 | 843 | 2624682 | 46 | Transformer only | Animal | Other | 6 | 276 | 37.2952 | -120.4201 | No | Partly Cloudy-Fog;32-90 F | Service conductor | Together | 24-0135395 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989602 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320560430011 | 20241114 | 819 | 20241114 | 942 | 2624733 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 83 | 37.3231 | -120.306 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0135434 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989680 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 961393 | 20241114 | 1208 | 20241114 | 1543 | 2625079 | 215 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 4945 | 37.9442 | -120.2429 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0135516 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989738 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | FUSE | 1526 | 20241114 | 1230 | 20241114 | 1852 | 2625125 | 382 | Distribution Circuit | Equipment Failure/Involved | Underground | 175 | 22750 | 37.3153 | -120.4731 | No | Overcast;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0135594 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989773 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 2333 | 20241114 | 1414 | 20241114 | 1613 | 2625207 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2093 | 38.0412 | -120.3199 | No | Partly Cloudy;32-90 F |  |  | 24-0135654 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989804 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321071245319 | 20241114 | 1740 | 20241114 | 1830 | 2625331 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 150 | 37.7464 | -120.1305 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0135695 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989810 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321071245319 | 20241114 | 1740 | 20241114 | 1830 | 2625331 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 150 | 37.7464 | -120.1305 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0135695 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989810 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 21072 | 20241114 | 1904 | 20241114 | 2011 | 2625399 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1273 | 37.3611 | -120.6867 | No | Partly Cloudy;32-90 F |  |  | 24-0135726 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989823 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1102 | 253881102 | TRANSFORMER | 320121830261 | 20241114 | 2023 | 20241115 | 7 | 2625445 | 224 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 448 | 37.332 | -120.4578 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0135741 | OH | Sus | 31717526 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1989829 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | JUMPER | OJ 2/E/OF FUCO 3882 | 20241114 | 2314 | 20241115 | 410 | 2625492 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2354 | 37.0596 | -120.8643 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0135746 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1989843 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3518 | 20241115 | 652 | 20241115 | 950 | 2625669 | 178 | Distribution Circuit | Animal | Bird found | 25 | 4450 | 36.96 | -120.6581 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0135872 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990046 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 84318 | 20241115 | 743 | 20241115 | 915 | 2625697 | 38 | Distribution Circuit | Animal | Squirrel | 780 | 29640 | 37.8546 | -120.2083 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0135797 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1989876 | 0 | EPSS Ckt | Y | 2024 | A&B
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 8640 | 20241115 | 925 | 20241115 | 1423 | 2625937 | 298 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 997 | 110234 | 37.5825 | -121.2084 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0135859 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1990032 | 0 | EPSS Ckt | N | 2024 | GRD- SGF
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L543 | 20241115 | 1008 | 20241115 | 1154 | 2625995 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 424 | 38.0208 | -120.3201 | No | Overcast-Fog;32-90 F |  |  | 24-0135932 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990079 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1101 | 162741101 | FUSE | 1027 | 20241115 | 1100 | 20241115 | 1416 | 2626050 | 196 | Distribution Circuit | Company Initiated | Improper Construction | 8 | 1568 | 37.3473 | -121.015 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0135984 | OH | Sus | 46389916 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990103 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | RECLOSER | 99922 | 20241115 | 1135 | 20241115 | 1152 | 2626081 | 17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 697 | 11849 | 36.9693 | -120.0562 | No | Overcast;32-90 F | Switch (OH) | Arcing | 24-0135924 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990075 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 4399 | 20241115 | 1230 | 20241115 | 1511 | 2626144 | 161 | Distribution Circuit | Animal | Other | 1 | 215 | 37.5355 | -121.2634 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0136028 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990118 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 8674 | 20241115 | 1425 | 20241115 | 2155 | 2626276 | 450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 3896 | 37.3592 | -120.6685 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0136054 | OH | Sus | 31717635 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990122 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 11539 | 20241116 | 827 | 20241116 | 1655 | 2626812 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1158 | 37.3642 | -120.6035 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0136197 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990258 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 5585 | 20241116 | 1243 | 20241116 | 1421 | 2627026 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3332 | 37.3999 | -119.6285 | No | Clear;32-90 F |  |  | 24-0136260 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990293 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | FUSE | 25437 | 20241116 | 1353 | 20241116 | 1501 | 2627069 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 272 | 37.3385 | -120.6238 | No | Clear;32-90 F |  |  | 24-0136259 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990292 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 4669 | 20241117 | 633 | 20241117 | 938 | 2627280 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 864 | 37.1857 | -120.6006 | No | Clear;32-90 F |  |  | 24-0136301 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990365 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1111 | 254461111 | FUSE | 2041 | 20241117 | 705 | 20241117 | 936 | 2627285 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 604 | 36.931 | -120.3422 | No | Clear;32-90 F |  |  | 24-0136302 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990366 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | S1439 | 20241117 | 1116 | 20241117 | 1741 | 2627422 | 121 | Distribution Circuit | Animal | Squirrel | 78 | 9438 | 37.7932 | -121.0147 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0136316 | OH | Sus | 31717721 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990380 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | FUSE | 5877 | 20241117 | 1336 | 20241117 | 2006 | 2627506 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1743 | 37.0254 | -120.3572 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0136344 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990404 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRIP-SAVER | 7056 | 20241117 | 1733 | 20241117 | 2209 | 2627598 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 11916 | 37.3599 | -120.6868 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0136358 | OH | Sus | 31717820 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1990416 | 0 | Non-EPSS | N | 2024 | B AND C
YOSEMITE | STANISLAUS | NEWMAN-1102 | 162741102 | FUSE | 24681 | 20241118 | 43 | 20241118 | 836 | 2627719 | 473 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 473 | 37.3186 | -121.0586 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0136372 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990436 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | MTR#1010798096 | 20241118 | 801 | 20241118 | 1047 | 2627851 | 166 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 332 | 37.353 | -120.6757 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0136413 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990504 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | RECLOSER | 90220 | 20241118 | 1333 | 20241118 | 1743 | 2628386 | 250 | Distribution Circuit | 3rd Party | Vehicle | 17 | 394 | 37.2292 | -120.4898 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0136638 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1990689 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 7445 | 20241118 | 1434 | 20241118 | 1508 | 2628467 | 34 | Distribution Circuit | 3rd Party | Metallic Balloon | 41 | 1394 | 37.3107 | -120.3249 | No | Clear;32-90 F | Fuse | Normal | 24-0136711 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990714 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 13102 | 20241118 | 1613 | 20241118 | 1752 | 2628553 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 990 | 37.0798 | -120.2954 | No | Clear;32-90 F |  |  | 24-0136784 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990742 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1101 | 255121101 | TRANSFORMER | 321702716965 | 20241118 | 2109 | 20241119 | 243 | 2628711 | 334 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1670 | 36.9641 | -119.918 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0136820 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990768 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | TRANSFORMER | 320310528695 | 20241119 | 724 | 20241119 | 844 | 2628828 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 240 | 37.2881 | -120.3927 | No | Clear;32-90 F | Fuse | Broken | 24-0136928 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990860 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | FUSE | 21087 | 20241119 | 750 | 20241119 | 1058 | 2628847 | 188 | Distribution Circuit | Company Initiated | Improper Construction | 117 | 21996 | 37.3085 | -120.4616 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0136908 | OH | Sus | 46393828 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1990825 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | T97597 | 20241119 | 818 | 20241119 | 1436 | 2628911 | 378 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 378 | 37.284 | -120.5964 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0136967 | UG | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1990951 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320892949444 | 20241119 | 1425 | 20241119 | 1435 | 2629519 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 60 | 37.8573 | -120.1915 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 24-0137259 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991071 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | FUSE | 20563 | 20241120 | 718 | 20241120 | 1315 | 2630171 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1071 | 37.7452 | -120.8949 | No | Overcast;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0137491 | OH | Sus | 46394531 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1991199 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | FUSE | 5724 | 20241120 | 1105 | 20241120 | 1320 | 2630727 | 135 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 18 | 2430 | 37.3181 | -119.6261 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0137717 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1991409 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4585 | 20241120 | 1227 | 20241120 | 1304 | 2630926 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 129 | 4773 | 37.4543 | -119.8243 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0137720 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991411 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1108 | 252801108 | FUSE | 57897 | 20241120 | 1241 | 20241120 | 1910 | s1991549 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 778 | 37.2735 | -120.5018 | No | Clear;32-90 F | Jumper | Broken | 24-0137961 | OH | Sus | 31718077 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991549 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BIOLA-1102 | 252211102 | RECLOSER | 6170 | 20241120 | 1414 | 20241121 | 253 | 2631337 | 759 | Distribution Circuit | Vegetation | Tree - branch fell on line | 78 | 23516 | 36.7935 | -120.1788 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0137938 | OH | Sus | 46396432 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1991540 | 0 | Non-EPSS | N | 2024 | AC
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | JUMPER | OJ SOURCE SIDE OF 42038 | 20241120 | 1544 | 20241120 | 1637 | 2631506 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 53 | 37.0544 | -120.4055 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0137931 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991531 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | HAMMONDS-1102 | 253401102 | FUSE | 24422 | 20241120 | 1614 | 20241120 | 2144 | 2631581 | 330 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1 | 330 | 36.7298 | -120.6033 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0137970 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991554 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | TRANSFORMER | 319433031669 | 20241121 | 833 | 20241121 | 1225 | 2632398 | 232 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 232 | 37.3698 | -120.6956 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0138298 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991780 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | TRANSFORMER | 322902326008 | 20241121 | 1017 | 20241121 | 1250 | 2632559 | 153 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 306 | 37.2117 | -119.5037 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0138321 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991798 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | JUMPER | OJ 1 POLE S/OF CGC 320678053441 | 20241121 | 1308 | 20241121 | 1510 | 2632805 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 366 | 37.9672 | -120.2654 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0138440 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991850 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | TRANSFORMER | 9838 | 20241121 | 1319 | 20241121 | 1609 | 2632958 | 170 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 2890 | 37.3352 | -120.9048 | No | Overcast;32-90 F |  |  | 24-0138525 | OH | Sus | 31718125 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1991890 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | TRANSFORMER | 320094729514 | 20241121 | 2201 | 20241121 | 2327 | 2633349 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 344 | 37.3112 | -120.4672 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0138699 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1991954 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | JUMPER | OJ 2P N/OF CGC #321024915417 | 20241122 | 1030 | 20241122 | 1218 | 2634229 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 108 | 36.9237 | -120.1496 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0138874 | OH | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1992115 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | FUSE | 13102 | 20241122 | 1523 | 20241122 | 1800 | 2634938 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1047 | 37.0798 | -120.2954 | No | Overcast;32-90 F |  |  | 24-0139235 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992258 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 8646 | 20241122 | 1740 | 20241123 | 41 | 2635167 | 421 | Distribution Circuit | 3rd Party | Vehicle | 40 | 6517 | 37.4183 | -120.614 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0139243 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1992263 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1117 | 255371117 | FUSE | 9673 | 20241122 | 1859 | 20241123 | 452 | 2635381 | 593 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 8302 | 36.8821 | -120.7217 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0139327 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1992334 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BONITA-1101 | 255391101 | FUSE | 88398 | 20241122 | 1927 | 20241122 | 2339 | 2635412 | 252 | Distribution Circuit | 3rd Party | Gun Shot | 27 | 6804 | 37.0183 | -120.1841 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139303 | OH | Sus | 46399126 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1992311 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | S2189 | 20241122 | 2247 | 20241123 | 125 | 2635642 | 158 | Distribution Circuit | Animal | Other | 5 | 790 | 37.273 | -121.0675 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0139372 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992378 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 20241122 | 2311 | 20241122 | 2332 | 2635652 | 21 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 271 | 5691 | 38.03 | -120.2447 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0139344 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992352 | 0 | EPSS Ckt | Y | 2024 | C- GROUND- INST OC
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | RECLOSER | 5040 | 20241122 | 2339 | 20241123 | 945 | 2635665 | 606 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 537 | 120018 | 36.9264 | -120.1105 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0139348 | OH | Sus | 46399068 | CENTRAL VALLEY | NOV | Multi-Fault | 0 | No | Yes | No | 1992356 | 0 | Non-EPSS | N | 2024 | AB- GROUND
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241122 | 2340 | 20241123 | 1 | 2635668 | 21 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 368 | 7728 | 37.9754 | -120.4464 | No | Overcast-Rain;32-90 F |  |  | 24-0139349 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992358 | 0 | EPSS Ckt | Y | 2024 | AC- INST OC
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | T1356 | 20241123 | 9 | 20241123 | 136 | 2635691 | 87 | Transformer only | Unknown Cause | Patrol - found nothing | 19 | 1653 | 37.287 | -120.4919 | No | Overcast-Rain;32-90 F |  |  | 24-0139368 | UG | Sus | 0 | CENTRAL VALLEY | NOV | None | 0 | No | No | No | 1992375 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1111 | 252421111 | FUSE | 862425 | 20241123 | 12 | 20241123 | 1315 | 2635732 | 727 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 17 | 5275 | 37.069 | -120.3186 | No | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0139364 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1992370 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241123 | 15 | 20241123 | 40 | 2635700 | 25 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 368 | 9200 | 37.9754 | -120.4464 | No | Overcast-Rain;32-90 F |  |  | 24-0139357 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992365 | 0 | EPSS Ckt | Y | 2024 | AC- IOC
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 916436 | 20241123 | 16 | 20241123 | 55 | 2635698 | 39 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 461 | 17683 | 37.7217 | -120.2738 | No | Overcast-Heavy Rain;32-90 F |  |  | 24-0139356 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992364 | 0 | EPSS Ckt | Y | 2024 | B & INST OC
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20241123 | 57 | 20241123 | 943 | 2635727 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 688 | 324123 | 38.1888 | -120.0082 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139363 | OH | Sus | 46399156 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | No | 1992369 | 0 | EPSS Ckt | Y | 2024 | C- G- IOC
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9570 | 20241123 | 125 | 20241123 | 216 | 2635739 | 51 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 513 | 25711 | 37.7155 | -120.2024 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0139366 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992372 | 0 | EPSS Ckt | Y | 2024 | AB- IOC
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | RECLOSER | 47488 | 20241123 | 141 | 20241123 | 208 | 2635757 | 27 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 590 | 15930 | 37.9655 | -120.2508 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0139373 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992380 | 0 | EPSS Ckt | Y | 2024 | A & C
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | FUSE | 6616 | 20241123 | 220 | 20241123 | 1430 | 2635768 | 730 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 11 | 8030 | 37.0107 | -120.3845 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0139386 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992392 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | JUMPER | 205056 | 20241123 | 242 | 20241123 | 440 | 2635782 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 189 | 21673 | 36.95 | -120.0737 | No | Overcast-Rain;32-90 F | Jumper | Burned Open | 24-0139385 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1992391 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L2153 | 20241123 | 308 | 20241123 | 535 | 2635785 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 5733 | 37.9491 | -120.2657 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0139398 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992408 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 5325 | 20241123 | 326 | 20241123 | 500 | 2635793 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2444 | 37.5367 | -121.2505 | No | Clear;32-90 F |  |  | 24-0139396 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992403 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 284317 | 20241123 | 349 | 20241123 | 2102 | 2635809 | 1033 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 18 | 12973 | 37.2461 | -121.0777 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0139415 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1992425 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1106 | 253981106 | FUSE | 6753 | 20241123 | 438 | 20241123 | 1605 | 2635821 | 687 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 15 | 2817 | 36.8585 | -120.1304 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0139403 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992410 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321779417659 | 20241123 | 503 | 20241123 | 1328 | 2635828 | 505 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 505 | 36.9835 | -119.8913 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139451 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992459 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | 77073 | 20241123 | 556 | 20241123 | 936 | 2635858 | 220 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 11 | 980 | 37.9736 | -120.359 | No | Overcast-Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0139405 | OH | Sus | 31718457 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992414 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20241123 | 645 | 20241123 | 703 | 2635890 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 480 | 8640 | 37.4305 | -120.0996 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139412 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992421 | 0 | EPSS Ckt | Y | 2024 | B- INST OC
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 6764 | 20241123 | 655 | 20241123 | 1021 | 2635898 | 206 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 1442 | 37.0101 | -120.147 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0139498 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992492 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 321182834676 | 20241123 | 745 | 20241123 | 1452 | 2636170 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 854 | 37.4518 | -120.0923 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Broken | 24-0139510 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992502 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | TRANSFORMER | 318553927665 | 20241123 | 844 | 20241123 | 1400 | 2636068 | 316 | Transformer only | 3rd Party | Vehicle | 4 | 1264 | 37.2587 | -120.9978 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0139496 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992490 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 11517 | 20241123 | 912 | 20241123 | 1005 | 2636084 | 53 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 71 | 37.4799 | -120.5037 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0139486 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992482 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20241123 | 930 | 20241123 | 944 | 2636120 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 478 | 6692 | 37.4305 | -120.0996 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Broken | 24-0139465 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992470 | 0 | EPSS Ckt | Y | 2024 | B- OC
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | JUMPER | FB'S 1 S/OF CGC# 318554327653 | 20241123 | 1108 | 20241123 | 1400 | 2636278 | 172 | Distribution Circuit | 3rd Party | Vehicle | 3 | 516 | 37.258 | -120.9976 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0139516 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992508 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | OTHER | WIRE DOWN JUST N/OF 3343 | 20241123 | 1846 | 20241123 | 2302 | 2636666 | 256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 4608 | 37.9458 | -120.8437 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0139619 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | Yes | 1992576 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1105 | 253881105 | OTHER | CAR POLE W/ WIRE DOWN 1 N/OF C572 | 20241123 | 2022 | 20241124 | 1615 | s1992585 | 1193 | Distribution Circuit | 3rd Party | Vehicle | 1907 | 210169 | 37.3158 | -120.4786 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 24-0139626 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | Yes | 1992585 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2101 | 252802101 | OCB | 2101/2 | 20241124 | 45 | 20241124 | 1744 | 2636782 | 1019 | Distribution Circuit | 3rd Party | Vehicle | 5159 | 334941 | 37.2731 | -120.4872 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0139631 | OH | Sus | 35599981 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992592 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 554053 | 20241124 | 701 | 20241124 | 828 | 2636843 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 2871 | 37.3387 | -120.8784 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0139664 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992624 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | TRANSFORMER | 320197923350 | 20241124 | 735 | 20241124 | 1409 | 2636855 | 394 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 394 | 37.1421 | -120.4329 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139677 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992632 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | MTR#1004735911 | 20241124 | 834 | 20241124 | 1133 | 2636938 | 179 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 358 | 37.998 | -120.2575 | No | Partly Cloudy-Drizzle;32-90 F | Transformer | Arcing | 24-0139689 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992639 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 823548 | 20241124 | 1259 | 20241124 | 2155 | 2637011 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 11256 | 38.0441 | -120.248 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 24-0139718 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1992656 | 0 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | FIGARDEN-2112 | 254552112 | FUSE | 23525 | 20241124 | 1756 | 20241124 | 2038 | 2637242 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 486 | 36.8602 | -119.8375 | No | Partly Cloudy;32-90 F |  |  | 24-0139789 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992694 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1105 | 252421105 | FUSE | 6613 | 20241125 | 812 | 20241125 | 1438 | 2637386 | 386 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 5 | 1930 | 36.9382 | -120.3805 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Burned/flashed | 24-0139991 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992775 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1116 | 252761116 | FUSE | 5848 | 20241125 | 814 | 20241125 | 920 | 2637391 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 924 | 36.9239 | -120.0332 | No | Overcast-Drizzle;32-90 F |  |  | 24-0139887 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992739 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320585243589 | 20241125 | 853 | 20241125 | 1710 | 2637419 | 497 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1491 | 37.7002 | -120.2969 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139940 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992757 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320721156238 | 20241125 | 1030 | 20241125 | 1116 | 2637562 | 46 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 4 | 184 | 38.0443 | -120.2502 | No | Overcast-Fog-Rain;32-90 F | Fuse | Normal | 24-0139982 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992771 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1104 | 252261104 | FUSE | 8697 | 20241125 | 1033 | 20241125 | 1500 | 2637561 | 267 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 144 | 10158 | 37.3779 | -120.7236 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0139959 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992762 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 20241125 | 1244 | 20241125 | 1629 | 2637747 | 225 | Distribution Circuit | 3rd Party | Vehicle | 231 | 48803 | 37.7156 | -120.1933 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0140012 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1992786 | 0 | EPSS Ckt | N | 2024 | A- B- C
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | RECLOSER | 59800 | 20241126 | 126 | 20241126 | 816 | 2638172 | 410 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3544 | 37.1579 | -120.2714 | No | Overcast-Fog-Rain;32-90 F | Insulator | Burned/flashed | 24-0140221 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992873 | 0 | Non-EPSS | N | 2024 | AC
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | FUSE | 2063 | 20241126 | 153 | 20241126 | 628 | 2638180 | 275 | Distribution Circuit | Animal | Bird found | 3 | 825 | 37.0982 | -120.1312 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0140238 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992888 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10623 | 20241126 | 257 | 20241126 | 1106 | 2638195 | 489 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 19947 | 37.2255 | -119.716 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0140233 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992887 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | PANOCHE-1102 | 253671102 | OCB | 1102/2 | 20241126 | 409 | 20241126 | 733 | 2638211 | 204 | Distribution Circuit | Animal | Other | 113 | 23052 | 36.6512 | -120.5803 | No | Overcast-Fog-Rain;32-90 F | Recloser | Failed/Faulted | 24-0140227 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | No | No | 1992880 | 0 | Non-EPSS | N | 2024 | ABC- TOC
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 63495 | 20241126 | 513 | 20241126 | 701 | 2638227 | 108 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 21 | 2268 | 38.0386 | -120.3817 | No | Overcast-Fog;32-90 F |  |  | 24-0140244 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992891 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L1473 | 20241126 | 730 | 20241126 | 1334 | 2638313 | 364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 4368 | 38.0422 | -120.3768 | No | Overcast-Fog;32-90 F | Insulator | Broken | 24-0140292 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992914 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 10368 | 20241126 | 1309 | 20241126 | 1317 | 2638728 | 8 | Distribution Circuit | Equipment Failure/Involved | Overhead | 139 | 1112 | 37.217 | -119.4867 | No | Overcast-Fog-Drizzle;32-90 F | Connector or Splice (OH) | Broken | 24-0140523 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1993027 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BONITA-1103 | 255391103 | TRANSFORMER | 320858017032 | 20241126 | 1402 | 20241126 | 1516 | 2638771 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 74 | 36.9677 | -120.2075 | No | Overcast;32-90 F | Fuse | Broken | 24-0140605 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993049 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 11539 | 20241127 | 807 | 20241127 | 924 | 2639163 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 308 | 37.3642 | -120.6035 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0140854 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993142 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L2183 | 20241127 | 1151 | 20241127 | 1320 | 2639391 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 89 | 37.9908 | -120.4797 | No | Clear;32-90 F |  |  | 24-0141032 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993183 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | TRIP-SAVER | 47747 | 20241127 | 2011 | 20241128 | 1125 | 2639692 | 914 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 24506 | 37.7133 | -120.6189 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141172 | OH | Sus | 31718837 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993219 | 1 | EPSS Ckt | N | 2024 | N/A
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | JUMPER | DDE JMPRS 1 E & 1 S OF CGC# 319004420677 | 20241128 | 812 | 20241128 | 1037 | 2639786 | 145 | Distribution Circuit | 3rd Party | Vehicle | 11 | 1595 | 37.0668 | -120.8418 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0141190 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1993233 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | NEWHALL-1109 | 254461109 | JUMPER | BURNT OJ 1/E/OF CGC# 320582513575 | 20241128 | 1254 | 20241128 | 1501 | 2639871 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 915 | 36.8729 | -120.3008 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0141216 | OH | Sus | 46401454 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1993261 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 99295 | 20241128 | 2043 | 20241128 | 2227 | 2639979 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2704 | 37.5445 | -120.4624 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0141236 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993283 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321210618922 | 20241129 | 11 | 20241129 | 752 | 2639999 | 461 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 922 | 37.0189 | -120.0868 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141254 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993299 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | SWITCH | 22247 | 20241129 | 1652 | 20241129 | 2145 | 2640284 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 586 | 36.7346 | -120.3238 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0141310 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1993341 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | JUMPER | 1 WIRE DOWN A PHASE | 20241129 | 1924 | 20241130 | 8 | 2640368 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1248 | 36.9054 | -120.7464 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0141327 | OH | Sus | 46402403 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | Yes | Yes | 1993355 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7734 | 20241130 | 739 | 20241130 | 1043 | 2640483 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 552 | 37.2639 | -120.7428 | No | Clear;32-90 F |  |  | 24-0141389 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993406 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | JUMPER | OJ 1 POLE S/OF 46379 | 20241130 | 827 | 20241130 | 1010 | 2640490 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 206 | 37.1016 | -120.2745 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Deteriorated | 24-0141363 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1993381 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | FUSE | 3857 | 20241130 | 1120 | 20241130 | 1233 | 2640653 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 1558 | 36.968 | -120.6085 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0141405 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993416 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WOODWARD-2101 | 255292101 | FUSE | 6738 | 20241130 | 1332 | 20241130 | 1440 | 2640732 | 68 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 136 | 36.9246 | -119.7684 | No | Clear;32-90 F |  |  | 24-0141422 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1993423 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | JUMPER | BURNED OPENED JUMPER CENTER PHASE | 20241130 | 1447 | 20241130 | 1953 | 2640813 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 146 | 19878 | 37.5436 | -120.4994 | No | Clear;32-90 F | Jumper | Burned Open | 24-0141431 | OH | Sus | 31718940 | CENTRAL VALLEY | NOV | Open Circuit | 0 | No | No | No | 1993428 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BORDEN-1102 | 255121102 | FUSE | 13187 | 20241130 | 2156 | 20241130 | 2250 | 2640911 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1080 | 36.9526 | -120.0284 | No | Overcast-Fog;32-90 F |  |  | 24-0141466 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993444 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320396552970 | 20241201 | 1019 | 20241201 | 1304 | 2641009 | 165 | Transformer only | 3rd Party | Vehicle | 1 | 165 | 37.9548 | -120.3637 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0141510 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1993478 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 3332 | 20241201 | 1638 | 20241201 | 1839 | 2641201 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 565 | 37.1434 | -120.6018 | No | Partly Cloudy;32-90 F |  |  | 24-0141562 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1993509 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CASSIDY-2108 | 254272108 | FUSE | 23123 | 20241202 | 828 | 20241202 | 937 | 2641446 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 69 | 36.8876 | -119.8574 | No | Clear;32-90 F |  |  | 24-0141683 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1993699 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | TRANSFORMER | 320822626092 | 20241202 | 904 | 20241202 | 1402 | 2641535 | 298 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 596 | 37.2159 | -120.2163 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141702 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1993711 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | JUMPER | OJ 1 POLE E/OF CGC#320240111821 | 20241202 | 926 | 20241202 | 1548 | 2641610 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 382 | 36.8248 | -120.4178 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken | 24-0141673 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1993682 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | FUSE | 24839 | 20241202 | 1308 | 20241202 | 1700 | 2641960 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1160 | 37.1271 | -120.3472 | No | Clear;32-90 F | Insulator | Broken | 24-0141777 | OH | Sus | 46402898 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1993757 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 3986 | 20241203 | 222 | 20241203 | 445 | 2642419 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1001 | 37.0979 | -120.6355 | No | Fog;32-90 F |  |  | 24-0141981 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1993840 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | FUSE | 3053 | 20241203 | 634 | 20241203 | 1039 | 2642437 | 245 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 980 | 36.8932 | -120.5998 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0142084 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994051 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 36862 | 20241203 | 702 | 20241203 | 805 | 2642442 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 210 | 37.2938 | -120.777 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0142019 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1993883 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 8817 | 20241203 | 831 | 20241203 | 1102 | 2642800 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 755 | 37.1859 | -120.548 | No | Partly Cloudy;32-90 F |  |  | 24-0142105 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1994066 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | TRANSFORMER | 319029322031 | 20241203 | 939 | 20241203 | 1254 | 2642757 | 195 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 195 | 37.1045 | -120.8338 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0142168 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994095 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | TRANSFORMER | 318984330234 | 20241203 | 1044 | 20241203 | 1119 | 2642773 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 140 | 37.3281 | -120.8504 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0142109 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994068 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BONITA-1102 | 255391102 | FUSE | 2116 | 20241203 | 1241 | 20241203 | 1338 | 2642989 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 285 | 36.9382 | -120.1557 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 24-0142193 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1994107 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 4762 | 20241203 | 1403 | 20241204 | 234 | 2643060 | 751 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 31542 | 37.3839 | -120.6162 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0142219 | OH | Sus | 31719155 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994119 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | FUSE | 25654 | 20241203 | 2247 | 20241204 | 242 | 2643350 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 777 | 36.909 | -120.7827 | No | Clear;32-90 F |  |  | 24-0142348 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994192 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | RECLOSER | 6230 | 20241204 | 1201 | 20241205 | 124 | 2643933 | 803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 12202 | 36.9965 | -120.0021 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0142520 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1994467 | 0 | EPSS Ckt | N | 2024 | BC
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 4665 | 20241204 | 1630 | 20241204 | 1745 | 2644120 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 450 | 37.5447 | -120.0949 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0142625 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1994513 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320693954885 | 20241204 | 1741 | 20241204 | 1903 | 2644213 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 328 | 38.0072 | -120.26 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 24-0142700 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1994530 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | FUSE | 3752 | 20241204 | 1850 | 20241205 | 108 | 2644252 | 378 | Distribution Circuit | 3rd Party | Vehicle | 53 | 20034 | 37.0984 | -120.747 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0142717 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1994534 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WRIGHT-1110 | 254641110 | FUSE | 9723 | 20241205 | 931 | 20241205 | 1300 | 2644632 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 209 | 37.106 | -120.9368 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0142863 | OH | Sus | 46404392 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1994788 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1101 | 252261101 | FUSE | 7734 | 20241206 | 714 | 20241206 | 812 | 2645557 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 174 | 37.2639 | -120.7428 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0143224 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995013 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | TRANSFORMER | 321434661441 | 20241206 | 1304 | 20241206 | 1745 | 2646035 | 281 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1967 | 38.1859 | -120.0017 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143402 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995193 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | TRANSFORMER | 320269426822 | 20241206 | 1315 | 20241206 | 1415 | 2646045 | 60 | Transformer only | 3rd Party | Customer Equipment | 4 | 240 | 37.2372 | -120.4089 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0143405 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995194 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321143116070 | 20241206 | 1435 | 20241206 | 1924 | 2646091 | 289 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 289 | 36.9408 | -120.1103 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143459 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995211 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SHEPHERD-2111 | 252062111 | TRANSFORMER | 322013021505 | 20241206 | 1440 | 20241206 | 1954 | 2646132 | 314 | Transformer only | Vegetation | Tree - fell into line | 1 | 314 | 37.0881 | -119.8097 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0143442 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995207 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320903549334 | 20241206 | 1609 | 20241206 | 2243 | 2646143 | 394 | Transformer only | Animal | Squirrel | 2 | 788 | 37.8543 | -120.188 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0143483 | OH | Sus | 31719421 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995216 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 19887 | 20241207 | 312 | 20241207 | 800 | 2646297 | 277 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1663 | 37.5171 | -121.1954 | No | Clear;32-90 F |  |  | 24-0143540 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995256 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | FUSE | 5484 | 20241207 | 1037 | 20241207 | 1118 | 2646468 | 41 | Distribution Circuit | 3rd Party | Customer Equipment | 4 | 164 | 37.2089 | -119.9792 | No | Clear;32-90 F | Customer Equipment | Normal | 24-0143575 | UG | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1995329 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1111 | 252421111 | FUSE | 6718 | 20241207 | 1218 | 20241207 | 1400 | 2646573 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1938 | 37.0981 | -120.3528 | No | Partly Cloudy;32-90 F |  |  | 24-0143621 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995374 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | RECLOSER | 6010 | 20241207 | 1810 | 20241207 | 1822 | 2646706 | 12 | Distribution Circuit | 3rd Party | Vehicle | 1237 | 14844 | 36.967 | -120.0081 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0143640 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1995392 | 0 | Non-EPSS | N | 2024 | N/A
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | SWITCH | 930777 | 20241207 | 1836 | 20241207 | 2310 | 2646712 | 274 | Distribution Circuit | 3rd Party | Vehicle | 1 | 274 | 36.9666 | -120.0114 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0143640 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1995395 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | RECLOSER | 3400 | 20241207 | 2007 | 20241208 | 1100 | 2646732 | 893 | Distribution Circuit | 3rd Party | Vehicle | 288 | 77166 | 36.9816 | -120.5941 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0143651 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1995401 | 0 | Non-EPSS | N | 2024 | A- B- C
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | 23514 | 20241207 | 2018 | 20241208 | 130 | 2646738 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 6402 | 38.0549 | -120.2648 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0143650 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995400 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1703 | 162981703 | RECLOSER | 768534 | 20241208 | 251 | 20241208 | 421 | 2646769 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 270 | 37.8867 | -120.925 | No | Overcast-Fog;32-90 F |  |  | 24-0143657 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995411 | 0 | EPSS Ckt | N | 2024 | B
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | 318590027810 | 20241208 | 522 | 20241208 | 1325 | 2646780 | 483 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 966 | 37.2627 | -120.9855 | No | Overcast;32-90 F | Fuse | Arcing | 24-0143675 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995425 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 5027 | 20241208 | 620 | 20241208 | 1631 | 2646786 | 609 | Distribution Circuit | 3rd Party | Vehicle | 25 | 15225 | 37.726 | -120.7977 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0143668 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1995421 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20241209 | 803 | 20241209 | 944 | 2647360 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 3030 | 37.9913 | -120.4128 | No | Clear;32-90 F |  |  | 24-0143860 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995702 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1106 | 252261106 | TRANSFORMER | T7525 | 20241209 | 919 | 20241209 | 1113 | 2647553 | 114 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 114 | 37.3886 | -120.7559 | No | Partly Cloudy;32-90 F |  |  | 24-0143906 | UG | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1995768 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320671054501 | 20241209 | 1040 | 20241209 | 1735 | 2647684 | 415 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 415 | 37.9966 | -120.2683 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143922 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1995773 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1102 | 253471102 | FUSE | 21765 | 20241209 | 1416 | 20241209 | 1539 | 2647886 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 332 | 36.8674 | -120.4553 | No | Clear;32-90 F |  |  | 24-0143977 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995824 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | FUSE | 24519 | 20241209 | 1738 | 20241209 | 1850 | 2648014 | 72 | Distribution Circuit | Animal | Bird found | 298 | 21456 | 36.9554 | -120.0744 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0144028 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1995851 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 27277 | 20241210 | 822 | 20241210 | 1355 | 2648436 | 333 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 666 | 37.0475 | -120.6097 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0144207 | OH | Sus | 46414910 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1996202 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | RECLOSER | 68650 | 20241210 | 1431 | 20241210 | 1812 | 2649023 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 3978 | 37.1274 | -120.3363 | No | Partly Cloudy;32-90 F |  |  | 24-0144281 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1996251 | 0 | Non-EPSS | N | 2024 | A B C GRD
YOSEMITE | YOSEMITE | CANAL-1106 | 252091106 | FUSE | 14532 | 20241210 | 1438 | 20241210 | 1553 | 2649025 | 75 | Distribution Circuit | 3rd Party | Vehicle | 134 | 10050 | 37.0527 | -120.8266 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Normal | 24-0144248 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1996230 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 6506 | 20241210 | 1602 | 20241210 | 1952 | 2649104 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 3680 | 36.9531 | -120.0941 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0144297 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1996260 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | FUSE | 6748 | 20241210 | 2017 | 20241210 | 2207 | 2649226 | 110 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 26 | 2860 | 36.9084 | -120.1375 | No | Clear;32-90 F |  |  | 24-0144309 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1996275 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1118 | 252761118 | FUSE | 6506 | 20241211 | 23 | 20241211 | 243 | 2649249 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2240 | 36.9531 | -120.0941 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0144317 | OH | Sus | 35604753 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1996289 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | JUMPER | CPH BURNED OJ 3P SS/OF C2298 | 20241211 | 647 | 20241211 | 1657 | 2649300 | 610 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 610 | 38.0592 | -120.4108 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 24-0144353 | OH | Sus | 46415094 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1996403 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | T97597 | 20241211 | 900 | 20241211 | 1020 | 2649473 | 80 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 80 | 37.284 | -120.5964 | No | Partly Cloudy;32-90 F |  |  | 24-0144381 | UG | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1996526 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20241211 | 1008 | 20241211 | 1108 | 2649637 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 1800 | 37.9913 | -120.4128 | No | Clear;32-90 F |  |  | 24-0144394 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1996541 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | S221 | 20241211 | 1015 | 20241211 | 1226 | 2649675 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 117 | 15327 | 37.7576 | -121.0327 | No | Clear;32-90 F |  |  | 24-0144405 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1996550 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | TRANSFORMER | 320168610951 | 20241211 | 1815 | 20241211 | 2016 | 2649914 | 121 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 363 | 36.7998 | -120.4433 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0144490 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1996630 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 13344 | 20241212 | 425 | 20241212 | 636 | 2650415 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 393 | 37.4424 | -120.6304 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0144545 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1996689 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | FUSE | 179439 | 20241212 | 530 | 20241212 | 1204 | 2650427 | 394 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 5 | 1360 | 37.1275 | -120.329 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Broken | 24-0144539 | OH | Sus | 31719861 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1996681 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | FUSE | 900235 | 20241212 | 801 | 20241212 | 1050 | 2650507 | 169 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 9397 | 36.966 | -120.0671 | No | Overcast-Fog-Rain;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0144578 | OH | Sus | 46416076 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1996755 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 38882 | 20241212 | 828 | 20241212 | 941 | 2650557 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 313 | 22849 | 37.7169 | -120.3056 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Together | 24-0144559 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1996737 | 0 | EPSS Ckt | N | 2024 | A-B
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | FUSE | 5952 | 20241212 | 1408 | 20241212 | 1420 | 2651047 | 12 | Distribution Circuit | Company Initiated | Return Circuit Normal | 9 | 108 | 36.9663 | -120.0666 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 24-0144578 | OH | Sus | 46416076 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1996916 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2110 | 253882110 | SWITCH | 1877 | 20241213 | 1026 | 20241213 | 1034 | 2651732 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 39 | 312 | 37.322 | -120.4566 | No | Overcast;32-90 F | Fuse | Normal | 24-0144777 | UG | Sus | 31719792 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1997124 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | TRANSFORMER | 321122216494 | 20241213 | 1123 | 20241213 | 1422 | 2651683 | 179 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 716 | 36.9529 | -120.1162 | No | Overcast;32-90 F | Secondary | Burned/flashed | 24-0144891 | OH | Sus | 46417769 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1997192 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 3789 | 20241213 | 1334 | 20241213 | 1503 | 2651970 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 2403 | 37.0254 | -120.6368 | No | Overcast;32-90 F |  |  | 24-0144895 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997195 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4601 | 20241213 | 2118 | 20241214 | 109 | 2652317 | 231 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 12 | 2692 | 37.757 | -120.1145 | No | Overcast-Drizzle;32-90 F |  |  | 24-0145028 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1997333 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CANAL-1105 | 252091105 | FUSE | 3594 | 20241213 | 2300 | 20241214 | 429 | 2652445 | 322 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 1819 | 37.0547 | -120.867 | No | Overcast;32-90 F | Transformer (UG) | Broken | 24-0144984 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1997289 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 20241214 | 308 | 20241214 | 548 | 2652908 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 5920 | 37.9718 | -120.2261 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0145085 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997388 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | RECLOSER | 3500 | 20241214 | 323 | 20241214 | 840 | 2652914 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 288 | 29782 | 37.0532 | -120.5543 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145072 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | Yes | No | 1997376 | 0 | Non-EPSS | N | 2024 | A-C & GRD
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241214 | 324 | 20241214 | 332 | 2652917 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 368 | 2944 | 37.9754 | -120.4464 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0145058 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997363 | 0 | EPSS Ckt | N | 2024 | A & C
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 38882 | 20241214 | 454 | 20241214 | 505 | 2652967 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 313 | 3443 | 37.7169 | -120.3056 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145079 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997383 | 0 | EPSS Ckt | N | 2024 | A & B
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241214 | 515 | 20241214 | 528 | 2653023 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 368 | 4784 | 37.9754 | -120.4464 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0145082 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997385 | 0 | EPSS Ckt | N | 2024 | A & C
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 38882 | 20241214 | 521 | 20241214 | 909 | 2653029 | 0 | Distribution Circuit | Equipment Failure/Involved | Overhead | 313 | 38864 | 37.7169 | -120.3056 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0145088 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997393 | 0 | EPSS Ckt | N | 2024 | A B
YOSEMITE | YOSEMITE | HAMMONDS-1101 | 253401101 | FUSE | 21004 | 20241214 | 557 | 20241214 | 1126 | 2653082 | 329 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 3290 | 36.6918 | -120.6218 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0145603 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997927 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241214 | 630 | 20241214 | 658 | 2653493 | 28 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 368 | 10304 | 37.9754 | -120.4464 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0145129 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997435 | 0 | EPSS Ckt | N | 2024 | NO TGTS
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 20299 | 20241214 | 639 | 20241214 | 1435 | 2653535 | 476 | Distribution Circuit | Vegetation | Tree - branch fell on line | 148 | 70448 | 37.8652 | -120.2186 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145243 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1997553 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 20363 | 20241214 | 645 | 20241214 | 1609 | 2653633 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 17484 | 38.0159 | -120.3105 | Yes | Overcast-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0145300 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | Yes | No | 1997613 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | FUSE | 7656 | 20241214 | 652 | 20241214 | 756 | 2653849 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 384 | 37.3162 | -120.5415 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0145222 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997531 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | OTHER | WIRE DOWN C/O CRESTA & MANZINITA | 20241214 | 653 | 20241214 | 1636 | 2653764 | 0 | Distribution Circuit | Vegetation | Tree - branch fell on line | 610 | 119910 | 38.0492 | -120.2341 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145263 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | Yes | No | 1997573 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | RECLOSER | 3160 | 20241214 | 659 | 20241214 | 1718 | 2653884 | 619 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 83565 | 36.7225 | -120.3811 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0145155 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1997461 | 0 | Non-EPSS | N | 2024 | C GRD
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | RECLOSER | 291534 | 20241214 | 729 | 20241215 | 1306 | 2654401 | 1774 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3116 | 534947 | 37.9881 | -120.3882 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145188 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | Yes | No | 1997495 | 0 | EPSS Ckt | N | 2024 | A B C SGF TOC
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20241214 | 730 | 20241214 | 2300 | 2654408 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 1312 | 883703 | 38.0063 | -120.3474 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145190 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1997497 | 0 | EPSS Ckt | N | 2024 | A GRD
YOSEMITE | STANISLAUS | CURTIS-1701 | 163351701 | FUSE | L1719 | 20241214 | 738 | 20241214 | 1640 | 2654531 | 542 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 52032 | 37.9765 | -120.3659 | Yes | Overcast-Rain-Strong Winds;32-90 F | Fuse | Burned Open | 24-0145867 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998201 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | L2095 | 20241214 | 738 | 20241215 | 1550 | 2654525 | 1932 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 24240 | 37.9566 | -120.3044 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145958 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1998290 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 767890 | 20241214 | 739 | 20241214 | 2219 | 2654596 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 1241 | 260047 | 38.0568 | -120.203 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145203 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1997511 | 0 | EPSS Ckt | N | 2024 | SGF
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | S2281 | 20241214 | 748 | 20241215 | 1529 | 2659245 | 1897 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 55302 | 38.0629 | -120.1863 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0145734 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1998065 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 10600 | 20241214 | 749 | 20241215 | 26 | 2654641 | 997 | Distribution Circuit | Vegetation | Tree - bark fell into line | 805 | 802585 | 38.066 | -120.1888 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145206 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | Yes | No | 1997514 | 0 | EPSS Ckt | N | 2024 | ABC GRD
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | 1887 | 20241214 | 755 | 20241214 | 1044 | 2654686 | 169 | Distribution Circuit | Vegetation | Tree - fell into line | 331 | 55938 | 38.0604 | -120.2692 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145402 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1997724 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 103437 | 20241214 | 757 | 20241215 | 1105 | 2654971 | 1628 | Distribution Circuit | Vegetation | Tree - fell into line | 264 | 65897 | 38.0127 | -120.3073 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0145577 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997900 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20241214 | 758 | 20241214 | 1208 | 2654688 | 250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 368 | 56426 | 37.9754 | -120.4464 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0145221 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997530 | 0 | EPSS Ckt | N | 2024 | AC
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | S1599 | 20241214 | 759 | 20241214 | 1509 | 2654768 | 430 | Distribution Circuit | 3rd Party | Other | 93 | 39990 | 37.9256 | -120.3412 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145790 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998122 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | JUMPER | 38800 | 20241214 | 800 | 20241214 | 947 | 2654729 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 4922 | 37.794 | -120.9325 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0145360 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 1997675 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1704 | 162981704 | FUSE | S1839 | 20241214 | 801 | 20241214 | 1040 | 2654800 | 159 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 2544 | 37.8494 | -120.9982 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145571 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997893 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 23334 | 20241214 | 802 | 20241214 | 1601 | 2654736 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 232 | 108712 | 37.9893 | -120.3329 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145582 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1997905 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 796199 | 20241214 | 802 | 20241214 | 1819 | 2658937 | 617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 51211 | 37.9997 | -120.3128 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145671 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1997997 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 2015 | 20241214 | 805 | 20241215 | 1457 | 2655053 | 1852 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 24076 | 37.8248 | -120.1543 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145644 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1997969 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1702 | 163711702 | RECLOSER | 6318 | 20241214 | 806 | 20241214 | 849 | 2654786 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 415 | 17845 | 37.7777 | -120.8494 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0145236 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997546 | 0 | Non-EPSS | N | 2024 | BC
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 20241214 | 807 | 20241214 | 1340 | 2654871 | 333 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 12321 | 37.9718 | -120.2261 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145751 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998083 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 6064 | 20241214 | 808 | 20241215 | 1437 | 2654780 | 1829 | Distribution Circuit | Equipment Failure/Involved | Overhead | 387 | 59169 | 37.9603 | -120.3771 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145239 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1997549 | 0 | EPSS Ckt | N | 2024 | ABC TIME OC
YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | L1261 | 20241214 | 808 | 20241215 | 1318 | 2654790 | 1750 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 213500 | 38.0345 | -120.2732 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145930 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1998261 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 20241214 | 810 | 20241214 | 825 | 2654882 | 15 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 231 | 3465 | 37.7156 | -120.1933 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145250 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997560 | 0 | EPSS Ckt | N | 2024 | A&B TIME OC
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | FUSE | 8958 | 20241214 | 812 | 20241214 | 1127 | 2654998 | 0 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1365 | 37.6392 | -120.3603 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145586 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997909 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 13430 | 20241214 | 817 | 20241215 | 1820 | 2654974 | 2041 | Distribution Circuit | Equipment Failure/Involved | Overhead | 129 | 233572 | 37.7499 | -120.1362 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0145256 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1997566 | 0 | EPSS Ckt | N | 2024 | SGF
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23223 | 20241214 | 824 | 20241215 | 959 | 2655063 | 1535 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 121265 | 37.9785 | -120.3151 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0146038 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998377 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | RECLOSER | 787277 | 20241214 | 825 | 20241214 | 1315 | 2655154 | 290 | Distribution Circuit | 3rd Party | Customer Equipment | 118 | 34220 | 37.9599 | -120.4518 | Yes | Overcast-Rain-Strong Winds;32-90 F | Customer Equipment | Broken | 24-0145640 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997965 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20241214 | 831 | 20241214 | 2227 | 2655404 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 56808 | 37.8183 | -120.0958 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145295 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1997608 | 0 | EPSS Ckt | N | 2024 | B C SGF
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320482052730 | 20241214 | 836 | 20241215 | 1741 | 2659707 | 1985 | Transformer only | Vegetation | Tree - bark fell into line | 2 | 3970 | 37.9494 | -120.3321 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0145809 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1998142 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 293732 | 20241214 | 837 | 20241215 | 1845 | 2655481 | 2048 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 701226 | 37.698 | -120.116 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145320 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1997633 | 0 | EPSS Ckt | N | 2024 | A TIME OC
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 19016 | 20241214 | 838 | 20241214 | 2217 | s1998456 | 0 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 819 | 0 | 0 | Yes | Clear;32-90 F |  |  | 24-0146111 |  | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998456 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 310816 | 20241214 | 900 | 20241215 | 1545 | 2656125 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 342613 | 37.5335 | -119.8351 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145341 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1997656 | 0 | EPSS Ckt | N | 2024 | B C
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10219 | 20241214 | 902 | 20241215 | 1822 | 2656036 | 2000 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12000 | 37.4816 | -119.7777 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145920 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1998252 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10218 | 20241214 | 907 | 20241215 | 1205 | 2656249 | 1618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 14562 | 37.4752 | -119.7417 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146198 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1998548 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 56325 | 20241214 | 910 | 20241214 | 1502 | 2656832 | 352 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 13728 | 37.4901 | -119.7903 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145852 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998187 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1711 | 163191711 | FUSE | 21119 | 20241214 | 916 | 20241214 | 1046 | 2657355 | 90 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 810 | 37.7669 | -120.8817 | Yes | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145474 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997797 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | FUSE | 23723 | 20241214 | 939 | 20241214 | 1439 | 2656613 | 300 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2001 | 37.2696 | -121.0491 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145833 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998166 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 9558 | 20241214 | 945 | 20241214 | 1301 | 2657062 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 915 | 37.179 | -120.7144 | Yes | Overcast;32-90 F |  |  | 24-0145663 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1997988 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL NIDO-1104 | 252451104 | FUSE | 9559 | 20241214 | 945 | 20241214 | 1502 | 2656820 | 317 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3487 | 37.1894 | -120.7084 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0145738 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998069 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1101 | 163111101 | TRANSFORMER | 318559227682 | 20241214 | 948 | 20241214 | 1407 | 2656598 | 259 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2590 | 37.2591 | -120.996 | Yes | Overcast;32-90 F | Connector or Splice (OH) | Broken | 24-0145782 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998113 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | SWITCH | 4349 | 20241214 | 950 | 20241214 | 1013 | 2655212 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 207 | 4761 | 37.6471 | -120.3297 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Arcing | 24-0145398 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1997720 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | RECLOSER | 10190 | 20241214 | 1003 | 20241215 | 1905 | 2657081 | 1982 | Distribution Circuit | Vegetation | Tree - fell into line | 725 | 232773 | 37.4145 | -119.6272 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0145431 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1997753 | 0 | EPSS Ckt | N | 2024 | SGF
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | RECLOSER | 90260 | 20241214 | 1021 | 20241214 | 1408 | 2657412 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 667 | 151409 | 37.2539 | -121.001 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0145777 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998110 | 0 | EPSS Ckt | N | 2024 | B C
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320244356037 | 20241214 | 1031 | 20241214 | 1831 | 2660305 | 480 | Transformer only | Vegetation | Tree - fell into line | 3 | 1440 | 38.0392 | -120.4158 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0145978 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998317 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 23255 | 20241214 | 1037 | 20241215 | 1557 | 2657713 | 1760 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5280 | 38.0105 | -120.3053 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145637 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1997962 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7344 | 20241214 | 1042 | 20241214 | 1421 | 2657814 | 219 | Distribution Circuit | Vegetation | Tree - branch fell on line | 54 | 11826 | 37.3593 | -120.8326 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0145602 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997926 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1102 | 163111102 | FUSE | 3285 | 20241214 | 1104 | 20241215 | 1250 | 2658041 | 0 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 7046 | 37.1536 | -121.0791 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145916 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998247 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1106 | 255371106 | RECLOSER | 3650 | 20241214 | 1122 | 20241214 | 2140 | 2658265 | 618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 51649 | 36.926 | -120.8187 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145596 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1997920 | 0 | EPSS Ckt | N | 2024 | AB TIME
YOSEMITE | YOSEMITE | MERCED-1116 | 252801116 | FUSE | 5527 | 20241214 | 1145 | 20241214 | 1559 | 2658513 | 254 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 9906 | 37.2518 | -120.4138 | Yes | Overcast;32-90 F |  |  | 24-0145909 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998240 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1104 | 255361104 | RECLOSER | 5050 | 20241214 | 1158 | 20241214 | 1457 | 2658643 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 4296 | 37.1589 | -120.1712 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145655 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997979 | 0 | EPSS Ckt | N | 2024 | A&B
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 2333 | 20241214 | 1213 | 20241215 | 1352 | 2660329 | 1539 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 29241 | 38.0412 | -120.3199 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145990 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | Yes | No | 1998330 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1715 | 163191715 | FUSE | S255 | 20241214 | 1225 | 20241214 | 2109 | 2658857 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 145 | 34370 | 37.7699 | -120.9412 | Yes | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0145732 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998062 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | FIREBAUGH-1101 | 253471101 | FUSE | 3934 | 20241214 | 1228 | 20241214 | 1608 | 2659095 | 220 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 293 | 36.778 | -120.441 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0145907 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998238 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320931546268 | 20241214 | 1242 | 20241215 | 1458 | 2659640 | 1576 | Transformer only | Vegetation | Tree - fell into line | 2 | 3152 | 37.7731 | -120.1784 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Broken | 24-0145783 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998114 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | TRANSFORMER | 320302954361 | 20241214 | 1311 | 20241215 | 1821 | 2659202 | 1750 | Transformer only | Environmental/External | Ice or snow | 1 | 1750 | 37.9928 | -120.3955 | Yes | Strong Winds-Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0145994 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998335 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 26964 | 20241214 | 1337 | 20241215 | 1240 | 2659518 | 1383 | Distribution Circuit | Environmental/External | Lightning | 10 | 7880 | 37.8523 | -120.1886 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0145942 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998272 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320928349278 | 20241214 | 1337 | 20241215 | 1356 | 2659665 | 1459 | Transformer only | Environmental/External | Ice or snow | 2 | 2918 | 37.8528 | -120.1794 | Yes | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0146019 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998358 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320904049261 | 20241214 | 1341 | 20241215 | 1200 | 2659458 | 1339 | Transformer only | Environmental/External | Lightning | 5 | 6695 | 37.8523 | -120.1878 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0145984 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998324 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 1945 | 20241214 | 1342 | 20241214 | 1540 | 2659465 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 4602 | 37.8518 | -120.1647 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0145876 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998210 | 0 | EPSS Ckt | N | 2024 | #3 HAD TARGET
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 20241214 | 1406 | 20241215 | 1515 | 2658466 | 1509 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 34969 | 37.7156 | -120.1933 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145784 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | Yes | Yes | 1998115 | 0 | EPSS Ckt | N | 2024 | NA
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 25533 | 20241214 | 1438 | 20241214 | 1634 | 2659735 | 116 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 4 | 464 | 37.1171 | -119.982 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0145934 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998264 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4629 | 20241214 | 1535 | 20241215 | 1418 | 2659965 | 1363 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 79054 | 37.7103 | -120.111 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0146304 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1998675 | 0 | EPSS Ckt | N | 2024 | NA
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | SWITCH | 176798 | 20241214 | 1536 | 20241215 | 1620 | 2656853 | 1484 | Distribution Circuit | Vegetation | Tree - fell into line | 249 | 73542 | 38.0617 | -120.1973 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145885 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | Yes | No | 1998219 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4609 | 20241214 | 1539 | 20241215 | 1431 | 2661706 | 1372 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 71344 | 37.7119 | -120.0982 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0146335 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998704 | 0 | EPSS Ckt | N | 2024 | NA
YOSEMITE | YOSEMITE | MERCED-1114 | 252801114 | FUSE | 4587 | 20241214 | 1615 | 20241214 | 1725 | 2660069 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1260 | 37.1927 | -120.4879 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145971 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998309 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321472539107 | 20241214 | 1621 | 20241215 | 1412 | 2660079 | 1311 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1311 | 37.5715 | -119.9926 | Yes | Overcast-Rain;32-90 F |  |  | 24-0146204 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998553 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320900149263 | 20241214 | 1725 | 20241215 | 1141 | 2660282 | 1096 | Transformer only | Environmental/External | Ice or snow | 2 | 2192 | 37.8524 | -120.1892 | Yes | Overcast-Fog-Drizzle;32-90 F | Transformer | Broken | 24-0145991 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998332 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 7322 | 20241214 | 1752 | 20241214 | 1905 | 2660360 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1095 | 37.4779 | -120.5849 | Yes | Partly Cloudy-Fog;32-90 F |  |  | 24-0146034 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998373 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320019828939 | 20241214 | 1842 | 20241214 | 1958 | 2660462 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 456 | 37.2951 | -120.4931 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 24-0146068 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998407 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | TRANSFORMER | 320065129452 | 20241214 | 1935 | 20241214 | 2202 | 2660552 | 147 | Transformer only | Environmental/External | Fire- Forest/Grass | 12 | 1764 | 37.3096 | -120.4775 | Yes | Partly Cloudy-Fog;32-90 F | Service conductor | Broken- wire on ground | 24-0146077 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998420 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | FUSE | 11603 | 20241214 | 2141 | 20241214 | 2323 | 2660671 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 3162 | 37.2874 | -120.2592 | Yes | Partly Cloudy;32-90 F |  |  | 24-0146120 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998466 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 23334 | 20241214 | 2211 | 20241215 | 1556 | 2660707 | 1065 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 237555 | 37.9893 | -120.3329 | Yes | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146172 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1998519 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | L1413 | 20241214 | 2334 | 20241215 | 1000 | 2660775 | 626 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 17528 | 38.0595 | -120.3823 | Yes | Partly Cloudy;32-90 F |  |  | 24-0146202 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998551 | 0 | EPSS Ckt | N | 2024 | A B
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | S1219 | 20241215 | 50 | 20241215 | 959 | 2660804 | 549 | Distribution Circuit | Vegetation | Tree - branch fell on line | 269 | 147572 | 38.058 | -120.1864 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0146200 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998550 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | OCB | 1102/2 | 20241215 | 209 | 20241215 | 338 | 2660813 | 89 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 563 | 50107 | 37.0551 | -120.3169 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0146147 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998496 | 0 | Non-EPSS | N | 2024 | AC
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 321022348363 | 20241215 | 827 | 20241215 | 1607 | 2661087 | 460 | Transformer only | Vegetation | Tree - fell into line | 3 | 1380 | 37.8274 | -120.1484 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0146316 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998687 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | S1219 | 20241215 | 1015 | 20241215 | 1114 | 2661318 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 269 | 15859 | 38.058 | -120.1864 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0146255 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1998630 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | JUMPER | WIRE DOWN AT CGC# 321862739465 | 20241215 | 1645 | 20241215 | 2225 | 2661935 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2105 | 37.5821 | -119.8584 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146437 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | Yes | 1998798 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 20241216 | 14 | 20241216 | 355 | 2662261 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 906 | 120711 | 37.6313 | -120.1536 | No | Clear;32-90 F | Regulator | Failed/Faulted | 24-0146476 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 1998844 | 0 | EPSS Ckt | N | 2024 | A- C- GRD
YOSEMITE | YOSEMITE | CANAL-1103 | 252091103 | RECLOSER | 12120 | 20241216 | 46 | 20241216 | 955 | 2662277 | 362 | Distribution Circuit | 3rd Party | Vehicle | 208 | 44916 | 37.0998 | -120.8406 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0146481 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 1998850 | 0 | Non-EPSS | N | 2024 | A- C- GRD
YOSEMITE | STANISLAUS | NEWMAN-1106 | 162741106 | FUSE | S875 | 20241216 | 712 | 20241216 | 1117 | 2662352 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 10535 | 37.2906 | -120.9777 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146510 | OH | Sus | 46418953 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1998883 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1104 | 253611104 | FUSE | 11539 | 20241216 | 934 | 20241216 | 1030 | 2662672 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 224 | 37.3642 | -120.6035 | No | Partly Cloudy;32-90 F |  |  | 24-0146552 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998937 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L543 | 20241216 | 1011 | 20241216 | 1420 | 2662761 | 249 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 996 | 38.0208 | -120.3201 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146568 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1998954 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | TRANSFORMER | 318938617890 | 20241216 | 1035 | 20241216 | 1041 | 2662688 | 6 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 6 | 36.9909 | -120.8644 | No | Partly Cloudy-Drizzle;32-90 F | Fuse | Failed/Faulted | 24-0146555 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998941 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1708 | 163711708 | FUSE | 20645 | 20241216 | 1230 | 20241216 | 1733 | 2663021 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1818 | 37.7433 | -120.8307 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0146643 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999025 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | TRANSFORMER | T97597 | 20241216 | 1449 | 20241216 | 1923 | 2663284 | 274 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 274 | 37.284 | -120.5964 | No | Overcast-Drizzle;32-90 F |  |  | 24-0146696 | UG | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1999073 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 321323336637 | 20241216 | 1556 | 20241216 | 2234 | 2663390 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1194 | 37.5048 | -120.0433 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146684 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999063 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1102 | 253541102 | RECLOSER | 9930 | 20241216 | 2352 | 20241217 | 234 | 2663750 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 8586 | 37.0548 | -120.7106 | No | Partly Cloudy-Fog;32-90 F | Recloser | Failed/Faulted | 24-0146720 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1999106 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRIP-SAVER | 9811 | 20241217 | 447 | 20241217 | 559 | 2663776 | 72 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 131 | 9432 | 37.8776 | -120.4476 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0146723 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1999110 | 0 | EPSS Ckt | N | 2024 | A B
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322708430195 | 20241217 | 1027 | 20241217 | 1631 | 2664350 | 364 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2548 | 37.3263 | -119.5696 | No | Clear;32-90 F | Secondary | Broken | 24-0146816 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999316 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | NEWMAN-1105 | 162741105 | TRANSFORMER | 318477229708 | 20241217 | 1049 | 20241217 | 1328 | 2664136 | 159 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 477 | 37.3146 | -121.0245 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0146780 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999270 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320754554573 | 20241217 | 1444 | 20241217 | 1613 | 2664383 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 89 | 37.9985 | -120.2391 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0146824 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999323 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MADERA-1114 | 252761114 | TRANSFORMER | 321254516771 | 20241217 | 1840 | 20241217 | 1856 | 2664581 | 16 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 64 | 36.9602 | -120.072 | No | Overcast;32-90 F |  |  | 24-0146870 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1999364 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 1617 | 20241217 | 2052 | 20241218 | 511 | 2664638 | 499 | Distribution Circuit | 3rd Party | Vehicle | 92 | 14048 | 37.3122 | -119.6203 | No | Clear-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146887 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1999388 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | 21973 | 20241218 | 723 | 20241218 | 832 | 2664743 | 69 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 598 | 37.538 | -121.264 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0146923 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999450 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1713 | 163191713 | TRANSFORMER | 318542847275 | 20241218 | 854 | 20241218 | 1008 | 2664849 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 518 | 37.7974 | -121.0054 | No | Overcast-Fog;32-90 F | Transformer (OH) | Leaking | 24-0146926 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999469 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-2109 | 253882109 | TRANSFORMER | 320079429476 | 20241218 | 1225 | 20241218 | 1300 | 2664964 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 140 | 37.3102 | -120.4726 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146973 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999602 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320629652118 | 20241218 | 1406 | 20241218 | 1509 | 2665308 | 63 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 63 | 37.9311 | -120.2828 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0147007 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999650 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | TRANSFORMER | 319991629102 | 20241218 | 2310 | 20241219 | 152 | 2665609 | 162 | Transformer only | 3rd Party | Vehicle | 1 | 162 | 37.2996 | -120.5027 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0147060 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999706 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RACETRACK-1703 | 163761703 | FUSE | L399 | 20241219 | 748 | 20241219 | 1633 | 2665680 | 525 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 13937 | 37.9932 | -120.4098 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0147088 | UG | Sus | 46420988 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999775 | 1 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320710054978 | 20241219 | 1020 | 20241219 | 1045 | 2665847 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 75 | 38.0094 | -120.2542 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0147096 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999807 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1103 | 253611103 | RECLOSER | 75276 | 20241219 | 1328 | 20241219 | 1847 | 2666040 | 319 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 42 | 4481 | 37.3749 | -120.6145 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147127 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1999858 | 0 | Non-EPSS | N | 2024 | B-C
YOSEMITE | YOSEMITE | SANTA NELLA-1104 | 254051104 | TRANSFORMER | T4065 | 20241219 | 1427 | 20241219 | 1556 | 2666098 | 89 | Transformer only | Equipment Failure/Involved | Underground | 4 | 356 | 37.1104 | -121.0145 | No | Clear;32-90 F | Secondary | Broken | 24-0147129 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999862 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 57405 | 20241219 | 1433 | 20241219 | 1524 | 2666106 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 204 | 37.4742 | -119.8744 | No | Clear;32-90 F |  |  | 24-0147138 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999870 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | SANTA RITA-1105 | 253541105 | FUSE | 7007 | 20241219 | 1440 | 20241219 | 1938 | 2666108 | 298 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1192 | 37.0928 | -120.5543 | No | Clear;32-90 F |  |  | 24-0147165 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1999893 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 9943 | 20241219 | 1606 | 20241219 | 1658 | 2666172 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 312 | 37.0277 | -120.895 | No | Clear;32-90 F |  |  | 24-0147151 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999880 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | RECLOSER | 11420 | 20241220 | 445 | 20241220 | 1259 | 2666346 | 494 | Distribution Circuit | 3rd Party | Vehicle | 1467 | 175729 | 37.1105 | -120.2672 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147188 | OH | Sus | 35606757 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1999927 | 0 | Non-EPSS | N | 2024 | A-C GRD
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | TRANSFORMER | 320503023635 | 20241220 | 813 | 20241220 | 1409 | 2666391 | 356 | Transformer only | 3rd Party | Vehicle | 1 | 356 | 37.1489 | -120.328 | No | Partly Cloudy-Fog;32-90 F | Secondary | Broken | 24-0147208 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000031 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | RECLOSER | 237522 | 20241220 | 1045 | 20241220 | 1129 | 2666688 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 1628 | 37.536 | -121.2758 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0147218 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000100 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | EL NIDO-1101 | 252451101 | FUSE | 24824 | 20241220 | 1329 | 20241220 | 1455 | 2666847 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 172 | 37.1035 | -120.4371 | No | Partly Cloudy;32-90 F |  |  | 24-0147247 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000154 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320929949548 | 20241220 | 1408 | 20241220 | 1750 | 2666902 | 222 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 888 | 37.8602 | -120.1793 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0147257 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000167 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 9943 | 20241220 | 1555 | 20241220 | 1817 | 2666986 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1278 | 37.0277 | -120.895 | No | Overcast;32-90 F |  |  | 24-0147260 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000170 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1104 | 254101104 | FUSE | 2236 | 20241220 | 1922 | 20241220 | 2046 | 2667086 | 84 | Distribution Circuit | 3rd Party | Metallic Balloon | 35 | 2940 | 37.0983 | -120.2193 | No | Overcast-Fog;32-90 F | Bushing | Normal | 24-0147267 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000178 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | OCB | 1109/2 | 20241220 | 2229 | 20241220 | 2318 | 2667119 | 49 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1886 | 73564 | 36.9832 | -120.0335 | No | Partly Cloudy-Fog;32-90 F | Customer Equipment | Normal | 24-0147273 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000184 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10557 | 20241221 | 107 | 20241221 | 545 | 2667145 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1390 | 37.2799 | -119.6664 | No | Partly Cloudy;32-90 F |  |  | 24-0147284 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000196 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 2351 | 20241221 | 429 | 20241221 | 630 | 2667172 | 121 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 726 | 37.1949 | -121.0305 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147291 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000205 | 1 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321827132343 | 20241221 | 911 | 20241221 | 1429 | 2667291 | 318 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 318 | 37.3873 | -119.8731 | No | Clear;32-90 F |  |  | 24-0147317 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000269 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 318911944454 | 20241221 | 1232 | 20241221 | 1530 | 2667396 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 178 | 37.7203 | -120.8762 | No | Overcast;32-90 F | Secondary | Broken | 24-0147328 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000284 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | VALLEY HOME-1702 | 162981702 | TRANSFORMER | 318893048340 | 20241221 | 1712 | 20241221 | 1757 | 2667516 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 180 | 37.8268 | -120.8843 | No | Overcast;32-90 F | Metering Equipment | Arcing | 24-0147342 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000299 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORTIGA-1106 | 254311106 | FUSE | 27149 | 20241221 | 1727 | 20241221 | 1855 | 2667537 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 176 | 37.0056 | -120.8554 | No | Overcast;32-90 F |  |  | 24-0147344 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000302 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | GUSTINE-1101 | 163111101 | TRANSFORMER | 318761030262 | 20241222 | 1029 | 20241222 | 1136 | 2667709 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 335 | 37.3281 | -120.9271 | No | Overcast-Fog;32-90 F | Fuse | Failed/Faulted | 24-0147378 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000359 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | JUMPER | OJ @ SAP 101197609 | 20241222 | 1246 | 20241222 | 1643 | 2667768 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 145 | 18057 | 37.536 | -120.4488 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0147384 | OH | Sus | 46432623 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 2000368 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 20419 | 20241222 | 1323 | 20241222 | 2243 | 2667787 | 560 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 8687 | 37.8258 | -120.2347 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0147397 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000381 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 13078 | 20241222 | 1428 | 20241222 | 1547 | 2667822 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 9006 | 36.9962 | -120.078 | No | Clear;32-90 F |  |  | 24-0147405 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000389 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 640291 | 20241223 | 802 | 20241223 | 1007 | 2668049 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2125 | 37.2458 | -121.0766 | No | Partly Cloudy;32-90 F |  |  | 24-0147469 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000503 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1113 | 252421113 | TRANSFORMER | 321009819691 | 20241223 | 901 | 20241223 | 953 | 2668119 | 52 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 52 | 37.0402 | -120.1556 | No | Partly Cloudy;32-90 F |  |  | 24-0147467 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 2000501 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | TRANSFORMER | 320822626092 | 20241223 | 1000 | 20241223 | 1251 | 2668218 | 171 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 342 | 37.2159 | -120.2163 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0147480 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000523 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1106 | 253881106 | OCB | 1106/2 | 20241223 | 1233 | 20241223 | 1718 | 2668360 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3314 | 152243 | 37.3359 | -120.5054 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0147484 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000532 | 0 | Non-EPSS | N | 2024 | B- C
YOSEMITE | YOSEMITE | DOS PALOS-1101 | 254041101 | FUSE | 9725 | 20241223 | 1302 | 20241223 | 2114 | 2668379 | 492 | Distribution Circuit | 3rd Party | Vehicle | 54 | 26568 | 36.9819 | -120.6356 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0147486 | OH | Sus | 35607182 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000535 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1102 | 253611102 | TRANSFORMER | 319592130004 | 20241223 | 1739 | 20241223 | 2200 | 2668488 | 261 | Transformer only | Equipment Failure/Involved | Underground | 1 | 261 | 37.3238 | -120.6416 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0147504 | UG | Sus | 46438503 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000552 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320384049368 | 20241224 | 549 | 20241224 | 1045 | 2668831 | 296 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 296 | 37.8564 | -120.3681 | No | Overcast-Rain;32-90 F | Jumper | Broken | 24-0147580 | OH | Sus | 46438600 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000633 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | TRIP-SAVER | 6906 | 20241224 | 646 | 20241224 | 814 | 2668844 | 88 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 14 | 1232 | 37.0971 | -120.2805 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0147579 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000632 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | WILSON-1103 | 254301103 | SWITCH | 26984 | 20241224 | 850 | 20241224 | 909 | 2669019 | 19 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 19 | 37.345 | -120.2137 | No | Overcast-Rain;32-90 F | Metering Equipment | Broken | 24-0147604 | UG | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000659 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 13078 | 20241224 | 909 | 20241224 | 1324 | 2669009 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 8436 | 36.9962 | -120.078 | No | Overcast-Heavy Rain;32-90 F | Lightning Arrestor | Broken | 24-0147625 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000683 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | COARSEGOLD-2102 | 254432102 | TRANSFORMER | 322671330413 | 20241224 | 1254 | 20241224 | 1859 | 2669258 | 365 | Transformer only | Vegetation | Tree - fell into line | 2 | 730 | 37.3322 | -119.5825 | No | Overcast-Heavy Rain;32-90 F | Secondary | Broken- wire on ground | 24-0147671 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000731 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1108 | 255371108 | FUSE | 85841 | 20241225 | 659 | 20241225 | 850 | 2669545 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 518 | 36.9095 | -120.5451 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147713 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000774 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ORO LOMA-1115 | 255371115 | TRANSFORMER | 319557116778 | 20241225 | 1152 | 20241225 | 1330 | 2669642 | 98 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 490 | 36.9607 | -120.653 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147737 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000797 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1103 | 254101103 | RECLOSER | 59800 | 20241225 | 1203 | 20241225 | 1417 | 2669644 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 1876 | 37.1579 | -120.2714 | No | Partly Cloudy;32-90 F | Insulator | Broken- wire on ground | 24-0147730 | OH | Sus | 46438707 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 2000791 | 0 | Non-EPSS | N | 2024 | A & GROUND
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | FUSE | 945427 | 20241225 | 2232 | 20241226 | 11 | 2669775 | 99 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 7 | 693 | 37.3209 | -120.5687 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0147761 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000821 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LIVINGSTON-1105 | 252261105 | FUSE | 7547 | 20241226 | 159 | 20241226 | 333 | 2669820 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3196 | 37.3347 | -120.8477 | No | Overcast-Fog;32-90 F |  |  | 24-0147769 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000829 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | TRANSFORMER | 320861512840 | 20241226 | 904 | 20241226 | 1447 | 2669951 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 343 | 36.8518 | -120.2061 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147818 | OH | Sus | 31720833 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000916 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | RIVERBANK-1714 | 163191714 | TRANSFORMER | 318808244705 | 20241226 | 1019 | 20241226 | 1127 | 2670010 | 68 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 204 | 37.7269 | -120.913 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0147798 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000882 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | RECLOSER | 68650 | 20241226 | 1309 | 20241226 | 1425 | 2670136 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1368 | 37.1274 | -120.3363 | No | Partly Cloudy;32-90 F |  |  | 24-0147814 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 2000911 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | STANISLAUS | CROWS LANDING-1101 | 163251101 | TRANSFORMER | 318345031212 | 20241226 | 1732 | 20241226 | 2138 | 2670209 | 246 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 492 | 37.3558 | -121.0701 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147835 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000929 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED-2102 | 252802102 | TRANSFORMER | 320002829255 | 20241226 | 1743 | 20241226 | 2030 | 2670320 | 167 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 167 | 37.3043 | -120.499 | No | Overcast;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0147840 | OH | Sus | 31720839 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2000934 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 26884 | 20241226 | 1750 | 20241226 | 2026 | 2670309 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2184 | 37.3311 | -120.6238 | No | Overcast;32-90 F |  |  | 24-0147846 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000940 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | GUSTINE-1102 | 163111102 | FUSE | 447617 | 20241227 | 842 | 20241227 | 1201 | 2670610 | 199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 308 | 25234 | 37.2094 | -121.0139 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0147913 | OH | Sus | 31720985 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2001035 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | MTR#1011042451 | 20241227 | 922 | 20241227 | 1112 | 2670656 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 110 | 36.9669 | -119.9705 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Normal | 24-0147933 | OH | Sus | 46440008 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001059 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | TAR FLAT-0402 | 163240402 | TRANSFORMER | 320338254582 | 20241227 | 1155 | 20241227 | 1351 | 2670808 | 116 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 232 | 37.9994 | -120.3834 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0147938 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2001064 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | DAIRYLAND-1102 | 252421102 | RECLOSER | 68650 | 20241227 | 1208 | 20241227 | 1253 | 2670821 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 810 | 37.1274 | -120.3363 | No | Overcast-Fog;32-90 F |  |  | 24-0147947 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 2001075 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 482838 | 20241227 | 1437 | 20241227 | 1620 | 2670934 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1411 | 120257 | 37.5247 | -120.3293 | No | Partly Cloudy;32-90 F |  |  | 24-0147962 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 2001093 | 0 | EPSS Ckt | N | 2024 | ABC- TOC- IOC
YOSEMITE | YOSEMITE | MADERA-1119 | 252761119 | RECLOSER | 9540 | 20241227 | 1605 | 20241228 | 4 | 2671011 | 479 | Distribution Circuit | 3rd Party | Vehicle | 411 | 29477 | 36.9042 | -120.0559 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0147976 | OH | Sus | 35607666 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 2001107 | 0 | Non-EPSS | N | 2024 | C/GRD
YOSEMITE | YOSEMITE | MENDOTA-1102 | 252311102 | TRANSFORMER | 415945051992 | 20241227 | 1833 | 20241227 | 2230 | 2671054 | 237 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 3318 | 36.7535 | -120.3848 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0147986 | OH | Sus | 46440018 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | No | No | 2001117 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | RECLOSER | 3290 | 20241228 | 56 | 20241228 | 1145 | 2671127 | 649 | Distribution Circuit | 3rd Party | Vehicle | 349 | 92001 | 37.7466 | -120.8398 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148002 | OH | Sus | 31721047 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | Yes | No | 2001133 | 0 | Non-EPSS | N | 2024 | A B C SGF TOC
YOSEMITE | YOSEMITE | COARSEGOLD-2103 | 254432103 | TRANSFORMER | 322121424335 | 20241228 | 908 | 20241228 | 1409 | 2671232 | 301 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 602 | 37.1663 | -119.7712 | No | Partly Cloudy;32-90 F | Service conductor | Broken- wire on ground | 24-0148030 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001167 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | MERCED FALLS-1102 | 252811102 | RECLOSER | 482838 | 20241228 | 1042 | 20241228 | 2012 | 2671287 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1429 | 682490 | 37.5247 | -120.3293 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0148029 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2001166 | 0 | EPSS Ckt | N | 2024 | BC
YOSEMITE | YOSEMITE | CRESSEY-2103 | 254702103 | FUSE | 99295 | 20241228 | 1331 | 20241228 | 1701 | 2671367 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 5460 | 37.5445 | -120.4624 | No | Partly Cloudy;32-90 F |  |  | 24-0148060 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2001201 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1107 | 254611107 | TRANSFORMER | T2054 | 20241228 | 2321 | 20241229 | 705 | 2671558 | 464 | Transformer only | Equipment Failure/Involved | Underground | 26 | 12064 | 36.9671 | -120.0507 | No | Overcast;32-90 F | Secondary | Broken | 24-0148085 | UG | Sus | 46440941 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2001227 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1108 | 254611108 | TRANSFORMER | 321605317066 | 20241229 | 1317 | 20241229 | 1445 | 2671836 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 176 | 36.9666 | -119.9504 | No | Overcast-Drizzle;32-90 F | Fuse | Burned Open | 24-0148137 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001286 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 23555 | 20241229 | 1502 | 20241229 | 1935 | 2671858 | 273 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 4718 | 38.0365 | -120.2255 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0148138 | OH | Sus | 46440928 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2001287 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | TRANSFORMER | 321157418430 | 20241229 | 1824 | 20241229 | 1922 | 2672018 | 58 | Transformer only | 3rd Party | Metallic Balloon | 3 | 174 | 37.0056 | -120.105 | No | Overcast-Fog-Rain;32-90 F | Fuse | Failed/Faulted | 24-0148158 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001308 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | LE GRAND-1106 | 255361106 | FUSE | 68783 | 20241229 | 2126 | 20241230 | 553 | 2672100 | 507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 7068 | 37.1416 | -120.4102 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148170 | OH | Sus | 35607825 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001321 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1106 | 253611106 | JUMPER | BURNED OJ 1P S/OF 24501 | 20241230 | 444 | 20241230 | 1008 | 2672194 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 288 | 46660 | 37.3169 | -120.5777 | No | Fog;32-90 F | Jumper | Broken- wire on ground | 24-0148178 | OH | Sus | 46440917 | CENTRAL VALLEY | DEC | Open Circuit | 0 | No | Yes | No | 2001331 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | CHOWCHILLA-1101 | 254101101 | RECLOSER | 11420 | 20241230 | 653 | 20241230 | 1603 | 2672206 | 550 | Distribution Circuit | 3rd Party | Vehicle | 1467 | 159524 | 37.1105 | -120.2672 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0148183 | OH | Sus | 35607817 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 2001335 | 0 | Non-EPSS | N | 2024 | B&C
YOSEMITE | YOSEMITE | EL PECO-1105 | 253981105 | FUSE | 5742 | 20241230 | 806 | 20241231 | 40 | 2672249 | 994 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 13 | 4382 | 36.8147 | -120.2053 | No | Partly Cloudy-Fog;32-90 F | Insulator | Arcing | 24-0148199 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 2001425 | 0 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320308752841 | 20241230 | 853 | 20241230 | 923 | 2672303 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 30 | 37.951 | -120.3942 | No | Partly Cloudy-Fog;32-90 F | Secondary | Broken | 24-0148190 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 2001368 | 0 | EPSS Ckt | N | 2024
YOSEMITE | YOSEMITE | ATWATER-1108 | 253611108 | FUSE | 4762 | 20241230 | 1039 | 20241230 | 1252 | 2672443 | 133 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 5586 | 37.3839 | -120.6162 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 24-0148188 | UG | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 2001436 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | TRANSFORMER | 321378820352 | 20241230 | 1059 | 20241230 | 1231 | 2672465 | 92 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 276 | 37.0587 | -120.0296 | No | Overcast;32-90 F |  |  | 24-0148216 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 2001454 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20241230 | 1527 | 20241230 | 1655 | 2672666 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 688 | 60544 | 38.1888 | -120.0082 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 24-0148228 | OH | Sus | 46442094 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2001476 | 0 | EPSS Ckt | N | 2024 | NONE
YOSEMITE | YOSEMITE | LE GRAND-1110 | 255361110 | OCB | 1110/2 | 20241230 | 1610 | 20241230 | 2333 | 2672712 | 443 | Distribution Circuit | 3rd Party | Vehicle | 1039 | 131119 | 37.1847 | -120.2736 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148231 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 2001479 | 0 | EPSS Ckt | N | 2024 | A&C
YOSEMITE | YOSEMITE | MADERA-1104 | 252761104 | FUSE | 24519 | 20241230 | 1731 | 20241230 | 1843 | 2672749 | 72 | Distribution Circuit | Animal | Bird found | 298 | 21456 | 36.9554 | -120.0744 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0148241 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2001489 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1104 | 254611104 | FUSE | 6764 | 20241231 | 327 | 20241231 | 1130 | 2672909 | 482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2250 | 37.0101 | -120.147 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0148298 | OH | Sus | 46442336 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001590 | 1 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | EL CAPITAN-1104 | 253881104 | RECLOSER | 9610 | 20241231 | 657 | 20241231 | 1309 | 2672946 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 24442 | 37.3406 | -120.5224 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0148272 | OH | Sus | 35607985 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2001529 | 0 | Non-EPSS | N | 2024 | NONE
YOSEMITE | YOSEMITE | ATWATER-1107 | 253611107 | FUSE | 26884 | 20241231 | 732 | 20241231 | 905 | 2673066 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 868 | 37.3311 | -120.6238 | No | Fog;32-90 F |  |  | 24-0148284 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2001565 | 1 | Non-EPSS | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | RECLOSER | 3290 | 20241231 | 842 | 20241231 | 1459 | 2673001 | 377 | Distribution Circuit | 3rd Party | Vehicle | 1459 | 104287 | 37.7466 | -120.8398 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0148282 | OH | Sus | 35607987 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 2001549 | 0 | Non-EPSS | N | 2024 | ABC
YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320476653348 | 20241231 | 1202 | 20241231 | 1459 | 2673206 | 177 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1416 | 37.9654 | -120.3355 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0148300 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2001592 | 0 | EPSS Ckt | N | 2024
YOSEMITE | STANISLAUS | COTTLE-1707 | 163711707 | FUSE | S277 | 20241231 | 1509 | 20241231 | 1516 | 2673350 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 35 | 245 | 37.6929 | -120.8485 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0148282 | OH | Sus | 35607987 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 2001611 | 0 | Non-EPSS | N | 2024
YOSEMITE | YOSEMITE | STOREY-1109 | 254611109 | FUSE | 5817 | 20241231 | 1752 | 20241231 | 2042 | 2673462 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1700 | 37.0238 | -119.947 | No | Clear;32-90 F |  |  | 24-0148341 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2001638 | 0 | EPSS Ckt | N | 2024

## SO Counts by Basic Cause
ME Day | Yes
Basic Cause | Count of Event #
3rd Party | 281
Animal | 106
Company Initiated | 99
Environmental/External | 472
Equipment Failure/Involved | 4524
Unknown Cause | 3965
Vegetation | 7790
Wildfire Mitigation | 306
Total Result | 17543